## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1650TE | 1650TE (非取樣點) | MTR | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1650NE | #1MTR(1650) |  | NE0 | 1651N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/1MTR | [13 empty] | no rule | B2/P06_A1 | [8 empty] | 山上PS.1651N | 1651N (非取樣點) | MTR | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1650BE | 1650BE (非取樣點) | MTR | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.750TE | 750TE (非取樣點) | MTR | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.750BE | 750BE (非取樣點) | MTR | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1660TE | 1660TE (非取樣點) | MTR | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1660NE | #2MTR(1660) |  | NE0 | 1661N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2MTR | [13 empty] | no rule | B2/P06_A1 | [8 empty] | 山上PS.1661N | 1661N (非取樣點) | MTR | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1660BE | 1660BE (非取樣點) | MTR | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.760TE | 760TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.760BE | 760BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1670TE | 1670TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670NE | #3MTR(1670) |  | NE0 | 1671N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3MTR | [13 empty] | no rule | B2/P06_A1 | [8 empty] | 山上PS.1671N | 1671N (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1670BE | 1670BE (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.770TE | 770TE (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.770BE | 770BE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1730LE | 1730LE (非取樣點) | LINE161 | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1730BE | 1730BE (非取樣點) | LINE161 | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.601E | 601E (非取樣點) | TIE | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.602E | 602E (非取樣點) | TIE | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1950BE | 1950BE (非取樣點) | MTR | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.650LE | 650LE (非取樣點) | LINE69 | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.680LE | 680LE (非取樣點) | LINE69 | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.680BE | 680BE (非取樣點) | LINE69 | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.820BE | 820BE (非取樣點) | SC | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.820CE | 820CE (非取樣點) | SC | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.830BE | 830BE (非取樣點) | SC | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.830CE | 830CE (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P06_A1 | [8 empty] | 山上PS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | E1 | 331E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.331E | 331E (非取樣點) | MTR | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.331 | 331 (非取樣點) | MTR | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.341 | 341 (非取樣點) | MTR | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | E1 | 341E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.341E | 341E (非取樣點) | MTR | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 390 | #3SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.391 | 391 (非取樣點) | OTHER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 390 | #3SSTR(390) |  | E1 | 391E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.391E | 391E (非取樣點) | OTHER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.211E | 211E (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.211 | 211 (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.221E | 221E (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.221 | 221 (非取樣點) | SC | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.231E | 231E (非取樣點) | SC | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.231 | 231 (非取樣點) | SC | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.241E | 241E (非取樣點) | SC | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.241 | 241 (非取樣點) | SC | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aapz | B2/P06_A1 | [8 empty] | 山上PS.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aapz | B2/P06_A1 | [8 empty] | 山上PS.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE1 | (非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/P06_A1 | [8 empty] | 山上PS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE2 | (非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/P06_A1 | [8 empty] | 山上PS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% |  | Card 1 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% |  | Card 1 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | 1510 | MW | 嘉義新營山上紅線 1510瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1510_MW | 嘉義新營紅線 MW | LINE161 | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 1510 | MVAR | 嘉義新營山上紅 線 1510乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1510_MVAR | 嘉義新營紅線 MVAR | LINE161 | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1520 | MW | 嘉義新營山上白線 1520瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1520_MW | 嘉義新營白線 MW | LINE161 | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1520 | MVAR | 嘉義新營山上白線 1520乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1520_MVAR | 嘉義新營白線 MVAR | LINE161 | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1540 | MW | 山上鹽行豐華白線1540 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1540_MW | 鹽行豐華白線 MW | LINE161 | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1540 | MVAR | 山上鹽行豐華白線1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1540_MVAR | 鹽行豐華白線 MVAR | LINE161 | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1570 | MW | 龍崎山上一路 1570 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1570_MW | 龍崎一路 MW | LINE161 | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1570 | MVAR | 龍崎山上一路 1570 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1570_MVAR | 龍崎一路 MVAR | LINE161 | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1580 | MW | 龍崎山上二路 1580 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1580_MW | 龍崎二路 MW | LINE161 | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1580 | MVAR | 龍崎山上二路 1580 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1580_MVAR | 龍崎二路 MVAR | LINE161 | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1610 | MW | 龍崎山上二甲三路 1610 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1610_MW | 龍崎二甲三路 MW | LINE161 | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1610 | MVAR | 龍崎山上二甲三路 1610 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1610_MVAR | 龍崎二甲三路 MVAR | LINE161 | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1620 | MW | 龍崎山上二甲四路 1620 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1620_MW | 龍崎二甲四路 MW | LINE161 | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1620 | MVAR | 龍崎山上二甲四路 1620 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1620_MVAR | 龍崎二甲四路 MVAR | LINE161 | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1630 | MW | 山上仁德線 1630 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1630_MW | 山上仁德線 MW | LINE161 | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1630 | MVAR | 山上仁德線 1630 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1630_MVAR | 山上仁德線 MVAR | LINE161 | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1640 | MW | 山上台南海線 1640 瓦 | MW_-448_448(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1640_MW | 台南海線 MW | LINE161 | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 1640 | MVAR | 山上台南海線 1640 乏 | MVAR_-448_448(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1640_MVAR | 台南海線 MVAR | LINE161 | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1710 | MW | 山上安南豐華紅線1710 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1710_MW | 安南豐華紅線 MW | LINE161 | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 1710 | MVAR | 山上安南豐華紅線1710 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1710_MVAR | 安南豐華紅線 MVAR | LINE161 | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 1720 | MW | 山上新化二路 1720 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1720_MW | 新化二路 MW | LINE161 | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 1720 | MVAR | 山上新化二路 1720 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1720_MVAR | 新化二路 MVAR | LINE161 | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 1730 | MW | 山上新化一路 1730 瓦 | MW_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1730_MW | 新化一路 MW | LINE161 | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 1730 | MVAR | 山上新化一路 1730 乏 | MVAR_-560_560(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1730_MVAR | 新化一路 MVAR | LINE161 | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0026 |  |  | 1-9A |  |  | #1BUS | KV | 161KV #1BUS PT電壓 | kV_-210_210(-2000_2000) | aaa | B2/P06_A1 | [8 empty] | 山上PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0027 |  |  | 1-9B |  |  | #2BUS | KV | 161KV #2BUS PT電壓 | kV_-210_210(-2000_2000) | aab | B2/P06_A1 | [8 empty] | 山上PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 1550 | MW | 豐德山上紅線 1550 瓦 | MW_-1120_1120(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1550_MW | 豐德紅線 MW | LINE161 | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 1550 | MVAR | 豐德山上紅線 1550 乏 | MVAR_-1120_1120(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1550_MVAR | 豐德紅線 MVAR | LINE161 | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 1560 | MW | 豐德山上白線 1560 瓦 | MW_-1120_1120(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1560_MW | 豐德白線 MW | LINE161 | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 1560 | MVAR | 豐德山上白線 1560 乏 | MVAR_-1120_1120(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1560_MVAR | 豐德白線 MVAR | LINE161 | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 750 | MW | #1MTR二次 750 瓦 | MW_-360_360(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#1MTR_MW | #1MTR二次側 MW | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 750 | MVAR | #1MTR二次 750 乏 | MVAR_-240_240(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 760 | MW | #2MTR二次 760 瓦 | MW_-360_360(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#2MTR_MW | #2MTR二次側 MW | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 760 | MVAR | #2MTR二次 760 乏 | MVAR_-240_240(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 770 | MW | #3MTR二次 770 瓦 | MW_-360_360(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#3MTR_MW | #3MTR二次側 MW | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 770 | MVAR | #3MTR二次 770 乏 | MVAR_-240_240(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0040 |  |  | 1-A8 |  |  | #1BUS | KV | 69KV #1BUS PT電壓 | kV_-90_90(-2000_2000) | aaa | B2/P06_A1 | [8 empty] | 山上PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P06 | 山上PS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0041 |  |  | 1-A9 |  |  | #2BUS | KV | 69KV #2BUS PT電壓 | kV_-90_90(-2000_2000) | aab | B2/P06_A1 | [8 empty] | 山上PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 600 | A | 69KV 600 TIE 電流 | A_-2000_2000(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 610 | MW | 山上山頂一路 610 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.610_MW | 山頂一路 MW | LINE69 | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 610 | MVAR | 山上山頂一路 610 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.610_MVAR | 山頂一路 MVAR | LINE69 | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 620 | MW | 山上山頂二路 620 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.620_MW | 山頂二路 MW | LINE69 | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 620 | MVAR | 山上山頂二路 620 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.620_MVAR | 山頂二路 MVAR | LINE69 | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 630 | MW | 山上善化一路 630 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.630_MW | 善化一路 MW | LINE69 | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 630 | MVAR | 山上善化一路 630 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.630_MVAR | 善化一路 MVAR | LINE69 | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 640 | MW | 山上善化二路 640 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.640_MW | 善化二路 MW | LINE69 | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 640 | MVAR | 山上善化二路 640 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.640_MVAR | 善化二路 MVAR | LINE69 | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 650 | MW | 山上善化三路 650 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.650_MW | 善化三路 MW | LINE69 | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 650 | MVAR | 山上善化三路 650 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.650_MVAR | 善化三路 MVAR | LINE69 | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 660 | MW | 山上新市一路 660 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.660_MW | 新市一路 MW | LINE69 | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 660 | MVAR | 山上新市一路 660 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.660_MVAR | 新市一路 MVAR | LINE69 | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 670 | MW | 山上新市三路 670 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.670_MW | 山上新市三路 MW | LINE69 | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 670 | MVAR | 山上新市三路 670 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.670_MVAR | 山上新市三路 MVAR | LINE69 | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% |  | Card 2 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% |  | Card 2 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 1540 | KV | 山上鹽行豐華白線1540 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1540LPD_KV | 鹽行豐華白線(1540) LPD KV | LINE161 | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 680 | MW | 山上歸仁線 680 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.680_MW | 歸仁線 MW | LINE69 | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 680 | MVAR | 山上歸仁線 680 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.680_MVAR | 歸仁線 MVAR | LINE69 | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 1710 | KV | 山上安南豐華紅線1710 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1710LPD_KV | 安南豐華紅線(1710) LPD KV | LINE161 | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 710 | MW | 山上新市二路 710 瓦 | MW_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.710_MW | 新市二路 MW | LINE69 | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 710 | MVAR | 山上新市二路 710 乏 | MVAR_-144_144(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.710_MVAR | 新市二路 MVAR | LINE69 | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0072 |  | 0199 | 1-C8 |  | 2-47 | #2MTR | 升/降 | #2MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_OIL | #2MTR 油溫 | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | #2MTR | ℃ | #2MTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_COIL | #2MTR 線溫 | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 1720 | KV | 山上新化二路1720 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1720LPD_KV | 山上新化二路(1720) LPD KV | LINE161 | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 1730 | KV | 山上新化一路1730 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1730LPD_KV | 山上新化一路(1730) LPD KV | LINE161 | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0078 |  | 0203 | 1-CE |  | 2-4B | #3MTR | 升/降 | #3MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | #3MTR | ℃ | #3MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_OIL | #3MTR 油溫 | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | #3MTR | ℃ | #3MTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_COIL | #3MTR 線溫 | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0081 |  | 0195 | 1-D1 |  | 2-43 | #1MTR | 升/降 | #1MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | #1MTR | ℃ | #1MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_OIL | #1MTR 油溫 | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | #1MTR | ℃ | #1MTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_COIL | #1MTR 線溫 | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 1550 | KV | 豐德山上紅線 1550 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1550LPD_KV | 豐德紅線(1550) LPD KV | LINE161 | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 1560 | KV | 豐德山上白線 1560 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1560LPD_KV | 豐德白線(1560) LPD KV | LINE161 | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 1570 | KV | 龍崎山上一路 1570 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1570LPD_KV | 龍崎一路(1570) LPD KV | LINE161 | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 1580 | KV | 龍崎山上二路 1580 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1580LPD_KV | 龍崎二路(1580) LPD KV | LINE161 | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | Locate Empty | V | DC-P | kV_-150_150(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | Locate Empty | V | DC-N | kV_-150_150(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 1610 | KV | 龍崎山上二甲三路 1610 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1610LPD_KV | 龍崎二甲三路(1610) LPD KV | LINE161 | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 1620 | KV | 龍崎山上二甲四路 1620 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1620LPD_KV | 龍崎二甲四路(1620) LPD KV | LINE161 | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 1510 | KV | 嘉義新營山上紅線 1510 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1510LPD_KV | 嘉義新營紅線(1510) LPD KV | LINE161 | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 1520 | KV | 嘉義新營山上白線 1520 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1520LPD_KV | 嘉義新營白線(1520) LPD KV | LINE161 | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 1630 | KV | 山上仁德線 1630 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1630LPD_KV | 山上仁德線(1630) LPD KV | LINE161 | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 1640 | KV | 台南海線 1640 LPD | kV_-210_210(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1640LPD_KV | 台南海線(1640) LPD KV | LINE161 | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 1500 | A | 161KV 1500 TIE 電流 | A_-2000_2000(-2000_2000) |  | B2/P06_A1 | [8 empty] | 山上PS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P06 | 山上PS |  |  | 1SHR | #1SHR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | #1 SH.R | QT | #1 SH.R 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 山上PS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 1SHR | #1SHR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | #1 SH.R | WT | #1 SH.R 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 山上PS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 6DTR | #6DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #6 DTR |  | #6 DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_OIL | #6DTR 油溫 | MTR | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 6DTR(A) | #6DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #6 DTR |  | #6 DTR(A) 線溫 | COIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_COIL | #6DTR(A) 線溫 | MTR | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 6DTR(B) | #6DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | #6 DTR |  | #6 DTR(B) 線溫 | COIL_-120_120(-2000_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_COIL | #6DTR(B) 線溫 | MTR | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS |  |  | 6DTR(A) | #6DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0102 |  | 0267 | 1-E6 |  | 3-0B | #6 DTR |  | #6 DTR(A) TAP | TAP_-8.5_8.5(0_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_TAP | #6DTR(A) OLTC TAP | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P06 | 山上PS |  |  | 6DTR(B) | #6DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0103 |  | 0269 | 1-E7 |  | 3-0D | #6 DTR |  | #6 DTR(B) TAP | TAP_-8.5_8.5(0_2000) |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_TAP | #6DTR(B) OLTC TAP | MTR | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 330(M1A) |  | 瓦 | MW_-54_54(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_MW | #6DTR二次側(A) MW | MTR | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 330(M1A) |  | 乏 | MVAR_-36_36(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_MVAR | #6DTR二次側(A) MVAR | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 330(M1A) |  | R | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_A1 | #6DTR二次側(A) R相AMP | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 330(M1A) |  | S | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_A2 | #6DTR二次側(A) S相AMP | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 330(M1A) |  | T | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_A3 | #6DTR二次側(A) T相AMP | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 6ABUS | #6ABUS |  | V_R |  | B3,Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0109 |  |  | 1-ED |  |  | PT-6A |  | PT-6A R相電壓 | kV_-9_9(-2000_2000) | aaa | B3/P06_A1 | [8 empty] | 山上PS.11KV#6ABUS_KV | 11KV #6ABUS KV | BUS | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 上11(4E11) |  | 上11(4E11) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上11線KVAR | 11KV上11線 KVAR | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 上11(4E11) |  | 上11(4E11) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上11線A1 | 11KV上11線 R相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 上11(4E11) |  | 上11(4E11) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上11線A2 | 11KV上11線 S相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 上11(4E11) |  | 上11(4E11) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上11線A3 | 11KV上11線 T相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 上11(4E11) |  | 上11(4E11) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上11線A0 | 11KV上11線 N相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 上12(4E12) |  | 上12(4E12) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上12線KVAR | 11KV上12線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 上12(4E12) |  | 上12(4E12) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上12線A1 | 11KV上12線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 上12(4E12) |  | 上12(4E12) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上12線A2 | 11KV上12線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 上12(4E12) |  | 上12(4E12) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上12線A3 | 11KV上12線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 上12(4E12) |  | 上12(4E12) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上12線A0 | 11KV上12線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 上13(4E13) |  | 上13(4E13) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上13線KVAR | 11KV上13線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 上13(4E13) |  | 上13(4E13) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上13線A1 | 11KV上13線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 上13(4E13) |  | 上13(4E13) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上13線A2 | 11KV上13線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 上13(4E13) |  | 上13(4E13) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上13線A3 | 11KV上13線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 上13(4E13) |  | 上13(4E13) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上13線A0 | 11KV上13線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 上14(4E14) |  | 上14(4E14) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上14線KVAR | 11KV上14線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 上14(4E14) |  | 上14(4E14) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上14線A1 | 11KV上14線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 上14(4E14) |  | 上14(4E14) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上14線A2 | 11KV上14線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 上14(4E14) |  | 上14(4E14) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上14線A3 | 11KV上14線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 上14(4E14) |  | 上14(4E14) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上14線A0 | 11KV上14線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 上15(4E15) |  | 上15(4E15) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上15線KVAR | 11KV上15線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 上15(4E15) |  | 上15(4E15) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上15線A1 | 11KV上15線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 上15(4E15) |  | 上15(4E15) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上15線A2 | 11KV上15線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 上15(4E15) |  | 上15(4E15) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上15線A3 | 11KV上15線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 上15(4E15) |  | 上15(4E15) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上15線A0 | 11KV上15線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 340(M1B) |  | 瓦 | MW_-54_54(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_MW | #6DTR二次側(B) MW | MTR | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 340(M1B) |  | 乏 | MVAR_-36_36(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_MVAR | #6DTR二次側(B) MVAR | MTR | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 340(M1B) |  | R | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_A1 | #6DTR二次側(B) R相AMP | MTR | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 340(M1B) |  | S | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_A2 | #6DTR二次側(B) S相AMP | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 340(M1B) |  | T | A_-3000_3000(-2000_2000) |  | B3/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_A3 | #6DTR二次側(B) T相AMP | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 6BBUS | #6BBUS |  | V_R |  | B3,Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0140 |  |  | 2-8C |  |  | PT-6B |  | PT-6B R相電壓 | kV_-9_9(-2000_2000) | aba | B3/P06_A1 | [8 empty] | 山上PS.11KV#6BBUS_KV | 11KV #6BBUS KV | BUS | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 上16(4E16) |  | 上16(4E16) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上16線KVAR | 11KV上16線 KVAR | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 上16(4E16) |  | 上16(4E16) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上16線A1 | 11KV上16線 R相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 上16(4E16) |  | 上16(4E16) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上16線A2 | 11KV上16線 S相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 上16(4E16) |  | 上16(4E16) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上16線A3 | 11KV上16線 T相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 上16(4E16) |  | 上16(4E16) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上16線A0 | 11KV上16線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 上17(4E17) |  | 上17(4E17) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上17線KVAR | 11KV上17線 KVAR | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 上17(4E17) |  | 上17(4E17) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上17線A1 | 11KV上17線 R相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 上17(4E17) |  | 上17(4E17) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上17線A2 | 11KV上17線 S相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 上17(4E17) |  | 上17(4E17) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上17線A3 | 11KV上17線 T相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 上17(4E17) |  | 上17(4E17) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上17線A0 | 11KV上17線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 上18(4E18) |  | 上18(4E18) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上18線KVAR | 11KV上18線 KVAR | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 上18(4E18) |  | 上18(4E18) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上18線A1 | 11KV上18線 R相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 上18(4E18) |  | 上18(4E18) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上18線A2 | 11KV上18線 S相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 上18(4E18) |  | 上18(4E18) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上18線A3 | 11KV上18線 T相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 上18(4E18) |  | 上18(4E18) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上18線A0 | 11KV上18線 N相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 上19(4E19) |  | 上19(4E19) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上19線KVAR | 11KV上19線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 上19(4E19) |  | 上19(4E19) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上19線A1 | 11KV上19線 R相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 上19(4E19) |  | 上19(4E19) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上19線A2 | 11KV上19線 S相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 上19(4E19) |  | 上19(4E19) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上19線A3 | 11KV上19線 T相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 上19(4E19) |  | 上19(4E19) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上19線A0 | 11KV上19線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 上20(4E20) |  | 上20(4E20) 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上20線KVAR | 11KV上20線 KVAR | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 上20(4E20) |  | 上20(4E20) R | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上20線A1 | 11KV上20線 R相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 上20(4E20) |  | 上20(4E20) S | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上20線A2 | 11KV上20線 S相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 上20(4E20) |  | 上20(4E20) T | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上20線A3 | 11KV上20線 T相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 上20(4E20) |  | 上20(4E20) N | A_-600_600(-2000_2000) |  | B2/P06_D1 | [8 empty] | 山上PS.上20線A0 | 11KV上20線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | #1MTR | ON/OFF | #1MTR 1650 CB |  | aacb | B2/P06_A1 | [8 empty] | 山上PS.1650_CB | 1650(#1MTR) CB | MTR | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0001 |  | 0026 | 1-00-01 |  | 1-1A | #1MTR | ON/OFF | #1MTR 750 CB |  | aaca | B2/P06_A1 | [8 empty] | 山上PS.750_CB | 750(#1MTR) CB | MTR | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | #1MTR | 51ZA | #1MTR 51ZA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1MTR | 1PHA | #1MTR 1 PHA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_PHA | #1MTR PHA | OTHER | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1MTR | 87A | #1MTR 87A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_87A | #1MTR 87RY | MTR | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1MTR | 96PA | #1MTR 機械保護動作(96PA) |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0006 |  | 0002 | 1-00-06 |  | 1-02 | #2MTR | ON/OFF | #2MTR 1660 CB |  | aafb | B2/P06_A1 | [8 empty] | 山上PS.1660_CB | 1660(#2MTR) CB | MTR | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0007 |  | 0027 | 1-00-07 |  | 1-1B | #2MTR | ON/OFF | #2MTR 760 CB |  | aaka | B2/P06_A1 | [8 empty] | 山上PS.760_CB | 760(#2MTR) CB | MTR | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #2MTR | 51ZA | #2MTR 51ZA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #2MTR | 1PHA | #2MTR 1 PHA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_PHA | #2MTR PHA | OTHER | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | #2MTR | 87A | #2MTR 87A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_87A | #2MTR 87RY | MTR | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | #2MTR | 96PA | #2MTR 機械保護動作(96PA) |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0012 |  | 0003 | 1-01-04 |  | 1-03 | #3MTR | ON/OFF | #3MTR 1670 CB |  | aaib | B2/P06_A1 | [8 empty] | 山上PS.1670_CB | 1670(#3MTR) CB | MTR | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0013 |  | 0028 | 1-01-05 |  | 1-1C | #3MTR | ON/OFF | #3MTR 770 CB |  | aapa | B2/P06_A1 | [8 empty] | 山上PS.770_CB | 770(#3MTR) CB | MTR | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #3MTR | 51ZA | #3MTR 51ZA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #3MTR | 1 PHA | #3MTR 1 PHA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_PHA | #3MTR PHA | OTHER | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #3MTR | 87A | #3MTR 87A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_87A | #3MTR 87RY | MTR | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #3MTR | 96PA | #3MTR 機械保護動作(96PA) |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN09R/T2 |  | 0018 |  | 0004 | 1-02-02 |  | 1-04 | 1510 | ON/OFF | 嘉義新營山上紅線1510 CB |  | aaaa | B2/P06_A1 | [8 empty] | 山上PS.1510_CB | 1510(嘉義新營紅線) CB | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1510 | 87A | 嘉義新營山上紅線 1510 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_87A | 嘉義新營紅線(1510) 87RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 1510 | PHA | 嘉義新營山上紅線 1510 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_PHA | 嘉義新營紅線(1510) 相間RY | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1510 | GDA | 嘉義新營山上紅線 1510 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_GDA | 嘉義新營紅線(1510) 接地RY | LINE161 | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN10W/T2 |  | 0022 |  | 0005 | 1-02-06 |  | 1-05 | 1520 | ON/OFF | 嘉義新營山上白線 1520 CB |  | aaba | B2/P06_A1 | [8 empty] | 山上PS.1520_CB | 1520(嘉義新營白線) CB | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1520 | 87A | 嘉義新營山上白線 1520 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_87A | 嘉義新營白線(1520) 87RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1520 | PHA | 嘉義新營山上白線 1520 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_PHA | 嘉義新營白線(1520) 相間RY | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 1520 | GDA | 嘉義新營山上白線 1520 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_GDA | 嘉義新營白線(1520) 接地RY | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E02P061/T2 |  | 0026 |  | 0006 | 1-03-02 |  | 1-06 | 1570 | ON/OFF | 龍崎山上一路 1570 CB |  | aaga | B2/P06_A1 | [8 empty] | 山上PS.1570_CB | 1570(龍崎一路) CB | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 1570 | 85A | 龍崎山上一路 1570 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_87A | 龍崎山上一路(1570) 87RY | LINE161 | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 1570 | PHA | 龍崎山上一路 1570 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_PHA | 龍崎一路(1570) 相間RY | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1570 | GDA | 龍崎山上一路 1570 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_GDA | 龍崎一路(1570) 接地RY | LINE161 | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E02P062/T2 |  | 0030 |  | 0007 | 1-03-06 |  | 1-07 | 1580 | ON/OFF | 龍崎山上二路 1580 CB |  | aaha | B2/P06_A1 | [8 empty] | 山上PS.1580_CB | 1580(龍崎二路) CB | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 1580 | 85A | 龍崎山上二路 1580 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_87A | 龍崎山上二路(1580) 87RY | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 1580 | PHA | 龍崎山上二路 1580 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_PHA | 龍崎二路(1580) 相間RY | LINE161 | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 1580 | GDA | 龍崎山上二路 1580 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_GDA | 龍崎二路(1580) 接地RY | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN113/T2 |  | 0034 |  | 0008 | 1-04-02 |  | 1-08 | 1610 | ON/OFF | 龍崎山上二甲三路 1610 CB |  | aaja | B2/P06_A1 | [8 empty] | 山上PS.1610_CB | 1610(龍崎二甲三路) CB | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 1610 | 85A | 龍崎山上二甲三路 1610 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_87A | 龍崎二甲三路(1610) 87RY | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 1610 | PHA | 龍崎山上二甲三路 1610 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_PHA | 龍崎二甲三路(1610) 相間RY | LINE161 | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 1610 | GDA | 龍崎山上二甲三路 1610 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_GDA | 龍崎二甲三路(1610) 接地RY | LINE161 | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN124/T2 |  | 0038 |  | 0009 | 1-04-06 |  | 1-09 | 1620 | ON/OFF | 龍崎山上二甲四路 1620 CB |  | aaka | B2/P06_A1 | [8 empty] | 山上PS.1620_CB | 1620(龍崎二甲四路) CB | LINE161 | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 1620 | 85A | 龍崎山上二甲四路 1620 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_87A | 龍崎二甲四路(1620) 87RY | LINE161 | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 1620 | PHA | 龍崎山上二甲四路 1620 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_PHA | 龍崎二甲四路(1620) 相間RY | LINE161 | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1620 | GDA | 龍崎山上二甲四路 1620 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_GDA | 龍崎二甲四路(1620) 接地RY | LINE161 | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06D16/T1 |  | 0042 |  | 0010 | 1-05-02 |  | 1-0A | 1630 | ON/OFF | 山上仁德線 1630 CB |  | aala | B2/P06_A1 | [8 empty] | 山上PS.1630_CB | 1630(山上仁德線) CB | LINE161 | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 1630 | 87A | 山上仁德線 1630 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_87A | 山上仁德線(1630) 87RY | LINE161 | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 1630 | PHA | 山上仁德線 1630 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_PHA | 山上仁德線(1630) 相間RY | LINE161 | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 1630 | GDA | 山上仁德線 1630 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_GDA | 山上仁德線(1630) 接地RY | LINE161 | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06P07O/T1 |  | 0046 |  | 0011 | 1-05-06 |  | 1-0B | 1640 | ON/OFF | 山上台南海線 1640 CB |  | aama | B2/P06_A1 | [8 empty] | 山上PS.1640_CB | 1640(台南海線) CB | LINE161 | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 1640 | 87A | 山上台南海線 1640 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_87A | 台南海線(1640) 87RY | LINE161 | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | 1640 | PHA | 山上台南海線 1640 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_PHA | 台南海線(1640) 相間RY | LINE161 | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 1640 | GDA | 山上台南海線 1640 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_GDA | 台南海線(1640) 接地RY | LINE161 | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN16W/T2 |  | 0050 |  | 0012 | 1-06-02 |  | 1-0C | 1540 | ON/OFF | 山上鹽行豐華白線1540 CB |  | aana | B2/P06_A1 | [8 empty] | 山上PS.1540_CB | 1540(鹽行豐華白線) CB | LINE161 | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 1540 | 87A1 | 山上鹽行豐華白線1540 87A1 |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_87A1 | 鹽行豐華白線(1540) #1 87RY | LINE161 | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 1540 | PHA | 山上鹽行豐華白線1540 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_PHA | 鹽行豐華白線(1540) 相間RY | LINE161 | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 1540 | GDA | 山上鹽行豐華白線1540 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_GDA | 鹽行豐華白線(1540) 接地RY | LINE161 | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06TN15R/T2 |  | 0054 |  | 0013 | 1-06-06 |  | 1-0D | 1710 | ON/OFF | 山上安南豐華紅線1710 CB |  | aaoa | B2/P06_A1 | [8 empty] | 山上PS.1710_CB | 1710(安南豐華紅線) CB | LINE161 | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 1710 | 87A1 | 山上安南豐華紅線1710 87A1 |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_87A1 | 安南豐華紅線(1710) #1 87RY | LINE161 | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 1710 | PHA | 山上安南豐華紅線1710 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_PHA | 安南豐華紅線(1710) 相間RY | LINE161 | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 1710 | GDA | 山上安南豐華紅線1710 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_GDA | 安南豐華紅線(1710) 接地RY | LINE161 | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06D152/T1 |  | 0058 |  | 0014 | 1-07-02 |  | 1-0E | 1720 | ON/OFF | 山上新化二路 1720 CB |  | aasa | B2/P06_A1 | [8 empty] | 山上PS.1720_CB | 1720(新化二路) CB | LINE161 | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | 1720 | 87A | 山上新化二路 1720 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_87A | 新化二路(1720) 87RY | LINE161 | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 1720 | PHA | 山上新化二路 1720 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_PHA | 新化二路(1720) 相間RY | LINE161 | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 1720 | GDA | 山上新化二路 1720 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_GDA | 新化二路(1720) 接地RY | LINE161 | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06D151/T1 |  | 0062 |  | 0015 | 1-07-06 |  | 1-0F | 1730 | ON/OFF | 山上新化一路 1730 CB |  | aata | B2/P06_A1 | [8 empty] | 山上PS.1730_CB | 1730(新化一路) CB | LINE161 | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | 1730 | 87A | 山上新化一路 1730 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_87A | 新化一路(1730) 87RY | LINE161 | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 1730 | PHA | 山上新化一路 1730 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_PHA | 新化一路(1730) 相間RY | LINE161 | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 1730 | GDA | 山上新化一路 1730 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_GDA | 新化一路(1730) 接地RY | LINE161 | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0066 |  | 0024 | 1-08-02 |  | 1-18 | 1730 | ON/OFF | 1500TIE CB |  | aauz | B2/P06_A1 | [8 empty] | 山上PS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 161KVBUS | 87B1A | 161KVBUS 87B1A |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 161KVBUS | 87B2A | 161KVBUS 87B2A |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 1500TIE | 50A | 1500TIE 50A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0070 |  | 0025 | 1-08-06 |  | 1-19 | 600TIE | ON/OFF | 600TIE CB |  | aabz | B2/P06_A1 | [8 empty] | 山上PS.600_CB | 600(TIE) CB | TIE | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 69KVBUS | 87B1A | 69KVBUS 87B1A |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 69KVBUS | 87B2A | 69KVBUS 87B2A |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 600 | #1 PHA | 600 TIE #1 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  |  | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 600 | #1 GDA | 600 TIE #1 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | OSCA | A/N | 69KV示波器啟動警報OSCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 161KV | A/N | 79RCA復閉電驛警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/T11P06R/T2 |  | 0081 |  | 0016 | 1-0A-01 |  | 1-10 | 1550 | ON/OFF | 豐德山上紅線 1550 CB |  | aara | B2/P06_A1 | [8 empty] | 山上PS.1550_CB | 1550(豐德紅線) CB | LINE161 | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 1550 | 85A | 豐德山上紅線 1550 85A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_85A | 豐德紅線(1550) 85RY | LINE161 | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 1550 | 87LA | 豐德山上紅線 1550 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_87A | 豐德紅線(1550) 87RY | LINE161 | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 1550 | PHA | 豐德山上紅線 1550 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_PHA | 豐德紅線(1550) 相間RY | LINE161 | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 1550 | GDA | 豐德山上紅線 1550 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_GDA | 豐德紅線(1550) 接地RY | LINE161 | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/T11P06W/T2 |  | 0086 |  | 0017 | 1-0A-06 |  | 1-11 | 1560 | ON/OFF | 豐德山上白線 1560 CB |  | aaqa | B2/P06_A1 | [8 empty] | 山上PS.1560_CB | 1560(豐德白線) CB | LINE161 | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 1560 | 85A | 豐德山上白線 1560 85A |  |  | B2/P06_A1 | [8 empty] | 山上PS.1560_85A | 豐德白線(1560) 85RY | LINE161 | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 1560 | 87LA | 豐德山上白線 1560 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1560_87A | 豐德白線(1560) 87RY | LINE161 | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 1560 | PHA | 豐德山上白線 1560 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1560_PHA | 豐德白線(1560) 相間RY | LINE161 | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 1560 | GDA | 豐德山上白線 1560 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1560_GDA | 豐德白線(1560) 接地RY | LINE161 | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0091 |  | 0018 | 1-0B-03 |  | 1-12 | 1950 | 52AS | #1 SH.R 1950 52AS |  | aaea | B2/P06_A1 | [8 empty] | 山上PS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 1950 | 87A | #1 SH.R 87A |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA |  | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 1950 | 96A | #1 SH.R 96PA |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 1950 | 51A | #1 SH.R 51A |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 1710 | 87A2 | 山上安南豐華紅線1710 87A2 |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_87A2 | 安南豐華紅線(1710) #2 87RY | LINE161 | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 1540 | 87A2 | 山上鹽行豐華白線1540 87A2 |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_87A2 | 鹽行豐華白線(1540) #2 87RY | LINE161 | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | #3MTR | GDA | #3MTr . GDA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_GDA | #3MTR GDA | OTHER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | #3MTR | 86A | #3MTr _86A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_86A | #3MTR 86RY | OTHER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | #2MTR | GDA | #2MTr . GDA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_GDA | #2MTR GDA | OTHER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | #2MTR | 86A | #2MTr _86A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_86A | #2MTR 86RY | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | #1MTR | GDA | #1MTr . GDA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_GDA | #1MTR GDA | OTHER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1MTR | 86A | #1MTr _86A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_86A | #1MTR 86RY | OTHER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S701/T1 |  | 0128 |  | 0029 | 1-10-00 |  | 1-1D | 610 | ON/OFF | 山上山頂一路 610 CB |  | aadb | B2/P06_A1 | [8 empty] | 山上PS.610_CB | 610(山頂一路) CB | LINE69 | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 610 | PHA | 山上山頂一路 610 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_PHA | 山頂一路(610) 相間RY | LINE69 | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 610 | GDA | 山上山頂一路 610 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_GDA | 山頂一路(610) 接地RY | LINE69 | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S702/T1 |  | 0131 |  | 0030 | 1-10-03 |  | 1-1E | 620 | ON/OFF | 山上山頂二路 620 CB |  | aaeb | B2/P06_A1 | [8 empty] | 山上PS.620_CB | 620(山頂二路) CB | LINE69 | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 620 | PHA | 山上山頂二路 620 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_PHA | 山頂二路(620) 相間RY | LINE69 | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 620 | GDA | 山上山頂二路 620 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_GDA | 山頂二路(620) 接地RY | LINE69 | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S711/T1 |  | 0134 |  | 0031 | 1-10-06 |  | 1-1F | 630 | ON/OFF | 山上善化一路 630 CB |  | aafb | B2/P06_A1 | [8 empty] | 山上PS.630_CB | 630(善化一路) CB | LINE69 | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 630 | PHA | 山上善化一路 630 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_PHA | 善化一路(630) 相間RY | LINE69 | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 630 | GDA | 山上善化一路 630 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_GDA | 善化一路(630) 接地RY | LINE69 | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S712/T1 |  | 0137 |  | 0032 | 1-11-01 |  | 1-20 | 640 | ON/OFF | 山上善化二路 640 CB |  | aagb | B2/P06_A1 | [8 empty] | 山上PS.640_CB | 640(善化二路) CB | LINE69 | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | 640 | PHA | 山上善化二路 640 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_PHA | 善化二路(640) 相間RY | LINE69 | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | 640 | GDA | 山上善化二路 640 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_GDA | 善化二路(640) 接地RY | LINE69 | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S713/T1 |  | 0140 |  | 0033 | 1-11-04 |  | 1-21 | 650 | ON/OFF | 山上善化三路 650 CB |  | aahb | B2/P06_A1 | [8 empty] | 山上PS.650_CB | 650(善化三路) CB | LINE69 | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 650 | PHA | 山上善化三路 650 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_PHA | 善化三路(650) 相間RY | LINE69 | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | 650 | GDA | 山上善化三路 650 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_GDA | 善化三路(650) 接地RY | LINE69 | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S681/T1 |  | 0143 |  | 0034 | 1-11-07 |  | 1-22 | 660 | ON/OFF | 山上新市一路 660 CB |  | aaib | B2/P06_A1 | [8 empty] | 山上PS.660_CB | 660(新市一路) CB | LINE69 | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | 660 | PHA | 山上新市一路 660 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_PHA | 新市一路(660) 相間RY | LINE69 | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 660 | GDA | 山上新市一路 660 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_GDA | 新市一路(660) 接地RY | LINE69 | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S683/T1 |  | 0146 |  | 0035 | 1-12-02 |  | 1-23 | 670 | ON/OFF | 山上新市三路 670 CB |  | aalb | B2/P06_A1 | [8 empty] | 山上PS.670_CB | 670(山上新市三路) CB | LINE69 | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | 670 | PHA | 山上新市三路 670 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_PHA | 山上新市三路(670) 相間RY | LINE69 | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | 670 | GDA | 山上新市三路 670 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_GDA | 山上新市三路(670) 接地RY | LINE69 | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S67/T1 |  | 0149 |  | 0036 | 1-12-05 |  | 1-24 | 680 | ON/OFF | 山上歸仁線 680 CB |  | aamb | B2/P06_A1 | [8 empty] | 山上PS.680_CB | 680(歸仁線) CB | LINE69 | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 680 | PHA | 山上歸仁線 680 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_PHA | 歸仁線(680) 相間RY | LINE69 | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | 680 | GDA | 山上歸仁線 680 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_GDA | 歸仁線(680) 接地RY | LINE69 | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06S682/T1 |  | 0152 |  | 0037 | 1-13-00 |  | 1-25 | 710 | ON/OFF | 山上新市二路 710 CB |  | aanb | B2/P06_A1 | [8 empty] | 山上PS.710_CB | 710(新市二路) CB | LINE69 | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | 710 | PHA | 山上新市二路 710 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_PHA | 新市二路(710) 相間RY | LINE69 | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | 710 | GDA | 山上新市二路 710 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_GDA | 新市二路(710) 接地RY | LINE69 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/2SC |  | 0155 |  | 0038 | 1-13-03 |  | 1-26 | 820 | ON/OFF | 69KV #2SC 820 CB |  | aajb | B2/P06_A1 | [8 empty] | 山上PS.820_CB | 820(69KV #2SC) CB | SC | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | 820 | SCA | 69KV #2SC 820 SCA |  |  | B2/P06_A1 | [8 empty] | 山上PS.820_SCA | 69KV #2SC 51,51N RY | SC | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 820 | UVA | 69KV #2SC 820 UVA |  |  | B2/P06_A1 | [8 empty] | 山上PS.820_OUVA | 69KV #2SC 27,59RY | SC | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/3SC |  | 0158 |  | 0039 | 1-13-06 |  | 1-27 | 830 | ON/OFF | 69KV #3SC 830 CB |  | aaob | B2/P06_A1 | [8 empty] | 山上PS.830_CB | 830(69KV #3SC) CB | SC | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | 830 | SCA | 69KV #3SC 830 SCA |  |  | B2/P06_A1 | [8 empty] | 山上PS.830_SCA | 69KV #3SC 51,51N RY | SC | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | 830 | UVA | 69KV #3SC 830 UVA |  |  | B2/P06_A1 | [8 empty] | 山上PS.830_OUVA | 69KV #3SC 27,59RY | SC | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 630 | 87A | 山上善化一路 630 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_87A | 山上善化一路(630) 87RY | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 640 | 87A | 山上善化二路 640 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_87A | 山上善化二路(640) 87RY | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | 650 | 87A | 山上善化三路 650 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_87A | 山上善化三路(650) 87RY | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | 670 | 87A | 山上新市三路 670 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_87A | 山上新市三路(670) 87RY | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 710 | 87A | 山上新市二路 710 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_87A | 山上新市二路(710) 87RY | OTHER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | 660 | 87A | 山上新市一路 660 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_87A | 山上新市一路(660) 87RY | OTHER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 680 | 87A | 山上歸仁線 680 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_87A | 山上歸仁線(680) 87RY | OTHER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 600 | #2PHA | 600 TIE #2 PHA |  |  | B2/P06_A1 | [8 empty] | 山上PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  |  | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 600 | #2GDA | 600 TIE #2 GDA |  |  | B2/P06_A1 | [8 empty] | 山上PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 620 | 87A | 山上山頂二路 620 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_87A | 山頂二路(620) 87RY | LINE69 | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 610 | 87A | 山上山頂一路 610 87RY |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_87A | 山頂一路(610) 87RY | LINE69 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/P06_A1 | [16 empty] | 393 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/6DTR |  | 0192 |  | 0019 | 1-18-00 |  | 1-13 | #6 DTR | ON/OFF | 1760 CB |  | aada | ELEM/P06_A1 | [8 empty] | 山上PS.1760_CB | 1760(#6DTR) CB | MTR | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #6 DTR | 87A | #6 DTR 87 Ry |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_87A | #6DTR 87RY | MTR | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #6 DTR | 51ZA | #6 DTR 51Z Ry |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_51ZA | #6DTR 51Z RY | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #6 DTR | 96PA | #6 DTR 機械保護電驛 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_96PA | #6DTR 機械保護動作 | MTR | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #6 DTR | PHA | #6 DTR PHA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_PHA | #6DTR 50/51 RY | OTHER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6ABUS | T/6DTR(A) |  |  | 0197 |  | 0216 | 1-18-05 |  | 2-58 | 330 | ON/OFF | 330 CB |  | aaca | ELEM/P06_A1 | [8 empty] | 山上PS.330_CB | 330(#6DTR) CB | MTR | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 330 | PHA | M1A(330) PHA |  |  | B3/P06_A1 | [8 empty] | 山上PS.330_51A | #6DTR二次側(330) 51RY | MTR | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 330 | GDA | M1A(330) GDA |  |  | B3/P06_A1 | [8 empty] | 山上PS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 330 | 81A/S | M1A(330) 81A/S |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.330_81A | 330(#6DTR) 81RY動作 | OTHER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6BBUS | T/6DTR(B) |  |  | 0201 |  | 0217 | 1-19-01 |  | 2-59 | 340 | ON/OFF | 340 CB |  | abia | ELEM/P06_A1 | [8 empty] | 山上PS.340_CB | 340(#6DTR) CB | MTR | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 340 | PHA | M1B(340) PHA |  |  | B3/P06_A1 | [8 empty] | 山上PS.340_51A | #6DTR二次側(340) 51RY | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 340 | GDA | M1B(340) GDA |  |  | B3/P06_A1 | [8 empty] | 山上PS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 340 | 81A/S | M1B(340) 81A/S |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.340_81A | 340(#6DTR) 81RY動作 | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | #6 DTR | GDA | #6 DTR GDA |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_GDA | #6DTR 50N/51N RY | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 390 | #3SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6ABUS | T/1SSTR |  |  | 0224 |  | 0218 | 1-1C-00 |  | 2-5A | 390 #3SSTR | ON/OFF | 390 #3SSTR CB |  | aabb | B3/P06_A1 | [8 empty] | 山上PS.390_CB | 390(#3SSTR) CB | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 390 | #3SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 390 #3SSTR | PHA | 390 #3SSTR PHA |  |  | B3/P06_A1 | [8 empty] | 山上PS.#3SSTR_51A | #3SSTR 51RY | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 390 | #3SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | 390 #3SSTR | GDA | 390 #3SSTR GDA |  |  | B3/P06_A1 | [8 empty] | 山上PS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6ABUS | L |  |  | 0227 |  | 0219 | 1-1C-03 |  | 2-5B | 上11(4E11) | ON/OFF | 上11(4E11) CB |  | aagb | B2/P06_D1 | [8 empty] | 山上PS.4E11_CB | 4E11(11KV上11線) CB | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 上11(4E11) | PHA | 上11(4E11) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E11_PHA | 11KV上11線(4E11) 相間RY | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 上11(4E11) | GDA | 上11(4E11) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E11_GDA | 11KV上11線(4E11) 接地RY | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6ABUS | L |  |  | 0230 |  | 0220 | 1-1C-06 |  | 2-5C | 上12(4E12) | ON/OFF | 上12(4E12) CB |  | aahb | B2/P06_D1 | [8 empty] | 山上PS.4E12_CB | 4E12(11KV上12線) CB | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 上12(4E12) | PHA | 上12(4E12) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E12_PHA | 11KV上12線(4E12) 相間RY | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | 上12(4E12) | GDA | 上12(4E12) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E12_GDA | 11KV上12線(4E12) 接地RY | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6ABUS | L |  |  | 0233 |  | 0221 | 1-1D-01 |  | 2-5D | 上13(4E13) | ON/OFF | 上13(4E13) CB |  | aaib | B2/P06_D1 | [8 empty] | 山上PS.4E13_CB | 4E13(11KV上13線) CB | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 上13(4E13) | PHA | 上13(4E13) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E13_PHA | 11KV上13線(4E13) 相間RY | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 上13(4E13) | GDA | 上13(4E13) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E13_GDA | 11KV上13線(4E13) 接地RY | FEEDER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6ABUS | L |  |  | 0236 |  | 0222 | 1-1D-04 |  | 2-5E | 上14(4E14) | ON/OFF | 上14(4E14) CB |  | aajb | B2/P06_D1 | [8 empty] | 山上PS.4E14_CB | 4E14(11KV上14線) CB | FEEDER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 上14(4E14) | PHA | 上14(4E14) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E14_PHA | 11KV上14線(4E14) 相間RY | FEEDER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 上14(4E14) | GDA | 上14(4E14) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E14_GDA | 11KV上14線(4E14) 接地RY | FEEDER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6ABUS | L |  |  | 0239 |  | 0223 | 1-1D-07 |  | 2-5F | 上15(4E15) | ON/OFF | 上15(4E15) CB |  | aakb | B2/P06_D1 | [8 empty] | 山上PS.4E15_CB | 4E15(11KV上15線) CB | FEEDER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 上15(4E15) | PHA | 上15(4E15) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E15_PHA | 11KV上15線(4E15) 相間RY | FEEDER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 上15(4E15) | GDA | 上15(4E15) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E15_GDA | 11KV上15線(4E15) 接地RY | FEEDER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6BBUS | L |  |  | 0242 |  | 0224 | 1-1E-02 |  | 2-60 | 上16(4E16) | ON/OFF | 上16(4E16) CB |  | abbb | B2/P06_D1 | [8 empty] | 山上PS.4E16_CB | 4E16(11KV上16線) CB | FEEDER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 上16(4E16) | PHA | 上16(4E16) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E16_PHA | 11KV上16線(4E16) 相間RY | FEEDER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 上16(4E16) | GDA | 上16(4E16) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E16_GDA | 11KV上16線(4E16) 接地RY | FEEDER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6BBUS | L |  |  | 0245 |  | 0225 | 1-1E-05 |  | 2-61 | 上17(4E17) | ON/OFF | 上17(4E17) CB |  | abcb | B2/P06_D1 | [8 empty] | 山上PS.4E17_CB | 4E17(11KV上17線) CB | FEEDER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | 上17(4E17) | PHA | 上17(4E17) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E17_PHA | 11KV上17線(4E17) 相間RY | FEEDER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | 上17(4E17) | GDA | 上17(4E17) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E17_GDA | 11KV上17線(4E17) 接地RY | FEEDER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6BBUS | L |  |  | 0248 |  | 0226 | 1-1F-00 |  | 2-62 | 上18(4E18) | ON/OFF | 上18(4E18) CB |  | abdb | B2/P06_D1 | [8 empty] | 山上PS.4E18_CB | 4E18(11KV上18線) CB | FEEDER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0249 |  |  | 1-1F-01 |  |  | 上18(4E18) | PHA | 上18(4E18) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E18_PHA | 11KV上18線(4E18) 相間RY | FEEDER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | 上18(4E18) | GDA | 上18(4E18) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E18_GDA | 11KV上18線(4E18) 接地RY | FEEDER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6BBUS | L |  |  | 0251 |  | 0227 | 1-1F-03 |  | 2-63 | 上19(4E19) | ON/OFF | 上19(4E19) CB |  | abeb | B2/P06_D1 | [8 empty] | 山上PS.4E19_CB | 4E19(11KV上19線) CB | FEEDER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0252 |  |  | 1-1F-04 |  |  | 上19(4E19) | PHA | 上19(4E19) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E19_PHA | 11KV上19線(4E19) 相間RY | FEEDER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0253 |  |  | 1-1F-05 |  |  | 上19(4E19) | GDA | 上19(4E19) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E19_GDA | 11KV上19線(4E19) 接地RY | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/6BBUS | L |  |  | 0254 |  | 0228 | 1-1F-06 |  | 2-64 | 上20(4E20) | ON/OFF | 上20(4E20) CB |  | abfb | B2/P06_D1 | [8 empty] | 山上PS.4E20_CB | 4E20(11KV上20線) CB | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | 上20(4E20) | PHA | 上20(4E20) PHA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E20_PHA | 11KV上20線(4E20) 相間RY | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 上20(4E20) | GDA | 上20(4E20) GDA |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E20_GDA | 11KV上20線(4E20) 接地RY | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6ABUS | C/1SC |  |  | 0257 |  | 0229 | 2-00-01 |  | 2-65 | 210(#1 SC) | ON/OFF | 210 # 1SC CB |  | aadb | B3/P06_A1 | [8 empty] | 山上PS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 210(#1 SC) | SCA | 210 # 1SC SCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | 210(#1 SC) | UVA | 210 # 1SC UVA |  |  | B3/P06_A1 | [8 empty] | 山上PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6ABUS | C/2SC |  |  | 0260 |  | 0230 | 2-00-04 |  | 2-66 | 220(#2 SC) | ON/OFF | 220 # 2 SC CB |  | aaeb | B3/P06_A1 | [8 empty] | 山上PS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | 220(#2 SC) | SCA | 220 # 2 SC SCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | 220(#2 SC) | UVA | 220 # 2 SC UVA |  |  | B3/P06_A1 | [8 empty] | 山上PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6BBUS | C/3SC |  |  | 0263 |  | 0231 | 2-00-07 |  | 2-67 | 230(#3 SC) | ON/OFF | 230 # 3 SC CB |  | abgb | B3/P06_A1 | [8 empty] | 山上PS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | 230(#3 SC) | SCA | 230 # 3 SC SCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | 230(#3 SC) | UVA | 230 # 3 SC UVA |  |  | B3/P06_A1 | [8 empty] | 山上PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/6BBUS | C/4SC |  |  | 0266 |  | 0232 | 2-01-02 |  | 2-68 | 240(#4 SC) | ON/OFF | 240 # 4 SC CB |  | abhb | B3/P06_A1 | [8 empty] | 山上PS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | 240(#4 SC) | SCA | 240 # 4 SC SCA |  |  | B3/P06_A1 | [8 empty] | 山上PS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | 240(#4 SC) | UVA | 240 # 4 SC UVA |  |  | B3/P06_A1 | [8 empty] | 山上PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS1 | 1651 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 | 0040 | 1-30-00 | 1-30-01 | 1-28 | 1651 | ON/OFF | #1MTR 1651 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1651_ABS | 1651(#1MTR) ABS | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS2 | 1652 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 | 0041 | 1-30-02 | 1-30-03 | 1-29 | 1652 | ON/OFF | #1MTR 1652 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1652_ABS | 1652(#1MTR) ABS | MTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 | 0042 | 1-30-04 | 1-30-05 | 1-2A | 1661 | ON/OFF | #2MTR 1661 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1661_ABS | 1661(#2MTR) ABS | MTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0774 | 775 | 0043 | 1-30-06 | 1-30-07 | 1-2B | 1662 | ON/OFF | #2MTR 1662 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1662_ABS | 1662(#2MTR) ABS | MTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 | 0044 | 1-30-08 | 1-30-09 | 1-2C | 1671 | ON/OFF | #3MTR 1671 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1671_ABS | 1671(#3MTR) ABS | MTR | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0778 | 779 | 0045 | 1-30-10 | 1-30-11 | 1-2D | 1672 | ON/OFF | #3MTR 1672 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1672_ABS | 1672(#3MTR) ABS | MTR | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | ABS1 | 1511 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 | 0046 | 1-30-12 | 1-30-13 | 1-2E | 1511 | ON/OFF | 嘉義新營山上紅線 1511 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1511_ABS | 1511(嘉義新營紅線) ABS | LINE161 | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | ABS2 | 1512 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0782 | 783 | 0047 | 1-30-14 | 1-30-15 | 1-2F | 1512 | ON/OFF | 嘉義新營山上紅線 1512 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1512_ABS | 1512(嘉義新營紅線) ABS | LINE161 | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | ABS3 | 1513 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 | 0048 | 1-31-00 | 1-31-01 | 1-30 | 1513 | ON/OFF | 嘉義新營山上紅線 1513 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1513_ABS | 1513(嘉義新營紅線) ABS | LINE161 | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0786 | 787 | 0049 | 1-31-02 | 1-31-03 | 1-31 | 1513E | ON/OFF | 嘉義新營山上紅線 1513 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1513E_ES | 1513E(嘉義新營紅線) ES | LINE161 | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | ABS1 | 1521 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0788 | 789 | 0050 | 1-31-04 | 1-31-05 | 1-32 | 1521 | ON/OFF | 嘉義新營山上白線 1521 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1521_ABS | 1521(嘉義新營白線) ABS | LINE161 | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | ABS2 | 1522 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0790 | 791 | 0051 | 1-31-06 | 1-31-07 | 1-33 | 1522 | ON/OFF | 嘉義新營山上白線 1522 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1522_ABS | 1522(嘉義新營白線) ABS | LINE161 | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | ABS3 | 1523 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0792 | 793 | 0052 | 1-31-08 | 1-31-09 | 1-34 | 1523 | ON/OFF | 嘉義新營山上白線 1523 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1523_ABS | 1523(嘉義新營白線) ABS | LINE161 | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0794 | 795 | 0053 | 1-31-10 | 1-31-11 | 1-35 | 1523E | ON/OFF | 嘉義新營山上白線 1523 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1523E_ES | 1523E(嘉義新營白線) ES | LINE161 | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | ABS1 | 1571 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0796 | 797 | 0054 | 1-31-12 | 1-31-13 | 1-36 | 1571 | ON/OFF | 龍崎山上一路 1571 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1571_ABS | 1571(龍崎一路) ABS | LINE161 | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | ABS2 | 1572 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0798 | 799 | 0055 | 1-31-14 | 1-31-15 | 1-37 | 1572 | ON/OFF | 龍崎山上一路 1572 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1572_ABS | 1572(龍崎一路) ABS | LINE161 | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | ABS3 | 1573 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0800 | 801 | 0056 | 1-32-00 | 1-32-01 | 1-38 | 1573 | ON/OFF | 龍崎山上一路 1573 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1573_ABS | 1573(龍崎一路) ABS | LINE161 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0802 | 803 | 0057 | 1-32-02 | 1-32-03 | 1-39 | 1573E | ON/OFF | 龍崎山上一路 1573 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1573E_ES | 1573E(龍崎一路) ES | LINE161 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | ABS1 | 1581 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0804 | 805 | 0058 | 1-32-04 | 1-32-05 | 1-3A | 1581 | ON/OFF | 龍崎山上二路 1581 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1581_ABS | 1581(龍崎二路) ABS | LINE161 | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | ABS2 | 1582 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0806 | 807 | 0059 | 1-32-06 | 1-32-07 | 1-3B | 1582 | ON/OFF | 龍崎山上二路 1582 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1582_ABS | 1582(龍崎二路) ABS | LINE161 | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | ABS3 | 1583 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0808 | 809 | 0060 | 1-32-08 | 1-32-09 | 1-3C | 1583 | ON/OFF | 龍崎山上二路 1583 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1583_ABS | 1583(龍崎二路) ABS | LINE161 | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0810 | 811 | 0061 | 1-32-10 | 1-32-11 | 1-3D | 1583E | ON/OFF | 龍崎山上二路 1583 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1583E_ES | 1583E(龍崎二路) ES | LINE161 | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | ABS1 | 1611 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0812 | 813 | 0062 | 1-32-12 | 1-32-13 | 1-3E | 1611 | ON/OFF | 龍崎山上二甲三路 1611 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1611_ABS | 1611(龍崎二甲三路) ABS | LINE161 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | ABS2 | 1612 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0814 | 815 | 0063 | 1-32-14 | 1-32-15 | 1-3F | 1612 | ON/OFF | 龍崎山上二甲三路 1612 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1612_ABS | 1612(龍崎二甲三路) ABS | LINE161 | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | ABS3 | 1613 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0816 | 817 | 0064 | 1-33-00 | 1-33-01 | 1-40 | 1613 | ON/OFF | 龍崎山上二甲三路 1613 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1613_ABS | 1613(龍崎二甲三路) ABS | LINE161 | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0818 | 819 | 0065 | 1-33-02 | 1-33-03 | 1-41 | 1613E | ON/OFF | 龍崎山上二甲三路 1613 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1613E_ES | 1613E(龍崎二甲三路) ES | LINE161 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | ABS1 | 1621 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0820 | 821 | 0066 | 1-33-04 | 1-33-05 | 1-42 | 1621 | ON/OFF | 龍崎山上二甲四路 1621 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1621_ABS | 1621(龍崎二甲四路) ABS | LINE161 | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | ABS2 | 1622 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0822 | 823 | 0067 | 1-33-06 | 1-33-07 | 1-43 | 1622 | ON/OFF | 龍崎山上二甲四路 1622 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1622_ABS | 1622(龍崎二甲四路) ABS | LINE161 | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | ABS3 | 1623 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0824 | 825 | 0068 | 1-33-08 | 1-33-09 | 1-44 | 1623 | ON/OFF | 龍崎山上二甲四路 1623 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1623_ABS | 1623(龍崎二甲四路) ABS | LINE161 | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0826 | 827 | 0069 | 1-33-10 | 1-33-11 | 1-45 | 1623E | ON/OFF | 龍崎山上二甲四路 1623 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1623E_ES | 1623E(龍崎二甲四路) ES | LINE161 | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | ABS1 | 1631 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0828 | 829 | 0070 | 1-33-12 | 1-33-13 | 1-46 | 1631 | ON/OFF | 山上仁德線 1631 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1631_ABS | 1631(山上仁德線) ABS | LINE161 | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | ABS2 | 1632 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0830 | 831 | 0071 | 1-33-14 | 1-33-15 | 1-47 | 1632 | ON/OFF | 山上仁德線 1632 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1632_ABS | 1632(山上仁德線) ABS | LINE161 | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | ABS3 | 1633 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0832 | 833 | 0072 | 1-34-00 | 1-34-01 | 1-48 | 1633 | ON/OFF | 山上仁德線 1633 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1633_ABS | 1633(山上仁德線) ABS | LINE161 | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | ES3 | 1633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0834 | 835 | 0073 | 1-34-02 | 1-34-03 | 1-49 | 1633E | ON/OFF | 山上仁德線 1633 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1633E_ES | 1633E(山上仁德線) ES | LINE161 | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | ABS1 | 1641 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0836 | 837 | 0074 | 1-34-04 | 1-34-05 | 1-4A | 1641 | ON/OFF | 山上台南海線 1641 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1641_ABS | 1641(台南海線) ABS | LINE161 | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | ABS2 | 1642 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0838 | 839 | 0075 | 1-34-06 | 1-34-07 | 1-4B | 1642 | ON/OFF | 山上台南海線 1642 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1642_ABS | 1642(台南海線) ABS | LINE161 | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | ABS3 | 1643 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0840 | 841 | 0076 | 1-34-08 | 1-34-09 | 1-4C | 1643 | ON/OFF | 山上台南海線 1643 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1643_ABS | 1643(台南海線) ABS | LINE161 | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | ES3 | 1643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0842 | 843 | 0077 | 1-34-10 | 1-34-11 | 1-4D | 1643E | ON/OFF | 山上台南海線 1643 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1643E_ES | 1643E(台南海線) ES | LINE161 | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | ABS1 | 1541 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0844 | 845 | 0078 | 1-34-12 | 1-34-13 | 1-4E | 1541 | ON/OFF | 山上鹽行豐華白線 1541 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1541_ABS | 1541(鹽行豐華白線) ABS | LINE161 | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | ABS2 | 1542 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0846 | 847 | 0079 | 1-34-14 | 1-34-15 | 1-4F | 1542 | ON/OFF | 山上鹽行豐華白線 1542 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1542_ABS | 1542(鹽行豐華白線) ABS | LINE161 | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | ABS3 | 1543 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0848 | 849 | 0080 | 1-35-00 | 1-35-01 | 1-50 | 1543 | ON/OFF | 山上鹽行豐華白線 1543 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1543_ABS | 1543(鹽行豐華白線) ABS | LINE161 | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0850 | 851 | 0081 | 1-35-02 | 1-35-03 | 1-51 | 1543E | ON/OFF | 山上鹽行豐華白線 1543 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1543E_ES | 1543E(鹽行豐華白線) ES | LINE161 | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | ABS1 | 1711 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0852 | 853 | 0082 | 1-35-04 | 1-35-05 | 1-52 | 1711 | ON/OFF | 山上安南豐華紅線 1711 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1711_ABS | 1711(安南豐華紅線) ABS | LINE161 | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | ABS2 | 1712 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0854 | 855 | 0083 | 1-35-06 | 1-35-07 | 1-53 | 1712 | ON/OFF | 山上安南豐華紅線 1712 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1712_ABS | 1712(安南豐華紅線) ABS | LINE161 | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | ABS3 | 1713 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0856 | 857 | 0084 | 1-35-08 | 1-35-09 | 1-54 | 1713 | ON/OFF | 山上安南豐華紅線 1713 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1713_ABS | 1713(安南豐華紅線) ABS | LINE161 | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | ES3 | 1713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0858 | 859 | 0085 | 1-35-10 | 1-35-11 | 1-55 | 1713E | ON/OFF | 山上安南豐華紅線 1713 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1713E_ES | 1713E(安南豐華紅線) ES | LINE161 | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | ABS1 | 1721 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0860 | 861 | 0086 | 1-35-12 | 1-35-13 | 1-56 | 1721 | ON/OFF | 山上新化二路 1721 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1721_ABS | 1721(新化二路) ABS | LINE161 | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | ABS2 | 1722 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0862 | 863 | 0087 | 1-35-14 | 1-35-15 | 1-57 | 1722 | ON/OFF | 山上新化二路 1722 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1722_ABS | 1722(新化二路) ABS | LINE161 | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | ABS3 | 1723 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0864 | 865 | 0088 | 1-36-00 | 1-36-01 | 1-58 | 1723 | ON/OFF | 山上新化二路 1723 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1723_ABS | 1723(新化二路) ABS | LINE161 | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | ES3 | 1723E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0866 | 867 | 0089 | 1-36-02 | 1-36-03 | 1-59 | 1723E | ON/OFF | 山上新化二路 1723 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1723E_ES | 1723E(新化二路) ES | LINE161 | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | ABS1 | 1731 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0090 | 1-36-04 | 1-36-05 | 1-5A | 1731 | ON/OFF | 山上新化一路 1731 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1731_ABS | 1731(新化一路) ABS | LINE161 | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | ABS2 | 1732 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0870 | 871 | 0091 | 1-36-06 | 1-36-07 | 1-5B | 1732 | ON/OFF | 山上新化一路 1732 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1732_ABS | 1732(新化一路) ABS | LINE161 | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | ABS3 | 1733 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0092 | 1-36-08 | 1-36-09 | 1-5C | 1733 | ON/OFF | 山上新化一路 1733 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1733_ABS | 1733(新化一路) ABS | LINE161 | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | ES3 | 1733E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0874 | 875 | 0093 | 1-36-10 | 1-36-11 | 1-5D | 1733E | ON/OFF | 山上新化一路 1733 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1733E_ES | 1733E(新化一路) ES | LINE161 | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1501 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0876 | 877 | 0094 | 1-36-12 | 1-36-13 | 1-5E | 1501 | ON/OFF | 161KV TIE 1501 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1501_ABS | 1501(TIE) ABS | TIE | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS2 | 1502 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0878 | 879 | 0095 | 1-36-14 | 1-36-15 | 1-5F | 1502 | ON/OFF | 161KV TIE 1502 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1502_ABS | 1502(TIE) ABS | TIE | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0880 | 881 | 0096 | 1-37-00 | 1-37-01 | 1-60 | 601 | ON/OFF | 69KV TIE 601 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.601_ABS | 601(TIE) ABS | TIE | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0882 | 883 | 0097 | 1-37-02 | 1-37-03 | 1-61 | 602 | ON/OFF | 69KV TIE 602 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.602_ABS | 602(TIE) ABS | TIE | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0884 | 885 | 0098 | 1-37-04 | 1-37-05 | 1-62 | #1MTR | ON/OFF | #1MTR 751 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.751_ABS | 751(#1MTR) ABS | MTR | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS2 | 752 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0886 | 887 | 0099 | 1-37-06 | 1-37-07 | 1-63 | #1MTR | ON/OFF | #1MTR 752 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.752_ABS | 752(#1MTR) ABS | MTR | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0888 | 889 | 0100 | 1-37-08 | 1-37-09 | 1-64 | #2MTR | ON/OFF | #2MTR 761 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.761_ABS | 761(#2MTR) ABS | MTR | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0890 | 891 | 0101 | 1-37-10 | 1-37-11 | 1-65 | #2MTR | ON/OFF | #2MTR 762 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.762_ABS | 762(#2MTR) ABS | MTR | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0892 | 893 | 0102 | 1-37-12 | 1-37-13 | 1-66 | #3MTR | ON/OFF | #3MTR 771 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.771_ABS | 771(#3MTR) ABS | MTR | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0894 | 895 | 0103 | 1-37-14 | 1-37-15 | 1-67 | #3MTR | ON/OFF | #3MTR 772 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.772_ABS | 772(#3MTR) ABS | MTR | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | ABS1 | 611 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0128 | 1-38-00 | 1-38-01 | 2-00 | 611 | ON/OFF | 山上山頂一路 611 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.611_ABS | 611(山頂一路) ABS | LINE69 | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | ABS2 | 612 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0129 | 1-38-02 | 1-38-03 | 2-01 | 612 | ON/OFF | 山上山頂一路 612 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.612_ABS | 612(山頂一路) ABS | LINE69 | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | ABS3 | 613 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0130 | 1-38-04 | 1-38-05 | 2-02 | 613 | ON/OFF | 山上山頂一路 613 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.613_ABS | 613(山頂一路) ABS | LINE69 | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | ES3 | 613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 903 | 0131 | 1-38-06 | 1-38-07 | 2-03 | 613E | ON/OFF | 山上山頂一路 613 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.613E_ES | 613E(山頂一路) ES | LINE69 | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ABS1 | 621 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0132 | 1-38-08 | 1-38-09 | 2-04 | 621 | ON/OFF | 山上山頂二路 621 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.621_ABS | 621(山頂二路) ABS | LINE69 | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ABS2 | 622 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0133 | 1-38-10 | 1-38-11 | 2-05 | 622 | ON/OFF | 山上山頂二路 622 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.622_ABS | 622(山頂二路) ABS | LINE69 | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ABS3 | 623 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0134 | 1-38-12 | 1-38-13 | 2-06 | 623 | ON/OFF | 山上山頂二路 623 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.623_ABS | 623(山頂二路) ABS | LINE69 | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ES3 | 623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 911 | 0135 | 1-38-14 | 1-38-15 | 2-07 | 623E | ON/OFF | 山上山頂二路 623 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.623E_ES | 623E(山頂二路) ES | LINE69 | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | ABS1 | 631 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0136 | 1-39-00 | 1-39-01 | 2-08 | 631 | ON/OFF | 山上善化一路 631 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.631_ABS | 631(善化一路) ABS | LINE69 | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | ABS2 | 632 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0137 | 1-39-02 | 1-39-03 | 2-09 | 632 | ON/OFF | 山上善化一路 632 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.632_ABS | 632(善化一路) ABS | LINE69 | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | ABS3 | 633 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0138 | 1-39-04 | 1-39-05 | 2-0A | 633 | ON/OFF | 山上善化一路 633 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.633_ABS | 633(善化一路) ABS | LINE69 | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | ES3 | 633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 919 | 0139 | 1-39-06 | 1-39-07 | 2-0B | 633E | ON/OFF | 山上善化一路 633 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.633E_ES | 633E(善化一路) ES | LINE69 | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | ABS1 | 641 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0140 | 1-39-08 | 1-39-09 | 2-0C | 641 | ON/OFF | 山上善化二路 641 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.641_ABS | 641(善化二路) ABS | LINE69 | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | ABS2 | 642 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0141 | 1-39-10 | 1-39-11 | 2-0D | 642 | ON/OFF | 山上善化二路 642 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.642_ABS | 642(善化二路) ABS | LINE69 | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | ABS3 | 643 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 925 | 0142 | 1-39-12 | 1-39-13 | 2-0E | 643 | ON/OFF | 山上善化二路 643 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.643_ABS | 643(善化二路) ABS | LINE69 | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | ES3 | 643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 927 | 0143 | 1-39-14 | 1-39-15 | 2-0F | 643E | ON/OFF | 山上善化二路 643 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.643E_ES | 643E(善化二路) ES | LINE69 | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | ABS1 | 651 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 929 | 0144 | 1-3A-00 | 1-3A-01 | 2-10 | 651 | ON/OFF | 山上善化三路 651 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.651_ABS | 651(善化三路) ABS | LINE69 | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | ABS2 | 652 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 931 | 0145 | 1-3A-02 | 1-3A-03 | 2-11 | 652 | ON/OFF | 山上善化三路 652 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.652_ABS | 652(善化三路) ABS | LINE69 | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | ABS3 | 653 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0932 | 933 | 0146 | 1-3A-04 | 1-3A-05 | 2-12 | 653 | ON/OFF | 山上善化三路 653 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.653_ABS | 653(善化三路) ABS | LINE69 | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | ES3 | 653E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0934 | 935 | 0147 | 1-3A-06 | 1-3A-07 | 2-13 | 653E | ON/OFF | 山上善化三路 653 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.653E_ES | 653E(善化三路) ES | LINE69 | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | ABS1 | 661 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 937 | 0148 | 1-3A-08 | 1-3A-09 | 2-14 | 661 | ON/OFF | 山上新市一路 661 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.661_ABS | 661(新市一路) ABS | LINE69 | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | ABS2 | 662 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 939 | 0149 | 1-3A-10 | 1-3A-11 | 2-15 | 662 | ON/OFF | 山上新市一路 662 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.662_ABS | 662(新市一路) ABS | LINE69 | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | ABS3 | 663 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0940 | 941 | 0150 | 1-3A-12 | 1-3A-13 | 2-16 | 663 | ON/OFF | 山上新市一路 663 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.663_ABS | 663(新市一路) ABS | LINE69 | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | ES3 | 663E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0942 | 943 | 0151 | 1-3A-14 | 1-3A-15 | 2-17 | 663E | ON/OFF | 山上新市一路 663 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.663E_ES | 663E(新市一路) ES | LINE69 | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | ABS1 | 671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0944 | 945 | 0152 | 1-3B-00 | 1-3B-01 | 2-18 | 671 | ON/OFF | 山上新市三路 671 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.671_ABS | 671(山上新市三路) ABS | LINE69 | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | ABS2 | 672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0946 | 947 | 0153 | 1-3B-02 | 1-3B-03 | 2-19 | 672 | ON/OFF | 山上新市三路 672 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.672_ABS | 672(山上新市三路) ABS | LINE69 | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | ABS3 | 673 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0948 | 949 | 0154 | 1-3B-04 | 1-3B-05 | 2-1A | 673 | ON/OFF | 山上新市三路 673 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.673_ABS | 673(山上新市三路) ABS | LINE69 | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | ES3 | 673E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0950 | 951 | 0155 | 1-3B-06 | 1-3B-07 | 2-1B | 673E | ON/OFF | 山上新市三路 673 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.673E_ES | 673E(山上新市三路) ES | LINE69 | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ABS1 | 681 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0952 | 953 | 0156 | 1-3B-08 | 1-3B-09 | 2-1C | 681 | ON/OFF | 山上歸仁線 681 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.681_ABS | 681(歸仁線) ABS | LINE69 | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ABS2 | 682 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0954 | 955 | 0157 | 1-3B-10 | 1-3B-11 | 2-1D | 682 | ON/OFF | 山上歸仁線 682 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.682_ABS | 682(歸仁線) ABS | LINE69 | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ABS3 | 683 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0956 | 957 | 0158 | 1-3B-12 | 1-3B-13 | 2-1E | 683 | ON/OFF | 山上歸仁線 683 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.683_ABS | 683(歸仁線) ABS | LINE69 | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ES3 | 683E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0958 | 959 | 0159 | 1-3B-14 | 1-3B-15 | 2-1F | 683E | ON/OFF | 山上歸仁線 683 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.683E_ES | 683E(歸仁線) ES | LINE69 | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | ABS1 | 711 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 961 | 0160 | 1-3C-00 | 1-3C-01 | 2-20 | 711 | ON/OFF | 山上新市二路 711 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.711_ABS | 711(新市二路) ABS | LINE69 | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | ABS2 | 712 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 963 | 0161 | 1-3C-02 | 1-3C-03 | 2-21 | 712 | ON/OFF | 山上新市二路 712 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.712_ABS | 712(新市二路) ABS | LINE69 | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | ABS3 | 713 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0964 | 965 | 0162 | 1-3C-04 | 1-3C-05 | 2-22 | 713 | ON/OFF | 山上新市二路 713 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.713_ABS | 713(新市二路) ABS | LINE69 | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | ES3 | 713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0966 | 967 | 0163 | 1-3C-06 | 1-3C-07 | 2-23 | 713E | ON/OFF | 山上新市二路 713 EABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.713E_ES | 713E(新市二路) ES | LINE69 | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0968 | 969 | 0164 | 1-3C-08 | 1-3C-09 | 2-24 | 821 | ON/OFF | 69KV #2SC 821 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.821_ABS | 821(69KV #2SC) ABS | SC | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0970 | 971 | 0165 | 1-3C-10 | 1-3C-11 | 2-25 | 822 | ON/OFF | 69KV #2SC 822 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.822_ABS | 822(69KV #2SC) ABS | SC | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0972 | 973 | 0166 | 1-3C-12 | 1-3C-13 | 2-26 | 831 | ON/OFF | 69KV #3SC 831 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.831_ABS | 831(69KV #3SC) ABS | SC | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0974 | 975 | 0167 | 1-3C-14 | 1-3C-15 | 2-27 | 832 | ON/OFF | 69KV #3SC 832 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.832_ABS | 832(69KV #3SC) ABS | SC | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0976 |  | 0000 | 1-3D-00 |  | 1-00 | RTU | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 山上PS.TEST_CB | TEST CB | OTHER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0977 |  |  | 1-3D-01 |  |  | RTU | L/R | L/R STATUS |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0978 |  |  | 1-3D-02 |  |  | #1 SH.R | A/N | #1 SH.R 96B1 |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0979 |  |  | 1-3D-03 |  |  | #1 SH.R | A/N | #1 SH.R 96B2 |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0980 |  |  | 1-3D-04 |  |  | #1 SH.R | A/N | #1 SH.R 96D |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0981 |  |  | 1-3D-05 |  |  | #1 SH.R | A/N | #1 SH.R 96P |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0982 |  |  | 1-3D-06 |  |  | #1 SH.R | A/N | #1 SH.R SRF |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0983 |  |  | 1-3D-07 |  |  | #1 SH.R | A/N | #1 SH.R SRA |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0984 |  |  | 1-3D-08 |  |  | #1 SH.R | A/N | #1 SH.R 87RS |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_87UL | 161KV #1SHR 87RY U/L | OTHER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51Z_UL |  | B3 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0985 |  |  | 1-3D-09 |  |  | #1 SH.R | A/N | #1 SH.R 51S |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1SHR_51UL | 161KV #1SHR 51RY U/L | OTHER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0986 |  |  | 1-3D-10 |  |  | #1 SH.R | A/N | #1 SH.R RYFA |  |  | B2/P06_A1 | [8 empty] | 山上PS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  | B3 | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0987 |  |  | 1-3D-11 |  |  | 161kV#1,2Bus | RYFA | 161kV#1,#2Bus 數位電驛故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0988 |  | 0214 | 1-3D-12 |  | 2-56 | 1710 | U/L 2 | 山上安南豐華紅線1710 #2 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_87UL2 | 安南豐華紅線(1710) #2 87RY U/L | LINE161 | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0989 |  | 0215 | 1-3D-13 |  | 2-57 | 1540 | U/L 2 | 山上鹽行豐華白線1540 #2 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_87UL2 | 鹽行豐華白線(1540) #2 87RY U/L | LINE161 | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | BUS_RYFA |  | B2,B3 | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0990 |  |  | 1-3D-14 |  |  | 69kV BUS | RYFA | 69KV BUS數位電驛故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | 87CTFA |  | B3 | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0991 |  |  | 1-3D-15 |  |  | 69kV BUS | A/N | 69KV BUS 87RY CT 迴路故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1024 |  |  | 2-30-00 |  |  | #1MTR | S/L | #1MTR OLTC S/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS |  |  | 1MTR | #1MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1025 |  | 0194 | 2-30-01 |  | 2-42 | #1MTR | A/M | #1MTR OLTC A/M |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P06 | 山上PS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 1026 |  |  | 2-30-02 |  |  | #1MTR | A/N | #1MTR 重故障 |  | a | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_TRA | #1MTR 重故障 | MTR | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1027 |  |  | 2-30-03 |  |  | #1MTR | A/N | #1MTR 輕故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_TRF | #1MTR 輕故障 | MTR | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1028 | 1029 | 0196 | 2-30-04 | 2-30-05 | 2-44 | #1MTR | M/F/I | #1MTR M/F/I |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  | 0278 | 2-30-06 |  | 3-16 | #1MTR | U/L | #1MTR #1 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1031 |  |  | 2-30-07 |  |  | #2MTR | S/L | #2MTR OLTC S/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS |  |  | 2MTR | #2MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1032 |  | 0198 | 2-30-08 |  | 2-46 | #2MTR | A/M | #2MTR OLTC A/M |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P06 | 山上PS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 1033 |  |  | 2-30-09 |  |  | #2MTR | A/N | #2MTR 重故障 |  | a | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_TRA | #2MTR 重故障 | MTR | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1034 |  |  | 2-30-10 |  |  | #2MTR | A/N | #2MTR 輕故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_TRF | #2MTR 輕故障 | MTR | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1035 |  | 0281 | 2-30-11 |  | 3-19 | #2MTR | U/L | #2MTR #1 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 2MTR | #2MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1036 | 1037 | 0200 | 2-30-12 | 2-30-13 | 2-48 | #2MTR | M/F/I | #2MTR M/F/I |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1038 |  |  | 2-30-14 |  |  | #3MTR | S/L | #3MTR OLTC S/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS |  |  | 3MTR | #3MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1039 |  | 0202 | 2-30-15 |  | 2-4A | #3MTR | A/M | #3MTR OLTC A/M |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P06 | 山上PS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 1040 |  |  | 2-31-00 |  |  | #3MTR | A/N | #3MTR 重故障 |  | a | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_TRA | #3MTR 重故障 | MTR | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1041 |  |  | 2-31-01 |  |  | #3MTR | A/N | #3MTR 輕故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_TRF | #3MTR 輕故障 | MTR | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1042 | 1043 | 0204 | 2-31-02 | 2-31-03 | 2-4C | #3MTR | M/F/I | #3MTR M/F/I |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  | 0284 | 2-31-04 |  | 3-1C | #3MTR | U/L | #3MTR #1 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1045 |  | 0168 | 2-31-05 |  | 2-28 | 1510 | U/L | 嘉義新營山上紅線 1510 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_79UL | 嘉義新營紅線(1510) 79RY U/L | LINE161 | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1047 |  | 0170 | 2-31-07 |  | 2-2A | 1520 | U/L | 嘉義新營山上白線 1520 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_79UL | 嘉義新營白線(1520) 79RY U/L | LINE161 | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1048 |  | 0171 | 2-31-08 |  | 2-2B | 1520 | U/L | 嘉義新營山上白線 1520 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_87UL | 嘉義新營白線(1520) 87RY U/L | LINE161 | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1049 |  | 0172 | 2-31-09 |  | 2-2C | 1570 | U/L | 龍崎山上一路 1570 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_79UL | 龍崎一路(1570) 79RY U/L | LINE161 | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1050 |  | 0173 | 2-31-10 |  | 2-2D | 1570 | U/L | 龍崎山上一路 1570 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_87UL | 龍崎山上一路(1570) 87RY U/L | LINE161 | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1051 |  | 0174 | 2-31-11 |  | 2-2E | 1580 | U/L | 龍崎山上二路 1580 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_79UL | 龍崎二路(1580) 79RY U/L | LINE161 | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1052 |  | 0175 | 2-31-12 |  | 2-2F | 1580 | U/L | 龍崎山上二路 1580 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_87UL | 龍崎山上二路(1580) 87RY U/L | LINE161 | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1053 |  | 0176 | 2-31-13 |  | 2-30 | 1610 | U/L | 龍崎山上二甲三路 1610 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_79UL | 龍崎二甲三路(1610) 79RY U/L | LINE161 | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1054 |  | 0177 | 2-31-14 |  | 2-31 | 1610 | U/L | 龍崎山上二甲三路 1610 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_87UL | 龍崎二甲三路(1610) 87RY U/L | LINE161 | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1055 |  | 0178 | 2-31-15 |  | 2-32 | 1620 | U/L | 龍崎山上二甲四路 1620 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_79UL | 龍崎二甲四路(1620) 79RY U/L | LINE161 | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1056 |  | 0179 | 2-32-00 |  | 2-33 | 1620 | U/L | 龍崎山上二甲四路 1620 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_87UL | 龍崎二甲四路(1620) 87RY U/L | LINE161 | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1057 |  | 0180 | 2-32-01 |  | 2-34 | 1630 | U/L | 山上仁德線 1630 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_79UL | 山上仁德線(1630) 79RY U/L | LINE161 | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1059 |  | 0182 | 2-32-03 |  | 2-36 | 1640 | U/L | 山上台南海線 1640 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_79UL | 台南海線(1640) 79RY U/L | LINE161 | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1060 |  | 0183 | 2-32-04 |  | 2-37 | 1640 | U/L | 山上台南海線 1640 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_87UL | 台南海線(1640) 87RY U/L | LINE161 | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1061 |  | 0184 | 2-32-05 |  | 2-38 | 1540 | U/L | 山上鹽行豐華白線1540 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_79UL | 鹽行豐華白線(1540) 79RY U/L | LINE161 | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1062 |  | 0185 | 2-32-06 |  | 2-39 | 1540 | U/L | 山上鹽行豐華白線1540 #1 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_87UL1 | 鹽行豐華白線(1540) #1 87RY U/L | LINE161 | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1063 |  | 0186 | 2-32-07 |  | 2-3A | 1710 | U/L | 山上安南豐華紅線1710 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_79UL | 安南豐華紅線(1710) 79RY U/L | LINE161 | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1064 |  | 0187 | 2-32-08 |  | 2-3B | 1710 | U/L 1 | 山上安南豐華紅線1710 #1 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_87UL1 | 安南豐華紅線(1710) #1 87RY U/L | LINE161 | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1065 |  | 0188 | 2-32-09 |  | 2-3C | 1720 | U/L | 山上新化二路 1720 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_79UL | 新化二路(1720) 79RY U/L | LINE161 | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1066 |  | 0189 | 2-32-10 |  | 2-3D | 1720 | U/L | 山上新化二路 1720 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_87UL | 新化二路(1720) 87RY U/L | LINE161 | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1067 |  | 0190 | 2-32-11 |  | 2-3E | 1730 | U/L | 山上新化一路 1730 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_79UL | 新化一路(1730) 79RY U/L | LINE161 | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1068 |  | 0191 | 2-32-12 |  | 2-3F | 1730 | U/L | 山上新化一路 1730 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_87UL | 新化一路(1730) 87RY U/L | LINE161 | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1069 |  | 0192 | 2-32-13 |  | 2-40 | 630 | U/L | 山上善化一路 630 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_79UL | 善化一路(630) 79RY U/L | LINE69 | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1070 |  | 0193 | 2-32-14 |  | 2-41 | 640 | U/L | 山上善化二路 640 79RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_79UL | 善化二路(640) 79RY U/L | LINE69 | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1071 |  | 0213 | 2-32-15 |  | 2-55 | 161KV #1BUS | U/L | 161KV #1BUS RY 87B1S |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1072 |  | 0212 | 2-33-00 |  | 2-54 | 161KV #2BUS | U/L | 161KV #2BUS RY 87B2S |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1073 |  | 0290 | 2-33-01 |  | 3-22 | 69KV #1BUS | USE/LOCE | 69KV #1 BUS╴87UL |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1074 |  | 0291 | 2-33-02 |  | 3-23 | 69KV #2BUS | USE/LOCE | 69KV #2 BUS╴87UL |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1075 |  |  | 2-33-03 |  |  | 69KV | A/N | 69KV CB 重故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_CBA | 69KV斷路器重故障 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1076 |  |  | 2-33-04 |  |  | 69KV | A/N | 69KV CB 輕故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1077 |  |  | 2-33-05 |  |  | CHG1 | A/N | CHG1 變電充電機故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1078 |  |  | 2-33-06 |  |  | OLTC | A/N | OLTCA(OLTC 15分鐘內連動3次警報) |  |  | B3/P06_A1 | [8 empty] | 山上PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1079 |  |  | 2-33-07 |  |  | 161KV #1BUS | A/N | 161KV#1BUSVUA1 電壓電驛 |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1080 |  |  | 2-33-08 |  |  | 161KV #2BUS | A/N | 161KV#2BUSVUA2 電壓電驛 |  |  | B2/P06_A1 | [8 empty] | 山上PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1081 |  |  | 2-33-09 |  |  | 69KV #1BUS | A/N | 69KV#1BUSVUA1 電壓電驛 |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1082 |  |  | 2-33-10 |  |  | 69KV #2BUS | A/N | 69KV#2BUS VUA2 電壓電驛 |  |  | B2/P06_A1 | [8 empty] | 山上PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1083 |  |  | 2-33-11 |  |  | 同步校核 | A/N | 同步校核 25PFA |  |  | B3/P06_A1 | [8 empty] | 山上PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1084 |  |  | 2-33-12 |  |  | 同步校核 | A/N | 同步校核 25TA |  |  | B3/P06_A1 | [8 empty] | 山上PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1085 |  |  | 2-33-13 |  |  | STUV | A/N | STUV 所內用電警報 |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1086 |  |  | 2-33-14 |  |  | 161KV | A/N | 161KV DCA 直流電源故障 |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1087 |  |  | 2-33-15 |  |  | 161KV | A/N | 161KV CB 重故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1088 |  |  | 2-34-00 |  |  | 161KV | A/N | 161KV CB 輕故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | NCA |  | B2 | Status | 中性點不平衡 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1089 |  |  | 2-34-01 |  |  | #820 | A/N | 69KV #820 SC NCA |  |  | B2/P06_A1 | [8 empty] | 山上PS.820_NCA | 69KV #2SC NCT RY | SC | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | NCA |  | B2 | Status | 中性點不平衡 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1090 |  |  | 2-34-02 |  |  | #830 | A/N | 69KV #830 SC NCA |  |  | B2/P06_A1 | [8 empty] | 山上PS.830_NCA | 69KV #3SC NCT RY | SC | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1091 |  |  | 2-34-03 |  |  | 1520 | A/N | 嘉義新營山上白線1520 87CFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_87CFA | 嘉義新營白線(1520)87RY通訊故障 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1092 |  |  | 2-34-04 |  |  | 1520 | A/N | 嘉義新營山上白線1520 RYFA(電驛故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1520_RYFA | 嘉義新營白線(1520)數位電驛故障 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1093 |  |  | 2-34-05 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/P06_A1 | [8 empty] | 山上PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1094 |  |  | 2-34-06 |  |  | 1720 | A/N | 山上新化二路 1720 87LCFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_87CFA | 山上新化二路(1720)87RY通訊故障 | OTHER | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1095 |  |  | 2-34-07 |  |  | 1730 | A/N | 山上新化一路 1730 87LCFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_87CFA | 山上新化一路(1730)87RY通訊故障 | OTHER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | 87CTFA |  | B3 | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1096 |  |  | 2-34-08 |  |  | 161kV#1,2Bus | CTFA | 161kV#1,#2Bus 差流電驛CT迴路故障警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1097 |  | 0206 | 2-34-09 |  | 2-4E | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/P06_A1 | [8 empty] | 山上PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 1098 |  | 0207 | 2-34-10 |  | 2-4F | ACB TIE | ON/OFF | 所內電源ACB TIE |  |  | B3/P06_A1 | [8 empty] | 山上PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1099 |  | 0208 | 2-34-11 |  | 2-50 | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/P06_A1 | [8 empty] | 山上PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1100 |  |  | 2-34-12 |  |  | 161KV | A/N | 161KV 89A |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1101 |  |  | 2-34-13 |  |  | 69KV | A/N | 69KV 89A |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1102 |  |  | 2-34-14 |  |  | 直流接地故障 | A/N | 直流接地故障 DCE |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 1103 |  |  | 2-34-15 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/P06_A1 | [8 empty] | 山上PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1104 |  |  | 2-35-00 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/P06_A1 | [8 empty] | 山上PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Fire2 | 建物-控制大樓CO2 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1105 |  |  | 2-35-01 |  |  | 火災警報(2) | A/N | 火災警報(2) 建物-控制大樓CO2 |  |  | B3/P06_A1 | [8 empty] | 山上PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1106 |  |  | 2-35-02 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/P06_A1 | [8 empty] | 山上PS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1107 |  |  | 2-35-03 |  |  | 無人化防盜 | A/N | SUPA1 無人化防盜(一)(保全系統) |  |  | B3/P06_A1 | [8 empty] | 山上PS.無人化防盜(1) | 無人化防盜(1) | OTHER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1108 |  |  | 2-35-04 |  |  | 無人化防盜 | A/N | SUPA2 無人化防盜(二) |  |  | B3/P06_A1 | [8 empty] | 山上PS.無人化防盜(2) | 無人化防盜(2) | OTHER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1109 |  |  | 2-35-05 |  |  | 無人化防盜 | A/N | SUPA3 無人化防盜(三) |  |  | B3/P06_A1 | [8 empty] | 山上PS.無人化防盜(3) | 無人化防盜(3) | OTHER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Door1 | 大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1110 |  |  | 2-35-06 |  |  | 無人化門禁 | A/N | DOR1 無人化門禁(一)(大門) |  |  | B3/P06_A1 | [8 empty] | 山上PS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1111 |  |  | 2-35-07 |  |  | 無人化門禁 | A/N | DOR2 無人化門禁(二)(控制室) |  |  | B3/P06_A1 | [8 empty] | 山上PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1112 |  |  | 2-35-08 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/P06_A1 | [8 empty] | 山上PS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1113 |  |  | 2-35-09 |  |  | 空調機 | A/N | 空調機警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1114 |  | 0209 | 2-35-10 |  | 2-51 | FLA |  | 開關場照明監視A |  |  | B3/P06_A1 | [8 empty] | 山上PS.開關場照明(A) | 161KV開關場照明 | OTHER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1115 |  | 0210 | 2-35-11 |  | 2-52 | FLB |  | 開關場照明監視B |  |  | B3/P06_A1 | [8 empty] | 山上PS.開關場照明(B) | 69KV開關場照明 | OTHER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1116 |  |  | 2-35-12 |  |  | 1710 | A/N | 山上安南豐華紅線1710 RYFA(數位電驛故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_RYFA | 安南豐華紅線(1710)數位電驛故障 | OTHER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 山上~王行一路(1710) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1117 |  |  | 2-35-13 |  |  | 1710 | A/N | 山上安南豐華紅線1710 87 CFA(通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1710_87CFA | 安南豐華紅線(1710)87RY通訊故障 | OTHER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1118 |  |  | 2-35-14 |  |  | 1540 | A/N | 山上鹽行豐華白線1540 RYFA(數位電驛故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_RYFA | 鹽行豐華白線(1540)數位電驛故障 | OTHER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 山上~王行二路(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1119 |  |  | 2-35-15 |  |  | 1540 | A/N | 山上鹽行豐華白線1540 87 CFA(通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1540_87CFA | 鹽行豐華白線(1540)87RY通訊故障 | OTHER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1120 |  |  | 2-36-00 |  |  | #1MTR | A/N | #1MTR 96D |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_96D | #1MTR 96D RY | MTR | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1121 |  |  | 2-36-01 |  |  | #1MTR | A/N | #1MTR 96P |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_96P | #1MTR 96P RY | MTR | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1122 |  |  | 2-36-02 |  |  | #1MTR | A/N | #1MTR 63Q |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_63Q | #1MTR 63Q RY | MTR | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1123 |  |  | 2-36-03 |  |  | #1MTR | A/N | #1MTR 96B1 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1124 |  |  | 2-36-04 |  |  | #1MTR | A/N | #1MTR 96B2 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1125 |  |  | 2-36-05 |  |  | #2MTR | A/N | #2MTR 96D |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_96D | #2MTR 96D RY | MTR | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1126 |  |  | 2-36-06 |  |  | #2MTR | A/N | #2MTR 96P |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_96P | #2MTR 96P RY | MTR | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1127 |  |  | 2-36-07 |  |  | #2MTR | A/N | #2MTR 63Q |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_63Q | #2MTR 63Q RY | MTR | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1128 |  |  | 2-36-08 |  |  | #2MTR | A/N | #2MTR 96B1 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1129 |  |  | 2-36-09 |  |  | #2MTR | A/N | #2MTR 96B2 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1130 |  |  | 2-36-10 |  |  | #3MTR | A/N | #3MTR 96D |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_96D | #3MTR 96D RY | MTR | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1131 |  |  | 2-36-11 |  |  | #3MTR | A/N | #3MTR 96P |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_96P | #3MTR 96P RY | MTR | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1132 |  |  | 2-36-12 |  |  | #3MTR | A/N | #3MTR 63Q |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_63Q | #3MTR 63Q RY | MTR | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1133 |  |  | 2-36-13 |  |  | #3MTR | A/N | #3MTR 33A |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1134 |  |  | 2-36-14 |  |  | 87LA | A/N | 山上新化二路 1720 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1720_RYFA | 山上新化二路(1720)數位電驛故障 | OTHER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1135 |  |  | 2-36-15 |  |  | 87LA | A/N | 山上新化一路 1730 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1730_RYFA | 山上新化一路(1730)數位電驛故障 | OTHER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | 85CFA | 豐德山上紅白線 |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1136 |  |  | 2-37-00 |  |  | 1550 1560 | A/N | 豐德山上紅白線 SIGN CHAN FAIL |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_1560_CFA | 豐德紅白線(1550 1560)通訊故障 | OTHER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | RYFA | 豐德山上紅白線 | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1137 |  |  | 2-37-01 |  |  | 1550 1560 | A/N | 豐德山上紅白線 85LRY FAIL |  |  | B2/P06_A1 | [8 empty] | 山上PS.1550_1560_RYFA | 豐德紅白線(1550 1560)RY故障 | OTHER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1138 |  |  | 2-37-02 |  |  | 1510 | A/N | 嘉義新營山上紅 線 1510 RAOA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_87CFA | 嘉義新營紅線(1510)87RY通訊故障 | OTHER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1139 |  |  | 2-37-03 |  |  | 1510 | A/N | 嘉義新營山上紅 線 1510 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1510_RYFA | 嘉義新營紅線(1510)數位電驛故障 | OTHER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1140 |  |  | 2-37-04 |  |  | 1630 | A/N | 山上仁德線 1630 CB RAOA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_87CFA | 山上仁德線(1630)87RY通訊故障 | OTHER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1141 |  |  | 2-37-05 |  |  | 1630 | A/N | 山上仁德線 1630 CB 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1630_RYFA | 山上仁德線(1630)數位電驛故障 | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1142 |  |  | 2-37-06 |  |  | 1570 | A/N | 龍崎山上一路 1570 87LCFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_87CFA | 龍崎一路(1570)87RY通訊故障 | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1143 |  |  | 2-37-07 |  |  | 1570 | A/N | 龍崎山上一路 1570 CB 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_RYFA | 龍崎一路(1570)數位電驛故障 | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1144 |  |  | 2-37-08 |  |  | 1580 | A/N | 龍崎山上二路 1580 87LCFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_87CFA | 龍崎二路(1580)87RY通訊故障 | OTHER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1145 |  |  | 2-37-09 |  |  | 1580 | A/N | 龍崎山上二路 1580 CB 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_RYFA | 龍崎二路(1580)數位電驛故障 | OTHER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1146 |  |  | 2-37-10 |  |  | 1610 | A/N | 龍崎山上二甲三路 1610 87CFA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_87CFA | 龍崎二甲三路(1610)87RY通訊故障 | OTHER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1147 |  |  | 2-37-11 |  |  | 1610 | A/N | 龍崎山上二甲三路 1610 RYFA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_RYFA | 龍崎二甲三路(1610)數位電驛故障 | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1148 |  |  | 2-37-12 |  |  | 1620 | A/N | 龍崎山上二甲四路 1620 87CFA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_87CFA | 龍崎二甲四路(1620)87RY通訊故障 | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1149 |  |  | 2-37-13 |  |  | 1620 | A/N | 龍崎山上二甲四路 1620 RYFA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_RYFA | 龍崎二甲四路(1620)數位電驛故障 | OTHER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1150 |  |  | 2-37-14 |  |  | 1640 | A/N | 山上台南海線 1640 87LCFA(87L通訊故障) |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_87CFA | 台南海線(1640)87RY通訊故障 | OTHER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1151 |  |  | 2-37-15 |  |  | 1640 | A/N | 山上台南海線 1640 87LA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1640_RYFA | 台南海線(1640)數位電驛故障 | OTHER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1152 | 1153 | 0104 | 2-38-00 | 2-38-01 | 1-68 | 1551 | ON/OFF | 豐德山上紅線 1551 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1551_DS | 1551(豐德紅線) DS | LINE161 | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1154 | 1155 | 0105 | 2-38-02 | 2-38-03 | 1-69 | 1552 | ON/OFF | 豐德山上紅線 1552 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1552_DS | 1552(豐德紅線) DS | LINE161 | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1156 | 1157 | 0106 | 2-38-04 | 2-38-05 | 1-6A | 1553 | ON/OFF | 豐德山上紅線 1553 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1553_DS | 1553(豐德紅線) DS | LINE161 | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1158 | 1159 | 0107 | 2-38-06 | 2-38-07 | 1-6B | 1553E | ON/OFF | 豐德山上紅線 1553E ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1553E_ES | 1553E(豐德紅線) ES | LINE161 | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | DS1 | 1561 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1160 | 1161 | 0108 | 2-38-08 | 2-38-09 | 1-6C | 1561 | ON/OFF | 豐德山上白線 1561 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1561_DS | 1561(豐德白線) DS | LINE161 | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | DS2 | 1562 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1162 | 1163 | 0109 | 2-38-10 | 2-38-11 | 1-6D | 1562 | ON/OFF | 豐德山上白線 1562 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1562_DS | 1562(豐德白線) DS | LINE161 | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | DS3 | 1563 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1164 | 1165 | 0110 | 2-38-12 | 2-38-13 | 1-6E | 1563 | ON/OFF | 豐德山上白線 1563 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1563_DS | 1563(豐德白線) DS | LINE161 | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1166 | 1167 | 0111 | 2-38-14 | 2-38-15 | 1-6F | 1563E | ON/OFF | 豐德山上白線 1563E ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1563E_ES | 1563E(豐德白線) ES | LINE161 | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1168 |  |  | 2-39-00 |  |  | 1570 | A/N | 龍崎山上一路 1570 CB DTTA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1570_DTTA | 龍崎一路(1570) 遠方遙跳 | OTHER | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1169 |  |  | 2-39-01 |  |  | 1580 | A/N | 龍崎山上二路 1580 CB DTTA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1580_DTTA | 龍崎二路(1580) 遠方遙跳 | OTHER | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1170 |  |  | 2-39-02 |  |  | 1610 | A/N | 龍崎山上二甲三路 1610 CB DTTA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1610_DTTA | 龍崎二甲三路(1610) 遠方遙跳 | OTHER | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1171 |  |  | 2-39-03 |  |  | 1620 | A/N | 龍崎山上二甲四路 1620 CB DTTA |  |  | B2/P06_A1 | [8 empty] | 山上PS.1620_DTTA | 龍崎二甲四路(1620) 遠方遙跳 | OTHER | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1172 |  |  | 2-39-04 |  |  | Locate Empty | A/N | 通訊設備 AC故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1173 |  |  | 2-39-05 |  |  | Locate Empty | A/N | 通訊充電機故障 |  |  | B3/P06_A1 | [8 empty] | 山上PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1175 |  |  | 2-39-07 |  |  | Locate Empty | A/N | 通信室溫控警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1176 |  |  | 2-39-08 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1177 |  |  | 2-39-09 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/P06_A1 | [8 empty] | 山上PS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1178 |  |  | 2-39-10 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/P06_A1 | [8 empty] | 山上PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1179 |  |  | 2-39-11 |  |  | OSCF | A/N | 69KV示波器缺紙或故障警報OSCF |  |  | B3/P06_A1 | [8 empty] | 山上PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS1 | 1951 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1180 | 1181 | 0112 | 2-39-12 | 2-39-13 | 1-70 | 1951 | ON/OFF | #1 SH.R 1951 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1951_ABS | 1951(161KV #1SHR) ABS | OTHER | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS2 | 1952 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1182 | 1183 | 0113 | 2-39-14 | 2-39-15 | 1-71 | 1952 | ON/OFF | #1 SH.R 1952 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1952_ABS | 1952(161KV #1SHR) ABS | OTHER | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1184 |  | 0270 | 2-3A-00 |  | 3-0E | #6DTR | USE/LOCK | #6 DTR 87 RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_87UL | #6DTR 87RY U/L | OTHER | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1185 |  |  | 2-3A-01 |  |  | #6DTR | USE/LOCK | #6 DTR 87-2 RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_87-2UL | #6DTR 87-2RY U/L | OTHER | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1186 |  |  | 2-3A-02 |  |  | #6DTR | USE/LOCK | #6 DTR 51Z U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_51ZUL | #6DTR 51Z RY U/L | OTHER | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 6DTR(A) | #6DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1187 |  |  | 2-3A-03 |  |  | #6DTR | S/L | #6 DTR (A) S/L |  | c | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_S/L | #6DTR(A) OLTC S/L | MTR | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS |  |  | 6DTR(A) | #6DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1188 |  | 0266 | 2-3A-04 |  | 3-0A | #6DTR | A/M | #6 DTR (A) OLTC A/M |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(A)_A/M | #6DTR(A) OLTC A/M | MTR | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P06 | 山上PS |  |  | 6DTR | #6DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1189 |  |  | 2-3A-05 |  |  | #6DTR | TRF | #6 DTR 輕故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_TRF | #6DTR 輕故障 | MTR | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 1190 |  |  | 2-3A-06 |  |  | #6DTR | TRA | #6 DTR 重故障 |  | a | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_TRA | #6DTR 重故障 | MTR | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR(B) | #6DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1191 |  |  | 2-3A-07 |  |  | #6DTR | S/L | #6 DTR (B) S/L |  | b | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_S/L | #6DTR(B) OLTC S/L | MTR | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS |  |  | 6DTR(B) | #6DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1192 |  | 0268 | 2-3A-08 |  | 3-0C | #6DTR | A/M | #6 DTR (B) OLTC A/M |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR(B)_A/M | #6DTR(B) OLTC A/M | MTR | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1193 |  |  | 2-3A-09 |  |  | #6DTR | ON/OFF | #6DTR 96P |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_96P | #6DTR 96P RY | MTR | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1194 |  |  | 2-3A-10 |  |  | #6DTR | ON/OFF | #6DTR 96D |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_96D | #6DTR 96D RY | MTR | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1195 |  |  | 2-3A-11 |  |  | #6DTR | ON/OFF | #6DTR 96B1 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_96B1 | #6DTR 96B1 RY | MTR | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1196 |  |  | 2-3A-12 |  |  | #6DTR | ON/OFF | #6DTR 96B2 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_96B2 | #6DTR 96B2 RY | MTR | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1197 |  |  | 2-3A-13 |  |  | #6DTR | ON/OFF | #6DTR 63Q |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_63Q | #6DTR 63Q RY | MTR | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1198 |  |  | 2-3A-14 |  |  | #6DTR | RYFA | #6DTR 數位電驛故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_RYFA | #6DTR 數位電驛故障 | OTHER | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 6DTR | #6DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1199 |  |  | 2-3A-15 |  |  | #6 DTR | 86A | #6 DTR 86(50/50N/51Z/87/96)Ry |  |  | B1/P06_A1 | [8 empty] | 山上PS.#6DTR_86A | #6DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1200 |  | 0271 | 2-3B-00 |  | 3-0F | 630 | U/L | 山上善化一路 630 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_87UL | 山上善化一路(630) 87RY U/L | OTHER | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1201 |  |  | 2-3B-01 |  |  | 630 | 87CFA | 山上善化一路 630 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_87CFA | 山上善化一路(630)87RY通訊故障 | OTHER | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1202 |  |  | 2-3B-02 |  |  | 630 | RYFA | 山上善化一路 630 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.630_RYFA | 山上善化一路(630)數位電驛故障 | OTHER | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 330 | #6DTR(A)(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1204 |  | 0233 | 2-3B-04 |  | 2-69 | 330(M1A) | U/L | 低頻電驛動作 330(M1A) 81Ry U/L |  |  | B3/P06_A1 | [8 empty] | 山上PS.330_81UL | 330(#6DTR) 81RY U/L | OTHER | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 340 | #6DTR(B)(340) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1206 |  | 0234 | 2-3B-06 |  | 2-6A | 340(M1B) | U/L | 低頻電驛動作 340(M1B) 81Ry U/L |  |  | B3/P06_A1 | [8 empty] | 山上PS.340_81UL | 340(#6DTR) 81RY U/L | OTHER | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1207 |  | 0235 | 2-3B-07 |  | 2-6B | 上11(4E11) | U/L | 上11(4E11) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E11_79UL | 11KV上11線(4E11) 79RY U/L | FEEDER | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1208 |  | 0236 | 2-3B-08 |  | 2-6C | 上11(4E11) | U/L | 上11(4E11) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E11_LCO_TAP | 11KV上11線(4E11) LCO TAP | FEEDER | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1209 |  | 0237 | 2-3B-09 |  | 2-6D | 上12(4E12) | U/L | 上12(4E12) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E12_79UL | 11KV上12線(4E12) 79RY U/L | FEEDER | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1210 |  | 0238 | 2-3B-10 |  | 2-6E | 上12(4E12) | U/L | 上12(4E12) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E12_LCO_TAP | 11KV上12線(4E12) LCO TAP | FEEDER | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1211 |  | 0239 | 2-3B-11 |  | 2-6F | 上13(4E13) | U/L | 上13(4E13) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E13_79UL | 11KV上13線(4E13) 79RY U/L | FEEDER | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1212 |  | 0240 | 2-3B-12 |  | 2-70 | 上13(4E13) | U/L | 上13(4E13) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E13_LCO_TAP | 11KV上13線(4E13) LCO TAP | FEEDER | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1213 |  | 0241 | 2-3B-13 |  | 2-71 | 上14(4E14) | U/L | 上14(4E14) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E14_79UL | 11KV上14線(4E14) 79RY U/L | FEEDER | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1214 |  | 0242 | 2-3B-14 |  | 2-72 | 上14(4E14) | U/L | 上14(4E14) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E14_LCO_TAP | 11KV上14線(4E14) LCO TAP | FEEDER | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1215 |  | 0243 | 2-3B-15 |  | 2-73 | 上15(4E15) | U/L | 上15(4E15) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E15_79UL | 11KV上15線(4E15) 79RY U/L | FEEDER | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1216 |  | 0244 | 2-3C-00 |  | 2-74 | 上15(4E15) | U/L | 上15(4E15) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E15_LCO_TAP | 11KV上15線(4E15) LCO TAP | FEEDER | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1217 |  | 0245 | 2-3C-01 |  | 2-75 | 上16(4E16) | U/L | 上16(4E16) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E16_79UL | 11KV上16線(4E16) 79RY U/L | FEEDER | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1218 |  | 0246 | 2-3C-02 |  | 2-76 | 上16(4E16) | U/L | 上16(4E16) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E16_LCO_TAP | 11KV上16線(4E16) LCO TAP | FEEDER | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1219 |  | 0247 | 2-3C-03 |  | 2-77 | 上17(4E17) | U/L | 上17(4E17) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E17_79UL | 11KV上17線(4E17) 79RY U/L | FEEDER | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1220 |  | 0256 | 2-3C-04 |  | 3-00 | 上17(4E17) | U/L | 上17(4E17) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E17_LCO_TAP | 11KV上17線(4E17) LCO TAP | FEEDER | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1221 |  | 0257 | 2-3C-05 |  | 3-01 | 上18(4E18) | U/L | 上18(4E18) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E18_79UL | 11KV上18線(4E18) 79RY U/L | FEEDER | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1222 |  | 0258 | 2-3C-06 |  | 3-02 | 上18(4E18) | U/L | 上18(4E18) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E18_LCO_TAP | 11KV上18線(4E18) LCO TAP | FEEDER | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1223 |  | 0259 | 2-3C-07 |  | 3-03 | 上19(4E19) | U/L | 上19(4E19) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E19_79UL | 11KV上19線(4E19) 79RY U/L | FEEDER | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1224 |  | 0260 | 2-3C-08 |  | 3-04 | 上19(4E19) | U/L | 上19(4E19) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E19_LCO_TAP | 11KV上19線(4E19) LCO TAP | FEEDER | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | 79UL |  | B3 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1225 |  | 0261 | 2-3C-09 |  | 3-05 | 上20(4E20) | U/L | 上20(4E20) 79Ry U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E20_79UL | 11KV上20線(4E20) 79RY U/L | FEEDER | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | 51_51NUL |  | B3 | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1226 |  | 0262 | 2-3C-10 |  | 3-06 | 上20(4E20) | U/L | 上20(4E20) 51N U/L |  |  | B2/P06_D1 | [8 empty] | 山上PS.4E20_LCO_TAP | 11KV上20線(4E20) LCO TAP | FEEDER | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P06 | 山上PS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1227 |  |  | 2-3C-11 |  |  | CBA | A/N | 23kV CBA |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1228 |  |  | 2-3C-12 |  |  | CBF | A/N | 23kV CBF |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 1229 |  |  | 2-3C-13 |  |  | SC | A/N | 23kV SC 60A |  |  | B3/P06_A1 | [8 empty] | 山上PS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1230 |  |  | 2-3C-14 |  |  | Locate Empty | A/N | PMA |  |  | ELEM/P06_A1 | [8 empty] | 山上PS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1231 |  |  | 2-3C-15 |  |  | Locate Empty | A/N | 11/23kV 79Ry復閉失敗 |  |  | B3/P06_A1 | [8 empty] | 山上PS.11/23KV_RCA | 11/23KV饋線79RY復閉失敗 | OTHER | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1232 |  | 0272 | 2-3D-00 |  | 3-10 | 640 | U/L | 山上善化二路 640 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_87UL | 山上善化二路(640) 87RY U/L | OTHER | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1233 |  |  | 2-3D-01 |  |  | 640 | 87CFA | 山上善化二路 640 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_87CFA | 山上善化二路(640)87RY通訊故障 | OTHER | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1234 |  |  | 2-3D-02 |  |  | 640 | RYFA | 山上善化二路 640 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.640_RYFA | 山上善化二路(640)數位電驛故障 | OTHER | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1235 |  | 0273 | 2-3D-03 |  | 3-11 | 650 | U/L | 山上善化三路 650 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_87UL | 山上善化三路(650) 87RY U/L | OTHER | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1236 |  |  | 2-3D-04 |  |  | 650 | 87CFA | 山上善化三路 650 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_87CFA | 山上善化三路(650)87RY通訊故障 | OTHER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1237 |  |  | 2-3D-05 |  |  | 650 | RYFA | 山上善化三路 650 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.650_RYFA | 山上善化三路(650)數位電驛故障 | OTHER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1238 |  | 0274 | 2-3D-06 |  | 3-12 | 670 | U/L | 山上新市三路 670 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_87UL | 山上新市三路(670) 87RY U/L | OTHER | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1239 |  |  | 2-3D-07 |  |  | 670 | 87CFA | 山上新市三路 670 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_87CFA | 山上新市三路(670)87RY通訊故障 | OTHER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS1 | 1761 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1240 | 1241 | 0264 | 2-3D-08 | 2-3D-09 | 3-08 | 1761 | ON | #6 DTR 1761 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1761_ABS | 1761(#6DTR) ABS | MTR | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS2 | 1762 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1242 | 1243 | 0265 | 2-3D-10 | 2-3D-11 | 3-09 | 1762 | ON | #6 DTR 1762 ABS |  |  | B2/P06_A1 | [8 empty] | 山上PS.1762_ABS | 1762(#6DTR) ABS | MTR | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1244 |  |  | 2-3D-12 |  |  | 670 | RYFA | 山上新市三路 670 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.670_RYFA | 山上新市三路(670)數位電驛故障 | OTHER | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1245 |  | 0275 | 2-3D-13 |  | 3-13 | 680 | U/L | 山上歸仁線 680 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_87UL | 山上歸仁線(680) 87RY U/L | OTHER | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1246 |  |  | 2-3D-14 |  |  | 680 | 87CFA | 山上歸仁線 680 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_87CFA | 山上歸仁線(680)87RY通訊故障 | OTHER | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1247 |  |  | 2-3D-15 |  |  | 680 | RYFA | 山上歸仁線 680 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.680_RYFA | 山上歸仁線(680)數位電驛故障 | OTHER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1248 |  | 0276 | 2-3E-00 |  | 3-14 | 710 | U/L | 山上新市二路 710 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_87UL | 山上新市二路(710) 87RY U/L | OTHER | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1249 |  |  | 2-3E-01 |  |  | 710 | 87CFA | 山上新市二路 710 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_87CFA | 山上新市二路(710)87RY通訊故障 | OTHER | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1250 |  |  | 2-3E-02 |  |  | 710 | RYFA | 山上新市二路 710 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.710_RYFA | 山上新市二路(710)數位電驛故障 | OTHER | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1251 |  | 0277 | 2-3E-03 |  | 3-15 | 660 | U/L | 山上新市一路 660 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_87UL | 山上新市一路(660) 87RY U/L | OTHER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1252 |  |  | 2-3E-04 |  |  | 660 | 87CFA | 山上新市一路 660 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_87CFA | 山上新市一路(660)87RY通訊故障 | OTHER | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1253 |  |  | 2-3E-05 |  |  | 660 | RYFA | 山上新市一路 660 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.660_RYFA | 山上新市一路(660)數位電驛故障 | OTHER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1254 |  | 0279 | 2-3E-06 |  | 3-17 | #1MTR | U/L | #1MTR #2 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 1MTR | #1MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1255 |  |  | 2-3E-07 |  |  | #1MTR | RYFA | #1MTr . 數位電驛故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 1MTR | #1MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1256 |  | 0280 | 2-3E-08 |  | 3-18 | #1MTR | U/L | #1MTR 51Z RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1257 |  | 0282 | 2-3E-09 |  | 3-1A | #2MTR | U/L | #2MTR #2 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 2MTR | #2MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1258 |  |  | 2-3E-10 |  |  | #2MTR | RYFA | #2MTr . 數位電驛故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 2MTR | #2MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1259 |  | 0283 | 2-3E-11 |  | 3-1B | #2MTR | U/L | #2MTR 51Z RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1260 |  | 0285 | 2-3E-12 |  | 3-1D | #3MTR | U/L | #3MTR #2 87RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS |  |  | 3MTR | #3MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1261 |  |  | 2-3E-13 |  |  | #3MTR | RYFA | #3MTr . 數位電驛故障 |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS |  |  | 3MTR | #3MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1262 |  | 0286 | 2-3E-14 |  | 3-1E | #3MTR | U/L | #3MTR 51Z RY U/L |  |  | B1/P06_A1 | [8 empty] | 山上PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1263 |  |  | 2-3E-15 |  |  | 600 | RYFA | 69kV TIE 600數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1264 |  |  | 2-3F-00 |  |  | 620 | U/L | 山上山頂二路 620 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_87UL | 山頂二路(620) 87RY U/L | LINE69 | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1265 |  |  | 2-3F-01 |  |  | 620 | 87CFA | 山上山頂二路 620 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_87CFA | 山上山頂二路(620)87RY通訊故障 | OTHER | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1266 |  |  | 2-3F-02 |  |  | 620 | RYFA | 山上山頂二路 620 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.620_RYFA | 山上山頂二路(620)數位電驛故障 | OTHER | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1267 |  |  | 2-3F-03 |  |  | 610 | U/L | 山上山頂一路 610 87RY U/L |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_87UL | 山頂一路(610) 87RY U/L | LINE69 | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1268 |  |  | 2-3F-04 |  |  | 610 | 87CFA | 山上山頂一路 610 87RY通訊故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_87CFA | 山上山頂一路(610)87RY通訊故障 | OTHER | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1269 |  |  | 2-3F-05 |  |  | 610 | RYFA | 山上山頂一路 610 數位電驛故障 |  |  | B2/P06_A1 | [8 empty] | 山上PS.610_RYFA | 山上山頂一路(610)數位電驛故障 | OTHER | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | E1 | 11(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | E1 | 12(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | E1 | 13(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | E1 | 14(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | E1 | 15(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | E1 | 16(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | E1 | 17(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | E1 | 18(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | E1 | 19(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | E1 | 20(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 6APT | #6APT |  | ES | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | BayFdrF | B/6ABUS | T/6APT | [12 empty] | aaab | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 6APT | #6APT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 6ABE | #6ABE |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1EthA | B/6ABUS | [13 empty] | aafb | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 6BPT | #6BPT |  | ES | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | BayFdrF | B/6BBUS | T/6BPT | [12 empty] | abjb | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P06 | 山上PS | 11 | 11kV | 6BPT | #6BPT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P06_A1 | [8 empty] | 山上PS.11DS | 11DS (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 6BBE | #6BBE |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1EthA | B/6BBUS | [13 empty] | abab | B3/P06_A1 | [8 empty] | 山上PS.11ES | 11ES (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
P06 | 山上PS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: P06/161/1BUS/V; OPRD2: P06/161/2BUS/V
P06 | 山上PS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: P06/69/1BUS/V; OPRD2: P06/69/2BUS/V
P06 | 山上PS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/P06_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: P06/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: P06/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
P06 | 山上PS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/P06_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_26 | OPRD1: P06/161/1510/MW; OPRD2: P06/161/1520/MW; OPRD3: P06/161/1540/MW; OPRD4: P06/161/1550/MW; OPRD5: P06/161/1560/MW; OPRD6: P06/161/1570/MW; OPRD7: P06/161/1580/MW; OPRD8: P06/161/1610/MW; OPRD9: P06/161/1620/MW; OPRD10: P06/161/1630/MW; OPRD11: P06/161/1640/MW; OPRD12: P06/161/1710/MW; OPRD13: P06/161/1720/MW; OPRD14: P06/161/1730/MW; OPRD15: P06/69/610/MW; OPRD16: P06/69/620/MW; OPRD17: P06/69/630/MW; OPRD18: P06/69/640/MW; OPRD19: P06/69/650/MW; OPRD20: P06/69/660/MW; OPRD21: P06/69/670/MW; OPRD22: P06/69/680/MW; OPRD23: P06/69/710/MW; OPRD24: P06/69/750/MW; OPRD25: P06/69/760/MW; OPRD26: P06/69/770/MW
P06 | 山上PS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/P06_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: P06/0/CalcPoint/OPRN2_MW
P06 | 山上PS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/P06_A1 | [17 empty] | none
P06 | 山上PS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/P06_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: P06/0/CalcPoint/OPRN1; OPRD2: P06/0/CalcPoint/OPRN2; OPRD3: P06/0/CalcPoint/PRFL_UL
P06 | 山上PS |  |  | 6DTR | 6DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P06/11/330/I_R; OPRD2: P06/11/340/I_R
P06 | 山上PS |  |  | 6DTR | 6DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P06/11/330/I_S; OPRD2: P06/11/340/I_S
P06 | 山上PS |  |  | 6DTR | 6DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P06/11/330/I_T; OPRD2: P06/11/340/I_T
P06 | 山上PS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P06_A1 | [12 empty] | 山上PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P06/69/750/MW; OPRD2: P06/69/750/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P06_A1 | [12 empty] | 山上PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P06/69/760/MW; OPRD2: P06/69/760/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P06_A1 | [12 empty] | 山上PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P06/69/770/MW; OPRD2: P06/69/770/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義～新營、山上紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1510_AMP | 嘉義新營紅線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P06/161/1510/MW; OPRD2: P06/161/1510/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義～新營、山上白線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1520_AMP | 嘉義新營白線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P06/161/1520/MW; OPRD2: P06/161/1520/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1540 | 山上～鹽行、豐華白線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1540_AMP | 鹽行豐華白線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P06/161/1540/MW; OPRD2: P06/161/1540/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1550 | 豐德～山上紅線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1550_AMP | 豐德紅線 AMP | LINE161 | AMP_CAL | C40R3652 | amp_cal | OPRD1: P06/161/1550/MW; OPRD2: P06/161/1550/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1560 | 豐德～山上白線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1560_AMP | 豐德白線 AMP | LINE161 | AMP_CAL | C40R3652 | amp_cal | OPRD1: P06/161/1560/MW; OPRD2: P06/161/1560/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎～山上一路(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1570_AMP | 龍崎一路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P06/161/1570/MW; OPRD2: P06/161/1570/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎～山上二路(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1580_AMP | 龍崎二路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P06/161/1580/MW; OPRD2: P06/161/1580/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1610_AMP | 龍崎二甲三路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P06/161/1610/MW; OPRD2: P06/161/1610/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1620_AMP | 龍崎二甲四路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P06/161/1620/MW; OPRD2: P06/161/1620/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1630 | 山上～仁德線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1630_AMP | 山上仁德線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P06/161/1630/MW; OPRD2: P06/161/1630/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1640 | 山上～台南海線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1640_AMP | 台南海線 AMP | LINE161 | AMP_CAL | C16R1328 | amp_cal | OPRD1: P06/161/1640/MW; OPRD2: P06/161/1640/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1710 | 山上～安南、豐華紅線(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1710_AMP | 安南豐華紅線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: P06/161/1710/MW; OPRD2: P06/161/1710/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1720_AMP | 山上新化二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P06/161/1720/MW; OPRD2: P06/161/1720/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 161 | 161kV | 1730 | 山上～新化一路(1730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.1730_AMP | 山上新化一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P06/161/1730/MW; OPRD2: P06/161/1730/MVAR; OPRD3: P06/0/CalcPoint/Vbs4
P06 | 山上PS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.610_AMP | 山頂一路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: P06/69/610/MW; OPRD2: P06/69/610/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.620_AMP | 山頂二路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: P06/69/620/MW; OPRD2: P06/69/620/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 630 | 山上～善化一路(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.630_AMP | 善化一路 AMP | LINE69 | AMP_CAL | C12R0640 | amp_cal | OPRD1: P06/69/630/MW; OPRD2: P06/69/630/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 640 | 山上～善化二路(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.640_AMP | 善化二路 AMP | LINE69 | AMP_CAL | C12R0640 | amp_cal | OPRD1: P06/69/640/MW; OPRD2: P06/69/640/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 650 | 山上～善化三路(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.650_AMP | 善化三路 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P06/69/650/MW; OPRD2: P06/69/650/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 660 | 山上～新市一路(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.660_AMP | 新市一路 AMP | LINE69 | AMP_CAL | C16R0879 | amp_cal | OPRD1: P06/69/660/MW; OPRD2: P06/69/660/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 670 | 山上～新市三路(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.670_AMP | 山上新市三路 AMP | LINE69 | AMP_CAL | C12R0947 | amp_cal | OPRD1: P06/69/670/MW; OPRD2: P06/69/670/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.680_AMP | 歸仁線 AMP | LINE69 | AMP_CAL | C12R0947 | amp_cal | OPRD1: P06/69/680/MW; OPRD2: P06/69/680/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS | 69 | 69kV | 710 | 山上～新市二路(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.710_AMP | 新市二路 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P06/69/710/MW; OPRD2: P06/69/710/MVAR; OPRD3: P06/0/CalcPoint/Vbs2
P06 | 山上PS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P06_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 山上PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P06/69/750/MW; OPRD2: P06/69/750/MVAR
P06 | 山上PS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P06_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 山上PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P06/69/760/MW; OPRD2: P06/69/760/MVAR
P06 | 山上PS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P06_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 山上PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P06/69/770/MW; OPRD2: P06/69/770/MVAR
P06 | 山上PS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#1MTR_LOAD | #1MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P06//1MTR/MVA; OPRD2: 0
P06 | 山上PS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#2MTR_LOAD | #2MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P06//2MTR/MVA; OPRD2: 0
P06 | 山上PS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#3MTR_LOAD | #3MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P06//3MTR/MVA; OPRD2: 0
P06 | 山上PS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#1MTR_PF | #1MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P06/69/750/MW; OPRD2: P06/69/750/MVAR
P06 | 山上PS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#2MTR_PF | #2MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P06/69/760/MW; OPRD2: P06/69/760/MVAR
P06 | 山上PS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#3MTR_PF | #3MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P06/69/770/MW; OPRD2: P06/69/770/MVAR
P06 | 山上PS |  |  | 6DTR(A) | #6DTR(A) |  | TR_PERM | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#6DTR(A)_PERM | #6DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P06//6DTR(A)/SupLocal; OPRD2: P06//6DTR(A)/Tap Chan
P06 | 山上PS |  |  | 6DTR(B) | #6DTR(B) |  | TR_PERM | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#6DTR(B)_PERM | #6DTR(B) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P06//6DTR(B)/SupLocal; OPRD2: P06//6DTR(B)/Tap Chan
P06 | 山上PS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P06//1MTR/SupLocal; OPRD2: P06//1MTR/Tap Chan; OPRD3: P06//1MTR/M_F_I
P06 | 山上PS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P06//2MTR/SupLocal; OPRD2: P06//2MTR/Tap Chan; OPRD3: P06//2MTR/M_F_I
P06 | 山上PS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/P06_A1 | [12 empty] | 山上PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P06//3MTR/SupLocal; OPRD2: P06//3MTR/Tap Chan; OPRD3: P06//3MTR/M_F_I
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E11/I_R; OPRD3: P06/11/4E11/I_S; OPRD4: P06/11/4E11/I_T
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E12/I_R; OPRD3: P06/11/4E12/I_S; OPRD4: P06/11/4E12/I_T
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E13/I_R; OPRD3: P06/11/4E13/I_S; OPRD4: P06/11/4E13/I_T
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E14/I_R; OPRD3: P06/11/4E14/I_S; OPRD4: P06/11/4E14/I_T
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E15/I_R; OPRD3: P06/11/4E15/I_S; OPRD4: P06/11/4E15/I_T
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E16/I_R; OPRD3: P06/11/4E16/I_S; OPRD4: P06/11/4E16/I_T
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E17/I_R; OPRD3: P06/11/4E17/I_S; OPRD4: P06/11/4E17/I_T
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E18/I_R; OPRD3: P06/11/4E18/I_S; OPRD4: P06/11/4E18/I_T
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E19/I_R; OPRD3: P06/11/4E19/I_S; OPRD4: P06/11/4E19/I_T
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P06/11/4E20/I_R; OPRD3: P06/11/4E20/I_S; OPRD4: P06/11/4E20/I_T
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E11/kVA; OPRD2: P06/11/4E11/KVAR
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E12/kVA; OPRD2: P06/11/4E12/KVAR
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E13/kVA; OPRD2: P06/11/4E13/KVAR
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E14/kVA; OPRD2: P06/11/4E14/KVAR
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E15/kVA; OPRD2: P06/11/4E15/KVAR
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E16/kVA; OPRD2: P06/11/4E16/KVAR
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E17/kVA; OPRD2: P06/11/4E17/KVAR
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E18/kVA; OPRD2: P06/11/4E18/KVAR
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E19/kVA; OPRD2: P06/11/4E19/KVAR
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P06/11/4E20/kVA; OPRD2: P06/11/4E20/KVAR
P06 | 山上PS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/P06_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P06/69/750/MW; OPRD2: P06/69/760/MW; OPRD3: P06/69/770/MW
P06 | 山上PS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/P06_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P06/69/750/MVAR; OPRD2: P06/69/760/MVAR; OPRD3: P06/69/770/MVAR
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P06_A1 | [12 empty] | 山上PS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P06/11/210/CB; OPRD2: 6.9; OPRD3: 0
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P06_A1 | [12 empty] | 山上PS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P06/11/220/CB; OPRD2: 6.9; OPRD3: 0
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P06_A1 | [12 empty] | 山上PS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P06/11/230/CB; OPRD2: 6.9; OPRD3: 0
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P06_A1 | [12 empty] | 山上PS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P06/11/240/CB; OPRD2: 6.9; OPRD3: 0
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.820_SC_MVAR | 69KV#2SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P06/69/820/CB; OPRD2: 69; OPRD3: 0
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P06_A1 | [12 empty] | 山上PS.830_SC_MVAR | 69KV#3SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P06/69/830/CB; OPRD2: 69; OPRD3: 0
P06 | 山上PS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/P06_A1 | [12 empty] | 山上PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_20 |  | com_alarm_44 | P06//1MTR/63Q | P06//1MTR/96D | P06//1MTR/96B1 | P06//1MTR/GDA | P06//1MTR/96B2 | P06//1MTR/87A | P06//1MTR/51ZA | P06//1MTR/96PA | P06//1MTR/TRA | P06//2MTR/96D | P06//2MTR/GDA | P06//2MTR/TRA | P06//2MTR/96B2 | P06//2MTR/87A | P06//2MTR/96PA | P06//2MTR/63Q | P06//2MTR/51ZA | P06//2MTR/96B1 | P06//3MTR/96B1 | P06//3MTR/96D | P06//3MTR/63Q | P06//3MTR/96PA | P06//3MTR/GDA | P06//3MTR/87A | P06//3MTR/TRA | P06//3MTR/51ZA | P06//6DTR/96D | P06//6DTR/87A | P06//6DTR/96B1 | P06//6DTR/63Q | P06//6DTR/96B2 | P06//6DTR/TRA | P06//6DTR/GDA | P06//6DTR/PHA | P06//6DTR/51ZA | P06//6DTR/96PA | P06/11/330/GDA | P06/11/330/PHA | P06/11/340/GDA | P06/11/340/PHA | P06/161/1BUS/87A | P06/161/2BUS/87A | P06/69/1BUS/87A | P06/69/2BUS/87A
P06 | 山上PS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/P06_A1 | [12 empty] | 山上PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_4 |  | com_alarm_4 | OPRD1: P06//1MTR/TRF; OPRD2: P06//2MTR/TRF; OPRD3: P06//3MTR/TRF; OPRD4: P06//6DTR/TRF
P06 | 山上PS | 161 | 161kV | 1760_D1 | #6DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/161/1760/CB
P06 | 山上PS | 11 | 11kV | 330_D1 | #6DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/11/330/CB
P06 | 山上PS | 11 | 11kV | 330_D1 | #6DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/11/330/81A
P06 | 山上PS | 11 | 11kV | 340_D1 | #6DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/11/340/CB
P06 | 山上PS | 11 | 11kV | 340_D1 | #6DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/11/340/81A
P06 | 山上PS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/0/RTU/RTU_R_L
P06 | 山上PS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/0/StaDev/STUV
P06 | 山上PS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/0/StaDev/DCA
P06 | 山上PS | 161 | 161kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/161/ComPoint/ABS_89A
P06 | 山上PS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/69/ComPoint/ABS_89A
P06 | 山上PS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/0/StaDev/DCE
P06 | 山上PS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/22/ComPoint/CBA
P06 | 山上PS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/22/ComPoint/CBF
P06 | 山上PS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P06_D1 | [17 empty] | lamp2CC | OPRD1: P06/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P06 | 山上PS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 山上PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | P06/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
P06 | 山上PS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 山上PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | P06/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1510_AMP | 嘉義新營紅線 AMP | LINE161 | P06/161/1510/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1520_AMP | 嘉義新營白線 AMP | LINE161 | P06/161/1520/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1540_AMP | 鹽行豐華白線 AMP | LINE161 | P06/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1570_AMP | 龍崎一路 AMP | LINE161 | P06/161/1570/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1580_AMP | 龍崎二路 AMP | LINE161 | P06/161/1580/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1610_AMP | 龍崎二甲三路 AMP | LINE161 | P06/161/1610/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1620_AMP | 龍崎二甲四路 AMP | LINE161 | P06/161/1620/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1630_AMP | 山上仁德線 AMP | LINE161 | P06/161/1630/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1640_AMP | 台南海線 AMP | LINE161 | P06/161/1640/I |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C16R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 1600.000000 | 2.780000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1710_AMP | 安南豐華紅線 AMP | LINE161 | P06/161/1710/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1720 | 山上新化二路(1720) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1720_AMP | 山上新化二路 AMP | LINE161 | P06/161/1720/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1730 | 山上新化一路(1730) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1730_AMP | 山上新化一路 AMP | LINE161 | P06/161/1730/I |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.610_AMP | 山頂一路 AMP | LINE69 | P06/69/610/I |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.620_AMP | 山頂二路 AMP | LINE69 | P06/69/620/I |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.630_AMP | 善化一路 AMP | LINE69 | P06/69/630/I |  | AMP_CAL |  |  | 18 | CalcAIPoint | [21 empty] | C12R0640 | 576.000000 | 576.000000 | 640.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.640_AMP | 善化二路 AMP | LINE69 | P06/69/640/I |  | AMP_CAL |  |  | 19 | CalcAIPoint | [21 empty] | C12R0640 | 576.000000 | 576.000000 | 640.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.650_AMP | 善化三路 AMP | LINE69 | P06/69/650/I |  | AMP_CAL |  |  | 20 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.660_AMP | 新市一路 AMP | LINE69 | P06/69/660/I |  | AMP_CAL |  |  | 21 | CalcAIPoint | [21 empty] | C16R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.670_AMP | 山上新市三路 AMP | LINE69 | P06/69/670/I |  | AMP_CAL |  |  | 22 | CalcAIPoint | [21 empty] | C12R0947 | 852.299988 | 852.299988 | 947.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.680_AMP | 歸仁線 AMP | LINE69 | P06/69/680/I |  | AMP_CAL |  |  | 23 | CalcAIPoint | [21 empty] | C12R0947 | 852.299988 | 852.299988 | 947.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.710_AMP | 新市二路 AMP | LINE69 | P06/69/710/I |  | AMP_CAL |  |  | 24 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | P06//1MTR/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_LOAD | #1MTR 負載率 | MTR | P06//1MTR/Loading |  | TR_LOAD_200 |  |  | 26 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_PF | #1MTR 功率因素 | MTR | P06//1MTR/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | P06//1MTR/I |  | AMP_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P06 | 山上PS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | P06//2MTR/MVA |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_LOAD | #2MTR 負載率 | MTR | P06//2MTR/Loading |  | TR_LOAD_200 |  |  | 30 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_PF | #2MTR 功率因素 | MTR | P06//2MTR/PF |  | RPDC_PF_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | P06//2MTR/I |  | AMP_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P06 | 山上PS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | P06//3MTR/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_LOAD | #3MTR 負載率 | MTR | P06//3MTR/Loading |  | TR_LOAD_200 |  |  | 34 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_PF | #3MTR 功率因素 | MTR | P06//3MTR/PF |  | RPDC_PF_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | P06//3MTR/I |  | AMP_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P06 | 山上PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MW) |  | MW | [25 empty] | ADCS_S | [8 empty] | 山上PS.RPDC_MTR_MW | SUM(161/69KV MTR MW) | MTR |  |  | RPDC_3MTR_MW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MVAR) |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.RPDC_MTR_MVAR | SUM(161/69KV MTR MVAR) | MTR |  |  | RPDC_3MTR_MVAR_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | RPDC_MTR | RPDC |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.RPDC_MTR_PF | RPDC MTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.820_SC_MVAR | 69KV#2SC MVAR | SC | P06/69/820/MVAR |  | SC_CAL_69 |  |  | 40 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.830_SC_MVAR | 69KV#3SC MVAR | SC | P06/69/830/MVAR |  | SC_CAL_69 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1550_AMP | 豐德紅線 AMP | LINE161 | P06/161/1550/I |  | AMP_CAL |  |  | 42 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 山上PS.1560_AMP | 豐德白線 AMP | LINE161 | P06/161/1560/I |  | AMP_CAL |  |  | 43 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P06 | 山上PS | 0 |  | TRTOT | 山上主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 山上PS.TRTOT_MW | 山上主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | TRTOT | 山上主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 山上PS.TRTOT_MVAR | 山上主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_4 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 161 | 161kV | 1950_SHR | #1SHR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.1950_SHR_MVAR | 161KV#1SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上11線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上11線KVA | 11KV上11線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上11線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上11線KW | 11KV上11線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上12線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上12線KVA | 11KV上12線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上12線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上12線KW | 11KV上12線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上13線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上13線KVA | 11KV上13線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上13線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上13線KW | 11KV上13線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上14線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上14線KVA | 11KV上14線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上14線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上14線KW | 11KV上14線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上15線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上15線KVA | 11KV上15線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上15線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上15線KW | 11KV上15線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上16線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上16線KVA | 11KV上16線KVA | FEEDER |  |  | KVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上16線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上16線KW | 11KV上16線KW | FEEDER |  |  | KW_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上17線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上17線KVA | 11KV上17線KVA | FEEDER |  |  | KVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上17線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上17線KW | 11KV上17線KW | FEEDER |  |  | KW_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上18線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上18線KVA | 11KV上18線KVA | FEEDER |  |  | KVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上18線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上18線KW | 11KV上18線KW | FEEDER |  |  | KW_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上19線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上19線KVA | 11KV上19線KVA | FEEDER |  |  | KVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上19線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上19線KW | 11KV上19線KW | FEEDER |  |  | KW_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上20線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上20線KVA | 11KV上20線KVA | FEEDER |  |  | KVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  |  |  |  | 上20線KW | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.上20線KW | 11KV上20線KW | FEEDER |  |  | KW_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_MVA | #6DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_LOAD | #6DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 68 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_PF | #6DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_MVA | #6DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_LOAD | #6DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 71 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_PF | #6DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_MW | #6DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_MVAR | #6DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | 6DTR | #6DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_MVA | #6DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_LOAD | #6DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 76 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P06 | 山上PS | 11 | 11kV | 210_SC | #1SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.210_SC_MVAR | 11KV#1SC MVAR | SC | P06/11/210/MVAR |  | SC_CAL_11 |  |  | 77 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 220_SC | #2SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.220_SC_MVAR | 11KV#2SC MVAR | SC | P06/11/220/MVAR |  | SC_CAL_11 |  |  | 78 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 230_SC | #3SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.230_SC_MVAR | 11KV#3SC MVAR | SC | P06/11/230/MVAR |  | SC_CAL_11 |  |  | 79 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 240_SC | #4SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 山上PS.240_SC_MVAR | 11KV#4SC MVAR | SC | P06/11/240/MVAR |  | SC_CAL_11 |  |  | 80 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | MTR_TOT | 山上MTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 山上PS.MTR_TOT_MW | 山上MTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 81 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 69 | 69kV | 610_CB | 山頂一路(610_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.610_CB_4 | 610(山頂一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 620_CB | 山頂二路(620_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.620_CB_4 | 620(山頂二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 630_CB | 善化一路(630_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.630_CB_4 | 630(善化一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 640_CB | 善化二路(640_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.640_CB_4 | 640(善化二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 650_CB | 善化三路(650_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.650_CB_4 | 650(善化三路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 660_CB | 新市一路(660_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.660_CB_4 | 660(新市一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 670_CB | 山上新市三路(670_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.670_CB_4 | 670(山上新市三路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 88 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 680_CB | 歸仁線(680_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.680_CB_4 | 680(歸仁線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 89 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 710_CB | 新市二路(710_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.710_CB_4 | 710(新市二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 90 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | MTR | MTR |  | A_M | [25 empty] | RPDC_AD | [8 empty] | 山上PS.MTR_A/M | MTR OLTC A/M | MTR |  |  | LCP_3PTR |  |  | 91 | CalcDIPoint | [38 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 69 | 69kV | _OSCA | 示波器啟動警報 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.69KV_OSCA_4 | 69KV示波器啟動警報 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 93 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P06 | 山上PS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 山上PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | P06/0/CalcPoint/SUBA |  | STATION_FAULT_20 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 山上PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | P06/0/CalcPoint/SUBF |  | STATION_FAULT_4 |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 96 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 97 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510_AMP | 嘉義新營紅線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1510_AMP_A | 嘉義新營紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1520_AMP | 嘉義新營白線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1520_AMP_A | 嘉義新營白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1540_AMP | 鹽行豐華白線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1540_AMP_A | 鹽行豐華白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1570_AMP | 龍崎一路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1570_AMP_A | 龍崎一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1580_AMP | 龍崎二路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1580_AMP_A | 龍崎二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1610_AMP | 龍崎二甲三路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1610_AMP_A | 龍崎二甲三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1620_AMP | 龍崎二甲四路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1620_AMP_A | 龍崎二甲四路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1630_AMP | 山上仁德線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1630_AMP_A | 山上仁德線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1640_AMP | 台南海線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1640_AMP_A | 台南海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1710_AMP | 安南豐華紅線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1710_AMP_A | 安南豐華紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1720_AMP | 新化二路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1720_AMP_A | 新化二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1730_AMP | 新化一路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1730_AMP_A | 新化一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 610_AMP | 山頂一路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.610_AMP_A | 山頂一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 610_AMP | 山頂一路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.610_AMP_4 | 山頂一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 620_AMP | 山頂二路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.620_AMP_A | 山頂二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 620_AMP | 山頂二路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.620_AMP_4 | 山頂二路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 630_AMP | 善化一路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.630_AMP_A | 善化一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 640_AMP | 善化二路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.640_AMP_A | 善化二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 650_AMP | 善化三路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.650_AMP_A | 善化三路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 650_AMP | 善化三路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.650_AMP_4 | 善化三路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 660_AMP | 新市一路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.660_AMP_A | 新市一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 660_AMP | 新市一路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.660_AMP_4 | 新市一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 119 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 670_AMP | 山上新市三路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.670_AMP_A | 山上新市三路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 670_AMP | 山上新市三路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.670_AMP_4 | 山上新市三路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 680_AMP | 歸仁線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.680_AMP_A | 歸仁線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 122 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 680_AMP | 歸仁線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.680_AMP_4 | 歸仁線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 123 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 710_AMP | 新市二路 | [27 empty] | ADCS_S | [8 empty] | 山上PS.710_AMP_A | 新市二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 124 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 69 | 69kV | 710_AMP | 新市二路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.710_AMP_4 | 新市二路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 125 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_MVA_A | #1MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 126 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | P06//1MTR/TR_PERM |  | MTR_PERM |  |  | 127 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_MVA_A | #2MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 128 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | P06//2MTR/TR_PERM |  | MTR_PERM |  |  | 129 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_MVA_A | #3MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 130 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | P06//3MTR/TR_PERM |  | MTR_PERM |  |  | 131 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1550_AMP | 豐德紅線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1550_AMP_A | 豐德紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 132 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 161 | 161kV | 1560_AMP | 豐德白線 | [27 empty] | ADCS_S | [8 empty] | 山上PS.1560_AMP_A | 豐德白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 133 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 山上PS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 134 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 135 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山上PS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 136 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_PERM | #6DTR(A) TAP PERMISSION POINT | MTR | P06//6DTR(A)/TR_PERM |  | DTR_PERM |  |  | 137 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_PERM | #6DTR(B) TAP PERMISSION POINT | MTR | P06//6DTR(B)/TR_PERM |  | DTR_PERM |  |  | 138 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 6DTR_MVA | #6DTR | [27 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_MVA_A | #6DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 139 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 6ABUS | #6ABUS |  | 11KV#6ABUSC | [25 empty] | CDCS | [8 empty] | 山上PS.11KV#6ABUSC | #6ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 140 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 6BBUS | #6BBUS |  | 11KV#6BBUSC | [25 empty] | CDCS | [8 empty] | 山上PS.11KV#6BBUSC | #6BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 141 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 山上PS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T2 |  |  | 142 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 山上PS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B2 |  |  | 143 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P06 | 山上PS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 山上PS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 144 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 山上PS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 145 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | P06/0/RTU/ADCH1 |  |  |  | CDC | 146 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | P06/0/RTU/ADCH2 |  |  |  | CDC | 147 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | P06/0/RTU/ADCL1 |  |  |  | CDC | 148 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | P06/0/RTU/ADCL2 |  |  |  | CDC | 149 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-9A | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | P06/161/1BUS/V |  |  |  | CDC | 150 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-9B | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | P06/161/2BUS/V |  |  |  | CDC | 151 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P06 | 山上PS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-A8 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | P06/69/1BUS/V |  |  |  | CDC | 152 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P06 | 山上PS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-A9 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | P06/69/2BUS/V |  |  |  | CDC | 153 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | MW | [17 empty] | 1-82 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1510_MW | 嘉義新營紅線 MW | LINE161 | P06/161/1510/MW |  |  |  | CDC | 154 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | MVAR | [17 empty] | 1-83 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1510_MVAR | 嘉義新營紅線 MVAR | LINE161 | P06/161/1510/MVAR |  |  |  | CDC | 155 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1510LPD | 嘉義新營紅線(1510) |  | V | [17 empty] | 1-DC | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1510LPD_KV | 嘉義新營紅線(1510) LPD KV | LINE161 | P06/161/1510/V |  |  |  | CDC | 156 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1520_MW | 嘉義新營白線 MW | LINE161 | P06/161/1520/MW |  |  |  | CDC | 157 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1520_MVAR | 嘉義新營白線 MVAR | LINE161 | P06/161/1520/MVAR |  |  |  | CDC | 158 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1520LPD | 嘉義新營白線(1520) |  | V | [17 empty] | 1-DD | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1520LPD_KV | 嘉義新營白線(1520) LPD KV | LINE161 | P06/161/1520/V |  |  |  | CDC | 159 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1540_MW | 鹽行豐華白線 MW | LINE161 | P06/161/1540/MW |  |  |  | CDC | 160 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1540_MVAR | 鹽行豐華白線 MVAR | LINE161 | P06/161/1540/MVAR |  |  |  | CDC | 161 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1570_MW | 龍崎一路 MW | LINE161 | P06/161/1570/MW |  |  |  | CDC | 162 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1570_MVAR | 龍崎一路 MVAR | LINE161 | P06/161/1570/MVAR |  |  |  | CDC | 163 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1570LPD | 龍崎一路(1570) |  | V | [17 empty] | 1-D6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1570LPD_KV | 龍崎一路(1570) LPD KV | LINE161 | P06/161/1570/V |  |  |  | CDC | 164 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1580_MW | 龍崎二路 MW | LINE161 | P06/161/1580/MW |  |  |  | CDC | 165 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1580_MVAR | 龍崎二路 MVAR | LINE161 | P06/161/1580/MVAR |  |  |  | CDC | 166 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1580LPD | 龍崎二路(1580) |  | V | [17 empty] | 1-D7 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1580LPD_KV | 龍崎二路(1580) LPD KV | LINE161 | P06/161/1580/V |  |  |  | CDC | 167 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1610_MW | 龍崎二甲三路 MW | LINE161 | P06/161/1610/MW |  |  |  | CDC | 168 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1610_MVAR | 龍崎二甲三路 MVAR | LINE161 | P06/161/1610/MVAR |  |  |  | CDC | 169 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1610LPD | 龍崎二甲三路(1610) |  | V | [17 empty] | 1-DA | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1610LPD_KV | 龍崎二甲三路(1610) LPD KV | LINE161 | P06/161/1610/V |  |  |  | CDC | 170 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1620_MW | 龍崎二甲四路 MW | LINE161 | P06/161/1620/MW |  |  |  | CDC | 171 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1620_MVAR | 龍崎二甲四路 MVAR | LINE161 | P06/161/1620/MVAR |  |  |  | CDC | 172 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1620LPD | 龍崎二甲四路(1620) |  | V | [17 empty] | 1-DB | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1620LPD_KV | 龍崎二甲四路(1620) LPD KV | LINE161 | P06/161/1620/V |  |  |  | CDC | 173 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1630_MW | 山上仁德線 MW | LINE161 | P06/161/1630/MW |  |  |  | CDC | 174 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1630_MVAR | 山上仁德線 MVAR | LINE161 | P06/161/1630/MVAR |  |  |  | CDC | 175 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1630LPD | 山上仁德線(1630) |  | V | [17 empty] | 1-DE | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1630LPD_KV | 山上仁德線(1630) LPD KV | LINE161 | P06/161/1630/V |  |  |  | CDC | 176 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1640_MW | 台南海線 MW | LINE161 | P06/161/1640/MW |  |  |  | CDC | 177 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1640_MVAR | 台南海線 MVAR | LINE161 | P06/161/1640/MVAR |  |  |  | CDC | 178 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1640LPD | 台南海線(1640) |  | V | [17 empty] | 1-DF | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1640LPD_KV | 台南海線(1640) LPD KV | LINE161 | P06/161/1640/V |  |  |  | CDC | 179 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | MW | [17 empty] | 1-94 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1710_MW | 安南豐華紅線 MW | LINE161 | P06/161/1710/MW |  |  |  | CDC | 180 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | MVAR | [17 empty] | 1-95 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1710_MVAR | 安南豐華紅線 MVAR | LINE161 | P06/161/1710/MVAR |  |  |  | CDC | 181 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | MW | [17 empty] | 1-96 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1720_MW | 新化二路 MW | LINE161 | P06/161/1720/MW |  |  |  | CDC | 182 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | MVAR | [17 empty] | 1-97 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1720_MVAR | 新化二路 MVAR | LINE161 | P06/161/1720/MVAR |  |  |  | CDC | 183 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | MW | [17 empty] | 1-98 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1730_MW | 新化一路 MW | LINE161 | P06/161/1730/MW |  |  |  | CDC | 184 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | MVAR | [17 empty] | 1-99 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1730_MVAR | 新化一路 MVAR | LINE161 | P06/161/1730/MVAR |  |  |  | CDC | 185 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | MW | [17 empty] | 1-AC | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.610_MW | 山頂一路 MW | LINE69 | P06/69/610/MW |  |  |  | CDC | 186 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | MVAR | [17 empty] | 1-AD | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.610_MVAR | 山頂一路 MVAR | LINE69 | P06/69/610/MVAR |  |  |  | CDC | 187 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | MW | [17 empty] | 1-AF | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.620_MW | 山頂二路 MW | LINE69 | P06/69/620/MW |  |  |  | CDC | 188 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | MVAR | [17 empty] | 1-B0 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.620_MVAR | 山頂二路 MVAR | LINE69 | P06/69/620/MVAR |  |  |  | CDC | 189 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | MW | [17 empty] | 1-B2 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.630_MW | 善化一路 MW | LINE69 | P06/69/630/MW |  |  |  | CDC | 190 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | MVAR | [17 empty] | 1-B3 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.630_MVAR | 善化一路 MVAR | LINE69 | P06/69/630/MVAR |  |  |  | CDC | 191 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | MW | [17 empty] | 1-B5 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.640_MW | 善化二路 MW | LINE69 | P06/69/640/MW |  |  |  | CDC | 192 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | MVAR | [17 empty] | 1-B6 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.640_MVAR | 善化二路 MVAR | LINE69 | P06/69/640/MVAR |  |  |  | CDC | 193 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | MW | [17 empty] | 1-B8 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.650_MW | 善化三路 MW | LINE69 | P06/69/650/MW |  |  |  | CDC | 194 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | MVAR | [17 empty] | 1-B9 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.650_MVAR | 善化三路 MVAR | LINE69 | P06/69/650/MVAR |  |  |  | CDC | 195 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | MW | [17 empty] | 1-BB | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.660_MW | 新市一路 MW | LINE69 | P06/69/660/MW |  |  |  | CDC | 196 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | MVAR | [17 empty] | 1-BC | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.660_MVAR | 新市一路 MVAR | LINE69 | P06/69/660/MVAR |  |  |  | CDC | 197 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | MW | [17 empty] | 1-BE | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.670_MW | 山上新市三路 MW | LINE69 | P06/69/670/MW |  |  |  | CDC | 198 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | MVAR | [17 empty] | 1-BF | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.670_MVAR | 山上新市三路 MVAR | LINE69 | P06/69/670/MVAR |  |  |  | CDC | 199 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | MW | [17 empty] | 1-C3 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.680_MW | 歸仁線 MW | LINE69 | P06/69/680/MW |  |  |  | CDC | 200 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | MVAR | [17 empty] | 1-C4 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.680_MVAR | 歸仁線 MVAR | LINE69 | P06/69/680/MVAR |  |  |  | CDC | 201 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | MW | [17 empty] | 1-C6 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.710_MW | 新市二路 MW | LINE69 | P06/69/710/MW |  |  |  | CDC | 202 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | MVAR | [17 empty] | 1-C7 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.710_MVAR | 新市二路 MVAR | LINE69 | P06/69/710/MVAR |  |  |  | CDC | 203 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P06 | 山上PS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-E0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1500TIE_AMP | 1500TIE AMP | TIE | P06/161/1500/I |  |  |  | CDC | 204 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-AA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.600TIE_AMP | 600TIE AMP | TIE | P06/69/600/I |  |  |  | CDC | 205 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-A0 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#1MTR_MW | #1MTR二次側 MW | MTR | P06/69/750/MW |  |  |  | CDC | 206 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-A1 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | P06/69/750/MVAR |  |  |  | CDC | 207 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-D1 |  | 2-43 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 山上PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | P06//1MTR/TapPosMv |  |  |  | CDC | 208 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-D2 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#1MTR_OIL | #1MTR 油溫 | MTR | P06//1MTR/OilTemp |  |  |  | CDC | 209 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-D3 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#1MTR_COIL | #1MTR 線溫 | MTR | P06//1MTR/CoilTemp |  |  |  | CDC | 210 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-A3 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#2MTR_MW | #2MTR二次側 MW | MTR | P06/69/760/MW |  |  |  | CDC | 211 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-A4 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | P06/69/760/MVAR |  |  |  | CDC | 212 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-C8 |  | 2-47 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 山上PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | P06//2MTR/TapPosMv |  |  |  | CDC | 213 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-C9 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#2MTR_OIL | #2MTR 油溫 | MTR | P06//2MTR/OilTemp |  |  |  | CDC | 214 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-CA | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#2MTR_COIL | #2MTR 線溫 | MTR | P06//2MTR/CoilTemp |  |  |  | CDC | 215 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-A6 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#3MTR_MW | #3MTR二次側 MW | MTR | P06/69/770/MW |  |  |  | CDC | 216 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P06 | 山上PS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-A7 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | P06/69/770/MVAR |  |  |  | CDC | 217 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-CE |  | 2-4B |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 山上PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | P06//3MTR/TapPosMv |  |  |  | CDC | 218 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-CF | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#3MTR_OIL | #3MTR 油溫 | MTR | P06//3MTR/OilTemp |  |  |  | CDC | 219 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-D0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#3MTR_COIL | #3MTR 線溫 | MTR | P06//3MTR/CoilTemp |  |  |  | CDC | 220 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-D9 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.直流N電源電壓 | 直流N電源電壓 | OTHER | P06/0/StaDev/DCV_N |  |  |  | CDC | 221 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P06 | 山上PS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-D8 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.直流P電源電壓 | 直流P電源電壓 | OTHER | P06/0/StaDev/DCV_P |  |  |  | CDC | 222 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-1120_1120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1550_MW | 豐德紅線 MW | LINE161 | P06/161/1550/MW |  |  |  | CDC | 223 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-1120_1120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1550_MVAR | 豐德紅線 MVAR | LINE161 | P06/161/1550/MVAR |  |  |  | CDC | 224 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1550LPD | 豐德紅線(1550) |  | V | [17 empty] | 1-D4 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1550LPD_KV | 豐德紅線(1550) LPD KV | LINE161 | P06/161/1550/V |  |  |  | CDC | 225 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | MW | [17 empty] | 1-9E | [5 empty] | MW_-1120_1120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1560_MW | 豐德白線 MW | LINE161 | P06/161/1560/MW |  |  |  | CDC | 226 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | MVAR | [17 empty] | 1-9F | [5 empty] | MVAR_-1120_1120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1560_MVAR | 豐德白線 MVAR | LINE161 | P06/161/1560/MVAR |  |  |  | CDC | 227 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
P06 | 山上PS | 161 | 161kV | 1560LPD | 豐德白線(1560) |  | V | [17 empty] | 1-D5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1560LPD_KV | 豐德白線(1560) LPD KV | LINE161 | P06/161/1560/V |  |  |  | CDC | 228 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [17 empty] | 1-E1 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | P06//1SHR/OilTemp |  |  |  | CDC | 229 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [17 empty] | 1-E2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | P06//1SHR/CoilTemp |  |  |  | CDC | 230 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 11 | 11kV | 6ABUS | #6ABUS |  | V | [17 empty] | 1-ED | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.11KV#6ABUS_KV | 11KV #6ABUS KV | BUS | P06/11/6ABUS/V_R |  |  |  | CDC | 231 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P06 | 山上PS | 11 | 11kV | 6BBUS | #6BBUS |  | V | [17 empty] | 2-8C | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.11KV#6BBUS_KV | 11KV #6BBUS KV | BUS | P06/11/6BBUS/V_R |  |  |  | CDC | 232 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P06 | 山上PS | 11 | 11kV | 上11線 | 上11線 |  | 上11線KVAR | [17 empty] | 1-EE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上11線KVAR | 11KV上11線 KVAR | FEEDER | P06/11/4E11/KVAR |  |  |  | CDC | 233 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上11線 | 上11線 |  | 上11線A1 | [17 empty] | 1-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上11線A1 | 11KV上11線 R相AMP | FEEDER | P06/11/4E11/I_R |  |  |  | CDC | 234 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上11線 | 上11線 |  | 上11線A2 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上11線A2 | 11KV上11線 S相AMP | FEEDER | P06/11/4E11/I_S |  |  |  | CDC | 235 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上11線 | 上11線 |  | 上11線A3 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上11線A3 | 11KV上11線 T相AMP | FEEDER | P06/11/4E11/I_T |  |  |  | CDC | 236 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上11線 | 上11線 |  | 上11線A0 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上11線A0 | 11KV上11線 N相AMP | FEEDER | P06/11/4E11/I_N |  |  |  | CDC | 237 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上12線 | 上12線 |  | 上12線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上12線KVAR | 11KV上12線 KVAR | FEEDER | P06/11/4E12/KVAR |  |  |  | CDC | 238 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上12線 | 上12線 |  | 上12線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上12線A1 | 11KV上12線 R相AMP | FEEDER | P06/11/4E12/I_R |  |  |  | CDC | 239 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上12線 | 上12線 |  | 上12線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上12線A2 | 11KV上12線 S相AMP | FEEDER | P06/11/4E12/I_S |  |  |  | CDC | 240 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上12線 | 上12線 |  | 上12線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上12線A3 | 11KV上12線 T相AMP | FEEDER | P06/11/4E12/I_T |  |  |  | CDC | 241 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上12線 | 上12線 |  | 上12線A0 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上12線A0 | 11KV上12線 N相AMP | FEEDER | P06/11/4E12/I_N |  |  |  | CDC | 242 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上13線 | 上13線 |  | 上13線KVAR | [17 empty] | 1-F8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上13線KVAR | 11KV上13線 KVAR | FEEDER | P06/11/4E13/KVAR |  |  |  | CDC | 243 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上13線 | 上13線 |  | 上13線A1 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上13線A1 | 11KV上13線 R相AMP | FEEDER | P06/11/4E13/I_R |  |  |  | CDC | 244 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上13線 | 上13線 |  | 上13線A2 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上13線A2 | 11KV上13線 S相AMP | FEEDER | P06/11/4E13/I_S |  |  |  | CDC | 245 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上13線 | 上13線 |  | 上13線A3 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上13線A3 | 11KV上13線 T相AMP | FEEDER | P06/11/4E13/I_T |  |  |  | CDC | 246 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上13線 | 上13線 |  | 上13線A0 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上13線A0 | 11KV上13線 N相AMP | FEEDER | P06/11/4E13/I_N |  |  |  | CDC | 247 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上14線 | 上14線 |  | 上14線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上14線KVAR | 11KV上14線 KVAR | FEEDER | P06/11/4E14/KVAR |  |  |  | CDC | 248 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上14線 | 上14線 |  | 上14線A1 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上14線A1 | 11KV上14線 R相AMP | FEEDER | P06/11/4E14/I_R |  |  |  | CDC | 249 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上14線 | 上14線 |  | 上14線A2 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上14線A2 | 11KV上14線 S相AMP | FEEDER | P06/11/4E14/I_S |  |  |  | CDC | 250 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上14線 | 上14線 |  | 上14線A3 | [17 empty] | 2-80 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上14線A3 | 11KV上14線 T相AMP | FEEDER | P06/11/4E14/I_T |  |  |  | CDC | 251 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上14線 | 上14線 |  | 上14線A0 | [17 empty] | 2-81 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上14線A0 | 11KV上14線 N相AMP | FEEDER | P06/11/4E14/I_N |  |  |  | CDC | 252 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上15線 | 上15線 |  | 上15線KVAR | [17 empty] | 2-82 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上15線KVAR | 11KV上15線 KVAR | FEEDER | P06/11/4E15/KVAR |  |  |  | CDC | 253 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上15線 | 上15線 |  | 上15線A1 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上15線A1 | 11KV上15線 R相AMP | FEEDER | P06/11/4E15/I_R |  |  |  | CDC | 254 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上15線 | 上15線 |  | 上15線A2 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上15線A2 | 11KV上15線 S相AMP | FEEDER | P06/11/4E15/I_S |  |  |  | CDC | 255 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上15線 | 上15線 |  | 上15線A3 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上15線A3 | 11KV上15線 T相AMP | FEEDER | P06/11/4E15/I_T |  |  |  | CDC | 256 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上15線 | 上15線 |  | 上15線A0 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上15線A0 | 11KV上15線 N相AMP | FEEDER | P06/11/4E15/I_N |  |  |  | CDC | 257 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上16線 | 上16線 |  | 上16線KVAR | [17 empty] | 2-8D | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上16線KVAR | 11KV上16線 KVAR | FEEDER | P06/11/4E16/KVAR |  |  |  | CDC | 258 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上16線 | 上16線 |  | 上16線A1 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上16線A1 | 11KV上16線 R相AMP | FEEDER | P06/11/4E16/I_R |  |  |  | CDC | 259 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上16線 | 上16線 |  | 上16線A2 | [17 empty] | 2-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上16線A2 | 11KV上16線 S相AMP | FEEDER | P06/11/4E16/I_S |  |  |  | CDC | 260 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上16線 | 上16線 |  | 上16線A3 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上16線A3 | 11KV上16線 T相AMP | FEEDER | P06/11/4E16/I_T |  |  |  | CDC | 261 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上16線 | 上16線 |  | 上16線A0 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上16線A0 | 11KV上16線 N相AMP | FEEDER | P06/11/4E16/I_N |  |  |  | CDC | 262 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上17線 | 上17線 |  | 上17線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上17線KVAR | 11KV上17線 KVAR | FEEDER | P06/11/4E17/KVAR |  |  |  | CDC | 263 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上17線 | 上17線 |  | 上17線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上17線A1 | 11KV上17線 R相AMP | FEEDER | P06/11/4E17/I_R |  |  |  | CDC | 264 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上17線 | 上17線 |  | 上17線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上17線A2 | 11KV上17線 S相AMP | FEEDER | P06/11/4E17/I_S |  |  |  | CDC | 265 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上17線 | 上17線 |  | 上17線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上17線A3 | 11KV上17線 T相AMP | FEEDER | P06/11/4E17/I_T |  |  |  | CDC | 266 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上17線 | 上17線 |  | 上17線A0 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上17線A0 | 11KV上17線 N相AMP | FEEDER | P06/11/4E17/I_N |  |  |  | CDC | 267 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上18線 | 上18線 |  | 上18線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上18線KVAR | 11KV上18線 KVAR | FEEDER | P06/11/4E18/KVAR |  |  |  | CDC | 268 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上18線 | 上18線 |  | 上18線A1 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上18線A1 | 11KV上18線 R相AMP | FEEDER | P06/11/4E18/I_R |  |  |  | CDC | 269 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上18線 | 上18線 |  | 上18線A2 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上18線A2 | 11KV上18線 S相AMP | FEEDER | P06/11/4E18/I_S |  |  |  | CDC | 270 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上18線 | 上18線 |  | 上18線A3 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上18線A3 | 11KV上18線 T相AMP | FEEDER | P06/11/4E18/I_T |  |  |  | CDC | 271 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上18線 | 上18線 |  | 上18線A0 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上18線A0 | 11KV上18線 N相AMP | FEEDER | P06/11/4E18/I_N |  |  |  | CDC | 272 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上19線 | 上19線 |  | 上19線KVAR | [17 empty] | 2-9C | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上19線KVAR | 11KV上19線 KVAR | FEEDER | P06/11/4E19/KVAR |  |  |  | CDC | 273 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上19線 | 上19線 |  | 上19線A1 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上19線A1 | 11KV上19線 R相AMP | FEEDER | P06/11/4E19/I_R |  |  |  | CDC | 274 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上19線 | 上19線 |  | 上19線A2 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上19線A2 | 11KV上19線 S相AMP | FEEDER | P06/11/4E19/I_S |  |  |  | CDC | 275 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上19線 | 上19線 |  | 上19線A3 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上19線A3 | 11KV上19線 T相AMP | FEEDER | P06/11/4E19/I_T |  |  |  | CDC | 276 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上19線 | 上19線 |  | 上19線A0 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上19線A0 | 11KV上19線 N相AMP | FEEDER | P06/11/4E19/I_N |  |  |  | CDC | 277 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上20線 | 上20線 |  | 上20線KVAR | [17 empty] | 2-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上20線KVAR | 11KV上20線 KVAR | FEEDER | P06/11/4E20/KVAR |  |  |  | CDC | 278 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上20線 | 上20線 |  | 上20線A1 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上20線A1 | 11KV上20線 R相AMP | FEEDER | P06/11/4E20/I_R |  |  |  | CDC | 279 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上20線 | 上20線 |  | 上20線A2 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上20線A2 | 11KV上20線 S相AMP | FEEDER | P06/11/4E20/I_S |  |  |  | CDC | 280 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上20線 | 上20線 |  | 上20線A3 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上20線A3 | 11KV上20線 T相AMP | FEEDER | P06/11/4E20/I_T |  |  |  | CDC | 281 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 11 | 11kV | 上20線 | 上20線 |  | 上20線A0 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山上PS.上20線A0 | 11KV上20線 N相AMP | FEEDER | P06/11/4E20/I_N |  |  |  | CDC | 282 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | MW | [17 empty] | 1-E8 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_MW | #6DTR二次側(A) MW | MTR | P06/11/330/KW |  |  |  | CDC | 283 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | MVAR | [17 empty] | 1-E9 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_MVAR | #6DTR二次側(A) MVAR | MTR | P06/11/330/KVAR |  |  |  | CDC | 284 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | I_R | [17 empty] | 1-EA | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_A1 | #6DTR二次側(A) R相AMP | MTR | P06/11/330/I_R |  |  |  | CDC | 285 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | I_S | [17 empty] | 1-EB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_A2 | #6DTR二次側(A) S相AMP | MTR | P06/11/330/I_S |  |  |  | CDC | 286 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR二次側(A) |  | I_T | [17 empty] | 1-EC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_A3 | #6DTR二次側(A) T相AMP | MTR | P06/11/330/I_T |  |  |  | CDC | 287 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | OilTemp | [17 empty] | 1-E3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR_OIL | #6DTR 油溫 | MTR | P06//6DTR/OilTemp |  |  |  | CDC | 288 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | CoilTemp | [17 empty] | 1-E4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_COIL | #6DTR(A) 線溫 | MTR | P06//6DTR(A)/CoilTemp |  |  |  | CDC | 289 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | TapPosMv | [17 empty] | 1-E6 |  | 3-0B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_TAP | #6DTR(A) OLTC TAP | MTR | P06//6DTR(A)/TapPosMv |  |  |  | CDC | 290 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | MW | [17 empty] | 2-87 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_MW | #6DTR二次側(B) MW | MTR | P06/11/340/KW |  |  |  | CDC | 291 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | MVAR | [17 empty] | 2-88 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_MVAR | #6DTR二次側(B) MVAR | MTR | P06/11/340/KVAR |  |  |  | CDC | 292 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | I_R | [17 empty] | 2-89 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_A1 | #6DTR二次側(B) R相AMP | MTR | P06/11/340/I_R |  |  |  | CDC | 293 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | I_S | [17 empty] | 2-8A | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_A2 | #6DTR二次側(B) S相AMP | MTR | P06/11/340/I_S |  |  |  | CDC | 294 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR二次側(B) |  | I_T | [17 empty] | 2-8B | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_A3 | #6DTR二次側(B) T相AMP | MTR | P06/11/340/I_T |  |  |  | CDC | 295 | GENERICAIPoint | PS012_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | CoilTemp | [17 empty] | 1-E5 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_COIL | #6DTR(B) 線溫 | MTR | P06//6DTR(B)/CoilTemp |  |  |  | CDC | 296 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | TapPosMv | [17 empty] | 1-E7 |  | 3-0D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_TAP | #6DTR(B) OLTC TAP | MTR | P06//6DTR(B)/TapPosMv |  |  |  | CDC | 297 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P06 | 山上PS | 161 | 161kV | 1540LPD | 鹽行豐華白線(1540) |  | V | [17 empty] | 1-C2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1540LPD_KV | 鹽行豐華白線(1540) LPD KV | LINE161 | P06/161/1540/V |  |  |  | CDC | 298 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1710LPD | 安南豐華紅線(1710) |  | V | [17 empty] | 1-C5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1710LPD_KV | 安南豐華紅線(1710) LPD KV | LINE161 | P06/161/1710/V |  |  |  | CDC | 299 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1720LPD | 山上新化二路(1720) |  | V | [17 empty] | 1-CB | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1720LPD_KV | 山上新化二路(1720) LPD KV | LINE161 | P06/161/1720/V |  |  |  | CDC | 300 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1730LPD | 山上新化一路(1730) |  | V | [17 empty] | 1-CC | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 山上PS.1730LPD_KV | 山上新化一路(1730) LPD KV | LINE161 | P06/161/1730/V |  |  |  | CDC | 301 | GENERICAIPoint | PS012_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | PHA | [17 empty] | 1-02-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1510_PHA | 嘉義新營紅線(1510) 相間RY | LINE161 | P06/161/1510/PHA |  |  |  | CDC | 302 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | GDA | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1510_GDA | 嘉義新營紅線(1510) 接地RY | LINE161 | P06/161/1510/GDA |  |  |  | CDC | 303 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | CB | [17 empty] | 1-02-02 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1510_CB | 1510(嘉義新營紅線) CB | LINE161 | P06/161/1510/CB |  |  |  | CDC | 304 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | 79UL | [17 empty] | 2-31-05 |  | 2-28 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1510_79UL | 嘉義新營紅線(1510) 79RY U/L | LINE161 | P06/161/1510/79UL |  |  |  | CDC | 305 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | ABS1 | 1511 | [16 empty] | 1-30-12 | 1-30-13 | 1-2E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1511_ABS | 1511(嘉義新營紅線) ABS | LINE161 | P06/161/1510/ABS1 |  |  |  | CDC | 306 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | ABS2 | 1512 | [16 empty] | 1-30-14 | 1-30-15 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1512_ABS | 1512(嘉義新營紅線) ABS | LINE161 | P06/161/1510/ABS2 |  |  |  | CDC | 307 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | ABS3 | 1513 | [16 empty] | 1-31-00 | 1-31-01 | 1-30 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1513_ABS | 1513(嘉義新營紅線) ABS | LINE161 | P06/161/1510/ABS3 |  |  |  | CDC | 308 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | E3 | 1513E | [16 empty] | 1-31-02 | 1-31-03 | 1-31 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1513E_ES | 1513E(嘉義新營紅線) ES | LINE161 | P06/161/1510/ES3 |  |  |  | CDC | 309 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | PHA | [17 empty] | 1-03-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1520_PHA | 嘉義新營白線(1520) 相間RY | LINE161 | P06/161/1520/PHA |  |  |  | CDC | 310 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | GDA | [17 empty] | 1-03-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1520_GDA | 嘉義新營白線(1520) 接地RY | LINE161 | P06/161/1520/GDA |  |  |  | CDC | 311 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | CB | [17 empty] | 1-02-06 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1520_CB | 1520(嘉義新營白線) CB | LINE161 | P06/161/1520/CB |  |  |  | CDC | 312 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | 79UL | [17 empty] | 2-31-07 |  | 2-2A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1520_79UL | 嘉義新營白線(1520) 79RY U/L | LINE161 | P06/161/1520/79UL |  |  |  | CDC | 313 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | ABS1 | 1521 | [16 empty] | 1-31-04 | 1-31-05 | 1-32 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1521_ABS | 1521(嘉義新營白線) ABS | LINE161 | P06/161/1520/ABS1 |  |  |  | CDC | 314 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | ABS2 | 1522 | [16 empty] | 1-31-06 | 1-31-07 | 1-33 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1522_ABS | 1522(嘉義新營白線) ABS | LINE161 | P06/161/1520/ABS2 |  |  |  | CDC | 315 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | ABS3 | 1523 | [16 empty] | 1-31-08 | 1-31-09 | 1-34 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1523_ABS | 1523(嘉義新營白線) ABS | LINE161 | P06/161/1520/ABS3 |  |  |  | CDC | 316 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | E3 | 1523E | [16 empty] | 1-31-10 | 1-31-11 | 1-35 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1523E_ES | 1523E(嘉義新營白線) ES | LINE161 | P06/161/1520/ES3 |  |  |  | CDC | 317 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | PHA | [17 empty] | 1-06-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1540_PHA | 鹽行豐華白線(1540) 相間RY | LINE161 | P06/161/1540/PHA |  |  |  | CDC | 318 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | GDA | [17 empty] | 1-06-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1540_GDA | 鹽行豐華白線(1540) 接地RY | LINE161 | P06/161/1540/GDA |  |  |  | CDC | 319 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | CB | [17 empty] | 1-06-02 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 山上PS.1540_CB | 1540(鹽行豐華白線) CB | LINE161 | P06/161/1540/CB |  |  |  | CDC | 320 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | 79UL | [17 empty] | 2-32-05 |  | 2-38 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1540_79UL | 鹽行豐華白線(1540) 79RY U/L | LINE161 | P06/161/1540/79UL |  |  |  | CDC | 321 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | ABS1 | 1541 | [16 empty] | 1-34-12 | 1-34-13 | 1-4E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1541_ABS | 1541(鹽行豐華白線) ABS | LINE161 | P06/161/1540/ABS1 |  |  |  | CDC | 322 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | ABS2 | 1542 | [16 empty] | 1-34-14 | 1-34-15 | 1-4F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1542_ABS | 1542(鹽行豐華白線) ABS | LINE161 | P06/161/1540/ABS2 |  |  |  | CDC | 323 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | ABS3 | 1543 | [16 empty] | 1-35-00 | 1-35-01 | 1-50 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1543_ABS | 1543(鹽行豐華白線) ABS | LINE161 | P06/161/1540/ABS3 |  |  |  | CDC | 324 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | E3 | 1543E | [16 empty] | 1-35-02 | 1-35-03 | 1-51 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1543E_ES | 1543E(鹽行豐華白線) ES | LINE161 | P06/161/1540/ES3 |  |  |  | CDC | 325 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1570_PHA | 龍崎一路(1570) 相間RY | LINE161 | P06/161/1570/PHA |  |  |  | CDC | 326 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1570_GDA | 龍崎一路(1570) 接地RY | LINE161 | P06/161/1570/GDA |  |  |  | CDC | 327 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | CB | [17 empty] | 1-03-02 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1570_CB | 1570(龍崎一路) CB | LINE161 | P06/161/1570/CB |  |  |  | CDC | 328 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | 79UL | [17 empty] | 2-31-09 |  | 2-2C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1570_79UL | 龍崎一路(1570) 79RY U/L | LINE161 | P06/161/1570/79UL |  |  |  | CDC | 329 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | ABS1 | 1571 | [16 empty] | 1-31-12 | 1-31-13 | 1-36 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1571_ABS | 1571(龍崎一路) ABS | LINE161 | P06/161/1570/ABS1 |  |  |  | CDC | 330 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | ABS2 | 1572 | [16 empty] | 1-31-14 | 1-31-15 | 1-37 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1572_ABS | 1572(龍崎一路) ABS | LINE161 | P06/161/1570/ABS2 |  |  |  | CDC | 331 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | ABS3 | 1573 | [16 empty] | 1-32-00 | 1-32-01 | 1-38 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1573_ABS | 1573(龍崎一路) ABS | LINE161 | P06/161/1570/ABS3 |  |  |  | CDC | 332 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | E3 | 1573E | [16 empty] | 1-32-02 | 1-32-03 | 1-39 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1573E_ES | 1573E(龍崎一路) ES | LINE161 | P06/161/1570/ES3 |  |  |  | CDC | 333 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | PHA | [17 empty] | 1-04-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1580_PHA | 龍崎二路(1580) 相間RY | LINE161 | P06/161/1580/PHA |  |  |  | CDC | 334 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | GDA | [17 empty] | 1-04-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1580_GDA | 龍崎二路(1580) 接地RY | LINE161 | P06/161/1580/GDA |  |  |  | CDC | 335 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | CB | [17 empty] | 1-03-06 |  | 1-07 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1580_CB | 1580(龍崎二路) CB | LINE161 | P06/161/1580/CB |  |  |  | CDC | 336 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | 79UL | [17 empty] | 2-31-11 |  | 2-2E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1580_79UL | 龍崎二路(1580) 79RY U/L | LINE161 | P06/161/1580/79UL |  |  |  | CDC | 337 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | ABS1 | 1581 | [16 empty] | 1-32-04 | 1-32-05 | 1-3A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1581_ABS | 1581(龍崎二路) ABS | LINE161 | P06/161/1580/ABS1 |  |  |  | CDC | 338 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | ABS2 | 1582 | [16 empty] | 1-32-06 | 1-32-07 | 1-3B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1582_ABS | 1582(龍崎二路) ABS | LINE161 | P06/161/1580/ABS2 |  |  |  | CDC | 339 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | ABS3 | 1583 | [16 empty] | 1-32-08 | 1-32-09 | 1-3C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1583_ABS | 1583(龍崎二路) ABS | LINE161 | P06/161/1580/ABS3 |  |  |  | CDC | 340 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | E3 | 1583E | [16 empty] | 1-32-10 | 1-32-11 | 1-3D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1583E_ES | 1583E(龍崎二路) ES | LINE161 | P06/161/1580/ES3 |  |  |  | CDC | 341 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | PHA | [17 empty] | 1-04-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1610_PHA | 龍崎二甲三路(1610) 相間RY | LINE161 | P06/161/1610/PHA |  |  |  | CDC | 342 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | GDA | [17 empty] | 1-04-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1610_GDA | 龍崎二甲三路(1610) 接地RY | LINE161 | P06/161/1610/GDA |  |  |  | CDC | 343 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | CB | [17 empty] | 1-04-02 |  | 1-08 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1610_CB | 1610(龍崎二甲三路) CB | LINE161 | P06/161/1610/CB |  |  |  | CDC | 344 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | 79UL | [17 empty] | 2-31-13 |  | 2-30 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1610_79UL | 龍崎二甲三路(1610) 79RY U/L | LINE161 | P06/161/1610/79UL |  |  |  | CDC | 345 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | ABS1 | 1611 | [16 empty] | 1-32-12 | 1-32-13 | 1-3E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1611_ABS | 1611(龍崎二甲三路) ABS | LINE161 | P06/161/1610/ABS1 |  |  |  | CDC | 346 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | ABS2 | 1612 | [16 empty] | 1-32-14 | 1-32-15 | 1-3F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1612_ABS | 1612(龍崎二甲三路) ABS | LINE161 | P06/161/1610/ABS2 |  |  |  | CDC | 347 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | ABS3 | 1613 | [16 empty] | 1-33-00 | 1-33-01 | 1-40 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1613_ABS | 1613(龍崎二甲三路) ABS | LINE161 | P06/161/1610/ABS3 |  |  |  | CDC | 348 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | E3 | 1613E | [16 empty] | 1-33-02 | 1-33-03 | 1-41 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1613E_ES | 1613E(龍崎二甲三路) ES | LINE161 | P06/161/1610/ES3 |  |  |  | CDC | 349 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | PHA | [17 empty] | 1-05-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1620_PHA | 龍崎二甲四路(1620) 相間RY | LINE161 | P06/161/1620/PHA |  |  |  | CDC | 350 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | GDA | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1620_GDA | 龍崎二甲四路(1620) 接地RY | LINE161 | P06/161/1620/GDA |  |  |  | CDC | 351 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | CB | [17 empty] | 1-04-06 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1620_CB | 1620(龍崎二甲四路) CB | LINE161 | P06/161/1620/CB |  |  |  | CDC | 352 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | 79UL | [17 empty] | 2-31-15 |  | 2-32 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1620_79UL | 龍崎二甲四路(1620) 79RY U/L | LINE161 | P06/161/1620/79UL |  |  |  | CDC | 353 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | ABS1 | 1621 | [16 empty] | 1-33-04 | 1-33-05 | 1-42 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1621_ABS | 1621(龍崎二甲四路) ABS | LINE161 | P06/161/1620/ABS1 |  |  |  | CDC | 354 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | ABS2 | 1622 | [16 empty] | 1-33-06 | 1-33-07 | 1-43 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1622_ABS | 1622(龍崎二甲四路) ABS | LINE161 | P06/161/1620/ABS2 |  |  |  | CDC | 355 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | ABS3 | 1623 | [16 empty] | 1-33-08 | 1-33-09 | 1-44 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1623_ABS | 1623(龍崎二甲四路) ABS | LINE161 | P06/161/1620/ABS3 |  |  |  | CDC | 356 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | E3 | 1623E | [16 empty] | 1-33-10 | 1-33-11 | 1-45 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1623E_ES | 1623E(龍崎二甲四路) ES | LINE161 | P06/161/1620/ES3 |  |  |  | CDC | 357 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | PHA | [17 empty] | 1-05-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1630_PHA | 山上仁德線(1630) 相間RY | LINE161 | P06/161/1630/PHA |  |  |  | CDC | 358 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | GDA | [17 empty] | 1-05-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1630_GDA | 山上仁德線(1630) 接地RY | LINE161 | P06/161/1630/GDA |  |  |  | CDC | 359 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | CB | [17 empty] | 1-05-02 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 山上PS.1630_CB | 1630(山上仁德線) CB | LINE161 | P06/161/1630/CB |  |  |  | CDC | 360 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | 79UL | [17 empty] | 2-32-01 |  | 2-34 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1630_79UL | 山上仁德線(1630) 79RY U/L | LINE161 | P06/161/1630/79UL |  |  |  | CDC | 361 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | ABS1 | 1631 | [16 empty] | 1-33-12 | 1-33-13 | 1-46 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1631_ABS | 1631(山上仁德線) ABS | LINE161 | P06/161/1630/ABS1 |  |  |  | CDC | 362 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | ABS2 | 1632 | [16 empty] | 1-33-14 | 1-33-15 | 1-47 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1632_ABS | 1632(山上仁德線) ABS | LINE161 | P06/161/1630/ABS2 |  |  |  | CDC | 363 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | ABS3 | 1633 | [16 empty] | 1-34-00 | 1-34-01 | 1-48 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1633_ABS | 1633(山上仁德線) ABS | LINE161 | P06/161/1630/ABS3 |  |  |  | CDC | 364 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | E3 | 1633E | [16 empty] | 1-34-02 | 1-34-03 | 1-49 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1633E_ES | 1633E(山上仁德線) ES | LINE161 | P06/161/1630/ES3 |  |  |  | CDC | 365 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | PHA | [17 empty] | 1-06-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1640_PHA | 台南海線(1640) 相間RY | LINE161 | P06/161/1640/PHA |  |  |  | CDC | 366 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | GDA | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1640_GDA | 台南海線(1640) 接地RY | LINE161 | P06/161/1640/GDA |  |  |  | CDC | 367 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | CB | [17 empty] | 1-05-06 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 山上PS.1640_CB | 1640(台南海線) CB | LINE161 | P06/161/1640/CB |  |  |  | CDC | 368 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | 79UL | [17 empty] | 2-32-03 |  | 2-36 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1640_79UL | 台南海線(1640) 79RY U/L | LINE161 | P06/161/1640/79UL |  |  |  | CDC | 369 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | ABS1 | 1641 | [16 empty] | 1-34-04 | 1-34-05 | 1-4A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1641_ABS | 1641(台南海線) ABS | LINE161 | P06/161/1640/ABS1 |  |  |  | CDC | 370 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | ABS2 | 1642 | [16 empty] | 1-34-06 | 1-34-07 | 1-4B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1642_ABS | 1642(台南海線) ABS | LINE161 | P06/161/1640/ABS2 |  |  |  | CDC | 371 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | ABS3 | 1643 | [16 empty] | 1-34-08 | 1-34-09 | 1-4C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1643_ABS | 1643(台南海線) ABS | LINE161 | P06/161/1640/ABS3 |  |  |  | CDC | 372 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | E3 | 1643E | [16 empty] | 1-34-10 | 1-34-11 | 1-4D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1643E_ES | 1643E(台南海線) ES | LINE161 | P06/161/1640/ES3 |  |  |  | CDC | 373 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | PHA | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1710_PHA | 安南豐華紅線(1710) 相間RY | LINE161 | P06/161/1710/PHA |  |  |  | CDC | 374 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | GDA | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1710_GDA | 安南豐華紅線(1710) 接地RY | LINE161 | P06/161/1710/GDA |  |  |  | CDC | 375 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | CB | [17 empty] | 1-06-06 |  | 1-0D | [5 empty] | 161KV_S | [8 empty] | 山上PS.1710_CB | 1710(安南豐華紅線) CB | LINE161 | P06/161/1710/CB |  |  |  | CDC | 376 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | 79UL | [17 empty] | 2-32-07 |  | 2-3A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1710_79UL | 安南豐華紅線(1710) 79RY U/L | LINE161 | P06/161/1710/79UL |  |  |  | CDC | 377 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | ABS1 | 1711 | [16 empty] | 1-35-04 | 1-35-05 | 1-52 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1711_ABS | 1711(安南豐華紅線) ABS | LINE161 | P06/161/1710/ABS1 |  |  |  | CDC | 378 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | ABS2 | 1712 | [16 empty] | 1-35-06 | 1-35-07 | 1-53 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1712_ABS | 1712(安南豐華紅線) ABS | LINE161 | P06/161/1710/ABS2 |  |  |  | CDC | 379 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | ABS3 | 1713 | [16 empty] | 1-35-08 | 1-35-09 | 1-54 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1713_ABS | 1713(安南豐華紅線) ABS | LINE161 | P06/161/1710/ABS3 |  |  |  | CDC | 380 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | E3 | 1713E | [16 empty] | 1-35-10 | 1-35-11 | 1-55 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1713E_ES | 1713E(安南豐華紅線) ES | LINE161 | P06/161/1710/ES3 |  |  |  | CDC | 381 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | PHA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1720_PHA | 新化二路(1720) 相間RY | LINE161 | P06/161/1720/PHA |  |  |  | CDC | 382 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | GDA | [17 empty] | 1-07-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1720_GDA | 新化二路(1720) 接地RY | LINE161 | P06/161/1720/GDA |  |  |  | CDC | 383 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | CB | [17 empty] | 1-07-02 |  | 1-0E | [5 empty] | 161KV_S | [8 empty] | 山上PS.1720_CB | 1720(新化二路) CB | LINE161 | P06/161/1720/CB |  |  |  | CDC | 384 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | 79UL | [17 empty] | 2-32-09 |  | 2-3C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1720_79UL | 新化二路(1720) 79RY U/L | LINE161 | P06/161/1720/79UL |  |  |  | CDC | 385 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | ABS1 | 1721 | [16 empty] | 1-35-12 | 1-35-13 | 1-56 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1721_ABS | 1721(新化二路) ABS | LINE161 | P06/161/1720/ABS1 |  |  |  | CDC | 386 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | ABS2 | 1722 | [16 empty] | 1-35-14 | 1-35-15 | 1-57 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1722_ABS | 1722(新化二路) ABS | LINE161 | P06/161/1720/ABS2 |  |  |  | CDC | 387 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | ABS3 | 1723 | [16 empty] | 1-36-00 | 1-36-01 | 1-58 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1723_ABS | 1723(新化二路) ABS | LINE161 | P06/161/1720/ABS3 |  |  |  | CDC | 388 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | E3 | 1723E | [16 empty] | 1-36-02 | 1-36-03 | 1-59 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1723E_ES | 1723E(新化二路) ES | LINE161 | P06/161/1720/ES3 |  |  |  | CDC | 389 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | PHA | [17 empty] | 1-08-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1730_PHA | 新化一路(1730) 相間RY | LINE161 | P06/161/1730/PHA |  |  |  | CDC | 390 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1730_GDA | 新化一路(1730) 接地RY | LINE161 | P06/161/1730/GDA |  |  |  | CDC | 391 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | CB | [17 empty] | 1-07-06 |  | 1-0F | [5 empty] | 161KV_S | [8 empty] | 山上PS.1730_CB | 1730(新化一路) CB | LINE161 | P06/161/1730/CB |  |  |  | CDC | 392 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | 79UL | [17 empty] | 2-32-11 |  | 2-3E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1730_79UL | 新化一路(1730) 79RY U/L | LINE161 | P06/161/1730/79UL |  |  |  | CDC | 393 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | ABS1 | 1731 | [16 empty] | 1-36-04 | 1-36-05 | 1-5A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1731_ABS | 1731(新化一路) ABS | LINE161 | P06/161/1730/ABS1 |  |  |  | CDC | 394 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | ABS2 | 1732 | [16 empty] | 1-36-06 | 1-36-07 | 1-5B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1732_ABS | 1732(新化一路) ABS | LINE161 | P06/161/1730/ABS2 |  |  |  | CDC | 395 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | ABS3 | 1733 | [16 empty] | 1-36-08 | 1-36-09 | 1-5C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1733_ABS | 1733(新化一路) ABS | LINE161 | P06/161/1730/ABS3 |  |  |  | CDC | 396 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | E3 | 1733E | [16 empty] | 1-36-10 | 1-36-11 | 1-5D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1733E_ES | 1733E(新化一路) ES | LINE161 | P06/161/1730/ES3 |  |  |  | CDC | 397 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | 69KV_S | [8 empty] | 山上PS.610_PHA | 山頂一路(610) 相間RY | LINE69 | P06/69/610/PHA |  |  |  | CDC | 398 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | 69KV_S | [8 empty] | 山上PS.610_GDA | 山頂一路(610) 接地RY | LINE69 | P06/69/610/GDA |  |  |  | CDC | 399 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | CB | [17 empty] | 1-10-00 |  | 1-1D | [5 empty] | 69KV_S | [8 empty] | 山上PS.610_CB | 610(山頂一路) CB | LINE69 | P06/69/610/CB |  |  |  | CDC | 400 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | ABS1 | 611 | [16 empty] | 1-38-00 | 1-38-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 山上PS.611_ABS | 611(山頂一路) ABS | LINE69 | P06/69/610/ABS1 |  |  |  | CDC | 401 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | ABS2 | 612 | [16 empty] | 1-38-02 | 1-38-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 山上PS.612_ABS | 612(山頂一路) ABS | LINE69 | P06/69/610/ABS2 |  |  |  | CDC | 402 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | ABS3 | 613 | [16 empty] | 1-38-04 | 1-38-05 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 山上PS.613_ABS | 613(山頂一路) ABS | LINE69 | P06/69/610/ABS3 |  |  |  | CDC | 403 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | E3 | 613E | [16 empty] | 1-38-06 | 1-38-07 | 2-03 | [5 empty] | ADCS_S | [8 empty] | 山上PS.613E_ES | 613E(山頂一路) ES | LINE69 | P06/69/610/ES3 |  |  |  | CDC | 404 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | 69KV_S | [8 empty] | 山上PS.620_PHA | 山頂二路(620) 相間RY | LINE69 | P06/69/620/PHA |  |  |  | CDC | 405 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | 69KV_S | [8 empty] | 山上PS.620_GDA | 山頂二路(620) 接地RY | LINE69 | P06/69/620/GDA |  |  |  | CDC | 406 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | CB | [17 empty] | 1-10-03 |  | 1-1E | [5 empty] | 69KV_S | [8 empty] | 山上PS.620_CB | 620(山頂二路) CB | LINE69 | P06/69/620/CB |  |  |  | CDC | 407 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | ABS1 | 621 | [16 empty] | 1-38-08 | 1-38-09 | 2-04 | [5 empty] | ADCS_S | [8 empty] | 山上PS.621_ABS | 621(山頂二路) ABS | LINE69 | P06/69/620/ABS1 |  |  |  | CDC | 408 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | ABS2 | 622 | [16 empty] | 1-38-10 | 1-38-11 | 2-05 | [5 empty] | ADCS_S | [8 empty] | 山上PS.622_ABS | 622(山頂二路) ABS | LINE69 | P06/69/620/ABS2 |  |  |  | CDC | 409 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | ABS3 | 623 | [16 empty] | 1-38-12 | 1-38-13 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 山上PS.623_ABS | 623(山頂二路) ABS | LINE69 | P06/69/620/ABS3 |  |  |  | CDC | 410 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | E3 | 623E | [16 empty] | 1-38-14 | 1-38-15 | 2-07 | [5 empty] | ADCS_S | [8 empty] | 山上PS.623E_ES | 623E(山頂二路) ES | LINE69 | P06/69/620/ES3 |  |  |  | CDC | 411 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | 69KV_S | [8 empty] | 山上PS.630_PHA | 善化一路(630) 相間RY | LINE69 | P06/69/630/PHA |  |  |  | CDC | 412 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | 69KV_S | [8 empty] | 山上PS.630_GDA | 善化一路(630) 接地RY | LINE69 | P06/69/630/GDA |  |  |  | CDC | 413 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | 79UL | [17 empty] | 2-32-13 |  | 2-40 | [5 empty] | ADCS_S | [8 empty] | 山上PS.630_79UL | 善化一路(630) 79RY U/L | LINE69 | P06/69/630/79UL |  |  |  | CDC | 414 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | CB | [17 empty] | 1-10-06 |  | 1-1F | [5 empty] | 69KV_S | [8 empty] | 山上PS.630_CB | 630(善化一路) CB | LINE69 | P06/69/630/CB |  |  |  | CDC | 415 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | ABS1 | 631 | [16 empty] | 1-39-00 | 1-39-01 | 2-08 | [5 empty] | ADCS_S | [8 empty] | 山上PS.631_ABS | 631(善化一路) ABS | LINE69 | P06/69/630/ABS1 |  |  |  | CDC | 416 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | ABS2 | 632 | [16 empty] | 1-39-02 | 1-39-03 | 2-09 | [5 empty] | ADCS_S | [8 empty] | 山上PS.632_ABS | 632(善化一路) ABS | LINE69 | P06/69/630/ABS2 |  |  |  | CDC | 417 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | ABS3 | 633 | [16 empty] | 1-39-04 | 1-39-05 | 2-0A | [5 empty] | ADCS_S | [8 empty] | 山上PS.633_ABS | 633(善化一路) ABS | LINE69 | P06/69/630/ABS3 |  |  |  | CDC | 418 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | E3 | 633E | [16 empty] | 1-39-06 | 1-39-07 | 2-0B | [5 empty] | ADCS_S | [8 empty] | 山上PS.633E_ES | 633E(善化一路) ES | LINE69 | P06/69/630/ES3 |  |  |  | CDC | 419 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | 69KV_S | [8 empty] | 山上PS.640_PHA | 善化二路(640) 相間RY | LINE69 | P06/69/640/PHA |  |  |  | CDC | 420 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | 69KV_S | [8 empty] | 山上PS.640_GDA | 善化二路(640) 接地RY | LINE69 | P06/69/640/GDA |  |  |  | CDC | 421 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | 79UL | [17 empty] | 2-32-14 |  | 2-41 | [5 empty] | ADCS_S | [8 empty] | 山上PS.640_79UL | 善化二路(640) 79RY U/L | LINE69 | P06/69/640/79UL |  |  |  | CDC | 422 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | CB | [17 empty] | 1-11-01 |  | 1-20 | [5 empty] | 69KV_S | [8 empty] | 山上PS.640_CB | 640(善化二路) CB | LINE69 | P06/69/640/CB |  |  |  | CDC | 423 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | ABS1 | 641 | [16 empty] | 1-39-08 | 1-39-09 | 2-0C | [5 empty] | ADCS_S | [8 empty] | 山上PS.641_ABS | 641(善化二路) ABS | LINE69 | P06/69/640/ABS1 |  |  |  | CDC | 424 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | ABS2 | 642 | [16 empty] | 1-39-10 | 1-39-11 | 2-0D | [5 empty] | ADCS_S | [8 empty] | 山上PS.642_ABS | 642(善化二路) ABS | LINE69 | P06/69/640/ABS2 |  |  |  | CDC | 425 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | ABS3 | 643 | [16 empty] | 1-39-12 | 1-39-13 | 2-0E | [5 empty] | ADCS_S | [8 empty] | 山上PS.643_ABS | 643(善化二路) ABS | LINE69 | P06/69/640/ABS3 |  |  |  | CDC | 426 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | E3 | 643E | [16 empty] | 1-39-14 | 1-39-15 | 2-0F | [5 empty] | ADCS_S | [8 empty] | 山上PS.643E_ES | 643E(善化二路) ES | LINE69 | P06/69/640/ES3 |  |  |  | CDC | 427 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | 69KV_S | [8 empty] | 山上PS.650_PHA | 善化三路(650) 相間RY | LINE69 | P06/69/650/PHA |  |  |  | CDC | 428 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | 69KV_S | [8 empty] | 山上PS.650_GDA | 善化三路(650) 接地RY | LINE69 | P06/69/650/GDA |  |  |  | CDC | 429 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | CB | [17 empty] | 1-11-04 |  | 1-21 | [5 empty] | 69KV_S | [8 empty] | 山上PS.650_CB | 650(善化三路) CB | LINE69 | P06/69/650/CB |  |  |  | CDC | 430 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | ABS1 | 651 | [16 empty] | 1-3A-00 | 1-3A-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 山上PS.651_ABS | 651(善化三路) ABS | LINE69 | P06/69/650/ABS1 |  |  |  | CDC | 431 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | ABS2 | 652 | [16 empty] | 1-3A-02 | 1-3A-03 | 2-11 | [5 empty] | ADCS_S | [8 empty] | 山上PS.652_ABS | 652(善化三路) ABS | LINE69 | P06/69/650/ABS2 |  |  |  | CDC | 432 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | ABS3 | 653 | [16 empty] | 1-3A-04 | 1-3A-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 山上PS.653_ABS | 653(善化三路) ABS | LINE69 | P06/69/650/ABS3 |  |  |  | CDC | 433 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | E3 | 653E | [16 empty] | 1-3A-06 | 1-3A-07 | 2-13 | [5 empty] | ADCS_S | [8 empty] | 山上PS.653E_ES | 653E(善化三路) ES | LINE69 | P06/69/650/ES3 |  |  |  | CDC | 434 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | PHA | [17 empty] | 1-12-00 | [7 empty] | 69KV_S | [8 empty] | 山上PS.660_PHA | 新市一路(660) 相間RY | LINE69 | P06/69/660/PHA |  |  |  | CDC | 435 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | GDA | [17 empty] | 1-12-01 | [7 empty] | 69KV_S | [8 empty] | 山上PS.660_GDA | 新市一路(660) 接地RY | LINE69 | P06/69/660/GDA |  |  |  | CDC | 436 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | CB | [17 empty] | 1-11-07 |  | 1-22 | [5 empty] | 69KV_S | [8 empty] | 山上PS.660_CB | 660(新市一路) CB | LINE69 | P06/69/660/CB |  |  |  | CDC | 437 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | ABS1 | 661 | [16 empty] | 1-3A-08 | 1-3A-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 山上PS.661_ABS | 661(新市一路) ABS | LINE69 | P06/69/660/ABS1 |  |  |  | CDC | 438 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | ABS2 | 662 | [16 empty] | 1-3A-10 | 1-3A-11 | 2-15 | [5 empty] | ADCS_S | [8 empty] | 山上PS.662_ABS | 662(新市一路) ABS | LINE69 | P06/69/660/ABS2 |  |  |  | CDC | 439 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | ABS3 | 663 | [16 empty] | 1-3A-12 | 1-3A-13 | 2-16 | [5 empty] | ADCS_S | [8 empty] | 山上PS.663_ABS | 663(新市一路) ABS | LINE69 | P06/69/660/ABS3 |  |  |  | CDC | 440 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | E3 | 663E | [16 empty] | 1-3A-14 | 1-3A-15 | 2-17 | [5 empty] | ADCS_S | [8 empty] | 山上PS.663E_ES | 663E(新市一路) ES | LINE69 | P06/69/660/ES3 |  |  |  | CDC | 441 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | PHA | [17 empty] | 1-12-03 | [7 empty] | 69KV_S | [8 empty] | 山上PS.670_PHA | 山上新市三路(670) 相間RY | LINE69 | P06/69/670/PHA |  |  |  | CDC | 442 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | GDA | [17 empty] | 1-12-04 | [7 empty] | 69KV_S | [8 empty] | 山上PS.670_GDA | 山上新市三路(670) 接地RY | LINE69 | P06/69/670/GDA |  |  |  | CDC | 443 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | CB | [17 empty] | 1-12-02 |  | 1-23 | [5 empty] | 69KV_S | [8 empty] | 山上PS.670_CB | 670(山上新市三路) CB | LINE69 | P06/69/670/CB |  |  |  | CDC | 444 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | ABS1 | 671 | [16 empty] | 1-3B-00 | 1-3B-01 | 2-18 | [5 empty] | ADCS_S | [8 empty] | 山上PS.671_ABS | 671(山上新市三路) ABS | LINE69 | P06/69/670/ABS1 |  |  |  | CDC | 445 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | ABS2 | 672 | [16 empty] | 1-3B-02 | 1-3B-03 | 2-19 | [5 empty] | ADCS_S | [8 empty] | 山上PS.672_ABS | 672(山上新市三路) ABS | LINE69 | P06/69/670/ABS2 |  |  |  | CDC | 446 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | ABS3 | 673 | [16 empty] | 1-3B-04 | 1-3B-05 | 2-1A | [5 empty] | ADCS_S | [8 empty] | 山上PS.673_ABS | 673(山上新市三路) ABS | LINE69 | P06/69/670/ABS3 |  |  |  | CDC | 447 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | E3 | 673E | [16 empty] | 1-3B-06 | 1-3B-07 | 2-1B | [5 empty] | ADCS_S | [8 empty] | 山上PS.673E_ES | 673E(山上新市三路) ES | LINE69 | P06/69/670/ES3 |  |  |  | CDC | 448 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | 69KV_S | [8 empty] | 山上PS.680_PHA | 歸仁線(680) 相間RY | LINE69 | P06/69/680/PHA |  |  |  | CDC | 449 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | 69KV_S | [8 empty] | 山上PS.680_GDA | 歸仁線(680) 接地RY | LINE69 | P06/69/680/GDA |  |  |  | CDC | 450 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | CB | [17 empty] | 1-12-05 |  | 1-24 | [5 empty] | 69KV_S | [8 empty] | 山上PS.680_CB | 680(歸仁線) CB | LINE69 | P06/69/680/CB |  |  |  | CDC | 451 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | ABS1 | 681 | [16 empty] | 1-3B-08 | 1-3B-09 | 2-1C | [5 empty] | ADCS_S | [8 empty] | 山上PS.681_ABS | 681(歸仁線) ABS | LINE69 | P06/69/680/ABS1 |  |  |  | CDC | 452 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | ABS2 | 682 | [16 empty] | 1-3B-10 | 1-3B-11 | 2-1D | [5 empty] | ADCS_S | [8 empty] | 山上PS.682_ABS | 682(歸仁線) ABS | LINE69 | P06/69/680/ABS2 |  |  |  | CDC | 453 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | ABS3 | 683 | [16 empty] | 1-3B-12 | 1-3B-13 | 2-1E | [5 empty] | ADCS_S | [8 empty] | 山上PS.683_ABS | 683(歸仁線) ABS | LINE69 | P06/69/680/ABS3 |  |  |  | CDC | 454 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | E3 | 683E | [16 empty] | 1-3B-14 | 1-3B-15 | 2-1F | [5 empty] | ADCS_S | [8 empty] | 山上PS.683E_ES | 683E(歸仁線) ES | LINE69 | P06/69/680/ES3 |  |  |  | CDC | 455 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | 69KV_S | [8 empty] | 山上PS.710_PHA | 新市二路(710) 相間RY | LINE69 | P06/69/710/PHA |  |  |  | CDC | 456 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | 69KV_S | [8 empty] | 山上PS.710_GDA | 新市二路(710) 接地RY | LINE69 | P06/69/710/GDA |  |  |  | CDC | 457 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | CB | [17 empty] | 1-13-00 |  | 1-25 | [5 empty] | 69KV_S | [8 empty] | 山上PS.710_CB | 710(新市二路) CB | LINE69 | P06/69/710/CB |  |  |  | CDC | 458 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | ABS1 | 711 | [16 empty] | 1-3C-00 | 1-3C-01 | 2-20 | [5 empty] | ADCS_S | [8 empty] | 山上PS.711_ABS | 711(新市二路) ABS | LINE69 | P06/69/710/ABS1 |  |  |  | CDC | 459 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | ABS2 | 712 | [16 empty] | 1-3C-02 | 1-3C-03 | 2-21 | [5 empty] | ADCS_S | [8 empty] | 山上PS.712_ABS | 712(新市二路) ABS | LINE69 | P06/69/710/ABS2 |  |  |  | CDC | 460 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | ABS3 | 713 | [16 empty] | 1-3C-04 | 1-3C-05 | 2-22 | [5 empty] | ADCS_S | [8 empty] | 山上PS.713_ABS | 713(新市二路) ABS | LINE69 | P06/69/710/ABS3 |  |  |  | CDC | 461 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | E3 | 713E | [16 empty] | 1-3C-06 | 1-3C-07 | 2-23 | [5 empty] | ADCS_S | [8 empty] | 山上PS.713E_ES | 713E(新市二路) ES | LINE69 | P06/69/710/ES3 |  |  |  | CDC | 462 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-08-02 |  | 1-18 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1500_CB | 1500(TIE) CB | TIE | P06/161/1500/CB |  |  |  | CDC | 463 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-08-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1500_50A | 161KV TIE(1500) 50RY | TIE | P06/161/1500/50A |  |  |  | CDC | 464 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1501 | [16 empty] | 1-36-12 | 1-36-13 | 1-5E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1501_ABS | 1501(TIE) ABS | TIE | P06/161/1500/ABS1 |  |  |  | CDC | 465 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS2 | 1502 | [16 empty] | 1-36-14 | 1-36-15 | 1-5F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1502_ABS | 1502(TIE) ABS | TIE | P06/161/1500/ABS2 |  |  |  | CDC | 466 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-08-06 |  | 1-19 | [5 empty] | 69KV_S | [8 empty] | 山上PS.600_CB | 600(TIE) CB | TIE | P06/69/600/CB |  |  |  | CDC | 467 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | [16 empty] | 1-37-00 | 1-37-01 | 1-60 | [5 empty] | ADCS_S | [8 empty] | 山上PS.601_ABS | 601(TIE) ABS | TIE | P06/69/600/ABS1 |  |  |  | CDC | 468 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | [16 empty] | 1-37-02 | 1-37-03 | 1-61 | [5 empty] | ADCS_S | [8 empty] | 山上PS.602_ABS | 602(TIE) ABS | TIE | P06/69/600/ABS2 |  |  |  | CDC | 469 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1650_CB | 1650(#1MTR) CB | MTR | P06/161/1650/CB |  |  |  | CDC | 470 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-1A | [5 empty] | 69KV_S | [8 empty] | 山上PS.750_CB | 750(#1MTR) CB | MTR | P06/69/750/CB |  |  |  | CDC | 471 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | PHA | [17 empty] | 1-00-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_PHA | #1MTR PHA | OTHER | P06//1MTR/PHA1 |  |  |  | CDC | 472 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | P06//1MTR/51ZA |  |  |  | CDC | 473 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#1MTR_87A | #1MTR 87RY | MTR | P06//1MTR/87A |  |  |  | CDC | 474 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | P06//1MTR/96PA |  |  |  | CDC | 475 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 2-36-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_96D | #1MTR 96D RY | MTR | P06//1MTR/96D |  |  |  | CDC | 476 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 2-36-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_96P | #1MTR 96P RY | MTR | P06//1MTR/96P |  |  |  | CDC | 477 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 2-36-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_63Q | #1MTR 63Q RY | MTR | P06//1MTR/63Q |  |  |  | CDC | 478 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 2-36-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | P06//1MTR/96B1 |  |  |  | CDC | 479 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 2-36-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | P06//1MTR/96B2 |  |  |  | CDC | 480 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_TRA | #1MTR 重故障 | MTR | P06//1MTR/TRA |  |  |  | CDC | 481 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 2-30-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_TRF | #1MTR 輕故障 | MTR | P06//1MTR/TRF |  |  |  | CDC | 482 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 2-30-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | P06//1MTR/SupLocal |  |  |  | CDC | 483 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 2-30-01 |  | 2-42 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | P06//1MTR/Tap Chan |  |  |  | CDC | 484 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | M/F/I | [17 empty] | 2-30-04 | 2-30-05 | 2-44 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | P06//1MTR/M_F_I |  |  |  | CDC | 485 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS1 | 1651 | [16 empty] | 1-30-00 | 1-30-01 | 1-28 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1651_ABS | 1651(#1MTR) ABS | MTR | P06/161/1650/ABS1 |  |  |  | CDC | 486 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS2 | 1652 | [16 empty] | 1-30-02 | 1-30-03 | 1-29 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1652_ABS | 1652(#1MTR) ABS | MTR | P06/161/1650/ABS2 |  |  |  | CDC | 487 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-37-04 | 1-37-05 | 1-62 | [5 empty] | ADCS_S | [8 empty] | 山上PS.751_ABS | 751(#1MTR) ABS | MTR | P06/69/750/ABS1 |  |  |  | CDC | 488 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS2 | 752 | [16 empty] | 1-37-06 | 1-37-07 | 1-63 | [5 empty] | ADCS_S | [8 empty] | 山上PS.752_ABS | 752(#1MTR) ABS | MTR | P06/69/750/ABS2 |  |  |  | CDC | 489 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | [17 empty] | 1-00-06 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1660_CB | 1660(#2MTR) CB | MTR | P06/161/1660/CB |  |  |  | CDC | 490 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-00-07 |  | 1-1B | [5 empty] | 69KV_S | [8 empty] | 山上PS.760_CB | 760(#2MTR) CB | MTR | P06/69/760/CB |  |  |  | CDC | 491 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | PHA | [17 empty] | 1-01-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_PHA | #2MTR PHA | OTHER | P06//2MTR/PHA1 |  |  |  | CDC | 492 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | P06//2MTR/51ZA |  |  |  | CDC | 493 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#2MTR_87A | #2MTR 87RY | MTR | P06//2MTR/87A |  |  |  | CDC | 494 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | P06//2MTR/96PA |  |  |  | CDC | 495 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 2-36-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_96D | #2MTR 96D RY | MTR | P06//2MTR/96D |  |  |  | CDC | 496 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 2-36-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_96P | #2MTR 96P RY | MTR | P06//2MTR/96P |  |  |  | CDC | 497 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 2-36-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_63Q | #2MTR 63Q RY | MTR | P06//2MTR/63Q |  |  |  | CDC | 498 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 2-36-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | P06//2MTR/96B1 |  |  |  | CDC | 499 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 2-36-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | P06//2MTR/96B2 |  |  |  | CDC | 500 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 2-30-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_TRA | #2MTR 重故障 | MTR | P06//2MTR/TRA |  |  |  | CDC | 501 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 2-30-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_TRF | #2MTR 輕故障 | MTR | P06//2MTR/TRF |  |  |  | CDC | 502 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 2-30-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | P06//2MTR/SupLocal |  |  |  | CDC | 503 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 2-30-08 |  | 2-46 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | P06//2MTR/Tap Chan |  |  |  | CDC | 504 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | M/F/I | [17 empty] | 2-30-12 | 2-30-13 | 2-48 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | P06//2MTR/M_F_I |  |  |  | CDC | 505 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | [16 empty] | 1-30-04 | 1-30-05 | 1-2A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1661_ABS | 1661(#2MTR) ABS | MTR | P06/161/1660/ABS1 |  |  |  | CDC | 506 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | [16 empty] | 1-30-06 | 1-30-07 | 1-2B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1662_ABS | 1662(#2MTR) ABS | MTR | P06/161/1660/ABS2 |  |  |  | CDC | 507 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-37-08 | 1-37-09 | 1-64 | [5 empty] | ADCS_S | [8 empty] | 山上PS.761_ABS | 761(#2MTR) ABS | MTR | P06/69/760/ABS1 |  |  |  | CDC | 508 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | [16 empty] | 1-37-10 | 1-37-11 | 1-65 | [5 empty] | ADCS_S | [8 empty] | 山上PS.762_ABS | 762(#2MTR) ABS | MTR | P06/69/760/ABS2 |  |  |  | CDC | 509 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB | [17 empty] | 1-01-04 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1670_CB | 1670(#3MTR) CB | MTR | P06/161/1670/CB |  |  |  | CDC | 510 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-01-05 |  | 1-1C | [5 empty] | 69KV_S | [8 empty] | 山上PS.770_CB | 770(#3MTR) CB | MTR | P06/69/770/CB |  |  |  | CDC | 511 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | PHA | [17 empty] | 1-01-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_PHA | #3MTR PHA | OTHER | P06//3MTR/PHA1 |  |  |  | CDC | 512 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | P06//3MTR/51ZA |  |  |  | CDC | 513 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#3MTR_87A | #3MTR 87RY | MTR | P06//3MTR/87A |  |  |  | CDC | 514 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | P06//3MTR/96PA |  |  |  | CDC | 515 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 2-36-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_96D | #3MTR 96D RY | MTR | P06//3MTR/96D |  |  |  | CDC | 516 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 2-36-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_96P | #3MTR 96P RY | MTR | P06//3MTR/96P |  |  |  | CDC | 517 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 2-36-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_63Q | #3MTR 63Q RY | MTR | P06//3MTR/63Q |  |  |  | CDC | 518 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 2-36-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | P06//3MTR/96B1 |  |  |  | CDC | 519 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 2-31-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_TRA | #3MTR 重故障 | MTR | P06//3MTR/TRA |  |  |  | CDC | 520 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 2-31-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_TRF | #3MTR 輕故障 | MTR | P06//3MTR/TRF |  |  |  | CDC | 521 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 2-30-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | P06//3MTR/SupLocal |  |  |  | CDC | 522 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 2-30-15 |  | 2-4A | [5 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | P06//3MTR/Tap Chan |  |  |  | CDC | 523 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | M/F/I | [17 empty] | 2-31-02 | 2-31-03 | 2-4C | [5 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | P06//3MTR/M_F_I |  |  |  | CDC | 524 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | [16 empty] | 1-30-08 | 1-30-09 | 1-2C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1671_ABS | 1671(#3MTR) ABS | MTR | P06/161/1670/ABS1 |  |  |  | CDC | 525 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | [16 empty] | 1-30-10 | 1-30-11 | 1-2D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1672_ABS | 1672(#3MTR) ABS | MTR | P06/161/1670/ABS2 |  |  |  | CDC | 526 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-37-12 | 1-37-13 | 1-66 | [5 empty] | ADCS_S | [8 empty] | 山上PS.771_ABS | 771(#3MTR) ABS | MTR | P06/69/770/ABS1 |  |  |  | CDC | 527 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | [16 empty] | 1-37-14 | 1-37-15 | 1-67 | [5 empty] | ADCS_S | [8 empty] | 山上PS.772_ABS | 772(#3MTR) ABS | MTR | P06/69/770/ABS2 |  |  |  | CDC | 528 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | CB | [17 empty] | 1-13-03 |  | 1-26 | [5 empty] | 69KV_S | [8 empty] | 山上PS.820_CB | 820(69KV #2SC) CB | SC | P06/69/820/CB |  |  |  | CDC | 529 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | [16 empty] | 1-3C-08 | 1-3C-09 | 2-24 | [5 empty] | ADCS_S | [8 empty] | 山上PS.821_ABS | 821(69KV #2SC) ABS | SC | P06/69/820/ABS1 |  |  |  | CDC | 530 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | [16 empty] | 1-3C-10 | 1-3C-11 | 2-25 | [5 empty] | ADCS_S | [8 empty] | 山上PS.822_ABS | 822(69KV #2SC) ABS | SC | P06/69/820/ABS2 |  |  |  | CDC | 531 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | SCA | [17 empty] | 1-13-04 | [7 empty] | 69KV_S | [8 empty] | 山上PS.820_SCA | 69KV #2SC 51,51N RY | SC | P06/69/820/SCA |  |  |  | CDC | 532 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | UVA | [17 empty] | 1-13-05 | [7 empty] | 69KV_S | [8 empty] | 山上PS.820_OUVA | 69KV #2SC 27,59RY | SC | P06/69/820/UVA |  |  |  | CDC | 533 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | CB | [17 empty] | 1-13-06 |  | 1-27 | [5 empty] | 69KV_S | [8 empty] | 山上PS.830_CB | 830(69KV #3SC) CB | SC | P06/69/830/CB |  |  |  | CDC | 534 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | [16 empty] | 1-3C-12 | 1-3C-13 | 2-26 | [5 empty] | ADCS_S | [8 empty] | 山上PS.831_ABS | 831(69KV #3SC) ABS | SC | P06/69/830/ABS1 |  |  |  | CDC | 535 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | [16 empty] | 1-3C-14 | 1-3C-15 | 2-27 | [5 empty] | ADCS_S | [8 empty] | 山上PS.832_ABS | 832(69KV #3SC) ABS | SC | P06/69/830/ABS2 |  |  |  | CDC | 536 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | SCA | [17 empty] | 1-13-07 | [7 empty] | 69KV_S | [8 empty] | 山上PS.830_SCA | 69KV #3SC 51,51N RY | SC | P06/69/830/SCA |  |  |  | CDC | 537 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | UVA | [17 empty] | 1-14-00 | [7 empty] | 69KV_S | [8 empty] | 山上PS.830_OUVA | 69KV #3SC 27,59RY | SC | P06/69/830/UVA |  |  |  | CDC | 538 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | P06/161/1BUS/BUS_VUA |  |  |  | CDC | 539 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-08-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | P06/161/1BUS/87A |  |  |  | CDC | 540 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 2-32-15 |  | 2-55 | [5 empty] | ADCS_S | [8 empty] | 山上PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | P06/161/1BUS/87UL |  |  |  | CDC | 541 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | P06/161/2BUS/BUS_VUA |  |  |  | CDC | 542 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-08-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | P06/161/2BUS/87A |  |  |  | CDC | 543 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 2-33-00 |  | 2-54 | [5 empty] | ADCS_S | [8 empty] | 山上PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | P06/161/2BUS/87UL |  |  |  | CDC | 544 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | P06/69/1BUS/BUS_VUA |  |  |  | CDC | 545 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-08-07 | [7 empty] | 69KV_S | [8 empty] | 山上PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | P06/69/1BUS/87A |  |  |  | CDC | 546 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 2-33-01 |  | 3-22 | [5 empty] | ADCS_S | [8 empty] | 山上PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | P06/69/1BUS/87UL |  |  |  | CDC | 547 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | P06/69/2BUS/BUS_VUA |  |  |  | CDC | 548 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-09-00 | [7 empty] | 69KV_S | [8 empty] | 山上PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | P06/69/2BUS/87A |  |  |  | CDC | 549 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 2-33-02 |  | 3-23 | [5 empty] | ADCS_S | [8 empty] | 山上PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | P06/69/2BUS/87UL |  |  |  | CDC | 550 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-34-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | P06/161/ComPoint/ABS_89A |  |  |  | CDC | 551 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_CBA | 161KV斷路器重故障 | OTHER | P06/161/ComPoint/CBA |  |  |  | CDC | 552 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | P06/161/ComPoint/CBF |  |  |  | CDC | 553 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-09-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | P06/161/ComPoint/OSCA |  |  |  | CDC | 554 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0A-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | P06/161/ComPoint/RCA |  |  |  | CDC | 555 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-34-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | P06/69/ComPoint/ABS_89A |  |  |  | CDC | 556 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV |  |  |  | CBA | [17 empty] | 2-33-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_CBA | 69KV斷路器重故障 | OTHER | P06/69/ComPoint/CBA |  |  |  | CDC | 557 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV |  |  |  | CBF | [17 empty] | 2-33-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | P06/69/ComPoint/CBF |  |  |  | CDC | 558 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV |  |  |  | OSCA | [17 empty] | 1-09-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | P06/69/ComPoint/OSCA |  |  |  | CDC | 559 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-3D-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | P06/0/RTU/RTU_R_L |  |  |  | CDC | 560 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P06 | 山上PS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-3D-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 山上PS.TEST_CB | TEST CB | OTHER | P06/0/RTU/Test_CB |  |  |  | CDC | 561 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-35-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | P06/0/StaDev/Fire1 |  |  |  | CDC | 562 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Fire2 | [17 empty] | 2-35-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | P06/0/StaDev/Fire2 |  |  |  | CDC | 563 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Fire3 | [17 empty] | 2-35-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.火災警報(3) | 火災警報(3) | OTHER | P06/0/StaDev/Fire3 |  |  |  | CDC | 564 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-33-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | P06/0/ComPoint/25PFA |  |  |  | CDC | 565 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | 25TA | [17 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | P06/0/ComPoint/25TA |  |  |  | CDC | 566 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-34-09 |  | 2-4E | [5 empty] | ADCS_S | [8 empty] | 山上PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | P06/0/StaDev/ACB1 |  |  |  | CDC | 567 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P06 | 山上PS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-34-11 |  | 2-50 | [5 empty] | ADCS_S | [8 empty] | 山上PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | P06/0/StaDev/ACB2 |  |  |  | CDC | 568 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P06 | 山上PS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 2-34-10 |  | 2-4F | [5 empty] | ADCS_S | [8 empty] | 山上PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | P06/0/StaDev/ACBT |  |  |  | CDC | 569 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P06 | 山上PS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | P06/0/StaDev/STUV |  |  |  | CDC | 570 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.直流電源DCA | 直流電源故障警報 | OTHER | P06/0/StaDev/DCA |  |  |  | CDC | 571 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | DCE | [17 empty] | 2-34-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.直流電源DCE | 直流電源接地故障警報 | OTHER | P06/0/StaDev/DCE |  |  |  | CDC | 572 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-35-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.無人化防盜(1) | 無人化防盜(1) | OTHER | P06/0/StaDev/Burglar1 |  |  |  | CDC | 573 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Burglar2 | [17 empty] | 2-35-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.無人化防盜(2) | 無人化防盜(2) | OTHER | P06/0/StaDev/Burglar2 |  |  |  | CDC | 574 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Burglar3 | [17 empty] | 2-35-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.無人化防盜(3) | 無人化防盜(3) | OTHER | P06/0/StaDev/Burglar3 |  |  |  | CDC | 575 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | Door1 | [17 empty] | 2-35-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | P06/0/StaDev/Door1 |  |  |  | CDC | 576 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
P06 | 山上PS | 0 |  |  |  |  | Door2 | [17 empty] | 2-35-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | P06/0/StaDev/Door2 |  |  |  | CDC | 577 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-35-10 |  | 2-51 | [5 empty] | ADCS_S | [8 empty] | 山上PS.開關場照明(A) | 161KV開關場照明 | OTHER | P06/0/StaDev/Lights1 |  |  |  | CDC | 578 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P06 | 山上PS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-35-11 |  | 2-52 | [5 empty] | ADCS_S | [8 empty] | 山上PS.開關場照明(B) | 69KV開關場照明 | OTHER | P06/0/StaDev/Lights2 |  |  |  | CDC | 579 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P06 | 山上PS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 2-35-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | P06/0/StaDev/AIRCON |  |  |  | CDC | 580 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | PHA | [17 empty] | 1-0A-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1550_PHA | 豐德紅線(1550) 相間RY | LINE161 | P06/161/1550/PHA |  |  |  | CDC | 581 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1550_GDA | 豐德紅線(1550) 接地RY | LINE161 | P06/161/1550/GDA |  |  |  | CDC | 582 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | CB | [17 empty] | 1-0A-01 |  | 1-10 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1550_CB | 1550(豐德紅線) CB | LINE161 | P06/161/1550/CB |  |  |  | CDC | 583 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | DS1 | 1551 | [16 empty] | 2-38-00 | 2-38-01 | 1-68 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1551_DS | 1551(豐德紅線) DS | LINE161 | P06/161/1550/DS1 |  |  |  | CDC | 584 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | DS2 | 1552 | [16 empty] | 2-38-02 | 2-38-03 | 1-69 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1552_DS | 1552(豐德紅線) DS | LINE161 | P06/161/1550/DS2 |  |  |  | CDC | 585 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | DS3 | 1553 | [16 empty] | 2-38-04 | 2-38-05 | 1-6A | [5 empty] | ADCS_S | [8 empty] | 山上PS.1553_DS | 1553(豐德紅線) DS | LINE161 | P06/161/1550/DS3 |  |  |  | CDC | 586 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | E3 | 1553E | [16 empty] | 2-38-06 | 2-38-07 | 1-6B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1553E_ES | 1553E(豐德紅線) ES | LINE161 | P06/161/1550/ES3 |  |  |  | CDC | 587 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | PHA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1560_PHA | 豐德白線(1560) 相間RY | LINE161 | P06/161/1560/PHA |  |  |  | CDC | 588 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | GDA | [17 empty] | 1-0B-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1560_GDA | 豐德白線(1560) 接地RY | LINE161 | P06/161/1560/GDA |  |  |  | CDC | 589 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | CB | [17 empty] | 1-0A-06 |  | 1-11 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1560_CB | 1560(豐德白線) CB | LINE161 | P06/161/1560/CB |  |  |  | CDC | 590 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | DS1 | 1561 | [16 empty] | 2-38-08 | 2-38-09 | 1-6C | [5 empty] | ADCS_S | [8 empty] | 山上PS.1561_DS | 1561(豐德白線) DS | LINE161 | P06/161/1560/DS1 |  |  |  | CDC | 591 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | DS2 | 1562 | [16 empty] | 2-38-10 | 2-38-11 | 1-6D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1562_DS | 1562(豐德白線) DS | LINE161 | P06/161/1560/DS2 |  |  |  | CDC | 592 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | DS3 | 1563 | [16 empty] | 2-38-12 | 2-38-13 | 1-6E | [5 empty] | ADCS_S | [8 empty] | 山上PS.1563_DS | 1563(豐德白線) DS | LINE161 | P06/161/1560/DS3 |  |  |  | CDC | 593 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | E3 | 1563E | [16 empty] | 2-38-14 | 2-38-15 | 1-6F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1563E_ES | 1563E(豐德白線) ES | LINE161 | P06/161/1560/ES3 |  |  |  | CDC | 594 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1630_87A | 山上仁德線(1630) 87RY | LINE161 | P06/161/1630/87A |  |  |  | CDC | 595 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | 87A | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1510_87A | 嘉義新營紅線(1510) 87RY | LINE161 | P06/161/1510/87A |  |  |  | CDC | 596 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | P06/0/StaDev/CHG1 |  |  |  | CDC | 597 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-39-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | P06/0/StaDev/CHG2 |  |  |  | CDC | 598 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-34-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | P06/161/1500/50SA |  |  |  | CDC | 599 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820 | #2SC(820) |  | NCA | [17 empty] | 2-34-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.820_NCA | 69KV #2SC NCT RY | SC | P06/69/820/NCA |  |  |  | CDC | 600 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 830 | #3SC(830) |  | NCA | [17 empty] | 2-34-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.830_NCA | 69KV #3SC NCT RY | SC | P06/69/830/NCA |  |  |  | CDC | 601 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | 87A | [17 empty] | 1-04-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1620_87A | 龍崎二甲四路(1620) 87RY | LINE161 | P06/161/1620/87A |  |  |  | CDC | 602 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | 87UL | [17 empty] | 2-32-00 |  | 2-33 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1620_87UL | 龍崎二甲四路(1620) 87RY U/L | LINE161 | P06/161/1620/87UL |  |  |  | CDC | 603 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1570 | 龍崎一路(1570) |  | DTTA | [17 empty] | 2-39-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1570_DTTA | 龍崎一路(1570) 遠方遙跳 | OTHER | P06/161/1570/DTTA |  |  |  | CDC | 604 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1580 | 龍崎二路(1580) |  | DTTA | [17 empty] | 2-39-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1580_DTTA | 龍崎二路(1580) 遠方遙跳 | OTHER | P06/161/1580/DTTA |  |  |  | CDC | 605 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1610 | 龍崎二甲三路(1610) |  | DTTA | [17 empty] | 2-39-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1610_DTTA | 龍崎二甲三路(1610) 遠方遙跳 | OTHER | P06/161/1610/DTTA |  |  |  | CDC | 606 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1620 | 龍崎二甲四路(1620) |  | DTTA | [17 empty] | 2-39-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1620_DTTA | 龍崎二甲四路(1620) 遠方遙跳 | OTHER | P06/161/1620/DTTA |  |  |  | CDC | 607 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | 87A | [17 empty] | 1-04-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1610_87A | 龍崎二甲三路(1610) 87RY | LINE161 | P06/161/1610/87A |  |  |  | CDC | 608 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | 87UL | [17 empty] | 2-31-14 |  | 2-31 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1610_87UL | 龍崎二甲三路(1610) 87RY U/L | LINE161 | P06/161/1610/87UL |  |  |  | CDC | 609 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | 87A | [17 empty] | 1-03-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1580_87A | 龍崎山上二路(1580) 87RY | LINE161 | P06/161/1580/87A |  |  |  | CDC | 610 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | 87UL | [17 empty] | 2-31-12 |  | 2-2F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1580_87UL | 龍崎山上二路(1580) 87RY U/L | LINE161 | P06/161/1580/87UL |  |  |  | CDC | 611 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  |  |  |  | CommACF | [17 empty] | 2-39-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | P06/0/StaDev/CommACF |  |  |  | CDC | 612 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | 87A | [17 empty] | 1-03-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1570_87A | 龍崎山上一路(1570) 87RY | LINE161 | P06/161/1570/87A |  |  |  | CDC | 613 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | 87UL | [17 empty] | 2-31-10 |  | 2-2D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1570_87UL | 龍崎山上一路(1570) 87RY U/L | LINE161 | P06/161/1570/87UL |  |  |  | CDC | 614 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | 87A | [17 empty] | 1-05-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1640_87A | 台南海線(1640) 87RY | LINE161 | P06/161/1640/87A |  |  |  | CDC | 615 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | 87UL | [17 empty] | 2-32-04 |  | 2-37 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1640_87UL | 台南海線(1640) 87RY U/L | LINE161 | P06/161/1640/87UL |  |  |  | CDC | 616 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-39-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.通信機房溫度 | 通信機房溫度警報 | OTHER | P06/0/StaDev/R_Temp |  |  |  | CDC | 617 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-39-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.水位警報(1) | 地下室水位警報(1) | OTHER | P06/0/StaDev/Water1 |  |  |  | CDC | 618 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-39-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.水位警報(2) | 地下室水位警報(2) | OTHER | P06/0/StaDev/Water2 |  |  |  | CDC | 619 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | 87A | [17 empty] | 1-0A-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1550_87A | 豐德紅線(1550) 87RY | LINE161 | P06/161/1550/87A |  |  |  | CDC | 620 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | 87A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1560_87A | 豐德白線(1560) 87RY | LINE161 | P06/161/1560/87A |  |  |  | CDC | 621 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | 87A | [17 empty] | 1-07-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1730_87A | 新化一路(1730) 87RY | LINE161 | P06/161/1730/87A |  |  |  | CDC | 622 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | 87UL | [17 empty] | 2-32-12 |  | 2-3F | [5 empty] | ADCS_S | [8 empty] | 山上PS.1730_87UL | 新化一路(1730) 87RY U/L | LINE161 | P06/161/1730/87UL |  |  |  | CDC | 623 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1720_87A | 新化二路(1720) 87RY | LINE161 | P06/161/1720/87A |  |  |  | CDC | 624 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | 87UL | [17 empty] | 2-32-10 |  | 2-3D | [5 empty] | ADCS_S | [8 empty] | 山上PS.1720_87UL | 新化二路(1720) 87RY U/L | LINE161 | P06/161/1720/87UL |  |  |  | CDC | 625 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-39-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | P06/161/ComPoint/OSCF |  |  |  | CDC | 626 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV |  |  |  | OSCF | [17 empty] | 2-39-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | P06/69/ComPoint/OSCF |  |  |  | CDC | 627 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1540 | 鹽行豐華白線(1540) |  | RYFA | [17 empty] | 2-35-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1540_RYFA | 鹽行豐華白線(1540)數位電驛故障 | OTHER | P06/161/1540/RYFA |  |  |  | CDC | 628 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1510 | 嘉義新營紅線(1510) |  | 87CFA | [17 empty] | 2-37-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1510_87CFA | 嘉義新營紅線(1510)87RY通訊故障 | OTHER | P06/161/1510/87CFA |  |  |  | CDC | 629 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1510 | 嘉義新營紅線(1510) |  | RYFA | [17 empty] | 2-37-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1510_RYFA | 嘉義新營紅線(1510)數位電驛故障 | OTHER | P06/161/1510/RYFA |  |  |  | CDC | 630 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1550_1560 | 豐德紅白線(1550 1560) |  | CFA | [17 empty] | 2-37-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1550_1560_CFA | 豐德紅白線(1550 1560)通訊故障 | OTHER | P06/161/1550/85CFA |  |  |  | CDC | 631 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1550_1560 | 豐德紅白線(1550 1560) |  | RYFA | [17 empty] | 2-37-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1550_1560_RYFA | 豐德紅白線(1550 1560)RY故障 | OTHER | P06/161/1550/RYFA |  |  |  | CDC | 632 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1570 | 龍崎一路(1570) |  | 87CFA | [17 empty] | 2-37-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1570_87CFA | 龍崎一路(1570)87RY通訊故障 | OTHER | P06/161/1570/87CFA |  |  |  | CDC | 633 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1570 | 龍崎一路(1570) |  | RYFA | [17 empty] | 2-37-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1570_RYFA | 龍崎一路(1570)數位電驛故障 | OTHER | P06/161/1570/RYFA |  |  |  | CDC | 634 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1580 | 龍崎二路(1580) |  | 87CFA | [17 empty] | 2-37-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1580_87CFA | 龍崎二路(1580)87RY通訊故障 | OTHER | P06/161/1580/87CFA |  |  |  | CDC | 635 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1580 | 龍崎二路(1580) |  | RYFA | [17 empty] | 2-37-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1580_RYFA | 龍崎二路(1580)數位電驛故障 | OTHER | P06/161/1580/RYFA |  |  |  | CDC | 636 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1610 | 龍崎二甲三路(1610) |  | 87CFA | [17 empty] | 2-37-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1610_87CFA | 龍崎二甲三路(1610)87RY通訊故障 | OTHER | P06/161/1610/87CFA |  |  |  | CDC | 637 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1610 | 龍崎二甲三路(1610) |  | RYFA | [17 empty] | 2-37-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1610_RYFA | 龍崎二甲三路(1610)數位電驛故障 | OTHER | P06/161/1610/RYFA |  |  |  | CDC | 638 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1620 | 龍崎二甲四路(1620) |  | 87CFA | [17 empty] | 2-37-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1620_87CFA | 龍崎二甲四路(1620)87RY通訊故障 | OTHER | P06/161/1620/87CFA |  |  |  | CDC | 639 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1630 | 山上仁德線(1630) |  | 87CFA | [17 empty] | 2-37-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1630_87CFA | 山上仁德線(1630)87RY通訊故障 | OTHER | P06/161/1630/87CFA |  |  |  | CDC | 640 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1630 | 山上仁德線(1630) |  | RYFA | [17 empty] | 2-37-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1630_RYFA | 山上仁德線(1630)數位電驛故障 | OTHER | P06/161/1630/RYFA |  |  |  | CDC | 641 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1640 | 台南海線(1640) |  | 87CFA | [17 empty] | 2-37-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1640_87CFA | 台南海線(1640)87RY通訊故障 | OTHER | P06/161/1640/87CFA |  |  |  | CDC | 642 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1710 | 安南豐華紅線(1710) |  | RYFA | [17 empty] | 2-35-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1710_RYFA | 安南豐華紅線(1710)數位電驛故障 | OTHER | P06/161/1710/RYFA |  |  |  | CDC | 643 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1720 | 新化二路(1720) |  | 87CFA | [17 empty] | 2-34-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1720_87CFA | 山上新化二路(1720)87RY通訊故障 | OTHER | P06/161/1720/87CFA |  |  |  | CDC | 644 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1720 | 新化二路(1720) |  | RYFA | [17 empty] | 2-36-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1720_RYFA | 山上新化二路(1720)數位電驛故障 | OTHER | P06/161/1720/RYFA |  |  |  | CDC | 645 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1730 | 新化一路(1730) |  | 87CFA | [17 empty] | 2-34-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1730_87CFA | 山上新化一路(1730)87RY通訊故障 | OTHER | P06/161/1730/87CFA |  |  |  | CDC | 646 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1730 | 新化一路(1730) |  | RYFA | [17 empty] | 2-36-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1730_RYFA | 山上新化一路(1730)數位電驛故障 | OTHER | P06/161/1730/RYFA |  |  |  | CDC | 647 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1640 | 台南海線(1640) |  | RYFA | [17 empty] | 2-37-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1640_RYFA | 台南海線(1640)數位電驛故障 | OTHER | P06/161/1640/RYFA |  |  |  | CDC | 648 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1620 | 龍崎二甲四路(1620) |  | RYFA | [17 empty] | 2-37-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1620_RYFA | 龍崎二甲四路(1620)數位電驛故障 | OTHER | P06/161/1620/RYFA |  |  |  | CDC | 649 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | 87A | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1520_87A | 嘉義新營白線(1520) 87RY | LINE161 | P06/161/1520/87A |  |  |  | CDC | 650 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | 87UL | [17 empty] | 2-31-08 |  | 2-2B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1520_87UL | 嘉義新營白線(1520) 87RY U/L | LINE161 | P06/161/1520/87UL |  |  |  | CDC | 651 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | 85A | [17 empty] | 1-0A-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1550_85A | 豐德紅線(1550) 85RY | LINE161 | P06/161/1550/85A |  |  |  | CDC | 652 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | 85A | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1560_85A | 豐德白線(1560) 85RY | LINE161 | P06/161/1560/85A |  |  |  | CDC | 653 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1520 | 嘉義新營白線(1520) |  | 87CFA | [17 empty] | 2-34-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1520_87CFA | 嘉義新營白線(1520)87RY通訊故障 | OTHER | P06/161/1520/87CFA |  |  |  | CDC | 654 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1520 | 嘉義新營白線(1520) |  | RYFA | [17 empty] | 2-34-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1520_RYFA | 嘉義新營白線(1520)數位電驛故障 | OTHER | P06/161/1520/RYFA |  |  |  | CDC | 655 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [17 empty] | 1-0B-03 |  | 1-12 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1950_CB | 1950(161KV #1SHR) CB | OTHER | P06/161/1950/CB |  |  |  | CDC | 656 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 51A | [17 empty] | 1-0B-06 | [7 empty] | 161KV_S | [8 empty] | 山上PS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | P06/161/1950/51A |  |  |  | CDC | 657 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [17 empty] | 1-0B-04 | [7 empty] | 161KV_S | [8 empty] | 山上PS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | P06/161/1950/87A |  |  |  | CDC | 658 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 87UL | [17 empty] | 1-3D-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_87UL | 161KV #1SHR 87RY U/L | OTHER | P06/161/1950/87UL |  |  |  | CDC | 659 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1SHR | #1SHR |  | 161#1SHR96PA | [17 empty] | 1-0B-05 | [7 empty] | 161KV_S | [8 empty] | 山上PS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | P06/161/1950/96PA |  |  |  | CDC | 660 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [17 empty] | 1-3D-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | P06/161/1950/96D |  |  |  | CDC | 661 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [17 empty] | 1-3D-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | P06/161/1950/96P |  |  |  | CDC | 662 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [17 empty] | 1-3D-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | P06/161/1950/96B1 |  |  |  | CDC | 663 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [17 empty] | 1-3D-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | P06/161/1950/96B2 |  |  |  | CDC | 664 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [17 empty] | 1-3D-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | P06/161/1950/SHRA |  |  |  | CDC | 665 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [17 empty] | 1-3D-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | P06/161/1950/SHRF |  |  |  | CDC | 666 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS1 | 1951 | [16 empty] | 2-39-12 | 2-39-13 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1951_ABS | 1951(161KV #1SHR) ABS | OTHER | P06/161/1950/ABS1 |  |  |  | CDC | 667 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS2 | 1952 | [16 empty] | 2-39-14 | 2-39-15 | 1-71 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1952_ABS | 1952(161KV #1SHR) ABS | OTHER | P06/161/1950/ABS2 |  |  |  | CDC | 668 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1611SHR | #1SHR |  | 51UL | [17 empty] | 1-3D-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161#1SHR_51UL | 161KV #1SHR 51RY U/L | OTHER | P06/161/1950/51Z_UL |  |  |  | CDC | 669 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 161_1SHR | 161_1SHR |  | RYFA | [17 empty] | 1-3D-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | P06/161/1950/RYFA |  |  |  | CDC | 670 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-34-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | P06/161/ComPoint/87CTFA |  |  |  | CDC | 671 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-3D-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | P06/161/ComPoint/BUS_RYFA |  |  |  | CDC | 672 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | PHA | [17 empty] | 1-1C-04 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_PHA | 11KV上11線(4E11) 相間RY | FEEDER | P06/11/4E11/PHA |  |  |  | CDC | 673 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) |  | GDA | [17 empty] | 1-1C-05 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_GDA | 11KV上11線(4E11) 接地RY | FEEDER | P06/11/4E11/GDA |  |  |  | CDC | 674 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線(4E11) 79RY |  | 79UL | [17 empty] | 2-3B-07 |  | 2-6B | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_79UL | 11KV上11線(4E11) 79RY U/L | FEEDER | P06/11/4E11/79UL |  |  |  | CDC | 675 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E11_LCO | 上11線(4E11) LCO |  | TapPosMv | [17 empty] | 2-3B-08 |  | 2-6C | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_LCO_TAP | 11KV上11線(4E11) LCO TAP | FEEDER | P06/11/4E11/51_51NUL |  |  |  | CDC | 676 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E11 | 上11線 |  | CB | [17 empty] | 1-1C-03 |  | 2-5B | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_CB | 4E11(11KV上11線) CB | FEEDER | P06/11/4E11/CB |  |  |  | CDC | 677 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | PHA | [17 empty] | 1-1C-07 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_PHA | 11KV上12線(4E12) 相間RY | FEEDER | P06/11/4E12/PHA |  |  |  | CDC | 678 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) |  | GDA | [17 empty] | 1-1D-00 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_GDA | 11KV上12線(4E12) 接地RY | FEEDER | P06/11/4E12/GDA |  |  |  | CDC | 679 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線(4E12) 79RY |  | 79UL | [17 empty] | 2-3B-09 |  | 2-6D | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_79UL | 11KV上12線(4E12) 79RY U/L | FEEDER | P06/11/4E12/79UL |  |  |  | CDC | 680 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E12_LCO | 上12線(4E12) LCO |  | TapPosMv | [17 empty] | 2-3B-10 |  | 2-6E | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_LCO_TAP | 11KV上12線(4E12) LCO TAP | FEEDER | P06/11/4E12/51_51NUL |  |  |  | CDC | 681 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E12 | 上12線 |  | CB | [17 empty] | 1-1C-06 |  | 2-5C | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_CB | 4E12(11KV上12線) CB | FEEDER | P06/11/4E12/CB |  |  |  | CDC | 682 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | PHA | [17 empty] | 1-1D-02 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_PHA | 11KV上13線(4E13) 相間RY | FEEDER | P06/11/4E13/PHA |  |  |  | CDC | 683 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) |  | GDA | [17 empty] | 1-1D-03 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_GDA | 11KV上13線(4E13) 接地RY | FEEDER | P06/11/4E13/GDA |  |  |  | CDC | 684 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線(4E13) 79RY |  | 79UL | [17 empty] | 2-3B-11 |  | 2-6F | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_79UL | 11KV上13線(4E13) 79RY U/L | FEEDER | P06/11/4E13/79UL |  |  |  | CDC | 685 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E13_LCO | 上13線(4E13) LCO |  | TapPosMv | [17 empty] | 2-3B-12 |  | 2-70 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_LCO_TAP | 11KV上13線(4E13) LCO TAP | FEEDER | P06/11/4E13/51_51NUL |  |  |  | CDC | 686 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E13 | 上13線 |  | CB | [17 empty] | 1-1D-01 |  | 2-5D | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_CB | 4E13(11KV上13線) CB | FEEDER | P06/11/4E13/CB |  |  |  | CDC | 687 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | PHA | [17 empty] | 1-1D-05 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_PHA | 11KV上14線(4E14) 相間RY | FEEDER | P06/11/4E14/PHA |  |  |  | CDC | 688 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) |  | GDA | [17 empty] | 1-1D-06 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_GDA | 11KV上14線(4E14) 接地RY | FEEDER | P06/11/4E14/GDA |  |  |  | CDC | 689 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線(4E14) 79RY |  | 79UL | [17 empty] | 2-3B-13 |  | 2-71 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_79UL | 11KV上14線(4E14) 79RY U/L | FEEDER | P06/11/4E14/79UL |  |  |  | CDC | 690 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E14_LCO | 上14線(4E14) LCO |  | TapPosMv | [17 empty] | 2-3B-14 |  | 2-72 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_LCO_TAP | 11KV上14線(4E14) LCO TAP | FEEDER | P06/11/4E14/51_51NUL |  |  |  | CDC | 691 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E14 | 上14線 |  | CB | [17 empty] | 1-1D-04 |  | 2-5E | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_CB | 4E14(11KV上14線) CB | FEEDER | P06/11/4E14/CB |  |  |  | CDC | 692 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | PHA | [17 empty] | 1-1E-00 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_PHA | 11KV上15線(4E15) 相間RY | FEEDER | P06/11/4E15/PHA |  |  |  | CDC | 693 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) |  | GDA | [17 empty] | 1-1E-01 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_GDA | 11KV上15線(4E15) 接地RY | FEEDER | P06/11/4E15/GDA |  |  |  | CDC | 694 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線(4E15) 79RY |  | 79UL | [17 empty] | 2-3B-15 |  | 2-73 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_79UL | 11KV上15線(4E15) 79RY U/L | FEEDER | P06/11/4E15/79UL |  |  |  | CDC | 695 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E15_LCO | 上15線(4E15) LCO |  | TapPosMv | [17 empty] | 2-3C-00 |  | 2-74 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_LCO_TAP | 11KV上15線(4E15) LCO TAP | FEEDER | P06/11/4E15/51_51NUL |  |  |  | CDC | 696 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E15 | 上15線 |  | CB | [17 empty] | 1-1D-07 |  | 2-5F | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_CB | 4E15(11KV上15線) CB | FEEDER | P06/11/4E15/CB |  |  |  | CDC | 697 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | PHA | [17 empty] | 1-1E-03 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_PHA | 11KV上16線(4E16) 相間RY | FEEDER | P06/11/4E16/PHA |  |  |  | CDC | 698 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) |  | GDA | [17 empty] | 1-1E-04 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_GDA | 11KV上16線(4E16) 接地RY | FEEDER | P06/11/4E16/GDA |  |  |  | CDC | 699 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線(4E16) 79RY |  | 79UL | [17 empty] | 2-3C-01 |  | 2-75 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_79UL | 11KV上16線(4E16) 79RY U/L | FEEDER | P06/11/4E16/79UL |  |  |  | CDC | 700 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E16_LCO | 上16線(4E16) LCO |  | TapPosMv | [17 empty] | 2-3C-02 |  | 2-76 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_LCO_TAP | 11KV上16線(4E16) LCO TAP | FEEDER | P06/11/4E16/51_51NUL |  |  |  | CDC | 701 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E16 | 上16線 |  | CB | [17 empty] | 1-1E-02 |  | 2-60 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_CB | 4E16(11KV上16線) CB | FEEDER | P06/11/4E16/CB |  |  |  | CDC | 702 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | PHA | [17 empty] | 1-1E-06 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_PHA | 11KV上17線(4E17) 相間RY | FEEDER | P06/11/4E17/PHA |  |  |  | CDC | 703 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) |  | GDA | [17 empty] | 1-1E-07 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_GDA | 11KV上17線(4E17) 接地RY | FEEDER | P06/11/4E17/GDA |  |  |  | CDC | 704 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線(4E17) 79RY |  | 79UL | [17 empty] | 2-3C-03 |  | 2-77 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_79UL | 11KV上17線(4E17) 79RY U/L | FEEDER | P06/11/4E17/79UL |  |  |  | CDC | 705 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E17_LCO | 上17線(4E17) LCO |  | TapPosMv | [17 empty] | 2-3C-04 |  | 3-00 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_LCO_TAP | 11KV上17線(4E17) LCO TAP | FEEDER | P06/11/4E17/51_51NUL |  |  |  | CDC | 706 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E17 | 上17線 |  | CB | [17 empty] | 1-1E-05 |  | 2-61 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_CB | 4E17(11KV上17線) CB | FEEDER | P06/11/4E17/CB |  |  |  | CDC | 707 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | PHA | [17 empty] | 1-1F-01 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_PHA | 11KV上18線(4E18) 相間RY | FEEDER | P06/11/4E18/PHA |  |  |  | CDC | 708 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) |  | GDA | [17 empty] | 1-1F-02 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_GDA | 11KV上18線(4E18) 接地RY | FEEDER | P06/11/4E18/GDA |  |  |  | CDC | 709 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線(4E18) 79RY |  | 79UL | [17 empty] | 2-3C-05 |  | 3-01 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_79UL | 11KV上18線(4E18) 79RY U/L | FEEDER | P06/11/4E18/79UL |  |  |  | CDC | 710 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E18_LCO | 上18線(4E18) LCO |  | TapPosMv | [17 empty] | 2-3C-06 |  | 3-02 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_LCO_TAP | 11KV上18線(4E18) LCO TAP | FEEDER | P06/11/4E18/51_51NUL |  |  |  | CDC | 711 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E18 | 上18線 |  | CB | [17 empty] | 1-1F-00 |  | 2-62 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_CB | 4E18(11KV上18線) CB | FEEDER | P06/11/4E18/CB |  |  |  | CDC | 712 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | PHA | [17 empty] | 1-1F-04 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_PHA | 11KV上19線(4E19) 相間RY | FEEDER | P06/11/4E19/PHA |  |  |  | CDC | 713 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) |  | GDA | [17 empty] | 1-1F-05 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_GDA | 11KV上19線(4E19) 接地RY | FEEDER | P06/11/4E19/GDA |  |  |  | CDC | 714 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線(4E19) 79RY |  | 79UL | [17 empty] | 2-3C-07 |  | 3-03 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_79UL | 11KV上19線(4E19) 79RY U/L | FEEDER | P06/11/4E19/79UL |  |  |  | CDC | 715 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E19_LCO | 上19線(4E19) LCO |  | TapPosMv | [17 empty] | 2-3C-08 |  | 3-04 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_LCO_TAP | 11KV上19線(4E19) LCO TAP | FEEDER | P06/11/4E19/51_51NUL |  |  |  | CDC | 716 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E19 | 上19線 |  | CB | [17 empty] | 1-1F-03 |  | 2-63 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_CB | 4E19(11KV上19線) CB | FEEDER | P06/11/4E19/CB |  |  |  | CDC | 717 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | PHA | [17 empty] | 1-1F-07 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_PHA | 11KV上20線(4E20) 相間RY | FEEDER | P06/11/4E20/PHA |  |  |  | CDC | 718 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) |  | GDA | [17 empty] | 2-00-00 | [7 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_GDA | 11KV上20線(4E20) 接地RY | FEEDER | P06/11/4E20/GDA |  |  |  | CDC | 719 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線(4E20) 79RY |  | 79UL | [17 empty] | 2-3C-09 |  | 3-05 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_79UL | 11KV上20線(4E20) 79RY U/L | FEEDER | P06/11/4E20/79UL |  |  |  | CDC | 720 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 11 | 11kV | 4E20_LCO | 上20線(4E20) LCO |  | TapPosMv | [17 empty] | 2-3C-10 |  | 3-06 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_LCO_TAP | 11KV上20線(4E20) LCO TAP | FEEDER | P06/11/4E20/51_51NUL |  |  |  | CDC | 721 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P06 | 山上PS | 11 | 11kV | 4E20 | 上20線 |  | CB | [17 empty] | 1-1F-06 |  | 2-64 | [5 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_CB | 4E20(11KV上20線) CB | FEEDER | P06/11/4E20/CB |  |  |  | CDC | 722 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | CB | [17 empty] | 1-18-00 |  | 1-13 | [5 empty] | 161KV_S | [8 empty] | 山上PS.1760_CB | 1760(#6DTR) CB | MTR | P06/161/1760/CB |  |  |  | CDC | 723 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 51ZA | [17 empty] | 1-18-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#6DTR_51ZA | #6DTR 51Z RY | MTR | P06//6DTR/51ZA |  |  |  | CDC | 724 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 87A | [17 empty] | 1-18-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#6DTR_87A | #6DTR 87RY | MTR | P06//6DTR/87A |  |  |  | CDC | 725 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 96PA | [17 empty] | 1-18-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#6DTR_96PA | #6DTR 機械保護動作 | MTR | P06//6DTR/96PA |  |  |  | CDC | 726 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 96D | [17 empty] | 2-3A-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_96D | #6DTR 96D RY | MTR | P06//6DTR/96D |  |  |  | CDC | 727 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 96P | [17 empty] | 2-3A-09 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_96P | #6DTR 96P RY | MTR | P06//6DTR/96P |  |  |  | CDC | 728 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 63Q | [17 empty] | 2-3A-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_63Q | #6DTR 63Q RY | MTR | P06//6DTR/63Q |  |  |  | CDC | 729 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 96B1 | [17 empty] | 2-3A-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_96B1 | #6DTR 96B1 RY | MTR | P06//6DTR/96B1 |  |  |  | CDC | 730 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 96B2 | [17 empty] | 2-3A-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_96B2 | #6DTR 96B2 RY | MTR | P06//6DTR/96B2 |  |  |  | CDC | 731 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | TRA | [17 empty] | 2-3A-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_TRA | #6DTR 重故障 | MTR | P06//6DTR/TRA |  |  |  | CDC | 732 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | TRF | [17 empty] | 2-3A-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_TRF | #6DTR 輕故障 | MTR | P06//6DTR/TRF |  |  |  | CDC | 733 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | SupLocal | [17 empty] | 2-3A-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_S/L | #6DTR(A) OLTC S/L | MTR | P06//6DTR(A)/SupLocal |  |  |  | CDC | 734 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS | 0 |  | 6DTR(A) | #6DTR(A) |  | A_M | [17 empty] | 2-3A-04 |  | 3-0A | [5 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(A)_A/M | #6DTR(A) OLTC A/M | MTR | P06//6DTR(A)/Tap Chan |  |  |  | CDC | 735 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | SupLocal | [17 empty] | 2-3A-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_S/L | #6DTR(B) OLTC S/L | MTR | P06//6DTR(B)/SupLocal |  |  |  | CDC | 736 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P06 | 山上PS | 0 |  | 6DTR(B) | #6DTR(B) |  | A_M | [17 empty] | 2-3A-08 |  | 3-0C | [5 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR(B)_A/M | #6DTR(B) OLTC A/M | MTR | P06//6DTR(B)/Tap Chan |  |  |  | CDC | 737 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS1 | 1761 | [16 empty] | 2-3D-08 | 2-3D-09 | 3-08 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1761_ABS | 1761(#6DTR) ABS | MTR | P06/161/1760/ABS1 |  |  |  | CDC | 738 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS2 | 1762 | [16 empty] | 2-3D-10 | 2-3D-11 | 3-09 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1762_ABS | 1762(#6DTR) ABS | MTR | P06/161/1760/ABS2 |  |  |  | CDC | 739 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 2-00-01 |  | 2-65 | [5 empty] | ADCS_S | [8 empty] | 山上PS.210_CB | 210(11KV #1SC) CB | SC | P06/11/210/CB |  |  |  | CDC | 740 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 2-00-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.210_SCA | 11KV #1SC 51,51N RY | SC | P06/11/210/SCA |  |  |  | CDC | 741 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 2-00-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | P06/11/210/UVA |  |  |  | CDC | 742 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 2-00-04 |  | 2-66 | [5 empty] | ADCS_S | [8 empty] | 山上PS.220_CB | 220(11KV #2SC) CB | SC | P06/11/220/CB |  |  |  | CDC | 743 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 2-00-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.220_SCA | 11KV #2SC 51,51N RY | SC | P06/11/220/SCA |  |  |  | CDC | 744 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 2-00-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | P06/11/220/UVA |  |  |  | CDC | 745 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-00-07 |  | 2-67 | [5 empty] | ADCS_S | [8 empty] | 山上PS.230_CB | 230(11KV #3SC) CB | SC | P06/11/230/CB |  |  |  | CDC | 746 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-01-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.230_SCA | 11KV #3SC 51,51N RY | SC | P06/11/230/SCA |  |  |  | CDC | 747 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-01-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | P06/11/230/UVA |  |  |  | CDC | 748 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-01-02 |  | 2-68 | [5 empty] | ADCS_S | [8 empty] | 山上PS.240_CB | 240(11KV #4SC) CB | SC | P06/11/240/CB |  |  |  | CDC | 749 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-01-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.240_SCA | 11KV #4SC 51,51N RY | SC | P06/11/240/SCA |  |  |  | CDC | 750 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-01-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | P06/11/240/UVA |  |  |  | CDC | 751 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 2-3C-11 | [7 empty] | ADCS_S | [8 empty] | 山上PS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | P06/22/ComPoint/CBA |  |  |  | CDC | 752 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 2-3C-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | P06/22/ComPoint/CBF |  |  |  | CDC | 753 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | _SC | 11/ SC |  | 60A | [17 empty] | 2-3C-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.23KV_SC_60A | 11/23KV SC 60A | OTHER | P06/22/ComPoint/60A |  |  |  | CDC | 754 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 51Z_UL | [17 empty] | 2-3A-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_51ZUL | #6DTR 51Z RY U/L | OTHER | P06//6DTR/51Z_UL |  |  |  | CDC | 755 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | DTR_86A | [17 empty] | 2-3A-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_86A | #6DTR 86(50/50N/51Z/87/96)RY | OTHER | P06//6DTR/DTR_86A |  |  |  | CDC | 756 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 87UL | [17 empty] | 2-3A-00 |  | 3-0E | [5 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_87UL | #6DTR 87RY U/L | OTHER | P06//6DTR/1_87UL1 |  |  |  | CDC | 757 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | RYFA | [17 empty] | 2-3A-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_RYFA | #6DTR 數位電驛故障 | OTHER | P06//6DTR/RYFA |  |  |  | CDC | 758 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 22 | 22kV | 11_ | 11/ |  | RCA | [17 empty] | 2-3C-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.11/23KV_RCA | 11/23KV饋線79RY復閉失敗 | OTHER | P06/0/ComPoint/LOA |  |  |  | CDC | 759 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | PMA | [17 empty] | 2-3C-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.PMA | 電力量測表計故障 | OTHER | P06/0/StaDev/PMA |  |  |  | CDC | 760 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | CB | [17 empty] | 1-18-05 |  | 2-58 | [5 empty] | ADCS_S | [8 empty] | 山上PS.330_CB | 330(#6DTR) CB | MTR | P06/11/330/CB |  |  |  | CDC | 761 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | CB | [17 empty] | 1-19-01 |  | 2-59 | [5 empty] | ADCS_S | [8 empty] | 山上PS.340_CB | 340(#6DTR) CB | MTR | P06/11/340/CB |  |  |  | CDC | 762 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | 51A | [17 empty] | 1-18-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.330_51A | #6DTR二次側(330) 51RY | MTR | P06/11/330/PHA |  |  |  | CDC | 763 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | 51A | [17 empty] | 1-19-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.340_51A | #6DTR二次側(340) 51RY | MTR | P06/11/340/PHA |  |  |  | CDC | 764 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | 81A | [17 empty] | 1-19-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.330_81A | 330(#6DTR) 81RY動作 | OTHER | P06/11/330/81A |  |  |  | CDC | 765 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | 81AS | [17 empty] | 2-3B-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.330_81A/S | 330(#6DTR) 81RY動作/復歸 | OTHER |  |  |  |  | CDC | 766 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/RESET | RESET
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | 81UL | [17 empty] | 2-3B-04 |  | 2-69 | [5 empty] | ADCS_S | [8 empty] | 山上PS.330_81UL | 330(#6DTR) 81RY U/L | OTHER | P06/11/330/81UL |  |  |  | CDC | 767 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.330_GDA | 330開關箱IED RY GDA | OTHER | P06/11/330/GDA |  |  |  | CDC | 768 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | 81A | [17 empty] | 1-19-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.340_81A | 340(#6DTR) 81RY動作 | OTHER | P06/11/340/81A |  |  |  | CDC | 769 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | 81AS | [17 empty] | 2-3B-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.340_81A/S | 340(#6DTR) 81RY動作/復歸 | OTHER |  |  |  |  | CDC | 770 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/RESET | RESET
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | 81UL | [17 empty] | 2-3B-06 |  | 2-6A | [5 empty] | ADCS_S | [8 empty] | 山上PS.340_81UL | 340(#6DTR) 81RY U/L | OTHER | P06/11/340/81UL |  |  |  | CDC | 771 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | GDA | [17 empty] | 1-19-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.340_GDA | 340開關箱IED RY GDA | OTHER | P06/11/340/GDA |  |  |  | CDC | 772 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 390 | #3SSTR(390) |  | CB | [17 empty] | 1-1C-00 |  | 2-5A | [5 empty] | 161KV_S | [8 empty] | 山上PS.390_CB | 390(#3SSTR) CB | OTHER | P06/11/390/CB |  |  |  | CDC | 773 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-1C-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#3SSTR_51A | #3SSTR 51RY | OTHER | P06/11/390/PHA |  |  |  | CDC | 774 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-1C-02 | [7 empty] | 161KV_S | [8 empty] | 山上PS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | P06/11/390/GDA |  |  |  | CDC | 775 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-34-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | P06/0/ComPoint/GRZ100 |  |  |  | CDC | 776 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | 87A1 | [17 empty] | 1-06-07 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1710_87A1 | 安南豐華紅線(1710) #1 87RY | LINE161 | P06/161/1710/87A |  |  |  | CDC | 777 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | 87A2 | [17 empty] | 1-0C-00 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1710_87A2 | 安南豐華紅線(1710) #2 87RY | LINE161 | P06/161/1710/87A2 |  |  |  | CDC | 778 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | 1_87UL1 | [17 empty] | 2-32-08 |  | 2-3B | [5 empty] | ADCS_S | [8 empty] | 山上PS.1710_87UL1 | 安南豐華紅線(1710) #1 87RY U/L | LINE161 | P06/161/1710/1_87UL1 |  |  |  | CDC | 779 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | 1_87UL2 | [17 empty] | 1-3D-12 |  | 2-56 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1710_87UL2 | 安南豐華紅線(1710) #2 87RY U/L | LINE161 | P06/161/1710/1_87UL2 |  |  |  | CDC | 780 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1710 | 安南豐華紅線(1710) |  | 87CFA | [17 empty] | 2-35-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1710_87CFA | 安南豐華紅線(1710)87RY通訊故障 | OTHER | P06/161/1710/87CFA |  |  |  | CDC | 781 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | 87A1 | [17 empty] | 1-06-03 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1540_87A1 | 鹽行豐華白線(1540) #1 87RY | LINE161 | P06/161/1540/87A |  |  |  | CDC | 782 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | 87A2 | [17 empty] | 1-0C-01 | [7 empty] | 161KV_S | [8 empty] | 山上PS.1540_87A2 | 鹽行豐華白線(1540) #2 87RY | LINE161 | P06/161/1540/87A2 |  |  |  | CDC | 783 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | 1_87UL1 | [17 empty] | 2-32-06 |  | 2-39 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1540_87UL1 | 鹽行豐華白線(1540) #1 87RY U/L | LINE161 | P06/161/1540/1_87UL1 |  |  |  | CDC | 784 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | 1_87UL2 | [17 empty] | 1-3D-13 |  | 2-57 | [5 empty] | ADCS_S | [8 empty] | 山上PS.1540_87UL2 | 鹽行豐華白線(1540) #2 87RY U/L | LINE161 | P06/161/1540/1_87UL2 |  |  |  | CDC | 785 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1540 | 鹽行豐華白線(1540) |  | 87CFA | [17 empty] | 2-35-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1540_87CFA | 鹽行豐華白線(1540)87RY通訊故障 | OTHER | P06/161/1540/87CFA |  |  |  | CDC | 786 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 630 | 善化一路(630) |  | 87A | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.630_87A | 山上善化一路(630) 87RY | OTHER | P06/69/630/87A |  |  |  | CDC | 787 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 630 | 善化一路(630) |  | 87CFA | [17 empty] | 2-3B-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.630_87CFA | 山上善化一路(630)87RY通訊故障 | OTHER | P06/69/630/87CFA |  |  |  | CDC | 788 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 630 | 善化一路(630) |  | 87UL | [17 empty] | 2-3B-00 |  | 3-0F | [5 empty] | ADCS_S | [8 empty] | 山上PS.630_87UL | 山上善化一路(630) 87RY U/L | OTHER | P06/69/630/87UL |  |  |  | CDC | 789 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 630 | 善化一路(630) |  | RYFA | [17 empty] | 2-3B-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.630_RYFA | 山上善化一路(630)數位電驛故障 | OTHER | P06/69/630/RYFA |  |  |  | CDC | 790 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 640 | 善化二路(640) |  | 87A | [17 empty] | 1-14-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.640_87A | 山上善化二路(640) 87RY | OTHER | P06/69/640/87A |  |  |  | CDC | 791 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 640 | 善化二路(640) |  | 87CFA | [17 empty] | 2-3D-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.640_87CFA | 山上善化二路(640)87RY通訊故障 | OTHER | P06/69/640/87CFA |  |  |  | CDC | 792 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 640 | 善化二路(640) |  | 87UL | [17 empty] | 2-3D-00 |  | 3-10 | [5 empty] | ADCS_S | [8 empty] | 山上PS.640_87UL | 山上善化二路(640) 87RY U/L | OTHER | P06/69/640/87UL |  |  |  | CDC | 793 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 640 | 善化二路(640) |  | RYFA | [17 empty] | 2-3D-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.640_RYFA | 山上善化二路(640)數位電驛故障 | OTHER | P06/69/640/RYFA |  |  |  | CDC | 794 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 650 | 善化三路(650) |  | 87A | [17 empty] | 1-14-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.650_87A | 山上善化三路(650) 87RY | OTHER | P06/69/650/87A |  |  |  | CDC | 795 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 650 | 善化三路(650) |  | 87CFA | [17 empty] | 2-3D-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.650_87CFA | 山上善化三路(650)87RY通訊故障 | OTHER | P06/69/650/87CFA |  |  |  | CDC | 796 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 650 | 善化三路(650) |  | 87UL | [17 empty] | 2-3D-03 |  | 3-11 | [5 empty] | ADCS_S | [8 empty] | 山上PS.650_87UL | 山上善化三路(650) 87RY U/L | OTHER | P06/69/650/87UL |  |  |  | CDC | 797 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 650 | 善化三路(650) |  | RYFA | [17 empty] | 2-3D-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.650_RYFA | 山上善化三路(650)數位電驛故障 | OTHER | P06/69/650/RYFA |  |  |  | CDC | 798 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 680 | 歸仁線(680) |  | 87A | [17 empty] | 1-15-00 | [7 empty] | ADCS_S | [8 empty] | 山上PS.680_87A | 山上歸仁線(680) 87RY | OTHER | P06/69/680/87A |  |  |  | CDC | 799 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 680 | 歸仁線(680) |  | 87CFA | [17 empty] | 2-3D-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.680_87CFA | 山上歸仁線(680)87RY通訊故障 | OTHER | P06/69/680/87CFA |  |  |  | CDC | 800 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 680 | 歸仁線(680) |  | 87UL | [17 empty] | 2-3D-13 |  | 3-13 | [5 empty] | ADCS_S | [8 empty] | 山上PS.680_87UL | 山上歸仁線(680) 87RY U/L | OTHER | P06/69/680/87UL |  |  |  | CDC | 801 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 680 | 歸仁線(680) |  | RYFA | [17 empty] | 2-3D-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.680_RYFA | 山上歸仁線(680)數位電驛故障 | OTHER | P06/69/680/RYFA |  |  |  | CDC | 802 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 670 | 山上新市三路(670) |  | 87A | [17 empty] | 1-14-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.670_87A | 山上新市三路(670) 87RY | OTHER | P06/69/670/87A |  |  |  | CDC | 803 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 670 | 山上新市三路(670) |  | 87CFA | [17 empty] | 2-3D-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.670_87CFA | 山上新市三路(670)87RY通訊故障 | OTHER | P06/69/670/87CFA |  |  |  | CDC | 804 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 670 | 山上新市三路(670) |  | 87UL | [17 empty] | 2-3D-06 |  | 3-12 | [5 empty] | ADCS_S | [8 empty] | 山上PS.670_87UL | 山上新市三路(670) 87RY U/L | OTHER | P06/69/670/87UL |  |  |  | CDC | 805 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 670 | 山上新市三路(670) |  | RYFA | [17 empty] | 2-3D-12 | [7 empty] | ADCS_S | [8 empty] | 山上PS.670_RYFA | 山上新市三路(670)數位電驛故障 | OTHER | P06/69/670/RYFA |  |  |  | CDC | 806 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  |  |  |  | GEN | [17 empty] | 2-35-08 | [7 empty] | ADCS_S | [8 empty] | 山上PS.GEN | 緊急發電機運轉 | OTHER | P06/0/StaDev/1A5Other |  |  |  | CDC | 807 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | GDA | [17 empty] | 1-19-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_GDA | #6DTR 50N/51N RY | OTHER | P06//6DTR/GDA |  |  |  | CDC | 808 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | PHA | [17 empty] | 1-18-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_PHA | #6DTR 50/51 RY | OTHER | P06//6DTR/PHA |  |  |  | CDC | 809 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 710 | 新市二路(710) |  | 87A | [17 empty] | 1-14-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.710_87A | 山上新市二路(710) 87RY | OTHER | P06/69/710/87A |  |  |  | CDC | 810 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 710 | 新市二路(710) |  | 87CFA | [17 empty] | 2-3E-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.710_87CFA | 山上新市二路(710)87RY通訊故障 | OTHER | P06/69/710/87CFA |  |  |  | CDC | 811 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 710 | 新市二路(710) |  | 87UL | [17 empty] | 2-3E-00 |  | 3-14 | [5 empty] | ADCS_S | [8 empty] | 山上PS.710_87UL | 山上新市二路(710) 87RY U/L | OTHER | P06/69/710/87UL |  |  |  | CDC | 812 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 710 | 新市二路(710) |  | RYFA | [17 empty] | 2-3E-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.710_RYFA | 山上新市二路(710)數位電驛故障 | OTHER | P06/69/710/RYFA |  |  |  | CDC | 813 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 660 | 新市一路(660) |  | 87A | [17 empty] | 1-14-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.660_87A | 山上新市一路(660) 87RY | OTHER | P06/69/660/87A |  |  |  | CDC | 814 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 660 | 新市一路(660) |  | 87CFA | [17 empty] | 2-3E-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.660_87CFA | 山上新市一路(660)87RY通訊故障 | OTHER | P06/69/660/87CFA |  |  |  | CDC | 815 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 660 | 新市一路(660) |  | 87UL | [17 empty] | 2-3E-03 |  | 3-15 | [5 empty] | ADCS_S | [8 empty] | 山上PS.660_87UL | 山上新市一路(660) 87RY U/L | OTHER | P06/69/660/87UL |  |  |  | CDC | 816 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 660 | 新市一路(660) |  | RYFA | [17 empty] | 2-3E-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.660_RYFA | 山上新市一路(660)數位電驛故障 | OTHER | P06/69/660/RYFA |  |  |  | CDC | 817 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 2-3E-14 |  | 3-1E | [5 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | P06//3MTR/51Z_UL |  |  |  | CDC | 818 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_86A | #3MTR 86RY | OTHER | P06//3MTR/MTR_86A |  |  |  | CDC | 819 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 2-31-04 |  | 3-1C | [5 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | P06//3MTR/1_87UL1 |  |  |  | CDC | 820 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 2-3E-12 |  | 3-1D | [5 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | P06//3MTR/1_87UL2 |  |  |  | CDC | 821 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | GDA | [17 empty] | 1-0C-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_GDA | #3MTR GDA | OTHER | P06//3MTR/GDA |  |  |  | CDC | 822 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 2-3E-13 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | P06//3MTR/RYFA |  |  |  | CDC | 823 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 2-3E-08 |  | 3-18 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | P06//1MTR/51Z_UL |  |  |  | CDC | 824 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-0C-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_86A | #1MTR 86RY | OTHER | P06//1MTR/MTR_86A |  |  |  | CDC | 825 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 2-30-06 |  | 3-16 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | P06//1MTR/1_87UL1 |  |  |  | CDC | 826 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 2-3E-06 |  | 3-17 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | P06//1MTR/1_87UL2 |  |  |  | CDC | 827 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | GDA | [17 empty] | 1-0C-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_GDA | #1MTR GDA | OTHER | P06//1MTR/GDA |  |  |  | CDC | 828 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 2-3E-07 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | P06//1MTR/RYFA |  |  |  | CDC | 829 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 2-3E-11 |  | 3-1B | [5 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | P06//2MTR/51Z_UL |  |  |  | CDC | 830 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-0C-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_86A | #2MTR 86RY | OTHER | P06//2MTR/MTR_86A |  |  |  | CDC | 831 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 2-30-11 |  | 3-19 | [5 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | P06//2MTR/1_87UL1 |  |  |  | CDC | 832 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 2-3E-09 |  | 3-1A | [5 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | P06//2MTR/1_87UL2 |  |  |  | CDC | 833 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_GDA | #2MTR GDA | OTHER | P06//2MTR/GDA |  |  |  | CDC | 834 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 2-3E-10 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | P06//2MTR/RYFA |  |  |  | CDC | 835 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 1MOLTC | #1MTR |  | TAP連動 | [17 empty] | 2-01-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.1MOLTC_TAP連動 | #1MTR OLTC TAP連動,請確認處理 | OTHER |  |  |  |  | CDC | 836 | GENERICDIPoint | PS012_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | P06/69/600/GDA1 |  |  |  | CDC | 837 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 | [17 empty] | 1-15-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | P06/69/600/GDA2 |  |  |  | CDC | 838 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | P06/69/600/PHA1 |  |  |  | CDC | 839 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 | [17 empty] | 1-15-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | P06/69/600/PHA2 |  |  |  | CDC | 840 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | RYFA | [17 empty] | 2-3E-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | P06/69/600/RYFA |  |  |  | CDC | 841 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | 87A | [17 empty] | 1-15-04 | [7 empty] | 69KV_S | [8 empty] | 山上PS.610_87A | 山頂一路(610) 87RY | LINE69 | P06/69/610/87A |  |  |  | CDC | 842 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | 87UL | [17 empty] | 2-3F-03 |  | 3-21 | [5 empty] | ADCS_S | [8 empty] | 山上PS.610_87UL | 山頂一路(610) 87RY U/L | LINE69 | P06/69/610/87UL |  |  |  | CDC | 843 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | 87A | [17 empty] | 1-15-03 | [7 empty] | 69KV_S | [8 empty] | 山上PS.620_87A | 山頂二路(620) 87RY | LINE69 | P06/69/620/87A |  |  |  | CDC | 844 | GENERICDIPoint | PS012_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | 87UL | [17 empty] | 2-3F-00 |  | 3-20 | [5 empty] | ADCS_S | [8 empty] | 山上PS.620_87UL | 山頂二路(620) 87RY U/L | LINE69 | P06/69/620/87UL |  |  |  | CDC | 845 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | 610 | 山頂一路(610) |  | 87CFA | [17 empty] | 2-3F-04 | [7 empty] | ADCS_S | [8 empty] | 山上PS.610_87CFA | 山上山頂一路(610)87RY通訊故障 | OTHER | P06/69/610/87CFA |  |  |  | CDC | 846 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 610 | 山頂一路(610) |  | RYFA | [17 empty] | 2-3F-05 | [7 empty] | ADCS_S | [8 empty] | 山上PS.610_RYFA | 山上山頂一路(610)數位電驛故障 | OTHER | P06/69/610/RYFA |  |  |  | CDC | 847 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 620 | 山頂二路(620) |  | 87CFA | [17 empty] | 2-3F-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.620_87CFA | 山上山頂二路(620)87RY通訊故障 | OTHER | P06/69/620/87CFA |  |  |  | CDC | 848 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 620 | 山頂二路(620) |  | RYFA | [17 empty] | 2-3F-02 | [7 empty] | ADCS_S | [8 empty] | 山上PS.620_RYFA | 山上山頂二路(620)數位電驛故障 | OTHER | P06/69/620/RYFA |  |  |  | CDC | 849 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-3D-15 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | P06/69/ComPoint/87CTFA |  |  |  | CDC | 850 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-3D-14 | [7 empty] | ADCS_S | [8 empty] | 山上PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | P06/69/ComPoint/BUS_RYFA |  |  |  | CDC | 851 | GENERICDIPoint | PS012_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P06 | 山上PS | 0 |  | 6DTR | #6DTR |  | 87-2UL | [17 empty] | 2-3A-01 | [7 empty] | ADCS_S | [8 empty] | 山上PS.#6DTR_87-2UL | #6DTR 87-2RY U/L | OTHER | P06//6DTR/1_87UL2 |  |  |  | CDC | 852 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P06 | 山上PS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-33-06 | [7 empty] | ADCS_S | [8 empty] | 山上PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | P06/0/ComPoint/OLTC_A |  |  |  | CDC | 853 | GENERICDIPoint | PS012_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P06 | 山上PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.820_SC_CAP | 69KV#2SC 容量 | SC | [5 empty] | 854 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.830_SC_CAP | 69KV#3SC 容量 | SC | [5 empty] | 855 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 0 |  | TRD | 山上PS |  | 131 | [25 empty] | TRAIN_AD | [8 empty] | 山上PS.TRD_131 | 山上PS NT 69KV_Hi_Limit | [6 empty] | 856 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P06 | 山上PS | 0 |  | TRD | 山上PS |  | 132 | [25 empty] | TRAIN_AD | [8 empty] | 山上PS.TRD_132 | 山上PS NT 69KV_Lo_Limit | [6 empty] | 857 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P06 | 山上PS | 11 | 11kV | 210_SC | #1SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 858 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 220_SC | #2SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 859 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 230_SC | #3SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 860 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 11 | 11kV | 240_SC | #4SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 山上PS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 861 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1510LE | 1510LE (非取樣點) | LINE161 | P06/161/1510/LE0 |  |  |  |  | 862 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1510 | 嘉義新營紅線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1510BE | 1510BE (非取樣點) | LINE161 | P06/161/1510/BE0 |  |  |  |  | 863 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1520LE | 1520LE (非取樣點) | LINE161 | P06/161/1520/LE0 |  |  |  |  | 864 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1520 | 嘉義新營白線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1520BE | 1520BE (非取樣點) | LINE161 | P06/161/1520/BE0 |  |  |  |  | 865 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1540LE | 1540LE (非取樣點) | LINE161 | P06/161/1540/LE0 |  |  |  |  | 866 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1540 | 鹽行豐華白線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1540BE | 1540BE (非取樣點) | LINE161 | P06/161/1540/BE0 |  |  |  |  | 867 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1570LE | 1570LE (非取樣點) | LINE161 | P06/161/1570/LE0 |  |  |  |  | 868 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1570 | 龍崎一路(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1570BE | 1570BE (非取樣點) | LINE161 | P06/161/1570/BE0 |  |  |  |  | 869 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1580LE | 1580LE (非取樣點) | LINE161 | P06/161/1580/LE0 |  |  |  |  | 870 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1580 | 龍崎二路(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1580BE | 1580BE (非取樣點) | LINE161 | P06/161/1580/BE0 |  |  |  |  | 871 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1610LE | 1610LE (非取樣點) | LINE161 | P06/161/1610/LE0 |  |  |  |  | 872 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1610 | 龍崎二甲三路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1610BE | 1610BE (非取樣點) | LINE161 | P06/161/1610/BE0 |  |  |  |  | 873 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1620LE | 1620LE (非取樣點) | LINE161 | P06/161/1620/LE0 |  |  |  |  | 874 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1620 | 龍崎二甲四路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1620BE | 1620BE (非取樣點) | LINE161 | P06/161/1620/BE0 |  |  |  |  | 875 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | LE0 | 1630LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1630LE | 1630LE (非取樣點) | LINE161 | P06/161/1630/LE0 |  |  |  |  | 876 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1630 | 山上仁德線(1630) |  | BE0 | 1630BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1630BE | 1630BE (非取樣點) | LINE161 | P06/161/1630/BE0 |  |  |  |  | 877 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | LE0 | 1640LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1640LE | 1640LE (非取樣點) | LINE161 | P06/161/1640/LE0 |  |  |  |  | 878 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1640 | 台南海線(1640) |  | BE0 | 1640BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1640BE | 1640BE (非取樣點) | LINE161 | P06/161/1640/BE0 |  |  |  |  | 879 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | LE0 | 1710LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1710LE | 1710LE (非取樣點) | LINE161 | P06/161/1710/LE0 |  |  |  |  | 880 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1710 | 安南豐華紅線(1710) |  | BE0 | 1710BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1710BE | 1710BE (非取樣點) | LINE161 | P06/161/1710/BE0 |  |  |  |  | 881 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | LE0 | 1720LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1720LE | 1720LE (非取樣點) | LINE161 | P06/161/1720/LE0 |  |  |  |  | 882 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1720 | 新化二路(1720) |  | BE0 | 1720BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1720BE | 1720BE (非取樣點) | LINE161 | P06/161/1720/BE0 |  |  |  |  | 883 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | LE0 | 1730LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1730LE | 1730LE (非取樣點) | LINE161 | P06/161/1730/LE0 |  |  |  |  | 884 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1730 | 新化一路(1730) |  | BE0 | 1730BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1730BE | 1730BE (非取樣點) | LINE161 | P06/161/1730/BE0 |  |  |  |  | 885 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | LE0 | 610LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.610LE | 610LE (非取樣點) | LINE69 | P06/69/610/LE0 |  |  |  |  | 886 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 610 | 山頂一路(610) |  | BE0 | 610BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.610BE | 610BE (非取樣點) | LINE69 | P06/69/610/BE0 |  |  |  |  | 887 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.620LE | 620LE (非取樣點) | LINE69 | P06/69/620/LE0 |  |  |  |  | 888 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 620 | 山頂二路(620) |  | BE0 | 620BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.620BE | 620BE (非取樣點) | LINE69 | P06/69/620/BE0 |  |  |  |  | 889 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.630LE | 630LE (非取樣點) | LINE69 | P06/69/630/LE0 |  |  |  |  | 890 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 630 | 善化一路(630) |  | BE0 | 630BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.630BE | 630BE (非取樣點) | LINE69 | P06/69/630/BE0 |  |  |  |  | 891 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | LE0 | 640LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.640LE | 640LE (非取樣點) | LINE69 | P06/69/640/LE0 |  |  |  |  | 892 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 640 | 善化二路(640) |  | BE0 | 640BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.640BE | 640BE (非取樣點) | LINE69 | P06/69/640/BE0 |  |  |  |  | 893 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | LE0 | 650LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.650LE | 650LE (非取樣點) | LINE69 | P06/69/650/LE0 |  |  |  |  | 894 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 650 | 善化三路(650) |  | BE0 | 650BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.650BE | 650BE (非取樣點) | LINE69 | P06/69/650/BE0 |  |  |  |  | 895 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | LE0 | 660LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.660LE | 660LE (非取樣點) | LINE69 | P06/69/660/LE0 |  |  |  |  | 896 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 660 | 新市一路(660) |  | BE0 | 660BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.660BE | 660BE (非取樣點) | LINE69 | P06/69/660/BE0 |  |  |  |  | 897 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | LE0 | 670LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.670LE | 670LE (非取樣點) | LINE69 | P06/69/670/LE0 |  |  |  |  | 898 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 670 | 山上新市三路(670) |  | BE0 | 670BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.670BE | 670BE (非取樣點) | LINE69 | P06/69/670/BE0 |  |  |  |  | 899 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | LE0 | 680LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.680LE | 680LE (非取樣點) | LINE69 | P06/69/680/LE0 |  |  |  |  | 900 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 680 | 歸仁線(680) |  | BE0 | 680BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.680BE | 680BE (非取樣點) | LINE69 | P06/69/680/BE0 |  |  |  |  | 901 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | LE0 | 710LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.710LE | 710LE (非取樣點) | LINE69 | P06/69/710/LE0 |  |  |  |  | 902 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 710 | 新市二路(710) |  | BE0 | 710BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.710BE | 710BE (非取樣點) | LINE69 | P06/69/710/BE0 |  |  |  |  | 903 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 山上PS.1501E | 1501E (非取樣點) | TIE | P06/161/1500/E1 |  |  |  |  | 904 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 山上PS.1502E | 1502E (非取樣點) | TIE | P06/161/1500/E2 |  |  |  |  | 905 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_S | [8 empty] | 山上PS.601E | 601E (非取樣點) | TIE | P06/69/600/E1 |  |  |  |  | 906 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_S | [8 empty] | 山上PS.602E | 602E (非取樣點) | TIE | P06/69/600/E2 |  |  |  |  | 907 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1650TE | 1650TE (非取樣點) | MTR | P06/161/1650/TE0 |  |  |  |  | 908 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.750TE | 750TE (非取樣點) | MTR | P06/69/750/TE0 |  |  |  |  | 909 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | NE0 | 1651N | [24 empty] | ADCS_S | [8 empty] | 山上PS.1651N | 1651N (非取樣點) | MTR | P06/161/1650/NE0 |  |  |  |  | 910 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1650BE | 1650BE (非取樣點) | MTR | P06/161/1650/BE0 |  |  |  |  | 911 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.750BE | 750BE (非取樣點) | MTR | P06/69/750/BE0 |  |  |  |  | 912 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1660TE | 1660TE (非取樣點) | MTR | P06/161/1660/TE0 |  |  |  |  | 913 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.760TE | 760TE (非取樣點) | MTR | P06/69/760/TE0 |  |  |  |  | 914 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | NE0 | 1661N | [24 empty] | ADCS_S | [8 empty] | 山上PS.1661N | 1661N (非取樣點) | MTR | P06/161/1660/NE0 |  |  |  |  | 915 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1660BE | 1660BE (非取樣點) | MTR | P06/161/1660/BE0 |  |  |  |  | 916 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.760BE | 760BE (非取樣點) | MTR | P06/69/760/BE0 |  |  |  |  | 917 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | 1670TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1670TE | 1670TE (非取樣點) | MTR | P06/161/1670/TE0 |  |  |  |  | 918 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.770TE | 770TE (非取樣點) | MTR | P06/69/770/TE0 |  |  |  |  | 919 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | NE0 | 1671N | [24 empty] | ADCS_S | [8 empty] | 山上PS.1671N | 1671N (非取樣點) | MTR | P06/161/1670/NE0 |  |  |  |  | 920 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | 1670BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1670BE | 1670BE (非取樣點) | MTR | P06/161/1670/BE0 |  |  |  |  | 921 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.770BE | 770BE (非取樣點) | MTR | P06/69/770/BE0 |  |  |  |  | 922 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 820BE | 820BE |  | 820BE | 820BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.820BE | 820BE (非取樣點) | SC | P06/69/820/BE0 |  |  |  |  | 923 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 820CE | 820CE |  | 820CE | 820CE | [24 empty] | ADCS_S | [8 empty] | 山上PS.820CE | 820CE (非取樣點) | SC | P06/69/820/CE0 |  |  |  |  | 924 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 830BE | 830BE |  | 830BE | 830BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.830BE | 830BE (非取樣點) | SC | P06/69/830/BE0 |  |  |  |  | 925 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 830CE | 830CE |  | 830CE | 830CE | [24 empty] | ADCS_S | [8 empty] | 山上PS.830CE | 830CE (非取樣點) | SC | P06/69/830/CE0 |  |  |  |  | 926 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_S | [8 empty] | 山上PS.161B1E | 161B1E (非取樣點) | BUS | P06/161/161B1E/BE1 |  |  |  |  | 927 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_S | [8 empty] | 山上PS.161B2E | 161B2E (非取樣點) | BUS | P06/161/161B2E/BE2 |  |  |  |  | 928 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 山上PS.69B1E | 69B1E (非取樣點) | BUS | P06/69/69B1E/BE1 |  |  |  |  | 929 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_S | [8 empty] | 山上PS.69B2E | 69B2E (非取樣點) | BUS | P06/69/69B2E/BE2 |  |  |  |  | 930 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 山上PS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 931 | NotelDIPoint | [38 empty] | START/STOP | STOP
P06 | 山上PS | 69 | 69kV | 1510 | 嘉義新營紅線(1510) |  | PW1UL | 1510_PW1UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1510_PW1UL | 新營紅線(1510)PW1_UL(非取樣點) | LINE69 | [5 empty] | 932 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1510 | 嘉義新營紅線(1510) |  | PW2UL | 1510_PW2UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1510_PW2UL | 新營紅線(1510)PW2_UL(非取樣點) | LINE69 | [5 empty] | 933 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P06 | 山上PS | 69 | 69kV | 1510 | 嘉義新營紅線(1510) |  | HCBUL | 1510_HCBUL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1510_HCBUL | 新營紅線(1510)HCB_UL(非取樣點) | LINE69 | [5 empty] | 934 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1520 | 嘉義新營白線(1520) |  | PW1UL | 1520_PW1UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1520_PW1UL | 新營白線(1520)PW1_UL(非取樣點) | LINE69 | [5 empty] | 935 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1520 | 嘉義新營白線(1520) |  | PW2UL | 1520_PW2UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1520_PW2UL | 新營白線(1520)PW2_UL(非取樣點) | LINE69 | [5 empty] | 936 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P06 | 山上PS | 69 | 69kV | 1520 | 嘉義新營白線(1520) |  | HCBUL | 1520_HCBUL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1520_HCBUL | 新營白線(1520)HCB_UL(非取樣點) | LINE69 | [5 empty] | 937 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1730 | 新化一路(1730) |  | PW1UL | 1730_PW1UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1730_PW1UL | 新化一路(1730)PW1_UL(非取樣點) | LINE69 | [5 empty] | 938 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1730 | 新化一路(1730) |  | PW2UL | 1730_PW2UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1730_PW2UL | 新化一路(1730)PW2_UL(非取樣點) | LINE69 | [5 empty] | 939 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P06 | 山上PS | 69 | 69kV | 1730 | 新化一路(1730) |  | HCBUL | 1730_HCBUL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1730_HCBUL | 新化一路(1730)HCB_UL(非取樣點) | LINE69 | [5 empty] | 940 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1720 | 新化二路(1720) |  | PW1UL | 1720_PW1UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1720_PW1UL | 新化二路(1720)PW1_UL(非取樣點) | LINE69 | [5 empty] | 941 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 69 | 69kV | 1720 | 新化二路(1720) |  | PW2UL | 1720_PW2UL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1720_PW2UL | 新化二路(1720)PW2_UL(非取樣點) | LINE69 | [5 empty] | 942 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P06 | 山上PS | 69 | 69kV | 1720 | 新化二路(1720) |  | HCBUL | 1720_HCBUL | [24 empty] | ADCS_S | [8 empty] | 山上PS.1720_HCBUL | 新化二路(1720)HCB_UL(非取樣點) | LINE69 | [5 empty] | 943 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1550LE | 1550LE (非取樣點) | LINE161 | P06/161/1550/LE0 |  |  |  |  | 944 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1550 | 豐德紅線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1550BE | 1550BE (非取樣點) | LINE161 | P06/161/1550/BE0 |  |  |  |  | 945 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1560LE | 1560LE (非取樣點) | LINE161 | P06/161/1560/LE0 |  |  |  |  | 946 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1560 | 豐德白線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1560BE | 1560BE (非取樣點) | LINE161 | P06/161/1560/BE0 |  |  |  |  | 947 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 山上PS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 948 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 山上PS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 949 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 山上PS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 950 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 山上PS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 951 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | 1950BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1950BE | 1950BE (非取樣點) | MTR | P06/161/1950/BE0 |  |  |  |  | 952 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1950RE | 1950RE(非取樣點) | OTHER | P06/161/1950/RE0 |  |  |  |  | 953 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E11 | 4E11_DS |  | DS1 | 4E11_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_DS | 4E11_DS (非取樣點) | FEEDER | [5 empty] | 954 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E11 | 4E11_ES |  | E110 | 4E11_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E11_ES | 4E11_ES (非取樣點) | FEEDER | [5 empty] | 955 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E12 | 4E12_DS |  | DS1 | 4E12_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_DS | 4E12_DS (非取樣點) | FEEDER | [5 empty] | 956 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E12 | 4E12_ES |  | E120 | 4E12_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E12_ES | 4E12_ES (非取樣點) | FEEDER | [5 empty] | 957 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E13 | 4E13_DS |  | DS1 | 4E13_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_DS | 4E13_DS (非取樣點) | FEEDER | [5 empty] | 958 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E13 | 4E13_ES |  | E130 | 4E13_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E13_ES | 4E13_ES (非取樣點) | FEEDER | [5 empty] | 959 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E14 | 4E14_DS |  | DS1 | 4E14_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_DS | 4E14_DS (非取樣點) | FEEDER | [5 empty] | 960 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E14 | 4E14_ES |  | E140 | 4E14_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E14_ES | 4E14_ES (非取樣點) | FEEDER | [5 empty] | 961 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E15 | 4E15_DS |  | DS1 | 4E15_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_DS | 4E15_DS (非取樣點) | FEEDER | [5 empty] | 962 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E15 | 4E15_ES |  | E150 | 4E15_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E15_ES | 4E15_ES (非取樣點) | FEEDER | [5 empty] | 963 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E16 | 4E16_DS |  | DS1 | 4E16_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_DS | 4E16_DS (非取樣點) | FEEDER | [5 empty] | 964 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E16 | 4E16_ES |  | E160 | 4E16_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E16_ES | 4E16_ES (非取樣點) | FEEDER | [5 empty] | 965 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E17 | 4E17_DS |  | DS1 | 4E17_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_DS | 4E17_DS (非取樣點) | FEEDER | [5 empty] | 966 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E17 | 4E17_ES |  | E170 | 4E17_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E17_ES | 4E17_ES (非取樣點) | FEEDER | [5 empty] | 967 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E18 | 4E18_DS |  | DS1 | 4E18_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_DS | 4E18_DS (非取樣點) | FEEDER | [5 empty] | 968 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E18 | 4E18_ES |  | E180 | 4E18_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E18_ES | 4E18_ES (非取樣點) | FEEDER | [5 empty] | 969 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E19 | 4E19_DS |  | DS1 | 4E19_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_DS | 4E19_DS (非取樣點) | FEEDER | [5 empty] | 970 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E19 | 4E19_ES |  | E190 | 4E19_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E19_ES | 4E19_ES (非取樣點) | FEEDER | [5 empty] | 971 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 4E20 | 4E20_DS |  | DS1 | 4E20_DS | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_DS | 4E20_DS (非取樣點) | FEEDER | [5 empty] | 972 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 4E20 | 4E20_ES |  | E200 | 4E20_ES | [24 empty] | DDCS4_2 | [8 empty] | 山上PS.4E20_ES | 4E20_ES (非取樣點) | FEEDER | [5 empty] | 973 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1760TE | 1760TE (非取樣點) | MTR | P06/161/1760/TE0 |  |  |  |  | 974 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 161 | 161kV | 1760 | #6DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.1760BE | 1760BE (非取樣點) | MTR | P06/161/1760/BE0 |  |  |  |  | 975 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 山上PS.211E | 211E (非取樣點) | SC | P06/11/210/E1 |  |  |  |  | 976 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 山上PS.211 | 211 (非取樣點) | SC | P06/11/210/D1 |  |  |  |  | 977 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 山上PS.221E | 221E (非取樣點) | SC | P06/11/220/E1 |  |  |  |  | 978 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 山上PS.221 | 221 (非取樣點) | SC | P06/11/220/D1 |  |  |  |  | 979 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 山上PS.231E | 231E (非取樣點) | SC | P06/11/230/E1 |  |  |  |  | 980 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 山上PS.231 | 231 (非取樣點) | SC | P06/11/230/D1 |  |  |  |  | 981 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 山上PS.241E | 241E (非取樣點) | SC | P06/11/240/E1 |  |  |  |  | 982 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 山上PS.241 | 241 (非取樣點) | SC | P06/11/240/D1 |  |  |  |  | 983 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 330 | #6DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 山上PS.331E | 331E (非取樣點) | MTR | P06/11/330/E1 |  |  |  |  | 984 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 山上PS.341 | 341 (非取樣點) | MTR | P06/11/340/D1 |  |  |  |  | 985 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 340 | #6DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 山上PS.341E | 341E (非取樣點) | MTR | P06/11/340/E1 |  |  |  |  | 986 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 山上PS.331 | 331 (非取樣點) | MTR | P06/11/330/D1 |  |  |  |  | 987 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 山上PS.391 | 391 (非取樣點) | OTHER | P06/11/390/D1 |  |  |  |  | 988 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 山上PS.391E | 391E (非取樣點) | OTHER | P06/11/390/E1 |  |  |  |  | 989 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 6A | #6A |  | BE | #6A_BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.#6A_BE | #6A BE(非取樣點) | OTHER | [5 empty] | 990 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 6B | #6B |  | BE | #6B_BE | [24 empty] | ADCS_S | [8 empty] | 山上PS.#6B_BE | #6B BE(非取樣點) | OTHER | [5 empty] | 991 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 230CB | 山上PS(230CB) |  | A_M | [25 empty] | ADCS_S | [8 empty] | 山上PS.230CB_A/M | 山上PS 230CB 自動投切功能 | SC | [5 empty] | 992 | NotelDIPoint | [38 empty] | AUTO/MANUAL | MANUAL
P06 | 山上PS | 0 |  | 240CB | 山上PS(240CB) |  | A_M | [25 empty] | ADCS_S | [8 empty] | 山上PS.240CB_A/M | 山上PS 240CB 自動投切功能 | SC | [5 empty] | 993 | NotelDIPoint | [38 empty] | AUTO/MANUAL | MANUAL
P06 | 山上PS | 0 |  | 6ABUS | 6ABUS |  | PTE | 6ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 山上PS.6ABUS_PTE | #6ABUS_PTE(非取樣點) | OTHER | [5 empty] | 994 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 6ABUS | 6ABUS |  | PTD | 6ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 山上PS.6ABUS_PTD | #6ABUS_PTD(非取樣點) | OTHER | [5 empty] | 995 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P06 | 山上PS | 0 |  | 6BBUS | 6BBUS |  | PTE | 6BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 山上PS.6BBUS_PTE | #6BBUS_PTE(非取樣點) | OTHER | [5 empty] | 996 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P06 | 山上PS | 0 |  | 6BBUS | 6BBUS |  | PTD | 6BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 山上PS.6BBUS_PTD | #6BBUS_PTD(非取樣點) | OTHER | [5 empty] | 997 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo