## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | LE0 | 1520LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | LE0 | 1510LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | LE0 | 1560LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | LE0 | 1550LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | LE0 | 1530LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | LE0 | 1540LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.601E | 601E (非取樣點) | TIE | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.602E | 602E (非取樣點) | TIE | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1650TE | 1650TE (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1651N | #1MTR |  | NE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/1MTR(W) | [13 empty] | no rule | B2/P07_A1 | [8 empty] | 台南PS.1651N | 1651N (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1650BE | 1650BE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.750TE | 750TE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.750BE | 750BE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1660TE | 1660TE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1661N | #2MTR |  | NE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2MTR(W) | [13 empty] | no rule | B2/P07_A1 | [8 empty] | 台南PS.1661N | 1661N (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1660BE | 1660BE (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.760TE | 760TE (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.760BE | 760BE (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1670TE | 1670TE (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1671N | #3MTR |  | NE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3MTR(W) | [13 empty] | no rule | B2/P07_A1 | [8 empty] | 台南PS.1671N | 1671N (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1670BE | 1670BE (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.770TE | 770TE (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.770BE | 770BE (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.350_DS | 350_DS (非取樣點) | MTR | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.350_ES | 350_ES (非取樣點) | MTR | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(B)(320) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.320_DS | 320_DS (非取樣點) | MTR | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(B)(320) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.320_ES | 320_ES(非取樣點) | MTR | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | DS1 | 371(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.371 | 371 (非取樣點) | MTR | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | BE0 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.371E | 371E (非取樣點) | MTR | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | DS1 | 381(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.381 | 381 (非取樣點) | MTR | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | BE0 | 381E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.381E | 381E (非取樣點) | MTR | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.310A1_DS | 310A1_DS (非取樣點) | MTR | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.310A1_DS | 310A1_DS (非取樣點) | MTR | [5 empty] | 54 | [5 empty] | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.310A2_DS | 310A2_DS (非取樣點) | MTR | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.310A2_DS | 310A2_DS (非取樣點) | MTR | [5 empty] | 56 | [5 empty] | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | LE0 | 720LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.720LE | 720LE (非取樣點) | LINE69 | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | LE0 | 710LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | LE0 | 670LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | LE0 | 660LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | LE0 | 630LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | LE0 | 620LE | Del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.810BE | 810BE (非取樣點) | SC | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.810CE | 810CE (非取樣點) | SC | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.820BE | 820BE (非取樣點) | SC | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.820CE | 820CE (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.830BE | 830BE (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_A1 | [8 empty] | 台南PS.830CE | 830CE (非取樣點) | SC | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH61_DS | KH61_DS (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH61_ES | KH61_ES (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH62_DS | KH62_DS (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH62_ES | KH62_ES (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH63_DS | KH63_DS (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH63_ES | KH63_ES (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH64_DS | KH64_DS (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH64_ES | KH64_ES (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH65_DS | KH65_DS (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH65_ES | KH65_ES (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH66_DS | KH66_DS (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH66_ES | KH66_ES (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.240E | 240E (非取樣點) | SC | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.250E | 250E (非取樣點) | SC | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | D1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH31_DS | KH31_DS (非取樣點) | FEEDER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH31_ES | KH31_ES (非取樣點) | FEEDER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH32_DS | KH32_DS (非取樣點) | FEEDER | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH32_ES | KH32_ES (非取樣點) | FEEDER | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH33_DS | KH33_DS (非取樣點) | FEEDER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH33_ES | KH33_ES (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.210E | 210E (非取樣點) | SC | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH36_DS | KH36_DS (非取樣點) | FEEDER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH36_ES | KH36_ES (非取樣點) | FEEDER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH37_DS | KH37_DS (非取樣點) | FEEDER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH37_ES | KH37_ES (非取樣點) | FEEDER | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH38_DS | KH38_DS (非取樣點) | FEEDER | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH38_ES | KH38_ES (非取樣點) | FEEDER | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.220E | 220E (非取樣點) | SC | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | D1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.270_ES | 270_ES (非取樣點) | SC | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.270_DS | 270_DS (非取樣點) | SC | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.270E | 270E (非取樣點) | SC | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.260E | 260E (非取樣點) | SC | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH71_DS | KH71_DS (非取樣點) | FEEDER | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH71_ES | KH71_ES (非取樣點) | FEEDER | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH72_DS | KH72_DS (非取樣點) | FEEDER | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH72_ES | KH72_ES (非取樣點) | FEEDER | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH73_DS | KH73_DS (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH73_ES | KH73_ES (非取樣點) | FEEDER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH74_DS | KH74_DS (非取樣點) | FEEDER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH74_ES | KH74_ES (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH75_DS | KH75_DS (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH75_ES | KH75_ES (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | DS1 | (非取樣點) | B3,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH76_DS | KH76_DS (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | E1 | (非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH76_ES | KH76_ES (非取樣點) | FEEDER | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | DS2 | (非取樣點) | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.230E | 230E (非取樣點) | SC | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH41_DS | KH41_DS (非取樣點) | FEEDER | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH41_ES | KH41_ES (非取樣點) | FEEDER | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH42_DS | KH42_DS (非取樣點) | FEEDER | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH42_ES | KH42_ES (非取樣點) | FEEDER | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH43_DS | KH43_DS (非取樣點) | FEEDER | [5 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH43_ES | KH43_ES (非取樣點) | FEEDER | [5 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH44_DS | KH44_DS (非取樣點) | FEEDER | [5 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH44_ES | KH44_ES (非取樣點) | FEEDER | [5 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH45_DS | KH45_DS (非取樣點) | FEEDER | [5 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH45_ES | KH45_ES (非取樣點) | FEEDER | [5 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH46_DS | KH46_DS (非取樣點) | FEEDER | [5 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | E1 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH46_ES | KH46_ES (非取樣點) | FEEDER | [5 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | BE0 | 411E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.411E | 411E (非取樣點) | SC | [5 empty] | 146 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | DS1 | 411(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.411 | 411 (非取樣點) | SC | [5 empty] | 147 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | BE0 | 421E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.421E | 421E (非取樣點) | SC | [5 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | DS1 | 421(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.421 | 421 (非取樣點) | SC | [5 empty] | 149 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH11_DS | KH11_DS (非取樣點) | FEEDER | [5 empty] | 150 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH11_ES | KH11_ES (非取樣點) | FEEDER | [5 empty] | 151 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH12_DS | KH12_DS (非取樣點) | FEEDER | [5 empty] | 152 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH12_ES | KH12_ES (非取樣點) | FEEDER | [5 empty] | 153 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH13_DS | KH13_DS (非取樣點) | FEEDER | [5 empty] | 154 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH13_ES | KH13_ES (非取樣點) | FEEDER | [5 empty] | 155 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH14_DS | KH14_DS (非取樣點) | FEEDER | [5 empty] | 156 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH14_ES | KH14_ES (非取樣點) | FEEDER | [5 empty] | 157 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH15_DS | KH15_DS (非取樣點) | FEEDER | [5 empty] | 158 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH15_ES | KH15_ES (非取樣點) | FEEDER | [5 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.301 | 301 (非取樣點) | TIE | [5 empty] | 160 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.301E | 301E (非取樣點) | TIE | [5 empty] | 161 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 390 | #3SSTR(390) |  | DS1 | 391(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.391 | 391 (非取樣點) | OTHER | [5 empty] | 162 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 390 | #3SSTR(390) |  | BE0 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.391E | 391E (非取樣點) | OTHER | [5 empty] | 163 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH20_DS | KH20_DS (非取樣點) | FEEDER | [5 empty] | 164 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH20_ES | KH20_ES (非取樣點) | FEEDER | [5 empty] | 165 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH19_DS | KH19_DS (非取樣點) | FEEDER | [5 empty] | 166 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH19_ES | KH19_ES (非取樣點) | FEEDER | [5 empty] | 167 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH18_DS | KH18_DS (非取樣點) | FEEDER | [5 empty] | 168 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH18_ES | KH18_ES (非取樣點) | FEEDER | [5 empty] | 169 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH17_DS | KH17_DS (非取樣點) | FEEDER | [5 empty] | 170 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH17_ES | KH17_ES (非取樣點) | FEEDER | [5 empty] | 171 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | DS1 | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH16_DS | KH16_DS (非取樣點) | FEEDER | [5 empty] | 172 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P07_D1 | [8 empty] | 台南PS.KH16_ES | KH16_ES (非取樣點) | FEEDER | [5 empty] | 173 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | BE0 | 441E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.441E | 441E (非取樣點) | SC | [5 empty] | 174 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | DS1 | 441(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.441 | 441 (非取樣點) | SC | [5 empty] | 175 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | BE0 | 431E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.431E | 431E (非取樣點) | SC | [5 empty] | 176 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | DS1 | 431(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.431 | 431 (非取樣點) | SC | [5 empty] | 177 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.401 | 401 (非取樣點) | TIE | [5 empty] | 178 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P07_A1 | [8 empty] | 台南PS.401E | 401E (非取樣點) | TIE | [5 empty] | 179 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aadz | B2/P07_A1 | [8 empty] | 台南PS.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 180 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aadz | B2/P07_A1 | [8 empty] | 台南PS.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 181 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aa | B2/P07_A1 | [8 empty] | 台南PS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 182 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aa | B2/P07_A1 | [8 empty] | 台南PS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 183 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | Locate Empty | KV | 161KV #1BUS電壓 | kV_-210_210(-2000_2000) | aaa | B2/P07_A1 | [8 empty] | 台南PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | Locate Empty | KV | 161KV #2BUS電壓 | kV_-210_210(-2000_2000) | aab | B2/P07_A1 | [8 empty] | 台南PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1570 | MW | 台南忠孝一路 1570 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1570_MW | 台南忠孝一路 MW | LINE161 | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1570 | MVAR | 台南忠孝一路 1570 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1570_MVAR | 台南忠孝一路 MVAR | LINE161 | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520 | MW | 山上台南海線 1520 瓦 | MW_-448_448(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1520_MW | 山上海線 MW | LINE161 | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520 | MVAR | 山上台南海線 1520 乏 | MVAR_-448_448(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1520_MVAR | 山上海線 MVAR | LINE161 | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1510 | MW | 台南仁德線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1510_MW | 台南仁德線 MW | LINE161 | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1510 | MVAR | 台南仁德線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1510_MVAR | 台南仁德線 MVAR | LINE161 | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1560 | MW | 台南忠孝二路 1560 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1560_MW | 台南忠孝二路 MW | LINE161 | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1560 | MVAR | 台南忠孝二路 1560 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1560_MVAR | 台南忠孝二路 MVAR | LINE161 | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1550 | MW | 台南延平線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1550_MW | 台南延平線 MW | LINE161 | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1550 | MVAR | 台南延平線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1550_MVAR | 台南延平線 MVAR | LINE161 | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1530 | MW | 龍崎台南山線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1530_MW | 龍崎山線 MW | LINE161 | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1530 | MVAR | 龍崎台南山線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1530_MVAR | 龍崎山線 MVAR | LINE161 | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1540 | MW | 龍崎台南海線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1540_MW | 龍崎海線 MW | LINE161 | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1540 | MVAR | 龍崎台南海線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1540_MVAR | 龍崎海線 MVAR | LINE161 | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1500 | A | 161KV TIE R相電流 1500 | A_-2000_2000(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | TEST CB |  |  | ELEM/ALL | [8 empty] | 台南PS.TEST_CB | TEST CB | OTHER | [5 empty] | 203 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1MTR | ℃ | #1MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_OIL | #1MTR 油溫 | MTR | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1MTR | ℃ | #1MTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_COIL | #1MTR 線溫 | MTR | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 11 | 11kV | 390 | #3SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | T/3SSTR |  |  | 0427 |  | 0001 | 2-15-03 |  | 1-01 | 390 | ON/OFF | #3SSTR 390 CB |  | aeab | B3/P07_A1 | [8 empty] | 台南PS.390_CB | 390(#3SSTR) CB | OTHER | [5 empty] | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_OIL | #2MTR 油溫 | MTR | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2MTR | ℃ | #2MTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_COIL | #2MTR 線溫 | MTR | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P06P07O/T2 |  | 0004 |  | 0002 | 1-00-04 |  | 1-02 | 1520 | ON/OFF | 山上台南海線 |  | aajb | B2/P07_A1 | [8 empty] | 台南PS.1520_CB | 1520(山上海線) CB | LINE161 | [5 empty] | 209 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #3MTR | ℃ | #3MTR 油溫 | OIL_-150_150(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_OIL | #3MTR 油溫 | MTR | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.3 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.300000
P07 | 台南PS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #3MTR | ℃ | #3MTR 線溫 | COIL_-150_150(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_COIL | #3MTR 線溫 | MTR | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.3 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.300000
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 1560 | KG | 1560 台南忠孝二路 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1560_OF_R | 台南忠孝二路 R相 油壓 | OTHER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 1560 | KG | 1550台南忠孝二路 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1560_OF_S | 台南忠孝二路 S相 油壓 | OTHER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS |  |  | 5DTR | #5DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #5DTR | ℃ | #5DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_OIL | #5DTR 油溫 | MTR | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | #5ADTR | ℃ | #5ADTR 線溫 (5A) | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_COIL | #5DTR(A) 線溫 | MTR | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 5DTR(B) | #5DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | #5BDTR | ℃ | #5BDTR 線溫 (5B) | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_COIL | #5DTR(B) 線溫 | MTR | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07D16/T1 |  | 0008 |  | 0003 | 1-01-00 |  | 1-03 | 1510 | ON/OFF | 台南仁德線 |  | aakb | B2/P07_A1 | [8 empty] | 台南PS.1510_CB | 1510(台南仁德線) CB | LINE161 | [5 empty] | 217 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07D182/T1 |  | 0012 |  | 0004 | 1-01-04 |  | 1-04 | 1560 | ON/OFF | 台南忠孝二路 |  | aana | B2/P07_A1 | [8 empty] | 台南PS.1560_CB | 1560(台南忠孝二路) CB | LINE161 | [5 empty] | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 8DTR | #8DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | Locate Empty | ℃ | #8DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_OIL | #8DTR 油溫 | MTR | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 6DTR | #6DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #6DTR | ℃ | #6DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_OIL | #6DTR 油溫 | MTR | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 6DTR | #6DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | #6DTR | ℃ | #6DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_COIL | #6DTR 線溫 | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 8DTR(A) | #8DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | Locate Empty | ℃ | #8DTR D4A 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_COIL | #8DTR(A) 線溫 | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07D25/T1 |  | 0016 |  | 0005 | 1-02-00 |  | 1-05 | 1550 | ON/OFF | 台南延平線 |  | aama | B2/P07_A1 | [8 empty] | 台南PS.1550_CB | 1550(台南延平線) CB | LINE161 | [5 empty] | 223 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 8DTR(B) | #8DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | Locate Empty | ℃ | #8DTR D4B 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_COIL | #8DTR(B) 線溫 | MTR | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 7DTR | #7DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | #7DTR | ℃ | #7DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_OIL | #7DTR 油溫 | MTR | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS |  |  | 7DTR | #7DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | #7DTR | ℃ | #7DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_COIL | #7DTR 線溫 | MTR | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/E02P07M/T2 |  | 0020 |  | 0006 | 1-02-04 |  | 1-06 | 1530 | ON/OFF | 龍崎台南山線 |  | aapa | B2/P07_A1 | [8 empty] | 台南PS.1530_CB | 1530(龍崎山線) CB | LINE161 | [5 empty] | 227 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/E02P07O/T2 |  | 0024 |  | 0007 | 1-03-00 |  | 1-07 | 1540 | ON/OFF | 龍崎台南海線 |  | aaqa | B2/P07_A1 | [8 empty] | 台南PS.1540_CB | 1540(龍崎海線) CB | LINE161 | [5 empty] | 228 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0028 |  | 0008 | 1-03-04 |  | 1-08 | 1500 | ON/OFF | 161KV TIE |  | aahz | B2/P07_A1 | [8 empty] | 台南PS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 229 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 1560 | KG | 1550台南忠孝二路 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1560_OF_T | 台南忠孝二路 T相 油壓 | OTHER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0054 |  |  | 1-B6 |  |  | #1BUS | KV | 69KV #1BUS電壓 | kV_-90_90(-2000_2000) | aaa | B2/P07_A1 | [8 empty] | 台南PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P07 | 台南PS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0055 |  |  | 1-B7 |  |  | #2BUS | KV | 69KV #2BUS電壓 | kV_-90_90(-2000_2000) | aab | B2/P07_A1 | [8 empty] | 台南PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 720 | MW | 台南大灣二路 720 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.720_MW | 台南大灣二路 MW | LINE69 | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 720 | MVAR | 台南大灣二路 720 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.720_MVAR | 台南大灣二路 MVAR | LINE69 | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 710 | MW | 台南南仁線 710 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.710_MW | 南仁線 MW | LINE69 | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 710 | MVAR | 台南南仁線 710 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.710_MVAR | 南仁線 MVAR | LINE69 | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 670 | MW | 台南大灣一路 670 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.670_MW | 台南大灣一路 MW | LINE69 | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 670 | MVAR | 台南大灣一路 670 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.670_MVAR | 台南大灣一路 MVAR | LINE69 | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 660 | MW | 台南後甲海線 660 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.660_MW | 台南後甲海線 MW | LINE69 | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 660 | MVAR | 台南後甲海線 660 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.660_MVAR | 台南後甲海線 MVAR | LINE69 | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 630 | MW | 台南光洲線 630 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.630_MW | 台南光洲線 MW | LINE69 | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 630 | MVAR | 台南光洲線 630 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.630_MVAR | 台南光洲線 MVAR | LINE69 | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 620 | MW | 台南保安線 620 瓦 | MW_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.620_MW | 保安線 MW | LINE69 | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 620 | MVAR | 台南保安線 620 乏 | MVAR_-144_144(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.620_MVAR | 保安線 MVAR | LINE69 | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 1550 | KG | 1550 台南延平線 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1550_OF_R | 台南延平線 R相 油壓 | OTHER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 1550 | KG | 1550 台南延平線 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1550_OF_S | 台南延平線 S相 油壓 | OTHER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 1550 | KG | 1550 台南延平線 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1550_OF_T | 台南延平線 T相 油壓 | OTHER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | RTU第二箱 | V | DCP 電壓 P-E | kV_-150_150(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | RTU第二箱 | V | DCN 電壓 N-E | kV_-150_150(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 600 | A | 69KV TIE R相電流 600 | A_-2000_2000(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | #1MTR | MW | #1MTR 瓦 二次側 750 | MW_-360_360(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#1MTR_MW | #1MTR二次側 MW | MTR | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | #1MTR | MVAR | #1MTR 乏 二次側 750 | MVAR_-240_240(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | #2MTR | MW | #2MTR 瓦 二次側 760 | MW_-360_360(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#2MTR_MW | #2MTR二次側 MW | MTR | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2MTR | MVAR | #2MTR 乏 二次側 760 | MVAR_-240_240(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #3MTR | MW | #3MTR 瓦 二次側 770 | MW_-360_360(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#3MTR_MW | #3MTR二次側 MW | MTR | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #3MTR | MVAR | #3MTR 乏 二次側 770 | MVAR_-240_240(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 1530 | KV | 龍崎山線 LPD 1530 | kV_-210_210(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1530LPD_KV | 龍崎山線(1530) LPD KV | LINE161 | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 1540 | KV | 龍崎海線 LPD 1540 | kV_-210_210(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1540LPD_KV | 龍崎海線(1540) LPD KV | LINE161 | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 22 | 22kV | 6BUS | #6BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0096 |  |  | 1-E0 |  |  | #6DTR | KV | #6DTR 22KV BUS 電壓 | kV_-18_18(-2000_2000) | baa | B3/P07_A1 | [8 empty] | 台南PS.23KV#6BUS_KV | 23KV #6BUS KV | BUS | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 330CB | MW | #6DTR 330CB 瓦 | MW_-72_72(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#6DTR_MW | #6DTR二次側 MW | MTR | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 330CB | MVAR | #6DTR 330CB 乏 | MVAR_-72_72(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#6DTR_MVAR | #6DTR二次側 MVAR | MTR | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 330CB | A | #6DTR 330CB R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#6DTR_A1 | #6DTR二次側 R相AMP | MTR | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 330CB | A | #6DTR 330CB S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#6DTR_A2 | #6DTR二次側 S相AMP | MTR | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 330CB | A | #6DTR 330CB T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#6DTR_A3 | #6DTR二次側 T相AMP | MTR | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | KH61 | MVAR | 台61線 KH61 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台61線KVAR | 23KV台61線 KVAR | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | KH61 | A | 台61線 KH61 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台61線A1 | 23KV台61線 R相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | KH61 | A | 台61線 KH61 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台61線A2 | 23KV台61線 S相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | KH61 | A | 台61線 KH61 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台61線A3 | 23KV台61線 T相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | KH62 | MVAR | 台62線 KH62 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台62線KVAR | 23KV台62線 KVAR | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | KH62 | A | 台62線 KH62 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台62線A1 | 23KV台62線 R相AMP | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | KH62 | A | 台62線 KH62 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台62線A2 | 23KV台62線 S相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | KH62 | A | 台62線 KH62 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台62線A3 | 23KV台62線 T相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | KH63 | MVAR | 台63線 KH63 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台63線KVAR | 23KV台63線 KVAR | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | KH63 | A | 台63線 KH63 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台63線A1 | 23KV台63線 R相AMP | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | KH63 | A | 台63線 KH63 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台63線A2 | 23KV台63線 S相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | KH63 | A | 台63線 KH63 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台63線A3 | 23KV台63線 T相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | KH64 | MVAR | 台64線 KH64 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台64線KVAR | 23KV台64線 KVAR | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | KH64 | A | 台64線 KH64 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台64線A1 | 23KV台64線 R相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | KH64 | A | 台64線 KH64 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台64線A2 | 23KV台64線 S相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | KH64 | A | 台64線 KH64 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台64線A3 | 23KV台64線 T相AMP | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | KH65 | MVAR | 台65線 KH65 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台65線KVAR | 23KV台65線 KVAR | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | KH65 | A | 台65線 KH65 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台65線A1 | 23KV台65線 R相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | KH65 | A | 台65線 KH65 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台65線A2 | 23KV台65線 S相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | KH65 | A | 台65線 KH65 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台65線A3 | 23KV台65線 T相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | KH66 | MVAR | 台66線 KH66 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台66線KVAR | 23KV台66線 KVAR | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | KH66 | A | 台66線 KH66 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台66線A1 | 23KV台66線 R相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | KH66 | A | 台66線 KH66 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台66線A2 | 23KV台66線 S相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | KH66 | A | 台66線 KH66 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台66線A3 | 23KV台66線 T相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 1510 | KV | 山上台南山線 1510LPD | kV_-210_210(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1510LPD_KV | 台南仁德線(1510) LPD KV | LINE161 | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 1520 | KV | 山上台南海線 LPD1520 | kV_-210_210(-2000_2000) |  | B2/P07_A1 | [8 empty] | 台南PS.1520LPD_KV | 山上海線(1520) LPD KV | LINE161 | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No3AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 200TIE | A | 22KV 200TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 200TIE | A | 22KV 200TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 200TIE | A | 22KV 200TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 100TIE | A | 11KV 100TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 100TIE | A | 11KV 100TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 100TIE | A | 11KV 100TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 5A1BUS | #5A1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0136 |  |  | 2-88 |  |  | #5A2 BUS | KV | #5DTR A1 11KV BUS 電壓 | kV_-9_9(-2000_2000) | aaa | B3/P07_A1 | [8 empty] | 台南PS.11KV#5A1BUS_KV | 11KV #5A1BUS KV | BUS | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 310A1CB | MW | #5DTR 310A1CB 瓦 | MW_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_MW | #5DTR二次側(A) MW | MTR | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 310A1CB | MVAR | #5DTR 310A1CB 乏 | MVAR_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_MVAR | #5DTR二次側(A) MVAR | MTR | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 310A1CB | A | #5DTR 310A1CB R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_A1 | #5DTR二次側(A) R相AMP | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 310A1CB | A | #5DTR 310A1CB S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_A2 | #5DTR二次側(A) S相AMP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 310A1CB | A | #5DTR 310A1CB T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_A3 | #5DTR二次側(A) T相AMP | MTR | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | KH31 | MVAR | 台31線 KH31 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台31線KVAR | 11KV台31線 KVAR | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | KH31 | A | 台31線 KH31 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台31線A1 | 11KV台31線 R相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | KH31 | A | 台31線 KH31 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台31線A2 | 11KV台31線 S相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | KH31 | A | 台31線 KH31 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台31線A3 | 11KV台31線 T相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | KH32 | MVAR | 台32線 KH32 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台32線KVAR | 11KV台32線 KVAR | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | KH32 | A | 台32線 KH32 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台32線A1 | 11KV台32線 R相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | KH32 | A | 台32線 KH32 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台32線A2 | 11KV台32線 S相AMP | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | KH32 | A | 台32線 KH32 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台32線A3 | 11KV台32線 T相AMP | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | KH33 | MVAR | 台33線 KH33 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台33線KVAR | 11KV台33線 KVAR | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | KH33 | A | 台33線 KH33 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台33線A1 | 11KV台33線 R相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | KH33 | A | 台33線 KH33 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台33線A2 | 11KV台33線 S相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | KH33 | A | 台33線 KH33 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台33線A3 | 11KV台33線 T相AMP | FEEDER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | KH36 | MVAR | 台36線 KH36 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台36線KVAR | 11KV台36線 KVAR | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | KH36 | A | 台36線 KH36 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台36線A1 | 11KV台36線 R相AMP | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | KH36 | A | 台36線 KH36 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台36線A2 | 11KV台36線 S相AMP | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | KH36 | A | 台36線 KH36 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台36線A3 | 11KV台36線 T相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | KH37 | MVAR | 台37線 KH37 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台37線KVAR | 11KV台37線 KVAR | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | KH37 | A | 台37線 KH37 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台37線A1 | 11KV台37線 R相AMP | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | KH37 | A | 台37線 KH37 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台37線A2 | 11KV台37線 S相AMP | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | KH37 | A | 台37線 KH37 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台37線A3 | 11KV台37線 T相AMP | FEEDER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | KH38 | MVAR | 台38線 KH38 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台38線KVAR | 11KV台38線 KVAR | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | KH38 | A | 台38線 KH38 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台38線A1 | 11KV台38線 R相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | KH38 | A | 台38線 KH38 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台38線A2 | 11KV台38線 S相AMP | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | KH38 | A | 台38線 KH38 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台38線A3 | 11KV台38線 T相AMP | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 5A2BUS | #5A2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0166 |  |  | 2-A6 |  |  | #5A2 BUS | KV | #5DTR A2 11KV BUS 電壓 | kV_-9_9(-2000_2000) | aba | B3/P07_A1 | [8 empty] | 台南PS.11KV#5A2BUS_KV | 11KV #5A2BUS KV | BUS | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 310A2CB | MW | #5DTR 310A2CB 瓦 | MW_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A2)_MW | #5DTR二次側(A2) MW | MTR | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 310A2CB | MVAR | #5DTR 310A2CB 乏 | MVAR_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A2)_MVAR | #5DTR二次側(A2) MVAR | MTR | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 310A2CB | A | #5DTR 310A2CB R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A2)_A1 | #5DTR二次側(A2) R相AMP | MTR | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 310A2CB | A | #5DTR 310A2CB S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A2)_A2 | #5DTR二次側(A2) S相AMP | MTR | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 310A2CB | A | #5DTR 310A2CB T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(A2)_A3 | #5DTR二次側(A2) T相AMP | MTR | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 7BUS | #7BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0172 |  |  | 2-AC |  |  | #7DTR | KV | #7DTR 22KV BUS 電壓 | kV_-18_18(-2000_2000) | bba | B3/P07_A1 | [8 empty] | 台南PS.23KV#7BUS_KV | 23KV #7BUS KV | BUS | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 350CB | MW | #7DTR 350CB 瓦 | MW_-72_72(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#7DTR_MW | #7DTR二次側 MW | MTR | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 350CB | MVAR | #7DTR 350CB 乏 | MVAR_-72_72(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#7DTR_MVAR | #7DTR二次側 MVAR | MTR | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 350CB | A | #7DTR 350CB R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#7DTR_A1 | #7DTR二次側 R相AMP | MTR | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 350CB | A | #7DTR 350CB S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#7DTR_A2 | #7DTR二次側 S相AMP | MTR | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 350CB | A | #7DTR 350CB T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#7DTR_A3 | #7DTR二次側 T相AMP | MTR | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | KH71 | MVAR | 台71線 KH71 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台71線KVAR | 23KV台71線 KVAR | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | KH71 | A | 台71線 KH71 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台71線A1 | 23KV台71線 R相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | KH71 | A | 台71線 KH71 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台71線A2 | 23KV台71線 S相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | KH71 | A | 台71線 KH71 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台71線A3 | 23KV台71線 T相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | KH72 | MVAR | 台72線 KH72 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台72線KVAR | 23KV台72線 KVAR | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | KH72 | A | 台72線 KH72 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台72線A1 | 23KV台72線 R相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | KH72 | A | 台72線 KH72 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台72線A2 | 23KV台72線 S相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | KH72 | A | 台72線 KH72 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台72線A3 | 23KV台72線 T相AMP | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | KH73 | MVAR | 台73線 KH73 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台73線KVAR | 23KV台73線 KVAR | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | KH73 | A | 台73線 KH73 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台73線A1 | 23KV台73線 R相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | KH73 | A | 台73線 KH73 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台73線A2 | 23KV台73線 S相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | KH73 | A | 台73線 KH73 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台73線A3 | 23KV台73線 T相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | KH74 | MVAR | 台74線 KH74 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台74線KVAR | 23KV台74線 KVAR | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | KH74 | A | 台74線 KH74 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台74線A1 | 23KV台74線 R相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No4AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | KH74 | A | 台74線 KH74 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台74線A2 | 23KV台74線 S相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | KH74 | A | 台74線 KH74 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台74線A3 | 23KV台74線 T相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | KH75 | MVAR | 台75線 KH75 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台75線KVAR | 23KV台75線 KVAR | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | KH75 | A | 台75線 KH75 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台75線A1 | 23KV台75線 R相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | KH75 | A | 台75線 KH75 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台75線A2 | 23KV台75線 S相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | KH75 | A | 台75線 KH75 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台75線A3 | 23KV台75線 T相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | KH76 | MVAR | F18 KH76 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台76線KVAR | 23KV台76線 KVAR | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | KH76 | A | F18 KH76 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台76線A1 | 23KV台76線 R相AMP | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | KH76 | A | F18 KH76 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台76線A2 | 23KV台76線 S相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | KH76 | A | F18 KH76 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台76線A3 | 23KV台76線 T相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.5AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No5AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 5BBUS | #5BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0258 |  |  | 3-82 |  |  | #5DTR | KV | 5B 11KV BUS 電壓 | kV_-9_9(-2000_2000) | aca | B3/P07_A1 | [8 empty] | 台南PS.11KV#5BBUS_KV | 11KV #5BBUS KV | BUS | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | 320CB | MW | #5DTR 320CB 瓦 | MW_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_MW | #5DTR二次側(B) MW | MTR | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 320CB | MVAR | #5DTR 320CB 乏 | MVAR_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_MVAR | #5DTR二次側(B) MVAR | MTR | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 320CB | A | #5DTR 320CB R相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_A1 | #5DTR二次側(B) R相AMP | MTR | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 320CB | A | #5DTR 320CB S相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_A2 | #5DTR二次側(B) S相AMP | MTR | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | 320CB | A | #5DTR 320CB T相電流 | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_A3 | #5DTR二次側(B) T相AMP | MTR | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | F19 | MVAR | 台41線 KH41乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台41線KVAR | 11KV台41線 KVAR | FEEDER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | F19 | A | 台41線 KH41 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台41線A1 | 11KV台41線 R相AMP | FEEDER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | F19 | A | 台41線 KH41 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台41線A2 | 11KV台41線 S相AMP | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | F19 | A | 台41線 KH41 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台41線A3 | 11KV台41線 T相AMP | FEEDER | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | F19 | A | 台41線 KH41 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台41線A0 | 11KV台41線 N相AMP | FEEDER | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | F20 | MVAR | 台42線 KH42 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台42線KVAR | 11KV台42線 KVAR | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | F20 | A | 台42線 KH42 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台42線A1 | 11KV台42線 R相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | F20 | A | 台42線 KH42 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台42線A2 | 11KV台42線 S相AMP | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | F20 | A | 台42線 KH42 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台42線A3 | 11KV台42線 T相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | F20 | A | 台42線 KH42 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台42線A0 | 11KV台42線 N相AMP | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | F21 | MVAR | 台43線 KH43 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台43線KVAR | 11KV台43線 KVAR | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | F21 | A | 台43線 KH43 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台43線A1 | 11KV台43線 R相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | F21 | A | 台43線 KH43 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台43線A2 | 11KV台43線 S相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | F21 | A | 台43線 KH43 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台43線A3 | 11KV台43線 T相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | F21 | A | 台43線 KH43 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台43線A0 | 11KV台43線 N相AMP | FEEDER | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | F22 | MVAR | 台44線 KH44乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台44線KVAR | 11KV台44線 KVAR | FEEDER | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | F22 | A | 台44線 KH44 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台44線A1 | 11KV台44線 R相AMP | FEEDER | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0281 |  |  | 3-99 |  |  | F22 | A | 台44線 KH44 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台44線A2 | 11KV台44線 S相AMP | FEEDER | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0282 |  |  | 3-9A |  |  | F22 | A | 台44線 KH44 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台44線A3 | 11KV台44線 T相AMP | FEEDER | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0283 |  |  | 3-9B |  |  | F22 | A | 台44線 KH44 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台44線A0 | 11KV台44線 N相AMP | FEEDER | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | F23 | MVAR | 備用線 KH45 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台45線KVAR | 11KV台45線 KVAR | FEEDER | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | F23 | A | 備用線 KH45 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台45線A1 | 11KV台45線 R相AMP | FEEDER | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | F23 | A | 備用線 KH45 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台45線A2 | 11KV台45線 S相AMP | FEEDER | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | F23 | A | 備用線 KH45 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台45線A3 | 11KV台45線 T相AMP | FEEDER | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | F23 | A | 備用線 KH45 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台45線A0 | 11KV台45線 N相AMP | FEEDER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | F24 | MVAR | 備用線 KH46 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台46線KVAR | 11KV台46線 KVAR | FEEDER | [5 empty] | 402 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0290 |  |  | 3-A2 |  |  | F24 | A | 備用線 KH46 R相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台46線A1 | 11KV台46線 R相AMP | FEEDER | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0291 |  |  | 3-A3 |  |  | F24 | A | 備用線 KH46 S相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台46線A2 | 11KV台46線 S相AMP | FEEDER | [5 empty] | 404 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0292 |  |  | 3-A4 |  |  | F24 | A | 備用線 KH46 T相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台46線A3 | 11KV台46線 T相AMP | FEEDER | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0293 |  |  | 3-A5 |  |  | F24 | A | 備用線 KH46 N相電流 | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台46線A0 | 11KV台46線 N相AMP | FEEDER | [5 empty] | 406 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 8ABUS | #8ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0294 |  |  | 3-A6 |  |  | Locate Empty | KV | #8DTR 4A PT BUS 電壓 | kV_-9_9(-2000_2000) | ada | B3/P07_A1 | [8 empty] | 台南PS.11KV#8ABUS_KV | 11KV #8ABUS KV | BUS | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0295 |  |  | 3-A7 |  |  | 370 | MW | D4A 370 瓦 | MW_-54_54(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_MW | #8DTR二次側(A) MW | MTR | [5 empty] | 408 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0296 |  |  | 3-A8 |  |  | 370 | MVAR | D4A 370 乏 | MVAR_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_MVAR | #8DTR二次側(A) MVAR | MTR | [5 empty] | 409 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0297 |  |  | 3-A9 |  |  | 370 | A | D4A 370 RA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_A1 | #8DTR二次側(A) R相AMP | MTR | [5 empty] | 410 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0298 |  |  | 3-AA |  |  | 370 | A | D4A 370 SA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_A2 | #8DTR二次側(A) S相AMP | MTR | [5 empty] | 411 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0299 |  |  | 3-AB |  |  | 370 | A | D4A 370 TA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_A3 | #8DTR二次側(A) T相AMP | MTR | [5 empty] | 412 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0300 |  |  | 3-AC |  |  | F25 | MVAR | 台11線 KH11 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台11線KVAR | 11KV台11線 KVAR | FEEDER | [5 empty] | 413 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0301 |  |  | 3-AD |  |  | F25 | A | 台11線 KH11 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台11線A1 | 11KV台11線 R相AMP | FEEDER | [5 empty] | 414 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0302 |  |  | 3-AE |  |  | F25 | A | 台11線 KH11 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台11線A2 | 11KV台11線 S相AMP | FEEDER | [5 empty] | 415 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0303 |  |  | 3-AF |  |  | F25 | A | 台11線 KH11 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台11線A3 | 11KV台11線 T相AMP | FEEDER | [5 empty] | 416 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0304 |  |  | 3-B0 |  |  | F25 | A | 台11線 KH11 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台11線A0 | 11KV台11線 N相AMP | FEEDER | [5 empty] | 417 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0305 |  |  | 3-B1 |  |  | F26 | MVAR | 台12線 KH12 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台12線KVAR | 11KV台12線 KVAR | FEEDER | [5 empty] | 418 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0306 |  |  | 3-B2 |  |  | F26 | A | 台12線 KH12 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台12線A1 | 11KV台12線 R相AMP | FEEDER | [5 empty] | 419 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0307 |  |  | 3-B3 |  |  | F26 | A | 台12線 KH12 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台12線A2 | 11KV台12線 S相AMP | FEEDER | [5 empty] | 420 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0308 |  |  | 3-B4 |  |  | F26 | A | 台12線 KH12 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台12線A3 | 11KV台12線 T相AMP | FEEDER | [5 empty] | 421 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0309 |  |  | 3-B5 |  |  | F26 | A | 台12線 KH12 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台12線A0 | 11KV台12線 N相AMP | FEEDER | [5 empty] | 422 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0310 |  |  | 3-B6 |  |  | F27 | MVAR | 台13線 KH13 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台13線KVAR | 11KV台13線 KVAR | FEEDER | [5 empty] | 423 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0311 |  |  | 3-B7 |  |  | F27 | A | 台13線 KH13 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台13線A1 | 11KV台13線 R相AMP | FEEDER | [5 empty] | 424 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0312 |  |  | 3-B8 |  |  | F27 | A | 台13線 KH13 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台13線A2 | 11KV台13線 S相AMP | FEEDER | [5 empty] | 425 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0313 |  |  | 3-B9 |  |  | F27 | A | 台13線 KH13 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台13線A3 | 11KV台13線 T相AMP | FEEDER | [5 empty] | 426 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0314 |  |  | 3-BA |  |  | F27 | A | 台13線 KH13 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台13線A0 | 11KV台13線 N相AMP | FEEDER | [5 empty] | 427 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0315 |  |  | 3-BB |  |  | F28 | MVAR | 台14線 KH14 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台14線KVAR | 11KV台14線 KVAR | FEEDER | [5 empty] | 428 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0316 |  |  | 3-BC |  |  | F28 | A | 台14線 KH14 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台14線A1 | 11KV台14線 R相AMP | FEEDER | [5 empty] | 429 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0317 |  |  | 3-BD |  |  | F28 | A | 台14線 KH14 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台14線A2 | 11KV台14線 S相AMP | FEEDER | [5 empty] | 430 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0318 |  |  | 3-BE |  |  | F28 | A | 台14線 KH14 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台14線A3 | 11KV台14線 T相AMP | FEEDER | [5 empty] | 431 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0319 |  |  | 3-BF |  |  | F28 | A | 台14線 KH14 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台14線A0 | 11KV台14線 N相AMP | FEEDER | [5 empty] | 432 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0322 |  |  | 3-C2 |  |  | F29 | MVAR | 台15線 KH15 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台15線KVAR | 11KV台15線 KVAR | FEEDER | [5 empty] | 433 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0323 |  |  | 3-C3 |  |  | F29 | A | 台15線 KH15 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台15線A1 | 11KV台15線 R相AMP | FEEDER | [5 empty] | 434 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0324 |  |  | 3-C4 |  |  | F29 | A | 台15線 KH15 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台15線A2 | 11KV台15線 S相AMP | FEEDER | [5 empty] | 435 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0325 |  |  | 3-C5 |  |  | F29 | A | 台15線 KH15 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台15線A3 | 11KV台15線 T相AMP | FEEDER | [5 empty] | 436 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0326 |  |  | 3-C6 |  |  | F29 | A | 台15線 KH15 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台15線A0 | 11KV台15線 N相AMP | FEEDER | [5 empty] | 437 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0327 |  |  | 3-C7 |  |  | 300 | A | TIE 5A 300 RA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_300_A1 | 11KV 300 R相AMP | TIE | [5 empty] | 438 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0328 |  |  | 3-C8 |  |  | 300 | A | TIE 5A 300 SA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_300_A2 | 11KV 300 S相AMP | TIE | [5 empty] | 439 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0329 |  |  | 3-C9 |  |  | 300 | A | TIE 5A 300 TA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_300_A3 | 11KV 300 T相AMP | TIE | [5 empty] | 440 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 8BBUS | #8BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0330 |  |  | 3-CA |  |  | Locate Empty | KV | #8DTR 4B PT BUS 電壓 | kV_-9_9(-2000_2000) | aea | B3/P07_A1 | [8 empty] | 台南PS.11KV#8BBUS_KV | 11KV #8BBUS KV | BUS | [5 empty] | 441 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(380) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0331 |  |  | 3-CB |  |  | 380 | MW | D4B 380 瓦 | MW_-54_54(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_MW | #8DTR二次側(B) MW | MTR | [5 empty] | 442 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(380) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0332 |  |  | 3-CC |  |  | 380 | MVAR | D4B 380 乏 | MVAR_-36_36(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_MVAR | #8DTR二次側(B) MVAR | MTR | [5 empty] | 443 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(380) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0333 |  |  | 3-CD |  |  | 380 | A | D4B 380 RA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_A1 | #8DTR二次側(B) R相AMP | MTR | [5 empty] | 444 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(380) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0334 |  |  | 3-CE |  |  | 380 | A | D4B 380 SA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_A2 | #8DTR二次側(B) S相AMP | MTR | [5 empty] | 445 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(380) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0335 |  |  | 3-CF |  |  | 380 | A | D4B 380 TA | A_-3000_3000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_A3 | #8DTR二次側(B) T相AMP | MTR | [5 empty] | 446 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0336 |  |  | 3-D0 |  |  | F30 | MVAR | 台20線 KH20 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台20線KVAR | 11KV台20線 KVAR | FEEDER | [5 empty] | 447 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0337 |  |  | 3-D1 |  |  | F30 | A | 台20線 KH20 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台20線A1 | 11KV台20線 R相AMP | FEEDER | [5 empty] | 448 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0338 |  |  | 3-D2 |  |  | F30 | A | 台20線 KH20 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台20線A2 | 11KV台20線 S相AMP | FEEDER | [5 empty] | 449 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0339 |  |  | 3-D3 |  |  | F30 | A | 台20線 KH20 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台20線A3 | 11KV台20線 T相AMP | FEEDER | [5 empty] | 450 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0340 |  |  | 3-D4 |  |  | F30 | A | 台20線 KH20 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台20線A0 | 11KV台20線 N相AMP | FEEDER | [5 empty] | 451 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0341 |  |  | 3-D5 |  |  | F31 | MVAR | 台19線 KH19 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台19線KVAR | 11KV台19線 KVAR | FEEDER | [5 empty] | 452 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0342 |  |  | 3-D6 |  |  | F31 | A | 台19線 KH19 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台19線A1 | 11KV台19線 R相AMP | FEEDER | [5 empty] | 453 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0343 |  |  | 3-D7 |  |  | F31 | A | 台19線 KH19 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台19線A2 | 11KV台19線 S相AMP | FEEDER | [5 empty] | 454 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0344 |  |  | 3-D8 |  |  | F31 | A | 台19線 KH19 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台19線A3 | 11KV台19線 T相AMP | FEEDER | [5 empty] | 455 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0345 |  |  | 3-D9 |  |  | F31 | A | 台19線 KH19 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台19線A0 | 11KV台19線 N相AMP | FEEDER | [5 empty] | 456 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0346 |  |  | 3-DA |  |  | F32 | MVAR | 台18線 KH18 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台18線KVAR | 11KV台18線 KVAR | FEEDER | [5 empty] | 457 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0347 |  |  | 3-DB |  |  | F32 | A | 台18線 KH18 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台18線A1 | 11KV台18線 R相AMP | FEEDER | [5 empty] | 458 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0348 |  |  | 3-DC |  |  | F32 | A | 台18線 KH18 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台18線A2 | 11KV台18線 S相AMP | FEEDER | [5 empty] | 459 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0349 |  |  | 3-DD |  |  | F32 | A | 台18線 KH18 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台18線A3 | 11KV台18線 T相AMP | FEEDER | [5 empty] | 460 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0350 |  |  | 3-DE |  |  | F32 | A | 台18線 KH18 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台18線A0 | 11KV台18線 N相AMP | FEEDER | [5 empty] | 461 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0351 |  |  | 3-DF |  |  | F33 | MVAR | 台17線 KH17 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台17線KVAR | 11KV台17線 KVAR | FEEDER | [5 empty] | 462 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0352 |  |  | 3-E0 |  |  | F33 | A | 台17線 KH17 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台17線A1 | 11KV台17線 R相AMP | FEEDER | [5 empty] | 463 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0353 |  |  | 3-E1 |  |  | F33 | A | 台17線 KH17 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台17線A2 | 11KV台17線 S相AMP | FEEDER | [5 empty] | 464 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0354 |  |  | 3-E2 |  |  | F33 | A | 台17線 KH17 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台17線A3 | 11KV台17線 T相AMP | FEEDER | [5 empty] | 465 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0355 |  |  | 3-E3 |  |  | F33 | A | 台17線 KH17 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台17線A0 | 11KV台17線 N相AMP | FEEDER | [5 empty] | 466 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0356 |  |  | 3-E4 |  |  | F34 | MVAR | 台16線 KH16 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台16線KVAR | 11KV台16線 KVAR | FEEDER | [5 empty] | 467 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0357 |  |  | 3-E5 |  |  | F34 | A | 台16線 KH16 RA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台16線A1 | 11KV台16線 R相AMP | FEEDER | [5 empty] | 468 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0358 |  |  | 3-E6 |  |  | F34 | A | 台16線 KH16 SA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台16線A2 | 11KV台16線 S相AMP | FEEDER | [5 empty] | 469 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0359 |  |  | 3-E7 |  |  | F34 | A | 台16線 KH16 TA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台16線A3 | 11KV台16線 T相AMP | FEEDER | [5 empty] | 470 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0360 |  |  | 3-E8 |  |  | F34 | A | 台16線 KH16 NA | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台16線A0 | 11KV台16線 N相AMP | FEEDER | [5 empty] | 471 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0361 |  |  | 3-E9 |  |  | 400 | A | TIE 5B 400 RA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 472 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0362 |  |  | 3-EA |  |  | 400 | A | TIE 5B 400 SA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 473 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0363 |  |  | 3-EB |  |  | 400 | A | TIE 5B 400 TA | A_-2000_2000(-2000_2000) |  | B3/P07_A1 | [8 empty] | 台南PS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 474 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0364 |  |  | 3-EC |  |  | 台31線 | A | 台31線F7 KH31 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台31線A0 | 11KV台31線 N相AMP | FEEDER | [5 empty] | 475 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0365 |  |  | 3-ED |  |  | 台32線 | A | 台32線F8 KH32 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台32線A0 | 11KV台32線 N相AMP | FEEDER | [5 empty] | 476 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0366 |  |  | 3-EE |  |  | 台33線 | A | 台33線F9 KH33 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台33線A0 | 11KV台33線 N相AMP | FEEDER | [5 empty] | 477 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0367 |  |  | 3-EF |  |  | 台36線 | A | 台36線F10 KH36 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台36線A0 | 11KV台36線 N相AMP | FEEDER | [5 empty] | 478 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0368 |  |  | 3-F0 |  |  | 台37線 | A | 台37線F11 KH37 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台37線A0 | 11KV台37線 N相AMP | FEEDER | [5 empty] | 479 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0369 |  |  | 3-F1 |  |  | 台38線 | A | 台38線F12 KH38 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台38線A0 | 11KV台38線 N相AMP | FEEDER | [5 empty] | 480 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0370 |  |  | 3-F2 |  |  | 台71線 | A | 台71線F1 KH71 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台71線A0 | 23KV台71線 N相AMP | FEEDER | [5 empty] | 481 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0371 |  |  | 3-F3 |  |  | 台72線 | A | 台72線F2 KH72 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台72線A0 | 23KV台72線 N相AMP | FEEDER | [5 empty] | 482 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0372 |  |  | 3-F4 |  |  | 台73線 | A | 台73線F3 KH73 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台73線A0 | 23KV台73線 N相AMP | FEEDER | [5 empty] | 483 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0373 |  |  | 3-F5 |  |  | 台74線 | A | 台74線F4 KH74 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台74線A0 | 23KV台74線 N相AMP | FEEDER | [5 empty] | 484 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0374 |  |  | 3-F6 |  |  | 台75線 | A | 台75線F5 KH75 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台75線A0 | 23KV台75線 N相AMP | FEEDER | [5 empty] | 485 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0375 |  |  | 3-F7 |  |  | 台76線 | A | 台76線F6 KH76 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台76線A0 | 23KV台76線 N相AMP | FEEDER | [5 empty] | 486 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0376 |  |  | 3-F8 |  |  | 台61線 | A | 台61線F13 KH61 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台61線A0 | 23KV台61線 N相AMP | FEEDER | [5 empty] | 487 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0377 |  |  | 3-F9 |  |  | 台62線 | A | 台62線F14 KH62 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台62線A0 | 23KV台62線 N相AMP | FEEDER | [5 empty] | 488 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0378 |  |  | 3-FA |  |  | 台63線 | A | 台63線F15 KH63 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台63線A0 | 23KV台63線 N相AMP | FEEDER | [5 empty] | 489 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0379 |  |  | 3-FB |  |  | 台64線 | A | 台64線F16 KH64 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台64線A0 | 23KV台64線 N相AMP | FEEDER | [5 empty] | 490 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0380 |  |  | 3-FC |  |  | 台65線 | A | 台65線F17 KH65 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台65線A0 | 23KV台65線 N相AMP | FEEDER | [5 empty] | 491 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0381 |  |  | 3-FD |  |  | 台66線 | A | 台66線F18 KH66 A (N) | A_-600_600(-2000_2000) |  | B2/P07_D1 | [8 empty] | 台南PS.台66線A0 | 23KV台66線 N相AMP | FEEDER | [5 empty] | 492 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0048 |  | 0009 | 1-06-00 |  | 1-09 | 600 | ON/OFF | 600 TIE CB |  | aabz | B2/P07_A1 | [8 empty] | 台南PS.600_CB | 600(TIE) CB | TIE | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1570 | 87A1 | 台南忠孝一路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_87A1 | 台南忠孝一路(1570)第一套87RY | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1570 | PHA | 台南忠孝一路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_PHA | 台南忠孝一路(1570) 相間RY | LINE161 | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1570 | GDA | 台南忠孝一路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_GDA | 台南忠孝一路(1570) 接地RY | LINE161 | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0053 |  | 0010 | 1-06-05 |  | 1-0A | 1650 | ON/OFF | #1MTR一次側 |  | aaob | B2/P07_A1 | [8 empty] | 台南PS.1650_CB | 1650(#1MTR) CB | MTR | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 1520 | 87A | 山上台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_87A | 山上海線(1520) 87RY | LINE161 | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | PHA | 山上台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_21A | 山上海線(1520) 21RY | LINE161 | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1520 | GDA | 山上台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_GDA | 山上海線(1520) 接地RY | LINE161 | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0054 |  | 0011 | 1-06-06 |  | 1-0B | 750 | ON/OFF | #1MTR二次 側 |  | aaoa | B2/P07_A1 | [8 empty] | 台南PS.750_CB | 750(#1MTR) CB | MTR | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1510 | 87A1 | 台南仁德線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_87A1 | 台南仁德線(1510)第一套87RY | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 1510 | PHA | 台南仁德線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_PHA | 台南仁德線(1510) 相間RY | LINE161 | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1510 | GDA | 台南仁德線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_GDA | 台南仁德線(1510) 接地RY | LINE161 | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0061 |  | 0012 | 1-07-05 |  | 1-0C | 1660 | ON/OFF | #2MTR 1660 CB |  | aalb | B2/P07_A1 | [8 empty] | 台南PS.1660_CB | 1660(#2MTR) CB | MTR | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1560 | 87A1 | 台南忠孝二路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_87A1 | 台南忠孝二路(1560)第一套87RY | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1560 | PHA | 台南忠孝二路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_PHA | 台南忠孝二路(1560) 相間RY | LINE161 | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | 1560 | GDA | 台南忠孝二路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_GDA | 台南忠孝二路(1560) 接地RY | LINE161 | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0062 |  | 0013 | 1-07-06 |  | 1-0D | 760 | ON/OFF | #2MTR二次 760 CB |  | aaja | B2/P07_A1 | [8 empty] | 台南PS.760_CB | 760(#2MTR) CB | MTR | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1550 | 87A | 台南延平線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_87A | 台南延平線(1550) 87RY | LINE161 | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1550 | PHA | 台南延平線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_PHA | 台南延平線(1550) 相間RY | LINE161 | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1550 | GDA | 台南延平線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_GDA | 台南延平線(1550) 接地RY | LINE161 | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0069 |  | 0014 | 1-08-05 |  | 1-0E | 1670 | ON/OFF | #3MTR 1670 CB |  | aaib | B2/P07_A1 | [8 empty] | 台南PS.1670_CB | 1670(#3MTR) CB | MTR | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1530 | 87A | 龍崎台南山線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_87A | 龍崎山線(1530) 87RY | LINE161 | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1530 | PHA | 龍崎台南山線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_PHA | 龍崎山線(1530) 相間RY | LINE161 | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1530 | GDA | 龍崎台南山線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_GDA | 龍崎山線(1530) 接地RY | LINE161 | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0070 |  | 0015 | 1-08-06 |  | 1-0F | 770 | ON/OFF | #3MTR二次 770 CB |  | aaea | B2/P07_A1 | [8 empty] | 台南PS.770_CB | 770(#3MTR) CB | MTR | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 1540 | 87A | 龍崎台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_87A | 龍崎海線(1540) 87RY | LINE161 | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1540 | PHA | 龍崎台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_PHA | 龍崎海線(1540) 相間RY | LINE161 | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 1540 | GDA | 龍崎台南海線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_GDA | 龍崎海線(1540) 接地RY | LINE161 | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | A/100 |  |  | 0424 |  | 0016 | 2-15-00 |  | 1-10 | 300 | ON/OFF | TIE 5A 300 CB |  | adjb | B3/P07_A1 | [8 empty] | 台南PS.300_CB | 300(TIE) CB | TIE | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1500 | PHA | 161KV TIE |  |  | B2/P07_A1 | [8 empty] | 台南PS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | 161KVBUS | 87B1A | 161KVBUS 87B1A |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 161KVBUS | 87B2A | 161KVBUS 87B2A |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 1570 | 87A2 | 台南忠孝一路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_87A2 | 台南忠孝一路(1570)第二套87RY | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 1510 | 87A2 | 台南仁德線 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_87A2 | 台南仁德線(1510)第二套87RY | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 1560 | 87A2 | 台南忠孝二路 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_87A2 | 台南忠孝二路(1560)第二套87RY | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | CB |  | N2為實線 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | B/5BBus |  |  | 0463 |  | 0017 | 2-19-07 |  | 1-11 | 400 | ON/OFF | TIE 5B 400 CB |  | aekb | B3/P07_A1 | [8 empty] | 台南PS.400_CB | 400(TIE) CB | TIE | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 600 | #1 PHA | 600 TIE #1 PHA |  |  | B2/P07_A1 | [8 empty] | 台南PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  |  | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 600 | #1 GDA | 600 TIE #1 GDA |  |  | B2/P07_A1 | [8 empty] | 台南PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 69KVBUS | 87B1A | 69KVBUS 87B1A |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 69KVBUS | 87B2A | 69KVBUS 87B2A |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/5DTR |  | 0086 |  | 0018 | 1-0A-06 |  | 1-12 | 1750 | ON/OFF | #5DTR 1750 CB |  | aaab | ELEM/P07_A1 | [8 empty] | 台南PS.1750_CB | 1750(#5DTR) CB | MTR | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/5A1Bus | A/310A2^T/5DTR(A) |  |  | 0160 |  | 0019 | 1-14-00 |  | 1-13 | 310A1 | ON/OFF | #5DTR 310A1 CB |  | aaea | ELEM/P07_A1 | [8 empty] | 台南PS.310A1_CB | 310A1(#5DTR) CB | MTR | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #1MTR | 96PA | #1MTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #1MTR | 87A | #1MTR 87A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_87A | #1MTR 87RY | MTR | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #1MTR | PHA | #1MTR _PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_PHA | #1MTR PHA | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #1MTR | 51Z | #1MTR 51ZA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/5A2Bus | A/310A1^T/5DTR(A) |  |  | 0162 |  | 0020 | 1-14-02 |  | 1-14 | 310A2 | ON/OFF | #5DTR 310A2 CB |  | abba | ELEM/P07_A1 | [8 empty] | 台南PS.310A2_CB | 310A2(#5DTR) CB | MTR | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/6DTR |  | 0093 |  | 0021 | 1-0B-05 |  | 1-15 | 1760 | ON/OFF | #6DTR 1760 CB |  | aabb | ELEM/P07_A1 | [8 empty] | 台南PS.1760_CB | 1760(#6DTR) CB | MTR | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #2MTR | 96PA | #2MTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | #2MTR | 87A | #2MTR 87A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_87A | #2MTR 87RY | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #2MTR | PHA | #2MTR _PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_PHA | #2MTR PHA | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #2MTR | 51Z | #2MTR 51Z |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/6Bus | T/6DTR |  |  | 0094 |  | 0022 | 1-0B-06 |  | 1-16 | 330 | ON/OFF | #6DTR二次 330 CB |  | baba | ELEM/P07_A1 | [8 empty] | 台南PS.330_CB | 330(#6DTR) CB | MTR | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/P07D181/T1 |  | 0000 |  | 0023 | 1-00-00 |  | 1-17 | 1570 | ON/OFF | 台南忠孝一路 |  | aafa | B2/P07_A1 | [8 empty] | 台南PS.1570_CB | 1570(台南忠孝一路) CB | LINE161 | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | #3MTR | 96PA | #3MTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | #3MTR | 87A | #3MTR 87A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_87A | #3MTR 87RY | MTR | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | #3MTR | PHA | #3MTR _PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_PHA | #3MTR PHA | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | #3MTR | 51Z | #3MTR 51ZA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 600 | #2PHA | 600 TIE #2 PHA |  |  | B2/P07_A1 | [8 empty] | 台南PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  |  | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 600 | #2GDA | 600 TIE #2 GDA |  |  | B2/P07_A1 | [8 empty] | 台南PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/P07_A1 | [16 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/7DTR |  | 0101 |  | 0024 | 1-0C-05 |  | 1-18 | 1770 | ON/OFF | #7DTR 1770 CB |  | aacb | ELEM/P07_A1 | [8 empty] | 台南PS.1770_CB | 1770(#7DTR) CB | MTR | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | #5DTR | 96PA | #5DTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_96PA | #5DTR 機械保護動作 | MTR | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | #5DTR | 87A | #5DTR 87 RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_87A | #5DTR 87RY | MTR | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | #5DTR | 51Z | #5DTR 51Z RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_51ZA | #5DTR 51Z RY | MTR | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | #5DTR | PHA | #5DTR_PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_PHA | #5DTR PHA | OTHER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | #5DTR | GDA | #5DTR _GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_GDA | #5DTR GDA | OTHER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/7Bus | T/7DTR |  |  | 0102 |  | 0025 | 1-0C-06 |  | 1-19 | 350 | ON/OFF | #7DTR二次 350 CB |  | bbia | ELEM/P07_A1 | [8 empty] | 台南PS.350_CB | 350(#7DTR) CB | MTR | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/8DTR |  | 0118 |  | 0026 | 1-0E-06 |  | 1-1A | #8DTR | 1780 CB | #8DTR 1780 CB |  | aaeb | ELEM/P07_A1 | [8 empty] | 台南PS.1780_CB | 1780(#8DTR) CB | MTR | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | #6DTR | 96PA | #6DTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_96PA | #6DTR 機械保護動作 | MTR | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | #6DTR | 87A | #6DTR 87 RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_87A | #6DTR 87RY | MTR | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | #6DTR | 51Z | #6DTR 51Z RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_51ZA | #6DTR 51Z RY | MTR | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | #6DTR | PHA | #6DTR_PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_PHA | #6DTR PHA | OTHER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | #6DTR | GDA | #6DTR _GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_GDA | #6DTR GDA | OTHER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | 330 | 51A | #6DTR二次 330 51 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.330_51A | #6DTR二次側(330) 51RY | MTR | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | T/8DTR(A) |  |  | 0124 |  | 0027 | 1-0F-04 |  | 1-1B | #8DTR | ON/OFF | #8DTR D4A 370 CB |  | adba | ELEM/P07_A1 | [8 empty] | 台南PS.370_CB | 370(#8DTR) CB | MTR | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | T/8DTR(B) |  |  | 0128 |  | 0028 | 1-10-00 |  | 1-1C | #8DTR | ON/OFF | #8DTR D4A 380 CB |  | aecb | ELEM/P07_A1 | [8 empty] | 台南PS.380_CB | 380(#8DTR) CB | MTR | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #7DTR | 96PA | #7DTR 機械保護動作(96PA) |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_96PA | #7DTR 機械保護動作 | MTR | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #7DTR | 87A | #7DTR 87 RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_87A | #7DTR 87RY | MTR | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | #7DTR | 51Z | #7DTR 51Z RY |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_51ZA | #7DTR 51Z RY | MTR | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #7DTR | PHA | #7DTR _PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_PHA | #7DTR PHA | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #7DTR | GDA | #7DTR _GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_GDA | #7DTR GDA | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 350 | 51A | #7DTR 350 51RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.350_51A | #7DTR二次側(350) 51RY | MTR | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | OSCA | A/N | 69KV示波器啟動警報OSCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | RY 盤 | 79 RY | 161KV 79 RY RCA警報 |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 710 | 81A | 台南南仁線 710 81 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.710_81A/S | (710) 81RY A/S | LINE69 | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0029 | 1-31-14 |  | 1-1D | 1520 | U/L | 山上台南海線 1520 87S RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_87UL | 山上海線(1520) 87RY U/L | LINE161 | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | 320 | 51A | #5DTR 5B二次側 320 51RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.320_51A | #5DTR二次側(320) 51RY | MTR | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0030 | 1-31-15 |  | 1-1E | 1520 | U/L | 山上台南海線 1520 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_79UL | 山上海線(1520) 79RY U/L | LINE161 | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | #8DTR | 87A | #8DTR 87A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_87A | #8DTR 87RY | MTR | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | #8DTR | 96 A | #8DTR 96PA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_96PA | #8DTR 機械保護動作 | MTR | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0F-01 |  |  | #8DTR | 51ZA | #8DTR 51ZA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_51ZA | #8DTR 51Z RY | MTR | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0122 |  |  | 1-0F-02 |  |  | #8DTR | PHA | #8DTR _PHA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_PHA | #8DTR PHA | OTHER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-03 |  |  | #8DTR | GDA | #8DTR_GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_GDA | #8DTR GDA | OTHER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0031 | 1-32-01 |  | 1-1F | 1510 | U/L | 台南仁德線 1510 #1 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_87UL1 | 台南仁德線(1510)#1 87RY U/L | OTHER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #8DTR | PHA(51-3ψ) | #8DTR D4A 370 PHA |  |  | B3/P07_A1 | [8 empty] | 台南PS.370_51A | #8DTR二次側(370) 51RY | MTR | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #8DTR | PHA(IED) | #8DTR D4A 370 PHA |  |  | B3/P07_A1 | [8 empty] | 台南PS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 370 | #8DTR(A)(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | #8DTR | GDA | #8DTR D4A 370 GDA |  |  | B3/P07_A1 | [8 empty] | 台南PS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0032 | 1-32-02 |  | 1-20 | 1510 | U/L | 台南仁德線 1510 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_79UL | 台南仁德線(1510) 79RY U/L | LINE161 | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | #8DTR | PHA(51-3ψ) | #8DTR D4A 380 PHA |  |  | B3/P07_A1 | [8 empty] | 台南PS.380_51A | #8DTR二次側(380) 51RY | MTR | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | #8DTR | PHA(IED) | #8DTR D4A 380 PHA |  |  | B3/P07_A1 | [8 empty] | 台南PS.380_PHA2 | 380開關箱IED RY PHA | OTHER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 380 | #8DTR(B)(380) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | #8DTR | GDA | #8DTR D4A 380 GDA |  |  | B3/P07_A1 | [8 empty] | 台南PS.380_GDA | 380開關箱IED RY GDA | OTHER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | #1MTR | GDA | #1MTR_GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_GDA | #1MTR GDA | OTHER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | #1MTR | 86A | #1MTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_86A | #1MTR 86RY | OTHER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | #2MTR | GDA | #2MTR_GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_GDA | #2MTR GDA | OTHER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | #2MTR | 86A | #2MTR_ 86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_86A | #2MTR 86RY | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #3MTR | GDA | #3MTR_GDA |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_GDA | #3MTR GDA | OTHER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #3MTR | 86A | #3MTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_86A | #3MTR 86RY | OTHER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | #5DTR | 86A | #5DTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_86A | #5DTR 86RY | OTHER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-04 |  |  | #6DTR | 86A | #6DTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_86A | #6DTR 86RY | OTHER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | #7DTR | 86A | #7DTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_86A | #7DTR 86RY | OTHER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | #8DTR | 86A | #8DTR _86A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_86A | #8DTR 86RY | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  | 0033 | 1-32-04 |  | 1-21 | 1560 | U/L | 台南忠孝二路 1560 #1 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_87UL1 | 台南忠孝二路(1560)#1 87RY U/L | OTHER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | #5DTR | 51A | #5DTR 310A1 CB 51 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.310A1_51A | #5DTR二次側(310A1) 51RY | MTR | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0805 |  | 0034 | 1-32-05 |  | 1-22 | 1560 | U/L | 台南忠孝二路 1560 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_79UL | 台南忠孝二路(1560) 79RY U/L | LINE161 | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 310A2 | #5DTR(A)(310A2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | #5DTR | 51A | #5DTR 310A2 CB 51 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.310A2_51A | #5DTR二次側(310A2) 51RY | MTR | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0035 | 1-32-07 |  | 1-23 | 1550 | U/L | 台南延平線 1550 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_87UL | 台南延平線(1550) 87RY U/L | LINE161 | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 720 | 87A | 台南大灣二路 720 87 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_87A | 台南大灣二路(720) 87RY | LINE69 | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 720 | PHA | 台南大灣二路 720 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_PHA | 台南大灣二路(720) 相間RY | LINE69 | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 720 | GDA | 台南大灣二路 720 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_GDA | 台南大灣二路(720) 接地RY | LINE69 | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0036 | 1-32-08 |  | 1-24 | 1550 | U/L | 台南延平線 1550 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_79UL | 台南延平線(1550) 79RY U/L | LINE161 | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 710 | 85A | 台南南仁線 710 85 RY |  |  | B2/P07_A1 | [16 empty] | 615 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 710 | 67 | 台南南仁線 710 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.710_PHA | 南仁線(710) 相間RY | LINE69 | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 710 | 67N | 台南南仁線 710 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.710_GDA | 南仁線(710) 接地RY | LINE69 | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 |  | 0037 | 1-32-10 |  | 1-25 | 1530 | U/L | 龍崎台南山線 1530 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_87UL | 龍崎山線(1530) 87RY U/L | LINE161 | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 670 | 87A | 台南大灣一路 670 87 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_87A | 台南大灣一路(670) 87RY | LINE69 | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 670 | 21 | 台南大灣一路 670 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_PHA | 台南大灣一路(670) 相間RY | LINE69 | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 670 | 51N+21N | 台南大灣一路 670 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_GDA | 台南大灣一路(670) 接地RY | LINE69 | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0811 |  | 0038 | 1-32-11 |  | 1-26 | 1530 | U/L | 龍崎台南山線 1530 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_79UL | 龍崎山線(1530) 79RY U/L | LINE161 | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 660 | 87A | 台南後甲海線 660 87 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_87A | 台南後甲海線(660) 87RY | LINE69 | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 660 | 21 | 台南後甲海線 660 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_PHA | 台南後甲海線(660) 相間RY | LINE69 | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 660 | 51N+21N | 台南後甲海線 660 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_GDA | 台南後甲海線(660) 接地RY | LINE69 | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0039 | 1-32-13 |  | 1-27 | 1540 | U/L | 龍崎台南海線 1540 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_87UL | 龍崎海線(1540) 87RY U/L | LINE161 | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 630 | 87A | 台南光洲線 630 87 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_87A | 台南光洲線(630) 87RY | LINE69 | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 630 | 21 | 台南光洲線 630 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_PHA | 台南光洲線(630) 相間RY | LINE69 | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 630 | 51N+21N | 台南光洲線 630 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_GDA | 台南光洲線(630) 接地RY | LINE69 | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0040 | 1-32-14 |  | 1-28 | 1540 | U/L | 龍崎台南海線 1540 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_79UL | 龍崎海線(1540) 79RY U/L | LINE161 | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 620 | 87A | 台南保安線 620 87 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_87A | 保安線(620) 87RY | LINE69 | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 620 | 21+67 | 台南保安線 620 PHA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_PHA | 保安線(620) 相間RY | LINE69 | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 620 | 67N | 台南保安線 620 GDA RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_GDA | 保安線(620) 接地RY | LINE69 | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0021 |  | 0041 | 1-95 |  | 1-29 | #1MTR | 升降 | #1MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | [5 empty] | 634 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS |  |  | 1MTR | #1MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0820 |  | 0042 | 1-33-04 |  | 1-2A | #1MTR | A/M | #1MTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 1MTR | #1MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0924 | 925 | 0043 | 1-39-12 | 1-39-13 | 1-2B | #1MTR | M/F/I | #1MTR M/F/I |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 810 | SCA | 69KV #1SC 51/51N RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.810_SCA | 69KV #1SC 51,51N RY | SC | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 810 | UVA | 69KV #1SC 27/59 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.810_OUVA | 69KV #1SC 27,59RY | SC | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 820 | SCA | 69KV #2SC 51/51N RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.820_SCA | 69KV #2SC 51,51N RY | SC | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | 820 | UVA | 69KV #2SC 27/59 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.820_OUVA | 69KV #2SC 27,59RY | SC | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 830 | SCA | 69KV #3SC 51/51N RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.830_SCA | 69KV #3SC 51,51N RY | SC | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | 830 | UVA | 69KV #3SC 27/59 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.830_OUVA | 69KV #3SC 27,59RY | SC | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0024 |  | 0045 | 1-98 |  | 1-2D | #2MTR | 升降 | #2MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | [5 empty] | 643 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS |  |  | 2MTR | #2MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0826 |  | 0046 | 1-33-10 |  | 1-2E | #2MTR | A/M | #2MTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 2MTR | #2MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0926 | 927 | 0047 | 1-39-14 | 1-39-15 | 1-2F | #2MTR | M/F/I | #2MTR M/F/I |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0049 | 1-9B |  | 1-31 | #3MTR | 升降 | #3MTR TAP 位置 | TAP_-6.5_6.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | [5 empty] | 646 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS |  |  | 3MTR | #3MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0832 |  | 0050 | 1-34-00 |  | 1-32 | #3MTR | A/M | #3MTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 3MTR | #3MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0928 | 929 | 0051 | 1-3A-00 | 1-3A-01 | 1-33 | #3MTR | M/F/I | #3MTR M/F/I |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1124 | 1125 | 0053 | 2-36-04 | 2-36-05 | 1-35 | 1571 | ON/OFF | 台南忠孝一路 1571 DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1571_DS | 1571(台南忠孝一路) DS | LINE161 | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1126 | 1127 | 0054 | 2-36-06 | 2-36-07 | 1-36 | 1572 | ON/OFF | 台南忠孝一路 1572 DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1572_DS | 1572(台南忠孝一路) DS | LINE161 | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | DS3 | 1573 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1128 | 1129 | 0055 | 2-36-08 | 2-36-09 | 1-37 | 1573 | ON/OFF | 台南忠孝一路 1573 DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1573_DS | 1573(台南忠孝一路) DS | LINE161 | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | E3 | 1573E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1130 | 1131 | 0056 | 2-36-10 | 2-36-11 | 1-38 | 1573E | ON/OFF | 台南忠孝一路 1573E DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1573E_ES | 1573E(台南忠孝一路) ES | LINE161 | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0035 |  | 0057 | 1-A3 |  | 1-39 | #5ADTR | 升降 | #5ADTR OLTC TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_TAP | #5DTR(A) OLTC TAP | MTR | [5 empty] | 653 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0844 |  | 0058 | 1-34-12 |  | 1-3A | #5ADTR | A/M | #5ADTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_A/M | #5DTR(A) OLTC A/M | MTR | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 5DTR(B) | #5DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0036 |  | 0059 | 1-A4 |  | 1-3B | #5BDTR | 升降 | #5BDTR OLTC TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_TAP | #5DTR(B) OLTC TAP | MTR | [5 empty] | 655 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 5DTR(B) | #5DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0846 |  | 0060 | 1-34-14 |  | 1-3C | #5BDTR | A/M | #5BDTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_A/M | #5DTR(B) OLTC A/M | MTR | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 6DTR | #6DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0041 |  | 0061 | 1-A9 |  | 1-3D | #6DTR | 升降 | #6DTR TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_TAP | #6DTR OLTC TAP | MTR | [5 empty] | 657 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 6DTR | #6DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0852 |  | 0062 | 1-35-04 |  | 1-3E | #6DTR | A/M | #6DTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_A/M | #6DTR OLTC A/M | MTR | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 8DTR(A) | #8DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0045 |  | 0063 | 1-AD |  | 1-3F | Locate Empty | 升降 | #8DTR D4A OLTC TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_TAP | #8DTR(A) OLTC TAP | MTR | [5 empty] | 659 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 8DTR(A) | #8DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0064 | 1-36-01 |  | 1-40 | Locate Empty | A/M | #8DTR D4A OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_A/M | #8DTR(A) OLTC A/M | MTR | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 7DTR | #7DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0046 |  | 0065 | 1-AE |  | 1-41 | #7DTR | 升降 | #7DTR TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_TAP | #7DTR OLTC TAP | MTR | [5 empty] | 661 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 7DTR | #7DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0860 |  | 0066 | 1-35-12 |  | 1-42 | #7DTR | A/M | #7DTR OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_A/M | #7DTR OLTC A/M | MTR | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS |  |  | 8DTR(B) | #8DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0047 |  | 0067 | 1-AF |  | 1-43 | Locate Empty | 升降 | #8DTR D4B OLTC TAP 位置 | TAP_-8.5_8.5(0_2000) |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_TAP | #8DTR(B) OLTC TAP | MTR | [5 empty] | 663 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS |  |  | 8DTR(B) | #8DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0068 | 1-36-03 |  | 1-44 | Locate Empty | A/M | #8DTR D4B OLTC A/M |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_A/M | #8DTR(B) OLTC A/M | MTR | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  | 0069 | 1-3A-02 |  | 1-45 | 1570 | U/L | 台南忠孝一路 1570 #1 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_87UL1 | 台南忠孝一路(1570)#1 87RY U/L | OTHER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  | 0070 | 1-3A-04 |  | 1-46 | 1570 | U/L | 台南忠孝一路 1570 79RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_79UL | 台南忠孝一路(1570) 79RY U/L | LINE161 | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | C/11SC |  |  | 0364 |  | 0071 | 2-0D-04 |  | 1-47 | 410 | ON/OFF | #4A1 410 #11SC CB |  | adcb | B3/P07_A1 | [8 empty] | 台南PS.410_CB | 410(11KV #11SC) CB | SC | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | C/12SC |  |  | 0367 |  | 0072 | 2-0D-07 |  | 1-48 | 420 | ON/OFF | #4A2 420 #12SC CB |  | addb | B3/P07_A1 | [8 empty] | 台南PS.420_CB | 420(11KV #12SC) CB | SC | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | KH61 | 51A | 台61線 KH61 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH61_PHA | 23KV台61線(KH61) 相間RY | FEEDER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | KH61 | 51NA | 台61線 KH61 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH61_GDA | 23KV台61線(KH61) 接地RY | FEEDER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | KH62 | 51A | 台62線 KH62 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH62_PHA | 23KV台62線(KH62) 相間RY | FEEDER | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | KH62 | 51NA | 台62線 KH62 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH62_GDA | 23KV台62線(KH62) 接地RY | FEEDER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | KH63 | 51A | 台63線 KH63 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH63_PHA | 23KV台63線(KH63) 相間RY | FEEDER | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | KH63 | 51NA | 台63線 KH63 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH63_GDA | 23KV台63線(KH63) 接地RY | FEEDER | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | KH64 | 51A | 台64線 KH64 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH64_PHA | 23KV台64線(KH64) 相間RY | FEEDER | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 2-05-02 |  |  | KH64 | 51NA | 台64線 KH64 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH64_GDA | 23KV台64線(KH64) 接地RY | FEEDER | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | KH65 | 51A | 台65線 KH65 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH65_PHA | 23KV台65線(KH65) 相間RY | FEEDER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | KH65 | 51NA | 台65線 KH65 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH65_GDA | 23KV台65線(KH65) 接地RY | FEEDER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 2-05-05 |  |  | KH66 | 51A | 台66線 KH66 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH66_PHA | 23KV台66線(KH66) 相間RY | FEEDER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | KH66 | 51NA | 台66線 KH66 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH66_GDA | 23KV台66線(KH66) 接地RY | FEEDER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | 240 | SCA | #4 SC 240 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 2-06-00 |  |  | 240 | UVA | #4 SC 240 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | 250 | SCA | #5 SC 250 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | 250 | UVA | #5 SC 250 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | 200TIE | 51A | 200 TIE 51 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | 200TIE | 51NA | 200 TIE 51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | KH31 | 51A | 台31線 KH31 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH31_PHA | 11KV台31線(KH31) 相間RY | FEEDER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | KH31 | 51NA | 台31線 KH31 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH31_GDA | 11KV台31線(KH31) 接地RY | FEEDER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | KH32 | 51A | 台32線 KH32 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH32_PHA | 11KV台32線(KH32) 相間RY | FEEDER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | KH32 | 51NA | 台32線 KH32 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH32_GDA | 11KV台32線(KH32) 接地RY | FEEDER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 2-07-01 |  |  | KH33 | 51A | 台33線 KH33 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH33_PHA | 11KV台33線(KH33) 相間RY | FEEDER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | KH33 | 51NA | 台33線 KH33 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH33_GDA | 11KV台33線(KH33) 接地RY | FEEDER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | KH36 | 51A | 台36線 KH36 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH36_PHA | 11KV台36線(KH36) 相間RY | FEEDER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 2-07-04 |  |  | KH36 | 51NA | 台36線 KH36 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH36_GDA | 11KV台36線(KH36) 接地RY | FEEDER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | KH37 | 51A | 台37線 KH37 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH37_PHA | 11KV台37線(KH37) 相間RY | FEEDER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | KH37 | 51NA | 台37線 KH37 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH37_GDA | 11KV台37線(KH37) 接地RY | FEEDER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0319 |  |  | 2-07-07 |  |  | KH38 | 51A | 台38線 KH38 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH38_PHA | 11KV台38線(KH38) 相間RY | FEEDER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | KH38 | 51NA | 台38線 KH38 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH38_GDA | 11KV台38線(KH38) 接地RY | FEEDER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | 210 | SCA | #1 SC 210 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | 210 | UVA | #1 SC 210 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | 220 | SCA | #2 SC 220 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | 220 | UVA | #2 SC 220 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | 100TIE | 51A | 100 TIE 51 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | 100TIE | 51NA | 100 TIE 51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 270 | SCA | #7 SC 270 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | 270 | UVA | #7 SC 270 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 260 | SCA | #6 SC 260 51/51N RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | 260 | UVA | #6 SC 260 27/59 RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | KH71 | 51A | 台71線 KH71 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH71_PHA | 23KV台71線(KH71) 相間RY | FEEDER | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | KH71 | 51NA | 台71線 KH71 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH71_GDA | 23KV台71線(KH71) 接地RY | FEEDER | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | KH72 | 51A | 台72線 KH72 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH72_PHA | 23KV台72線(KH72) 相間RY | FEEDER | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 2-09-06 |  |  | KH72 | 51NA | 台72線 KH72 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH72_GDA | 23KV台72線(KH72) 接地RY | FEEDER | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | KH73 | 51A | 台73線 KH73 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH73_PHA | 23KV台73線(KH73) 相間RY | FEEDER | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | KH73 | 51NA | 台73線 KH73 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH73_GDA | 23KV台73線(KH73) 接地RY | FEEDER | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | KH74 | 51A | 台74線 KH74 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH74_PHA | 23KV台74線(KH74) 相間RY | FEEDER | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | KH74 | 51NA | 台74線 KH74 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH74_GDA | 23KV台74線(KH74) 接地RY | FEEDER | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | KH75 | 51A | 台75線 KH75 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH75_PHA | 23KV台75線(KH75) 相間RY | FEEDER | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | KH75 | 51NA | 台75線 KH75 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH75_GDA | 23KV台75線(KH75) 接地RY | FEEDER | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | KH76 | 51A | 備用線KH76 F18 51 RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH76_PHA | 23KV台76線(KH76) 相間RY | FEEDER | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | KH76 | 51NA | 備用線KH76 F18 51N RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH76_GDA | 23KV台76線(KH76) 接地RY | FEEDER | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | C/14SC |  |  | 0457 |  | 0073 | 2-19-01 |  | 1-49 | 440 | ON/OFF | #4B2 440 #14SC CB |  | aeeb | B3/P07_A1 | [8 empty] | 台南PS.440_CB | 440(11KV #14SC) CB | SC | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | C/13SC |  |  | 0460 |  | 0074 | 2-19-04 |  | 1-4A | 430 | ON/OFF | #4B1 430 #13SC CB |  | aedb | B3/P07_A1 | [8 empty] | 台南PS.430_CB | 430(11KV #13SC) CB | SC | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | ABS1 | 1521 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0075 | 1-36-08 | 1-36-09 | 1-4B | 1521 | ON/OFF | 山上台南海線 1521 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1521_ABS | 1521(山上海線) ABS | LINE161 | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | ABS2 | 1522 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0874 | 875 | 0076 | 1-36-10 | 1-36-11 | 1-4C | 1522 | ON/OFF | 山上台南海線 1522 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1522_ABS | 1522(山上海線) ABS | LINE161 | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | ABS3 | 1523 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0876 | 877 | 0077 | 1-36-12 | 1-36-13 | 1-4D | 1523 | ON/OFF | 山上台南海線 1523 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1523_ABS | 1523(山上海線) ABS | LINE161 | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | E3 | 1523E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0878 | 879 | 0078 | 1-36-14 | 1-36-15 | 1-4E | 1523E | ON/OFF | 山上台南海線 1523E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1523E_ES | 1523E(山上海線) ES | LINE161 | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | ABS1 | 1511 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0880 | 881 | 0079 | 1-37-00 | 1-37-01 | 1-4F | 1511 | ON/OFF | 台南仁德線 1511 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1511_ABS | 1511(台南仁德線) ABS | LINE161 | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | 230 | SCA | 11KV #3SC 230 SCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | 230 | UVA | 11KV #3SC 230 UVA |  |  | B3/P07_A1 | [8 empty] | 台南PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 2-0C-00 |  |  | F19 | 51A | 11KV 台41線 KH41 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH41_PHA | 11KV台41線(KH41) 相間RY | FEEDER | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | F19 | 51N | 11KV 台41線 KH41 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH41_GDA | 11KV台41線(KH41) 接地RY | FEEDER | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | F20 | 51A | 11KV 台42線 KH42 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH42_PHA | 11KV台42線(KH42) 相間RY | FEEDER | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0355 |  |  | 2-0C-03 |  |  | F20 | 51N | 11KV 台42線 KH42 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH42_GDA | 11KV台42線(KH42) 接地RY | FEEDER | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | F21 | 51A | 11KV 台43線 KH43 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH43_PHA | 11KV台43線(KH43) 相間RY | FEEDER | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | F21 | 51N | 11KV 台43線 KH43 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH43_GDA | 11KV台43線(KH43) 接地RY | FEEDER | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 2-0C-06 |  |  | F22 | 51A | 11KV 台44線 KH44 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH44_PHA | 11KV台44線(KH44) 相間RY | FEEDER | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | F22 | 51N | 11KV 台44線 KH44 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH44_GDA | 11KV台44線(KH44) 接地RY | FEEDER | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | F23 | 51A | 11KV KH45 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH45_PHA | 11KV台45線(KH45) 相間RY | FEEDER | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | F23 | 51N | 11KV KH45 F23 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH45_GDA | 11KV台45線(KH45) 接地RY | FEEDER | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0362 |  |  | 2-0D-02 |  |  | F24 | 51A | 11KV KH46 PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH46_PHA | 11KV台46線(KH46) 相間RY | FEEDER | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0363 |  |  | 2-0D-03 |  |  | F24 | 51N | 11KV KH46 GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH46_GDA | 11KV台46線(KH46) 接地RY | FEEDER | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | ABS2 | 1512 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0882 | 883 | 0080 | 1-37-02 | 1-37-03 | 1-50 | 1512 | ON/OFF | 台南仁德線 1512 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1512_ABS | 1512(台南仁德線) ABS | LINE161 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0365 |  |  | 2-0D-05 |  |  | 410 | SCA | #4A1 410 #11SC 51/51NRY SCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.410_SCA | 11KV #11SC 51,51N RY | SC | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0366 |  |  | 2-0D-06 |  |  | 410 | UVA | #4A1 410 #11SC SC 27/59RY UVA |  |  | B3/P07_A1 | [8 empty] | 台南PS.410_UVA | 11KV #11SC 27RY(欠壓) | SC | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | ABS3 | 1513 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0884 | 885 | 0081 | 1-37-04 | 1-37-05 | 1-51 | 1513 | ON/OFF | 台南仁德線 1513 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1513_ABS | 1513(台南仁德線) ABS | LINE161 | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | 420 | SCA | #4A2 420 #12SC 51/51NRY SCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.420_SCA | 11KV #12SC 51,51N RY | SC | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0369 |  |  | 2-0E-01 |  |  | 420 | UVA | #4A2 420 #12SC 27/59RY UVA |  |  | B3/P07_A1 | [8 empty] | 台南PS.420_UVA | 11KV #12SC 27RY(欠壓) | SC | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | E3 | 1513E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0886 | 887 | 0082 | 1-37-06 | 1-37-07 | 1-52 | 1513E | ON/OFF | 台南仁德線 1513E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1513E_ES | 1513E(台南仁德線) ES | LINE161 | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0371 |  |  | 2-0E-03 |  |  | F25 | 51A | 台11線 KH11 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH11_PHA | 11KV台11線(KH11) 相間RY | FEEDER | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0372 |  |  | 2-0E-04 |  |  | F25 | 51N | 台11線 KH11 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH11_GDA | 11KV台11線(KH11) 接地RY | FEEDER | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | ABS1 | 1561 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0888 | 889 | 0083 | 1-37-08 | 1-37-09 | 1-53 | 1561 | ON/OFF | 台南忠孝二路 1561 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1561_ABS | 1561(台南忠孝二路) ABS | LINE161 | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0374 |  |  | 2-0E-06 |  |  | F26 | 51A | 台12線 KH12 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH12_PHA | 11KV台12線(KH12) 相間RY | FEEDER | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0375 |  |  | 2-0E-07 |  |  | F26 | 51N | 台12線 KH12 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH12_GDA | 11KV台12線(KH12) 接地RY | FEEDER | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | ABS2 | 1562 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0890 | 891 | 0084 | 1-37-10 | 1-37-11 | 1-54 | 1562 | ON/OFF | 台南忠孝二路 1562 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1562_ABS | 1562(台南忠孝二路) ABS | LINE161 | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0377 |  |  | 2-0F-01 |  |  | F27 | 51A | 台13線 KH13 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH13_PHA | 11KV台13線(KH13) 相間RY | FEEDER | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0378 |  |  | 2-0F-02 |  |  | F27 | 51N | 台13線 KH13 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH13_GDA | 11KV台13線(KH13) 接地RY | FEEDER | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | ABS3 | 1563 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0892 | 893 | 0085 | 1-37-12 | 1-37-13 | 1-55 | 1563 | ON/OFF | 台南忠孝二路 1563 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1563_ABS | 1563(台南忠孝二路) ABS | LINE161 | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0380 |  |  | 2-0F-04 |  |  | F28 | 51A | 台14線 KH14 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH14_PHA | 11KV台14線(KH14) 相間RY | FEEDER | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0381 |  |  | 2-0F-05 |  |  | F28 | 51N | 台14線 KH14 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH14_GDA | 11KV台14線(KH14) 接地RY | FEEDER | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | E3 | 1563E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0894 | 895 | 0086 | 1-37-14 | 1-37-15 | 1-56 | 1563E | ON/OFF | 台南忠孝二路 1563E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1563E_ES | 1563E(台南忠孝二路) ES | LINE161 | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0383 |  |  | 2-0F-07 |  |  | F29 | 51A | 台15線 KH15 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH15_PHA | 11KV台15線(KH15) 相間RY | FEEDER | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0423 |  |  | 2-14-07 |  |  | F29 | 51N | 台15線 KH15 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH15_GDA | 11KV台15線(KH15) 接地RY | FEEDER | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | ABS1 | 1551 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0087 | 1-38-00 | 1-38-01 | 1-57 | 1551 | ON/OFF | 台南延平線 1551 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1551_ABS | 1551(台南延平線) ABS | LINE161 | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 2-15-01 |  |  | 300 | 51A | TIE 5A 300 PHA 51RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.300_51A | 11KV TIE(300) 51RY | TIE | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 300 | TIE(300) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0426 |  |  | 2-15-02 |  |  | 300 | 51N | TIE 5A 300 GDA 51NRY |  |  | B3/P07_A1 | [8 empty] | 台南PS.300_51NA | 11KV TIE(300) 51N RY | TIE | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | ABS2 | 1552 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0088 | 1-38-02 | 1-38-03 | 1-58 | 1552 | ON/OFF | 台南延平線 1552 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1552_ABS | 1552(台南延平線) ABS | LINE161 | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 390 | #3SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 2-15-04 |  |  | 390 | PHA | #3SSTR 390 PHA |  |  | B3/P07_A1 | [8 empty] | 台南PS.#3SSTR_51A | #3SSTR 51RY | OTHER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 390 | #3SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0429 |  |  | 2-15-05 |  |  | 390 | GDA | #3SSTR 390 GDA |  |  | B3/P07_A1 | [8 empty] | 台南PS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | ABS3 | 1553 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0089 | 1-38-04 | 1-38-05 | 1-59 | 1553 | ON/OFF | 台南延平線 1553 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1553_ABS | 1553(台南延平線) ABS | LINE161 | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0431 |  |  | 2-15-07 |  |  | F30 | 51A | 台20線 KH20 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH20_PHA | 11KV台20線(KH20) 相間RY | FEEDER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0432 |  |  | 2-16-00 |  |  | F30 | 51N | 台20線 KH20 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH20_GDA | 11KV台20線(KH20) 接地RY | FEEDER | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | E3 | 1553E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0902 | 903 | 0090 | 1-38-06 | 1-38-07 | 1-5A | 1553E | ON/OFF | 台南延平線 1553E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1553E_ES | 1553E(台南延平線) ES | LINE161 | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0434 |  |  | 2-16-02 |  |  | F31 | 51A | 台19線 KH19 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH19_PHA | 11KV台19線(KH19) 相間RY | FEEDER | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0435 |  |  | 2-16-03 |  |  | F31 | 51N | 台19線 KH19 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH19_GDA | 11KV台19線(KH19) 接地RY | FEEDER | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | ABS1 | 1531 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0091 | 1-38-08 | 1-38-09 | 1-5B | 1531 | ON/OFF | 龍崎台南山線 1531 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1531_ABS | 1531(龍崎山線) ABS | LINE161 | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0449 |  |  | 2-18-01 |  |  | F32 | 51A | 台18線 KH18 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH18_PHA | 11KV台18線(KH18) 相間RY | FEEDER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0450 |  |  | 2-18-02 |  |  | F32 | 51N | 台18線 KH18 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH18_GDA | 11KV台18線(KH18) 接地RY | FEEDER | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | ABS2 | 1532 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0092 | 1-38-10 | 1-38-11 | 1-5C | 1532 | ON/OFF | 龍崎台南山線 1532 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1532_ABS | 1532(龍崎山線) ABS | LINE161 | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0452 |  |  | 2-18-04 |  |  | F33 | 51A | 台17線 KH17 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH17_PHA | 11KV台17線(KH17) 相間RY | FEEDER | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0453 |  |  | 2-18-05 |  |  | F33 | 51N | 台17線 KH17 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH17_GDA | 11KV台17線(KH17) 接地RY | FEEDER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | ABS3 | 1533 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0093 | 1-38-12 | 1-38-13 | 1-5D | 1533 | ON/OFF | 龍崎台南山線 1533 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1533_ABS | 1533(龍崎山線) ABS | LINE161 | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0455 |  |  | 2-18-07 |  |  | F34 | 51A | 台16線 KH16 CB PHA 51RY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH16_PHA | 11KV台16線(KH16) 相間RY | FEEDER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0456 |  |  | 2-19-00 |  |  | F34 | 51N | 台16線 KH16 CB GDA 51NRY |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH16_GDA | 11KV台16線(KH16) 接地RY | FEEDER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | E3 | 1533E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0910 | 911 | 0094 | 1-38-14 | 1-38-15 | 1-5E | 1533E | ON/OFF | 龍崎台南山線 1533E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1533E_ES | 1533E(龍崎山線) ES | LINE161 | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0458 |  |  | 2-19-02 |  |  | 440 | SCA | #4B2 440 #14SC 51/51NRY SCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.440_SCA | 11KV #14SC 51,51N RY | SC | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0459 |  |  | 2-19-03 |  |  | 440 | UVA | #4B2 440 #14SC 27/59RY UVA |  |  | B3/P07_A1 | [8 empty] | 台南PS.440_UVA | 11KV #14SC 27RY(欠壓) | SC | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | ABS1 | 1541 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0095 | 1-39-00 | 1-39-01 | 1-5F | 1541 | ON/OFF | 龍崎台南海線 1541 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1541_ABS | 1541(龍崎海線) ABS | LINE161 | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0461 |  |  | 2-19-05 |  |  | 430 | SCA | #4B1 430 #13SC 51/51NRY SCA |  |  | B3/P07_A1 | [8 empty] | 台南PS.430_SCA | 11KV #13SC 51,51N RY | SC | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0462 |  |  | 2-19-06 |  |  | 430 | UVA | #4B1 430 #13SC 27/59RY UVA |  |  | B3/P07_A1 | [8 empty] | 台南PS.430_UVA | 11KV #13SC 27RY(欠壓) | SC | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | ABS2 | 1542 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0096 | 1-39-02 | 1-39-03 | 1-60 | 1542 | ON/OFF | 龍崎台南海線 1542 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1542_ABS | 1542(龍崎海線) ABS | LINE161 | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0464 |  |  | 2-1A-00 |  |  | 400 | 51A | TIE 5B 400 PHA 51RY |  |  | B3/P07_A1 | [8 empty] | 台南PS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 400 | TIE(400) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0465 |  |  | 2-1A-01 |  |  | 400 | 51N | TIE 5B 400 GDA 51NRY |  |  | B3/P07_A1 | [8 empty] | 台南PS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0960 |  |  | 1-3C-00 |  |  | #8DTR | 96D | #8DTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_96D | #8DTR 96D RY | MTR | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0961 |  |  | 1-3C-01 |  |  | #8DTR | 96P | #8DTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_96P | #8DTR 96P RY | MTR | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0962 |  |  | 1-3C-02 |  |  | #8DTR | 63Q | #8DTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_63Q | #8DTR 63Q RY | MTR | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0963 |  |  | 1-3C-03 |  |  | #8DTR | 96B1 | #8DTR 96B1 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_96B1 | #8DTR 96B1 RY | MTR | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0964 |  |  | 1-3C-04 |  |  | #8DTR | 96B2 | #8DTR 96B2 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_96B2 | #8DTR 96B2 RY | MTR | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0977 |  |  | 1-3D-01 |  |  | #5DTR | 96D | #5DTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_96D | #5DTR 96D RY | MTR | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0978 |  |  | 1-3D-02 |  |  | #5DTR | 96P | #5DTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_96P | #5DTR 96P RY | MTR | [5 empty] | 799 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0979 |  |  | 1-3D-03 |  |  | #5DTR | 63Q | #5DTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_63Q | #5DTR 63Q RY | MTR | [5 empty] | 800 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0980 |  |  | 1-3D-04 |  |  | #5DTR | 96B1 | #5DTR 96B1 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_96B1 | #5DTR 96B1 RY | MTR | [5 empty] | 801 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0981 |  |  | 1-3D-05 |  |  | #5DTR | 96B2 | #5DTR 96B2 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_96B2 | #5DTR 96B2 RY | MTR | [5 empty] | 802 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0982 |  |  | 1-3D-06 |  |  | #6DTR | 96D | #6DTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_96D | #6DTR 96D RY | MTR | [5 empty] | 803 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0983 |  |  | 1-3D-07 |  |  | #6DTR | 96P | #6DTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_96P | #6DTR 96P RY | MTR | [5 empty] | 804 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0984 |  |  | 1-3D-08 |  |  | #6DTR | 63Q | #6DTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_63Q | #6DTR 63Q RY | MTR | [5 empty] | 805 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0985 |  |  | 1-3D-09 |  |  | #6DTR | 96B1 | #6DTR 96B1 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_96B1 | #6DTR 96B1 RY | MTR | [5 empty] | 806 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0986 |  |  | 1-3D-10 |  |  | #6DTR | 96B2 | #6DTR 96B2 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_96B2 | #6DTR 96B2 RY | MTR | [5 empty] | 807 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0987 |  |  | 1-3D-11 |  |  | #7DTR | 96D | #7DTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_96D | #7DTR 96D RY | MTR | [5 empty] | 808 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0988 |  |  | 1-3D-12 |  |  | #7DTR | 96P | #7DTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_96P | #7DTR 96P RY | MTR | [5 empty] | 809 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0989 |  |  | 1-3D-13 |  |  | #7DTR | 63Q | #7DTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_63Q | #7DTR 63Q RY | MTR | [5 empty] | 810 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0990 |  |  | 1-3D-14 |  |  | #7DTR | 96B1 | #7DTR 96B1 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_96B1 | #7DTR 96B1 RY | MTR | [5 empty] | 811 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0991 |  |  | 1-3D-15 |  |  | #7DTR | 96B2 | #7DTR 96B2 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_96B2 | #7DTR 96B2 RY | MTR | [5 empty] | 812 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | ABS3 | 1543 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0097 | 1-39-04 | 1-39-05 | 1-61 | 1543 | ON/OFF | 龍崎台南海線 1543 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1543_ABS | 1543(龍崎海線) ABS | LINE161 | [5 empty] | 813 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | RTU | L/S | L/R STATUS |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 814 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | E3 | 1543E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0918 | 919 | 0098 | 1-39-06 | 1-39-07 | 1-62 | 1543E | ON/OFF | 龍崎台南海線 1543E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1543E_ES | 1543E(龍崎海線) ES | LINE161 | [5 empty] | 815 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0099 | 1-39-08 | 1-39-09 | 1-63 | 1501 | ON/OFF | 161KV TIE 1501 DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1501_DS | 1501(TIE) DS | OTHER | [5 empty] | 816 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0100 | 1-39-10 | 1-39-11 | 1-64 | 1502 | ON/OFF | 161KV TIE 1502 DS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1502_DS | 1502(TIE) DS | OTHER | [5 empty] | 817 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0931 |  | 0102 | 1-3A-03 |  | 1-66 | 1570 | U/L | 台南忠孝一路 1570 #2 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_87UL2 | 台南忠孝一路(1570)#2 87RY U/L | OTHER | [5 empty] | 818 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | #1BUS | VUA1 | 161KV #1BUS VUA1 |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 819 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | #2BUS | VUA2 | 161KV #2BUS VUA2 |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 820 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 1-30-08 |  |  | #1BUS | VUA1 | 69KV #1BUS VUA1 |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | [5 empty] | 821 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | #2BUS | VUA2 | 69KV #2BUS VUA2 |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 822 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0778 |  |  | 1-30-10 |  |  | RY盤 | A/N | 同步校核裝置 25TA |  |  | B3/P07_A1 | [8 empty] | 台南PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 823 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | RY盤 | A/N | 同步校核裝置 25PFA |  |  | B3/P07_A1 | [8 empty] | 台南PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 824 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 1-30-12 |  |  | 直流電源 | A/N | 直流電源故障 DCA |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 825 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | 空壓機 | A/N | 空壓機超時運轉 16COMT |  |  | B3/P07_A1 | [8 empty] | 台南PS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 826 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0782 |  |  | 1-30-14 |  |  | 161KV | A/N | 161KV CBF |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 827 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0783 |  |  | 1-30-15 |  |  | 161KV | A/N | 161KV CBA |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 828 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0784 |  |  | 1-31-00 |  |  | 所內TR | A/N | 所內用電警報 STUV |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0785 |  |  | 1-31-01 |  |  | ABS | A/N | 161KV ABS 電源跳脫 |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 1-31-02 |  |  | 1550 | A/N | 台南延平線 1550 87CFA (87L通訊故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_87CFA | 台南延平線(1550)87RY通訊故障 | OTHER | [5 empty] | 831 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 1-31-03 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 832 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0788 |  |  | 1-31-04 |  |  | OSCF | A/N | 69KV示波器缺紙或故障警報OSCF |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 833 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0789 |  |  | 1-31-05 |  |  | 1550 | A/N | 台南延平線 1550 RYFA(電驛故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1550_RYFA | 台南延平線(1550)數位電驛故障 | OTHER | [5 empty] | 834 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0790 |  |  | 1-31-06 |  |  | 1510 | A/N | 台南仁德線 1510 87RY通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_87CFA | 台南仁德線(1510)87RY通訊故障 | OTHER | [5 empty] | 835 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | 1510 | A/N | 台南仁德線 1510 數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_RYFA | 台南仁德線(1510)數位電驛故障 | OTHER | [5 empty] | 836 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0792 |  |  | 1-31-08 |  |  | #2MTR | 96D | #2MTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_96D | #2MTR 96D RY | MTR | [5 empty] | 837 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | #2MTR | 96P | #2MTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_96P | #2MTR 96P RY | MTR | [5 empty] | 838 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0794 |  |  | 1-31-10 |  |  | #2MTR | 63Q | #2MTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_63Q | #2MTR 63Q RY | MTR | [5 empty] | 839 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0795 |  |  | 1-31-11 |  |  | #2MTR | 96B1 | #2MTR 96B1 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | [5 empty] | 840 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0796 |  |  | 1-31-12 |  |  | #2MTR | 96B2 | #2MTR 96B2 |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | [5 empty] | 841 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | 1560 | A/N | 台南忠孝二路 1560 87CFA (87L通訊故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_87CFA | 台南忠孝二路(1560)87RY通訊故障 | OTHER | [5 empty] | 842 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07S662/T1 |  | 0196 |  | 0106 | 1-18-04 |  | 1-6A | 720 | ON/OFF | 台南大灣二路 720 CB |  | aaab | B2/P07_A1 | [8 empty] | 台南PS.720_CB | 720(台南大灣二路) CB | LINE69 | [5 empty] | 843 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07TN17/T2 |  | 0200 |  | 0107 | 1-19-00 |  | 1-6B | 710 | ON/OFF | 台南南仁線 710 CB |  | aacb | B2/P07_A1 | [8 empty] | 台南PS.710_CB | 710(南仁線) CB | LINE69 | [5 empty] | 844 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | 1520 | A/N | 山上台南海線 1520 87L CFA(87L通訊故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_87CFA | 山上海線(1520)87RY通訊故障 | OTHER | [5 empty] | 845 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0935 |  | 0109 | 1-3A-07 |  | 1-6D | 1510 | U/L | 台南仁德線 1510 #2 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1510_87UL2 | 台南仁德線(1510)#2 87RY U/L | OTHER | [5 empty] | 846 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07S661/T1 |  | 0212 |  | 0110 | 1-1A-04 |  | 1-6E | 670 | ON/OFF | 台南大灣一路 670 CB |  | aahb | B2/P07_A1 | [8 empty] | 台南PS.670_CB | 670(台南大灣一路) CB | LINE69 | [5 empty] | 847 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0803 |  |  | 1-32-03 |  |  | 1520 | A/N | 山上台南海線 1520 87LA |  |  | B2/P07_A1 | [8 empty] | 台南PS.1520_RYFA | 山上海線(1520)數位電驛故障 | OTHER | [5 empty] | 848 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07S62O/T1 |  | 0216 |  | 0111 | 1-1B-00 |  | 1-6F | 660 | ON/OFF | 台南後甲海線 660 CB |  | aaib | B2/P07_A1 | [8 empty] | 台南PS.660_CB | 660(台南後甲海線) CB | LINE69 | [5 empty] | 849 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0809 |  | 0112 | 1-32-09 |  | 1-70 | 1560 | U/L | 台南忠孝二路 1560 #2 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_87UL2 | 台南忠孝二路(1560)#2 87RY U/L | OTHER | [5 empty] | 850 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 1-32-06 |  |  | 1560 | A/N | 台南忠孝二路 1560 RYFA(電驛故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1560_RYFA | 台南忠孝二路(1560)數位電驛故障 | OTHER | [5 empty] | 851 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07S60/T1 |  | 0228 |  | 0114 | 1-1C-04 |  | 1-72 | 630 | ON/OFF | 台南光洲線 630 CB |  | aamb | B2/P07_A1 | [8 empty] | 台南PS.630_CB | 630(台南光洲線) CB | LINE69 | [5 empty] | 852 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbB | B/1Bus | B/2Bus | L/P07S65/T1 |  | 0232 |  | 0115 | 1-1D-00 |  | 1-73 | 620 | ON/OFF | 台南保安線 620 CB |  | aanb | B2/P07_A1 | [8 empty] | 台南PS.620_CB | 620(保安線) CB | LINE69 | [5 empty] | 853 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/1SC |  | 0248 |  | 0119 | 1-1F-00 |  | 1-77 | 820 | ON/OFF | 69KV #1SC 820 CB |  | aakb | B2/P07_A1 | [8 empty] | 台南PS.820_CB | 820(69KV #2SC) CB | SC | [5 empty] | 854 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/2SC |  | 0249 |  | 0120 | 1-1F-01 |  | 1-78 | 810 | ON/OFF | 69KV #2SC 810 CB |  | aapb | B2/P07_A1 | [8 empty] | 台南PS.810_CB | 810(69KV #1SC) CB | SC | [5 empty] | 855 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/3SC |  | 0250 |  | 0121 | 1-1F-02 |  | 1-79 | 830 | ON/OFF | 69KV #3SC 830 CB |  | aadb | B2/P07_A1 | [8 empty] | 台南PS.830_CB | 830(69KV #3SC) CB | SC | [5 empty] | 856 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | 1530 | A/N | 龍崎台南山線 1530 87L CFA(87L通訊故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_87CFA | 龍崎台南山線(1530)87RY通訊故障 | OTHER | [5 empty] | 857 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS1 | 1651 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1024 | 1025 | 0128 | 2-30-00 | 2-30-01 | 2-00 | 1651 | ON/OFF | #1MTR 1651 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1651_ABS | 1651(#1MTR) ABS | MTR | [5 empty] | 858 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS2 | 1652 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1026 | 1027 | 0129 | 2-30-02 | 2-30-03 | 2-01 | 1652 | ON/OFF | #1MTR 1652 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1652_ABS | 1652(#1MTR) ABS | MTR | [5 empty] | 859 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0815 |  |  | 1-32-15 |  |  | 1540 | A/N | 龍崎台南海線 1540 87L CFA(87L通訊故障) |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_87CFA | 龍崎台南海線(1540)87RY通訊故障 | OTHER | [5 empty] | 860 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | 1530 | A/N | 龍崎台南山線 1530 87LA |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_RYFA | 龍崎台南山線(1530)數位電驛故障 | OTHER | [5 empty] | 861 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 1-33-01 |  |  | 1540 | A/N | 龍崎台南海線 1540 87LA |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_RYFA | 龍崎台南海線(1540)數位電驛故障 | OTHER | [5 empty] | 862 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1028 | 1029 | 0130 | 2-30-04 | 2-30-05 | 2-02 | 751 | ON/OFF | #1MTR二次 751 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.751_ABS | 751(#1MTR) ABS | MTR | [5 empty] | 863 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS2 | 752 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1030 | 1031 | 0131 | 2-30-06 | 2-30-07 | 2-03 | 752 | ON/OFF | #1MTR二次 752 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.752_ABS | 752(#1MTR) ABS | MTR | [5 empty] | 864 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | #1MTR | S/L | #1MTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | [5 empty] | 865 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | #1MTR | A/N | #1MTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_TRF | #1MTR 輕故障 | MTR | [5 empty] | 866 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR2 |  |  |  |  | 0823 |  |  | 1-33-07 |  |  | #1MTR | A/N | #1MTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_TRA | #1MTR 重故障 | MTR | [5 empty] | 867 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 1-33-08 |  |  | 69kV BUS | RYFA | 69KV BUS數位電驛故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | [5 empty] | 868 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1032 | 1033 | 0132 | 2-30-08 | 2-30-09 | 2-04 | 1661 | ON/OFF | #2MTR 1661 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1661_ABS | 1661(#2MTR) ABS | MTR | [5 empty] | 869 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 | 0133 | 2-30-10 | 2-30-11 | 2-05 | 1662 | ON/OFF | #2MTR 1662 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1662_ABS | 1662(#2MTR) ABS | MTR | [5 empty] | 870 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 1-33-11 |  |  | #2MTR | S/L | #2MTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | [5 empty] | 871 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0828 |  |  | 1-33-12 |  |  | #2MTR | A/N | #2MTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_TRF | #2MTR 輕故障 | MTR | [5 empty] | 872 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR2 |  |  |  |  | 0829 |  |  | 1-33-13 |  |  | #2MTR | A/N | #2MTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_TRA | #2MTR 重故障 | MTR | [5 empty] | 873 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 1-33-14 |  |  | 69kV BUS | A/N | 69KV BUS 87RY CT 迴路故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 874 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1036 | 1037 | 0134 | 2-30-12 | 2-30-13 | 2-06 | 761 | ON/OFF | #2MTR二次 761 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.761_ABS | 761(#2MTR) ABS | MTR | [5 empty] | 875 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1038 | 1039 | 0135 | 2-30-14 | 2-30-15 | 2-07 | 762 | ON/OFF | #2MTR二次 762 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.762_ABS | 762(#2MTR) ABS | MTR | [5 empty] | 876 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0833 |  |  | 1-34-01 |  |  | #3MTR | S/L | #3MTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | [5 empty] | 877 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0834 |  |  | 1-34-02 |  |  | #3MTR | A/N | #3MTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_TRF | #3MTR 輕故障 | MTR | [5 empty] | 878 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR2 |  |  |  |  | 0835 |  |  | 1-34-03 |  |  | #3MTR | A/N | #3MTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_TRA | #3MTR 重故障 | MTR | [5 empty] | 879 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | #3MTR | 96D | #3MTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_96D | #3MTR 96D RY | MTR | [5 empty] | 880 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | #3MTR | 96P | #3MTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_96P | #3MTR 96P RY | MTR | [5 empty] | 881 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | #3MTR | 63Q | #3MTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_63Q | #3MTR 63Q RY | MTR | [5 empty] | 882 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 3A5Other | 33A | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | #3MTR | 33A | #3MTR 33A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | [5 empty] | 883 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | #1MTR | 96D | #1MTR 96D |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_96D | #1MTR 96D RY | MTR | [5 empty] | 884 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | #1MTR | 96P | #1MTR 96P |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_96P | #1MTR 96P RY | MTR | [5 empty] | 885 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/P07_A1 | [8 empty] | 台南PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 886 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1040 | 1041 | 0136 | 2-31-00 | 2-31-01 | 2-08 | 1671 | ON/OFF | #3MTR 1671 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1671_ABS | 1671(#3MTR) ABS | MTR | [5 empty] | 887 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1042 | 1043 | 0137 | 2-31-02 | 2-31-03 | 2-09 | 1672 | ON/OFF | #3MTR 1672 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1672_ABS | 1672(#3MTR) ABS | MTR | [5 empty] | 888 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | #5ADTR | S/L | #5ADTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(A)_S/L | #5DTR(A) OLTC S/L | MTR | [5 empty] | 889 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1044 | 1045 | 0138 | 2-31-04 | 2-31-05 | 2-0A | 771 | ON/OFF | #3MTR二次 771 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.771_ABS | 771(#3MTR) ABS | MTR | [5 empty] | 890 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS |  |  | 5DTR(B) | #5DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0847 |  |  | 1-34-15 |  |  | #5BDTR | S/L | #5BDTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR(B)_S/L | #5DTR(B) OLTC S/L | MTR | [5 empty] | 891 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 5DTR | #5DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | #5DTR | A/N | #5DTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_TRF | #5DTR 輕故障 | MTR | [5 empty] | 892 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR | #5DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0849 |  |  | 1-35-01 |  |  | #5DTR | A/N | #5DTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_TRA | #5DTR 重故障 | MTR | [5 empty] | 893 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1046 | 1047 | 0139 | 2-31-06 | 2-31-07 | 2-0B | 772 | ON/OFF | #3MTR二次 772 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.772_ABS | 772(#3MTR) ABS | MTR | [5 empty] | 894 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | ABS1 | 1751 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1056 | 1057 | 0144 | 2-32-00 | 2-32-01 | 2-10 | 1751 | ON/OFF | #5DTR 1751 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1751_ABS | 1751(#5DTR) ABS | MTR | [5 empty] | 895 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS |  |  | 6DTR | #6DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | #6DTR | S/L | #6DTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_S/L | #6DTR OLTC S/L | MTR | [5 empty] | 896 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | #1MTR | 63Q | #1MTR 63Q |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_63Q | #1MTR 63Q RY | MTR | [5 empty] | 897 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 3A5Other | 33A | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | #1MTR | 33A | #1MTR 33A |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | [5 empty] | 898 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | #6DTR | A/N | #6DTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_TRF | #6DTR 輕故障 | MTR | [5 empty] | 899 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 6DTR | #6DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0857 |  |  | 1-35-09 |  |  | #6DTR | A/N | #6DTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_TRA | #6DTR 重故障 | MTR | [5 empty] | 900 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | ABS2 | 1752 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1058 | 1059 | 0145 | 2-32-02 | 2-32-03 | 2-11 | 1752 | ON/OFF | #5DTR 1752 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1752_ABS | 1752(#5DTR) ABS | MTR | [5 empty] | 901 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS1 | 1761 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1060 | 1061 | 0146 | 2-32-04 | 2-32-05 | 2-12 | 1761 | ON/OFF | #6DTR 1761 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1761_ABS | 1761(#6DTR) ABS | MTR | [5 empty] | 902 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 7DTR | #7DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | #7DTR | S/L | #7DTR OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_S/L | #7DTR OLTC S/L | MTR | [5 empty] | 903 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 7DTR | #7DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | #7DTR | A/N | #7DTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_TRF | #7DTR 輕故障 | MTR | [5 empty] | 904 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 7DTR | #7DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0863 |  |  | 1-35-15 |  |  | #7DTR | A/N | #7DTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#7DTR_TRA | #7DTR 重故障 | MTR | [5 empty] | 905 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS2 | 1762 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1062 | 1063 | 0147 | 2-32-06 | 2-32-07 | 2-13 | 1762 | ON/OFF | #6DTR 1762 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1762_ABS | 1762(#6DTR) ABS | MTR | [5 empty] | 906 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | ABS1 | 1771 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1064 | 1065 | 0148 | 2-32-08 | 2-32-09 | 2-14 | 1771 | ON/OFF | #7DTR 1771 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1771_ABS | 1771(#7DTR) ABS | MTR | [5 empty] | 907 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS |  |  | 8DTR(A) | #8DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | Locate Empty | S/L | #8DTR D4A OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(A)_S/L | #8DTR(A) OLTC S/L | MTR | [5 empty] | 908 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | ABS2 | 1772 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1066 | 1067 | 0149 | 2-32-10 | 2-32-11 | 2-15 | 1772 | ON/OFF | #7DTR 1772 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1772_ABS | 1772(#7DTR) ABS | MTR | [5 empty] | 909 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 8DTR(B) | #8DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | Locate Empty | S/L | #8DTR D4B OLTC S/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR(B)_S/L | #8DTR(B) OLTC S/L | MTR | [5 empty] | 910 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS |  |  | 8DTR | #8DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | Locate Empty | A/N | #8DTR TRF |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_TRF | #8DTR 輕故障 | MTR | [5 empty] | 911 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 8DTR | #8DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0870 |  |  | 1-36-06 |  |  | Locate Empty | A/N | #8DTR TRA |  | a | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_TRA | #8DTR 重故障 | MTR | [5 empty] | 912 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | 4A5Other | MDAR | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | 710 | A/N | 台南南仁線 710 MDAR警報 |  |  | B2/P07_A1 | [8 empty] | 台南PS.710_MDARF | 710 MDAR RY故障警報 | OTHER | [5 empty] | 913 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1219 |  | 0150 | 2-3C-03 |  | 2-16 | 720 | 79 RY U/L | 台南大灣二路 720 79 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_79UL | 台南大灣二路(720) 79RY U/L | LINE69 | [5 empty] | 914 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1218 |  | 0151 | 2-3C-02 |  | 2-17 | 720 | 87 RY U/L | 台南大灣二路 720 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_87UL | 台南大灣二路(720) 87RY U/L | LINE69 | [5 empty] | 915 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1245 |  | 0152 | 2-3D-13 |  | 2-18 | 710 | 81 RY | 台南南仁線 81 RY |  |  | B2/P07_A1 | [8 empty] | 台南PS.710_81UL | (710) 81RY U/L | LINE69 | [5 empty] | 916 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0819 |  | 0153 | 1-33-03 |  | 2-19 | #1MTR | U/L | #1MTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | [5 empty] | 917 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1226 |  | 0155 | 2-3C-10 |  | 2-1B | 670 | USE/LOCK | 台南大灣一路 670 87RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_87UL | 台南大灣一路(670) 87RY U/L | LINE69 | [5 empty] | 918 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1228 |  | 0156 | 2-3C-12 |  | 2-1C | 660 | 87 RY U/L | 台南後甲海線 660 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_87UL | 台南後甲海線(660) 87RY U/L | LINE69 | [5 empty] | 919 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1234 |  | 0159 | 2-3D-02 |  | 2-1F | 630 | 87 RY U/L | 台南光洲線 630 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_87UL | 台南光洲線(630) 87RY U/L | LINE69 | [5 empty] | 920 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1236 |  | 0160 | 2-3D-04 |  | 2-20 | 620 | 87 RY U/L | 台南保安線 620 87 RY U/L |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_87UL | 保安線(620) 87RY U/L | LINE69 | [5 empty] | 921 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0825 |  | 0161 | 1-33-09 |  | 2-21 | #2MTR | U/L | #2MTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | [5 empty] | 922 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0831 |  | 0164 | 1-33-15 |  | 2-24 | #3MTR | U/L | #3MTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | [5 empty] | 923 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 5DTR | #5DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0843 |  | 0167 | 1-34-11 |  | 2-27 | #5DTR | U/L | #5DTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#5DTR_87UL1 | #5DTR #1 87RY U/L | OTHER | [5 empty] | 924 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | ABS1 | 721 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1076 | 1077 | 0170 | 2-33-04 | 2-33-05 | 2-2A | 721 | ON/OFF | 台南大灣二路 721 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.721_ABS | 721(台南大灣二路) ABS | LINE69 | [5 empty] | 925 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | ABS2 | 722 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1078 | 1079 | 0171 | 2-33-06 | 2-33-07 | 2-2B | 722 | ON/OFF | 台南大灣二路 722 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.722_ABS | 722(台南大灣二路) ABS | LINE69 | [5 empty] | 926 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | ABS3 | 723 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1080 | 1081 | 0172 | 2-33-08 | 2-33-09 | 2-2C | 723 | ON/OFF | 台南大灣二路 723 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.723_ABS | 723(台南大灣二路) ABS | LINE69 | [5 empty] | 927 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | E3 | 723E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1082 | 1083 | 0173 | 2-33-10 | 2-33-11 | 2-2D | 723E | ON/OFF | 台南大灣二路 723E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.723E_ES | 723E(台南大灣二路) ES | LINE69 | [5 empty] | 928 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | ABS1 | 711 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1084 | 1085 | 0174 | 2-33-12 | 2-33-13 | 2-2E | 711 | ON/OFF | 台南南仁線 711 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.711_ABS | 711(南仁線) ABS | LINE69 | [5 empty] | 929 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | ABS2 | 712 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1086 | 1087 | 0175 | 2-33-14 | 2-33-15 | 2-2F | 712 | ON/OFF | 台南南仁線 712 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.712_ABS | 712(南仁線) ABS | LINE69 | [5 empty] | 930 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | ABS3 | 713 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1088 | 1089 | 0176 | 2-34-00 | 2-34-01 | 2-30 | 713 | ON/OFF | 台南南仁線 713 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.713_ABS | 713(南仁線) ABS | LINE69 | [5 empty] | 931 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | E3 | 713E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1090 | 1091 | 0177 | 2-34-02 | 2-34-03 | 2-31 | 713E | ON/OFF | 台南南仁線 713E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.713E_ES | 713E(南仁線) ES | LINE69 | [5 empty] | 932 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0182 | 1-30-02 |  | 2-36 | #1BUS | USE/LOCE | 161KV #1 BUS╴87UL |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 933 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0183 | 1-30-03 |  | 2-37 | #2BUS | USE/LOCE | 161KV #2 BUS╴87UL |  |  | B2/P07_A1 | [8 empty] | 台南PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 934 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | ABS1 | 671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1108 | 1109 | 0186 | 2-35-04 | 2-35-05 | 2-3A | 671 | ON/OFF | 台南大灣一路 671 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.671_ABS | 671(台南大灣一路) ABS | LINE69 | [5 empty] | 935 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | ABS2 | 672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1110 | 1111 | 0187 | 2-35-06 | 2-35-07 | 2-3B | 672 | ON/OFF | 台南大灣一路 672 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.672_ABS | 672(台南大灣一路) ABS | LINE69 | [5 empty] | 936 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | ABS3 | 673 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1112 | 1113 | 0188 | 2-35-08 | 2-35-09 | 2-3C | 673 | ON/OFF | 台南大灣一路 673 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.673_ABS | 673(台南大灣一路) ABS | LINE69 | [5 empty] | 937 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | E3 | 673E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1114 | 1115 | 0189 | 2-35-10 | 2-35-11 | 2-3D | 673E | ON/OFF | 台南大灣一路 673 EABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.673E_ES | 673E(台南大灣一路) ES | LINE69 | [5 empty] | 938 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | ABS1 | 661 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1116 | 1117 | 0190 | 2-35-12 | 2-35-13 | 2-3E | 661 | ON/OFF | 台南後甲海線 661 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.661_ABS | 661(台南後甲海線) ABS | LINE69 | [5 empty] | 939 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | ABS2 | 662 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1118 | 1119 | 0191 | 2-35-14 | 2-35-15 | 2-3F | 662 | ON/OFF | 台南後甲海線 662 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.662_ABS | 662(台南後甲海線) ABS | LINE69 | [5 empty] | 940 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | ABS3 | 663 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1120 | 1121 | 0192 | 2-36-00 | 2-36-01 | 2-40 | 663 | ON/OFF | 台南後甲海線 663 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.663_ABS | 663(台南後甲海線) ABS | LINE69 | [5 empty] | 941 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | E3 | 663E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1122 | 1123 | 0193 | 2-36-02 | 2-36-03 | 2-41 | 663E | ON/OFF | 台南後甲海線 663E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.663E_ES | 663E(台南後甲海線) ES | LINE69 | [5 empty] | 942 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | L/KH11/T1 |  |  | 0370 |  | 0194 | 2-0E-02 |  | 2-42 | F25 | ON/OFF | 台11線 KH11 CB |  | adeb | B2/P07_D1 | [8 empty] | 台南PS.KH11_CB | KH11(11KV台11線) CB | FEEDER | [5 empty] | 943 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | L/KH12/T1 |  |  | 0373 |  | 0195 | 2-0E-05 |  | 2-43 | F26 | ON/OFF | 台12線 KH12 CB |  | adfb | B2/P07_D1 | [8 empty] | 台南PS.KH12_CB | KH12(11KV台12線) CB | FEEDER | [5 empty] | 944 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | L/KH13/T1 |  |  | 0376 |  | 0196 | 2-0F-00 |  | 2-44 | F27 | ON/OFF | 台13線 KH13 CB |  | adgb | B2/P07_D1 | [8 empty] | 台南PS.KH13_CB | KH13(11KV台13線) CB | FEEDER | [5 empty] | 945 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0933 |  |  | 1-3A-05 |  |  | 1570 | 87CFA | 台南忠孝一路 1570 87RY通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_87CFA | 台南忠孝一路(1570)87RY通訊故障 | OTHER | [5 empty] | 946 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0934 |  |  | 1-3A-06 |  |  | 1570 | RYFA | 台南忠孝一路 1570 數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1570_RYFA | 台南忠孝一路(1570)數位電驛故障 | OTHER | [5 empty] | 947 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | L/KH14/T1 |  |  | 0379 |  | 0197 | 2-0F-03 |  | 2-45 | F28 | ON/OFF | 台14線 KH14 CB |  | adhb | B2/P07_D1 | [8 empty] | 台南PS.KH14_CB | KH14(11KV台14線) CB | FEEDER | [5 empty] | 948 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0948 |  |  | 1-3B-04 |  |  | 161kV BUS | RYFA | 161KV BUS數位電驛故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 949 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0949 |  |  | 1-3B-05 |  |  | 161kV BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 950 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | ABS1 | 631 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1140 | 1141 | 0202 | 2-37-04 | 2-37-05 | 2-4A | 631 | ON/OFF | 台南光洲線 631 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.631_ABS | 631(台南光洲線) ABS | LINE69 | [5 empty] | 951 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | ABS2 | 632 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1142 | 1143 | 0203 | 2-37-06 | 2-37-07 | 2-4B | 632 | ON/OFF | 台南光洲線 632 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.632_ABS | 632(台南光洲線) ABS | LINE69 | [5 empty] | 952 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | ABS3 | 633 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1144 | 1145 | 0204 | 2-37-08 | 2-37-09 | 2-4C | 633 | ON/OFF | 台南光洲線 633 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.633_ABS | 633(台南光洲線) ABS | LINE69 | [5 empty] | 953 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | E3 | 633E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1146 | 1147 | 0205 | 2-37-10 | 2-37-11 | 2-4D | 633E | ON/OFF | 台南光洲線 633E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.633E_ES | 633E(台南光洲線) ES | LINE69 | [5 empty] | 954 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | ABS1 | 621 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1148 | 1149 | 0206 | 2-37-12 | 2-37-13 | 2-4E | 621 | ON/OFF | 台南保安線 621 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.621_ABS | 621(保安線) ABS | LINE69 | [5 empty] | 955 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | ABS2 | 622 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1150 | 1151 | 0207 | 2-37-14 | 2-37-15 | 2-4F | 622 | ON/OFF | 台南保安線 622 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.622_ABS | 622(保安線) ABS | LINE69 | [5 empty] | 956 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | ABS3 | 623 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1152 | 1153 | 0208 | 2-38-00 | 2-38-01 | 2-50 | 623 | ON/OFF | 台南保安線 623 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.623_ABS | 623(保安線) ABS | LINE69 | [5 empty] | 957 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | E3 | 623E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1154 | 1155 | 0209 | 2-38-02 | 2-38-03 | 2-51 | 623E | ON/OFF | 台南保安線 623E ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.623E_ES | 623E(保安線) ES | LINE69 | [5 empty] | 958 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS |  |  | 6DTR | #6DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0851 |  | 0210 | 1-35-03 |  | 2-52 | #6DTR | U/L | #6DTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#6DTR_87UL1 | #6DTR #1 87RY U/L | OTHER | [5 empty] | 959 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS |  |  | 7DTR | #7DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0859 |  | 0213 | 0-35-11 |  | 2-55 | #7DTR | U/L | #7DTR #1 87RY U/L |  |  | B1/P07_A1 | [16 empty] | 960 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P07 | 台南PS |  |  | 8DTR | #8DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0864 |  | 0216 | 1-36-00 |  | 2-58 | Locate Empty | U/L | #8DTR #1 87RY U/L |  |  | B1/P07_A1 | [8 empty] | 台南PS.#8DTR_87UL1 | #8DTR #1 87RY U/L | OTHER | [5 empty] | 961 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0219 | 1-30-04 |  | 2-5B | #1BUS | USE/LOCE | 69KV #1 BUS╴87UL |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | [5 empty] | 962 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | ABS1 | 1781 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1068 | 1069 | 0220 | 2-32-12 | 2-32-13 | 2-5C | 1781 | ON/OFF | #8DTR 1781 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1781_ABS | 1781(#8DTR) ABS | MTR | [5 empty] | 963 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | ABS2 | 1782 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1070 | 1071 | 0221 | 2-32-14 | 2-32-15 | 2-5D | 1782 | ON/OFF | #8DTR 1782 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.1782_ABS | 1782(#8DTR) ABS | MTR | [5 empty] | 964 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1180 | 1181 | 0222 | 2-39-12 | 2-39-13 | 2-5E | 821 | ON/OFF | 69KV #1SC 821 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.821_ABS | 821(69KV #2SC) ABS | SC | [5 empty] | 965 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1182 | 1183 | 0223 | 2-39-14 | 2-39-15 | 2-5F | 822 | ON/OFF | 69KV #1SC 822 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.822_ABS | 822(69KV #2SC) ABS | SC | [5 empty] | 966 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1184 | 1185 | 0224 | 2-3A-00 | 2-3A-01 | 2-60 | 811 | ON/OFF | 69KV #2SC 811 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.811_ABS | 811(69KV #1SC) ABS | SC | [5 empty] | 967 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | ABS2 | 812 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1186 | 1187 | 0225 | 2-3A-02 | 2-3A-03 | 2-61 | 812 | ON/OFF | 69KV #2SC 812 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.812_ABS | 812(69KV #1SC) ABS | SC | [5 empty] | 968 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1188 | 1189 | 0226 | 2-3A-04 | 2-3A-05 | 2-62 | 831 | ON/OFF | 69KV #3SC 831 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.831_ABS | 831(69KV #3SC) ABS | SC | [5 empty] | 969 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1190 | 1191 | 0227 | 2-3A-06 | 2-3A-07 | 2-63 | 832 | ON/OFF | 69KV #3SC 832 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.832_ABS | 832(69KV #3SC) ABS | SC | [5 empty] | 970 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1192 | 1193 | 0228 | 2-3A-08 | 2-3A-09 | 2-64 | 601 | ON/OFF | 69KV TIE 601 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.601_ABS | 601(TIE) ABS | TIE | [5 empty] | 971 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1194 | 1195 | 0229 | 2-3A-10 | 2-3A-11 | 2-65 | 602 | ON/OFF | 69KV TIE 602 ABS |  |  | B2/P07_A1 | [8 empty] | 台南PS.602_ABS | 602(TIE) ABS | TIE | [5 empty] | 972 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH61/T1 |  |  | 0265 |  | 0230 | 2-01-01 |  | 2-66 | KH61 | ON/OFF | 台61線 KH61 CB |  | badb | B2/P07_D1 | [8 empty] | 台南PS.KH61_CB | KH61(23KV台61線) CB | FEEDER | [5 empty] | 973 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH62/T1 |  |  | 0266 |  | 0231 | 2-01-02 |  | 2-67 | KH62 | ON/OFF | 台62線 KH62 CB |  | baeb | B2/P07_D1 | [8 empty] | 台南PS.KH62_CB | KH62(23KV台62線) CB | FEEDER | [5 empty] | 974 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH63/T1 |  |  | 0267 |  | 0232 | 2-01-03 |  | 2-68 | KH63 | ON/OFF | 台63線 KH63 CB |  | bafb | B2/P07_D1 | [8 empty] | 台南PS.KH63_CB | KH63(23KV台63線) CB | FEEDER | [5 empty] | 975 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH64/T1 |  |  | 0268 |  | 0233 | 2-01-04 |  | 2-69 | KH64 | ON/OFF | 台64線 KH64 CB |  | bagb | B2/P07_D1 | [8 empty] | 台南PS.KH64_CB | KH64(23KV台64線) CB | FEEDER | [5 empty] | 976 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH65/T1 |  |  | 0269 |  | 0234 | 2-01-05 |  | 2-6A | KH65 | ON/OFF | 台65線 KH65 CB |  | bahb | B2/P07_D1 | [8 empty] | 台南PS.KH65_CB | KH65(23KV台65線) CB | FEEDER | [5 empty] | 977 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/6Bus | L/KH66/T1 |  |  | 0270 |  | 0235 | 2-01-06 |  | 2-6B | KH66 | ON/OFF | 台66線 KH66 CB |  | baib | B2/P07_D1 | [8 empty] | 台南PS.KH66_CB | KH66(23KV台66線) CB | FEEDER | [5 empty] | 978 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/6Bus | C/4SC |  |  | 0271 |  | 0236 | 2-01-07 |  | 2-6C | 240 | ON/OFF | #4 SC 240 CB |  | bacb | B3/P07_A1 | [8 empty] | 台南PS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 979 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/6Bus | C/5SC |  |  | 0272 |  | 0237 | 2-02-00 |  | 2-6D | 250 | ON/OFF | #5 SC 250 CB |  | bajb | B3/P07_A1 | [8 empty] | 台南PS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 980 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/6Bus | B/7Bus |  |  | 0273 |  | 0238 | 2-02-01 |  | 2-6E | 200TIE | ON/OFF | 200 TIE CB |  | bakb | B3/P07_A1 | [8 empty] | 台南PS.200_CB | 200(TIE) CB | TIE | [5 empty] | 981 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A1Bus | L/KH31/T1 |  |  | 0274 |  | 0239 | 2-02-02 |  | 2-6F | KH31 | ON/OFF | 台31線 KH31 CB |  | aaab | B2/P07_D1 | [8 empty] | 台南PS.KH31_CB | KH31(11KV台31線) CB | FEEDER | [5 empty] | 982 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A1Bus | L/KH32/T1 |  |  | 0275 |  | 0240 | 2-02-03 |  | 2-70 | KH32 | ON/OFF | 台32線 KH32 CB |  | aabb | B2/P07_D1 | [8 empty] | 台南PS.KH32_CB | KH32(11KV台32線) CB | FEEDER | [5 empty] | 983 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A1Bus | L/KH33/T1 |  |  | 0276 |  | 0241 | 2-02-04 |  | 2-71 | KH33 | ON/OFF | 台33線 KH33 CB |  | aacb | B2/P07_D1 | [8 empty] | 台南PS.KH33_CB | KH33(11KV台33線) CB | FEEDER | [5 empty] | 984 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A2Bus | L/KH36/T1 |  |  | 0278 |  | 0242 | 2-02-06 |  | 2-72 | KH36 | ON/OFF | 台36線 KH36 CB |  | abdb | B2/P07_D1 | [8 empty] | 台南PS.KH36_CB | KH36(11KV台36線) CB | FEEDER | [5 empty] | 985 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A2Bus | L/KH37/T1 |  |  | 0279 |  | 0243 | 2-02-07 |  | 2-73 | KH37 | ON/OFF | 台37線 KH37 CB |  | abeb | B2/P07_D1 | [8 empty] | 台南PS.KH37_CB | KH37(11KV台37線) CB | FEEDER | [5 empty] | 986 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5A2Bus | L/KH38/T1 |  |  | 0280 |  | 0244 | 2-03-00 |  | 2-74 | KH38 | ON/OFF | 台38線 KH38 CB |  | abfb | B2/P07_D1 | [8 empty] | 台南PS.KH38_CB | KH38(11KV台38線) CB | FEEDER | [5 empty] | 987 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/5A1Bus | C/1SC |  |  | 0277 |  | 0245 | 2-02-05 |  | 2-75 | 210 | ON/OFF | #1 SC 210 CB |  | aadb | B3/P07_A1 | [8 empty] | 台南PS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 988 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/5A2Bus | C/2SC |  |  | 0281 |  | 0246 | 2-03-01 |  | 2-76 | 220 | ON/OFF | #2 SC 220 CB |  | abcb | B3/P07_A1 | [8 empty] | 台南PS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 989 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/5A1Bus | B/5A2Bus |  |  | 0282 |  | 0247 | 2-03-02 |  | 1-00 | 100TIE | ON/OFF | 100 TIE CB |  | abgb | B3/P07_A1 | [8 empty] | 台南PS.100_CB | 100(TIE) CB | TIE | [5 empty] | 990 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/7Bus | C/7SC |  |  | 0283 |  | 0248 | 2-03-03 |  | 2-78 | 270 | ON/OFF | #7 SC 270 CB |  | bbab | B3/P07_A1 | [8 empty] | 台南PS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 991 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/7Bus | C/8SC |  |  | 0284 |  | 0249 | 2-03-04 |  | 2-79 | 260 | ON/OFF | #6 SC 260 CB |  | bbhb | B3/P07_A1 | [8 empty] | 台南PS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 992 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH71/T1 |  |  | 0285 |  | 0250 | 2-03-05 |  | 2-7A | KH71 | ON/OFF | 台71線 KH71 CB |  | bbbb | B2/P07_D1 | [8 empty] | 台南PS.KH71_CB | KH71(23KV台71線) CB | FEEDER | [5 empty] | 993 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH72/T1 |  |  | 0286 |  | 0251 | 2-03-06 |  | 2-7B | KH72 | ON/OFF | 台72線 KH72 CB |  | bbcb | B2/P07_D1 | [8 empty] | 台南PS.KH72_CB | KH72(23KV台72線) CB | FEEDER | [5 empty] | 994 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH73/T1 |  |  | 0287 |  | 0252 | 2-03-07 |  | 2-7C | KH73 | ON/OFF | 台73線 KH73 CB |  | bbdb | B2/P07_D1 | [8 empty] | 台南PS.KH73_CB | KH73(23KV台73線) CB | FEEDER | [5 empty] | 995 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH74/T1 |  |  | 0288 |  | 0253 | 2-04-00 |  | 2-7D | KH74 | ON/OFF | 台74線 KH74 CB |  | bbeb | B2/P07_D1 | [8 empty] | 台南PS.KH74_CB | KH74(23KV台74線) CB | FEEDER | [5 empty] | 996 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH75/T1 |  |  | 0289 |  | 0254 | 2-04-01 |  | 2-7E | KH75 | ON/OFF | 台75線 KH75 CB |  | bbfb | B2/P07_D1 | [8 empty] | 台南PS.KH75_CB | KH75(23KV台75線) CB | FEEDER | [5 empty] | 997 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/7Bus | L/KH76/T1 |  |  | 0290 |  | 0255 | 2-04-02 |  | 2-7F | KH76 | ON/OFF | 備用線KH76 F18 CB |  | bbgb | B2/P07_D1 | [8 empty] | 台南PS.KH76_CB | KH76(23KV台76線) CB | FEEDER | [5 empty] | 998 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1306 |  | 0256 | 3-31-10 |  | 3-00 | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/P07_A1 | [8 empty] | 台南PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 999 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 1307 |  | 0257 | 3-31-11 |  | 3-01 | ACB TIE | ON/OFF | 所內電源ACB TIE |  |  | B3/P07_A1 | [8 empty] | 台南PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 1000 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1308 |  | 0258 | 3-31-12 |  | 3-02 | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/P07_A1 | [8 empty] | 台南PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 1001 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1280 |  | 0259 | 3-30-00 |  | 3-03 | KH61 | U/L | 台61線 KH61 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH61_79UL | 23KV台61線(KH61) 79RY U/L | FEEDER | [5 empty] | 1002 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1281 |  | 0260 | 3-30-01 |  | 3-04 | KH62 | U/L | 台62線 KH62 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH62_79UL | 23KV台62線(KH62) 79RY U/L | FEEDER | [5 empty] | 1003 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1282 |  | 0261 | 3-30-02 |  | 3-05 | KH63 | U/L | 台63線 KH63 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH63_79UL | 23KV台63線(KH63) 79RY U/L | FEEDER | [5 empty] | 1004 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1283 |  | 0262 | 3-30-03 |  | 3-06 | KH64 | U/L | 台64線 KH64 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH64_79UL | 23KV台64線(KH64) 79RY U/L | FEEDER | [5 empty] | 1005 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1284 |  | 0263 | 3-30-04 |  | 3-07 | KH65 | U/L | 台65線 KH65 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH65_79UL | 23KV台65線(KH65) 79RY U/L | FEEDER | [5 empty] | 1006 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1216 |  |  | 2-3C-00 |  |  | 1530 | A/N | 龍崎台南山線 遠方遙跳 DTTA |  |  | B2/P07_A1 | [8 empty] | 台南PS.1530_DTTA | 龍崎台南山線(1530) 遠方遙跳 | OTHER | [5 empty] | 1007 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1217 |  |  | 2-3C-01 |  |  | 1540 | A/N | 龍崎台南海線 遠方遙跳 DTTA |  |  | B2/P07_A1 | [8 empty] | 台南PS.1540_DTTA | 龍崎台南海線(1540) 遠方遙跳 | OTHER | [5 empty] | 1008 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1285 |  | 0264 | 3-30-05 |  | 3-08 | KH66 | U/L | 台66線 KH66 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH66_79UL | 23KV台66線(KH66) 79RY U/L | FEEDER | [5 empty] | 1009 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1286 |  | 0265 | 3-30-06 |  | 3-09 | 240 | A/M | #4 SC 240 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.240_A/M | 23KV #4SC 乏控器 A/M | SC | [5 empty] | 1010 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1224 |  |  | 2-3C-08 |  |  | 720 | 87 CFA | 台南大灣二路 720 87 CFA |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_87CFA | 台南大灣二路(720)87RY通訊故障 | OTHER | [5 empty] | 1011 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1225 |  |  | 2-3C-09 |  |  | 720 | 87 RYA | 台南大灣二路 720 87 RYA |  |  | B2/P07_A1 | [8 empty] | 台南PS.720_RYFA | 台南大灣二路(720)數位電驛故障 | OTHER | [5 empty] | 1012 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1287 |  | 0266 | 3-30-07 |  | 3-0A | 250 | A/M | #5 SC 250 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.250_A/M | 23KV #5SC 乏控器 A/M | SC | [5 empty] | 1013 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1227 |  |  | 2-3C-11 |  |  | 670 | 87CFA | 台南大灣一路 670 87Ry 通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_87CFA | 台南大灣ㄧ路(670)87RY通訊故障 | OTHER | [5 empty] | 1014 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1288 |  | 0267 | 3-30-08 |  | 3-0B | KH31 | U/L | 台31線 KH31 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH31_79UL | 11KV台31線(KH31) 79RY U/L | FEEDER | [5 empty] | 1015 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1229 |  |  | 2-3C-13 |  |  | 660 | 87CFA | 台南後甲海線 660 87 Ry通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_87CFA | 台南後甲海線(660)87RY通訊故障 | OTHER | [5 empty] | 1016 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1230 |  |  | 2-3C-14 |  |  | 630 | RYFA | 台南光洲線(630) 數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_RYFA | 台南光洲線(630)數位電驛故障 | OTHER | [5 empty] | 1017 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1231 |  |  | 2-3C-15 |  |  | 660 | RYFA | 台南後甲海線(660) 數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.660_RYFA | 台南後甲海線(660)數位電驛故障 | OTHER | [5 empty] | 1018 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1289 |  | 0268 | 3-30-09 |  | 3-0C | KH32 | U/L | 台32線 KH32 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH32_79UL | 11KV台32線(KH32) 79RY U/L | FEEDER | [5 empty] | 1019 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1235 |  |  | 2-3D-03 |  |  | 630 | 87CFA | 台南光洲線 630 87 Ry通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.630_87CFA | 台南光洲線(630)87RY通訊故障 | OTHER | [5 empty] | 1020 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1290 |  | 0269 | 3-30-10 |  | 3-0D | KH33 | U/L | 台33線 KH33 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH33_79UL | 11KV台33線(KH33) 79RY U/L | FEEDER | [5 empty] | 1021 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1237 |  |  | 2-3D-05 |  |  | 620 | 87 CFA | 台南保安線 620 87 RY通訊故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_87CFA | 台南保安線(620)87RY通訊故障 | OTHER | [5 empty] | 1022 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1238 |  |  | 2-3D-06 |  |  | 710 | RYFA | 台南南仁線低頻電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.81RYFA | 低頻電驛故障 | OTHER | [5 empty] | 1023 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1239 |  |  | 2-3D-07 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/P07_A1 | [8 empty] | 台南PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 1024 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1240 |  |  | 2-3D-08 |  |  | 620 | RYFA | 台南保安線 620 數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.620_RYFA | 台南保安線(620)數位電驛故障 | OTHER | [5 empty] | 1025 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1241 |  |  | 2-3D-09 |  |  | 670 | RYFA | 台南大灣一路 670數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.670_RYFA | 台南大灣ㄧ路(670)數位電驛故障 | OTHER | [5 empty] | 1026 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1242 |  |  | 2-3D-10 |  |  | 600 | RYFA | 69KV TIE 600數位電驛故障 |  |  | B2/P07_A1 | [8 empty] | 台南PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | [5 empty] | 1027 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1291 |  | 0270 | 3-30-11 |  | 3-0E | KH36 | U/L | 台36線 KH36 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH36_79UL | 11KV台36線(KH36) 79RY U/L | FEEDER | [5 empty] | 1028 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 1247 |  |  | 2-3D-15 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/P07_A1 | [8 empty] | 台南PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 1029 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1248 |  |  | 2-3E-00 |  |  | 69 KV | A/N | 69KV CBF |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | [5 empty] | 1030 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1249 |  |  | 2-3E-01 |  |  | 69 KV | A/N | 69KV CBA |  |  | B3/P07_A1 | [8 empty] | 台南PS.69KV_CBA | 69KV斷路器重故障 | OTHER | [5 empty] | 1031 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1250 |  |  | 2-3E-02 |  |  | 空壓機 | A/N | 空壓機超時運轉 6COMT |  |  | B3/P07_A1 | [8 empty] | 台南PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | [5 empty] | 1032 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1253 |  |  | 2-3E-05 |  |  | DC | A/N | 直流接地故障 DCE |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 1033 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1254 |  |  | 2-3E-06 |  |  | 充電機 | A/N | 變電設備充電機 CHG1 |  |  | B3/P07_A1 | [8 empty] | 台南PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 1034 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1255 |  |  | 2-3E-07 |  |  | 充電機 | A/N | 通訊充電機故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 1035 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1256 |  |  | 2-3E-08 |  |  | 通訊室 | A/N | 通訊設備 AC故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 1036 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1259 |  |  | 2-3E-11 |  |  | RY 盤 | A/N | 通信室溫控警報 |  |  | B3/P07_A1 | [8 empty] | 台南PS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 1037 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1260 |  |  | 2-3E-12 |  |  | RY 盤 | A/N | 油壓警報 OPA |  |  | B3/P07_A1 | [8 empty] | 台南PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 1038 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1261 |  |  | 2-3E-13 |  |  | 所內TR | A/N | 所內用電警報 ACBA |  |  | B3/P07_A1 | [8 empty] | 台南PS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 1039 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 集油池抽水泵警報 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1262 |  |  | 2-3E-14 |  |  | 集油池 | A/N | 集油池泵警報 OWA |  |  | B3/P07_A1 | [8 empty] | 台南PS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 1040 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | B1SC | #1SC |  | NCA |  |  | Status | 中性點不平衡 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1265 |  |  | 2-3F-01 |  |  | #1SC | A/N | 69KV #1SC 210 NCA |  |  | B1/P07_A1 | [8 empty] | 台南PS.810_NCA | 69KV #1SC NCT RY | SC | [5 empty] | 1041 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | B2SC | #2SC |  | NCA |  |  | Status | 中性點不平衡 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1266 |  |  | 2-3F-02 |  |  | #2SC | A/N | 69KV #2SC 220 NCA |  |  | B1/P07_A1 | [8 empty] | 台南PS.820_NCA | 69KV #2SC NCT RY | SC | [5 empty] | 1042 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | B3SC | #3SC |  | NCA |  |  | Status | 中性點不平衡 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1267 |  |  | 2-3F-03 |  |  | #3SC | A/N | 69KV #3SC 230 NCA |  |  | B1/P07_A1 | [8 empty] | 台南PS.830_NCA | 69KV #3SC NCT RY | SC | [5 empty] | 1043 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1268 |  |  | 2-3F-04 |  |  | 69KV | A/N | 69KV ABS 電源跳脫 |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 1044 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1269 |  |  | 2-3F-05 |  |  | 警報 | A/N | 其它警報 PSA |  |  | B3/P07_A1 | [8 empty] | 台南PS.其他重故障 | 161線路復閉壓力不足 | OTHER | [5 empty] | 1045 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1292 |  | 0271 | 3-30-12 |  | 3-0F | KH37 | U/L | 台37線 KH37 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH37_79UL | 11KV台37線(KH37) 79RY U/L | FEEDER | [5 empty] | 1046 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1293 |  | 0272 | 3-30-13 |  | 3-10 | KH38 | U/L | 台38線 KH38 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH38_79UL | 11KV台38線(KH38) 79RY U/L | FEEDER | [5 empty] | 1047 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1294 |  | 0273 | 3-30-14 |  | 3-11 | 210 | A/M | #1 SC 210 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 1048 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1295 |  | 0274 | 3-30-15 |  | 3-12 | 220 | A/M | #2 SC 220 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 1049 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1296 |  | 0275 | 3-31-00 |  | 3-13 | 270 | A/M | #7 SC 270 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.270_A/M | 23KV #7SC 乏控器 A/M | SC | [5 empty] | 1050 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1297 |  | 0276 | 3-31-01 |  | 3-14 | 260 | A/M | #6 SC 260 Q-CTL A/M |  |  | B3/P07_A1 | [8 empty] | 台南PS.260_A/M | 23KV #6SC 乏控器 A/M | SC | [5 empty] | 1051 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1298 |  | 0277 | 3-31-02 |  | 3-15 | KH71 | U/L | 台71線 KH71 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH71_79UL | 23KV台71線(KH71) 79RY U/L | FEEDER | [5 empty] | 1052 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1299 |  | 0278 | 3-31-03 |  | 3-16 | KH72 | U/L | 台72線 KH72 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH72_79UL | 23KV台72線(KH72) 79RY U/L | FEEDER | [5 empty] | 1053 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1300 |  | 0279 | 3-31-04 |  | 3-17 | KH73 | U/L | 台73線 KH73 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH73_79UL | 23KV台73線(KH73) 79RY U/L | FEEDER | [5 empty] | 1054 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1301 |  | 0280 | 3-31-05 |  | 3-18 | KH74 | U/L | 台74線 KH74 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH74_79UL | 23KV台74線(KH74) 79RY U/L | FEEDER | [5 empty] | 1055 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1302 |  | 0281 | 3-31-06 |  | 3-19 | KH75 | U/L | 台75線 KH75 79 RY U/L |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH75_79UL | 23KV台75線(KH75) 79RY U/L | FEEDER | [5 empty] | 1056 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1304 |  | 0283 | 3-31-08 |  | 3-1B | 開關場 | ON/OFF | 開關場照明(A) |  |  | B3/P07_A1 | [8 empty] | 台南PS.開關場照明(A) | 161KV開關場照明 | OTHER | [5 empty] | 1057 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1305 |  | 0284 | 3-31-09 |  | 3-1C | 開關場 | ON/OFF | 開關場照明(B) |  |  | B3/P07_A1 | [8 empty] | 台南PS.開關場照明(B) | 69KV開關場照明 | OTHER | [5 empty] | 1058 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P07 | 台南PS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0285 | 1-30-05 |  | 3-1D | #2BUS | USE/LOCE | 69KV #2 BUS╴87UL |  |  | B2/P07_A1 | [8 empty] | 台南PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | [5 empty] | 1059 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1326 |  | 0286 | 3-32-14 |  | 3-1E | KH61 | U/L | 台61線 KH61 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH61_ADJ | 23KV台61線(KH61) LCO分流器 U/L | FEEDER | [5 empty] | 1060 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1327 |  | 0287 | 3-32-15 |  | 3-1F | KH62 | U/L | 台62線 KH62 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH62_ADJ | 23KV台62線(KH62) LCO分流器 U/L | FEEDER | [5 empty] | 1061 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1328 |  | 0288 | 3-33-00 |  | 3-20 | KH63 | U/L | 台63線 KH63 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH63_ADJ | 23KV台63線(KH63) LCO分流器 U/L | FEEDER | [5 empty] | 1062 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1329 |  | 0289 | 3-33-01 |  | 3-21 | KH64 | U/L | 台64線 KH64 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH64_ADJ | 23KV台64線(KH64) LCO分流器 U/L | FEEDER | [5 empty] | 1063 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1330 |  | 0290 | 3-33-02 |  | 3-22 | KH65 | U/L | 台65線 KH65 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH65_ADJ | 23KV台65線(KH65) LCO分流器 U/L | FEEDER | [5 empty] | 1064 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1331 |  | 0291 | 3-33-03 |  | 3-23 | KH66 | U/L | 台66線 KH66 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH66_ADJ | 23KV台66線(KH66) LCO分流器 U/L | FEEDER | [5 empty] | 1065 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1332 |  | 0292 | 3-33-04 |  | 3-24 | KH31 | U/L | 台31線 KH31 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH31_ADJ | 11KV台31線(KH31) LCO分流器 U/L | FEEDER | [5 empty] | 1066 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1333 |  | 0293 | 3-33-05 |  | 3-25 | KH32 | U/L | 台32線 KH32 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH32_ADJ | 11KV台32線(KH32) LCO分流器 U/L | FEEDER | [5 empty] | 1067 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1334 |  | 0294 | 3-33-06 |  | 3-26 | KH33 | U/L | 台33線 KH33 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH33_ADJ | 11KV台33線(KH33) LCO分流器 U/L | FEEDER | [5 empty] | 1068 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1335 |  | 0295 | 3-33-07 |  | 3-27 | KH36 | U/L | 台36線 KH36 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH36_ADJ | 11KV台36線(KH36) LCO分流器 U/L | FEEDER | [5 empty] | 1069 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1336 |  | 0296 | 3-33-08 |  | 3-28 | KH37 | U/L | 台37線 KH37 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH37_ADJ | 11KV台37線(KH37) LCO分流器 U/L | FEEDER | [5 empty] | 1070 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1337 |  | 0297 | 3-33-09 |  | 3-29 | KH38 | U/L | 台38線 KH38 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH38_ADJ | 11KV台38線(KH38) LCO分流器 U/L | FEEDER | [5 empty] | 1071 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1338 |  | 0298 | 3-33-10 |  | 3-2A | KH71 | U/L | 台71線 KH71 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH71_ADJ | 23KV台71線(KH71) LCO分流器 U/L | FEEDER | [5 empty] | 1072 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1339 |  | 0299 | 3-33-11 |  | 3-2B | KH72 | U/L | 台72線 KH72 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH72_ADJ | 23KV台72線(KH72) LCO分流器 U/L | FEEDER | [5 empty] | 1073 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1309 |  |  | 3-31-13 |  |  | Locate Empty | A/N | 22KV 11KV LOA 79RY 復閉失敗 |  |  | B3/P07_A1 | [8 empty] | 台南PS.11/23KV_LOA | 11/23KV 79RY 饋線復閉失敗 | OTHER | [5 empty] | 1074 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Water1 | 地下室 0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1310 |  |  | 3-31-14 |  |  | 地下室 | A/N | 地下室 0.5M 水位警報 |  |  | B3/P07_A1 | [8 empty] | 台南PS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 1075 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Water2 | 地下室 1M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1311 |  |  | 3-31-15 |  |  | 地下室 | A/N | 地下室 1M 水位警報 |  |  | B3/P07_A1 | [8 empty] | 台南PS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 1076 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1312 |  |  | 3-32-00 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/P07_A1 | [8 empty] | 台南PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 1077 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Fire2 | 控制大樓CO2 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1313 |  |  | 3-32-01 |  |  | 火災警報(2) | A/N | 火災警報(2)建物-控制大樓CO2 |  |  | B3/P07_A1 | [8 empty] | 台南PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | [5 empty] | 1078 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Fire3 | 全區保全系統 |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1314 |  |  | 3-32-02 |  |  | 火災警報(3) | A/N | 火災警報(3)全區保全系統 |  |  | B3/P07_A1 | [8 empty] | 台南PS.火災警報(3) | 火災警報(3)全區保全系統 | OTHER | [5 empty] | 1079 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1315 |  |  | 3-32-03 |  |  | Locate Empty | A/N | 無人化防盜(1) 保全系統 |  |  | B3/P07_A1 | [8 empty] | 台南PS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 1080 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1316 |  |  | 3-32-04 |  |  | Locate Empty |  | 無人化防盜(2) |  |  | B3/P07_A1 | [8 empty] | 台南PS.無人化防盜(2) | 無人化防盜(2) | OTHER | [5 empty] | 1081 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS |  |  | 1MTR | #1MTR |  | IRFA | （資產管理） |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1317 |  |  | 3-32-05 |  |  | Locate Empty | A/N | #1MTR變壓器監視用IED故障（資產管理） |  |  | B1/P07_A1 | [8 empty] | 台南PS.IEDA | 變壓器資產管理監視IED故障 | OTHER | [5 empty] | 1082 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Door1 | 圍牆電動大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1318 |  |  | 3-32-06 |  |  | Locate Empty | A/N | 無人化門禁(1)圍牆電動大門 |  |  | B3/P07_A1 | [8 empty] | 台南PS.無人化門禁(1) | 無人化門禁(1)變電所大小門 | OTHER | [5 empty] | 1083 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1319 |  |  | 3-32-07 |  |  | Locate Empty |  | 無人化門禁(2)控制室 |  |  | B3/P07_A1 | [8 empty] | 台南PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 1084 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1320 |  |  | 3-32-08 |  |  | Locate Empty |  | 無人化門禁(3) |  |  | B3/P07_A1 | [8 empty] | 台南PS.無人化門禁(3) | 無人化門禁(3)sp | OTHER | [5 empty] | 1085 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1321 |  |  | 3-32-09 |  |  | 空調機 | A/N | 空調機故障 |  |  | B3/P07_A1 | [8 empty] | 台南PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 1086 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | Fire4 | #2MTR CO2 |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1322 |  |  | 3-32-10 |  |  | 火災警報(4) | A/N | 火災警報(4)-#2MTR CO2 |  |  | B3/P07_A1 | [8 empty] | 台南PS.火災警報(4) | 火災警報(4)-#2MTR CO2 | OTHER | [5 empty] | 1087 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 1323 |  |  | 3-32-11 |  |  | SC 60RY | A/N | 11KV 22KV SC60A(目前設備有監視 ) |  |  | B3/P07_A1 | [8 empty] | 台南PS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 1088 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1324 |  |  | 3-32-12 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/P07_A1 | [8 empty] | 台南PS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 1089 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1325 |  |  | 3-32-13 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/P07_A1 | [8 empty] | 台南PS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 1090 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1340 |  | 0300 | 3-33-12 |  | 3-2C | KH73 | U/L | 台73線 KH73 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH73_ADJ | 23KV台73線(KH73) LCO分流器 U/L | FEEDER | [5 empty] | 1091 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1341 |  | 0301 | 3-33-13 |  | 3-2D | KH74 | U/L | 台74線 KH74 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH74_ADJ | 23KV台74線(KH74) LCO分流器 U/L | FEEDER | [5 empty] | 1092 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1342 |  | 0302 | 3-33-14 |  | 3-2E | KH75 | U/L | 台75線 KH75 LCO 分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH75_ADJ | 23KV台75線(KH75) LCO分流器 U/L | FEEDER | [5 empty] | 1093 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1343 |  | 0303 | 3-33-15 |  | 3-2F | KH76 | U/L | 備用線F18 LCO分流器 |  |  | B2/P07_D1 | [8 empty] | 台南PS.KH76_ADJ | 23KV台76線(KH76) LCO分流器 U/L | FEEDER | [5 empty] | 1094 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/5BBus | T/5DTR(B) |  |  | 0116 |  | 0304 | 1-0E-04 |  | 3-30 | 320 | ON/OFF | #5DTR 5B二次側 320 CB |  | acba | ELEM/P07_A1 | [8 empty] | 台南PS.320_CB | 320(#5DTR) CB | MTR | [5 empty] | 1095 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbK | B/5BBus | C/3SC |  |  | 0343 |  | 0305 | 2-0A-07 |  | 3-31 | 230 | ON/OFF | 11KV #3SC 230 CB |  | accb | B3/P07_A1 | [8 empty] | 台南PS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 1096 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH41/T1 |  |  | 0344 |  | 0306 | 2-0B-00 |  | 3-32 | F19 | ON/OFF | 11KV 台41線 KH41 CB |  | acdb | B2/P07_D1 | [8 empty] | 台南PS.KH41_CB | KH41(11KV台41線) CB | FEEDER | [5 empty] | 1097 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH42/T1 |  |  | 0345 |  | 0307 | 2-0B-01 |  | 3-33 | F20 | ON/OFF | 11KV 台42線 KH42 CB |  | aceb | B2/P07_D1 | [8 empty] | 台南PS.KH42_CB | KH42(11KV台42線) CB | FEEDER | [5 empty] | 1098 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH43/T1 |  |  | 0346 |  | 0308 | 2-0B-02 |  | 3-34 | F21 | ON/OFF | 11KV 台43線 KH43 CB |  | acfb | B2/P07_D1 | [8 empty] | 台南PS.KH43_CB | KH43(11KV台43線) CB | FEEDER | [5 empty] | 1099 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH44/T1 |  |  | 0347 |  | 0309 | 2-0B-03 |  | 3-35 | F22 | ON/OFF | 11KV 台44線 KH44 CB |  | acgb | B2/P07_D1 | [8 empty] | 台南PS.KH44_CB | KH44(11KV台44線) CB | FEEDER | [5 empty] | 1100 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH45/T1 |  |  | 0348 |  | 0310 | 2-0B-04 |  | 3-36 | F23 | ON/OFF | 11KV KH45 CB |  | achb | B2/P07_D1 | [8 empty] | 台南PS.KH45_CB | KH45(11KV台45線) CB | FEEDER | [5 empty] | 1101 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/5BBus | L/KH46/T1 |  |  | 0349 |  | 0311 | 2-0B-05 |  | 3-37 | F24 | ON/OFF | 11KV KH46 CB |  | acib | B2/P07_D1 | [8 empty] | 台南PS.KH46_CB | KH46(11KV台46線) CB | FEEDER | [5 empty] | 1102 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8ABus | L/KH15/T1 |  |  | 0382 |  | 0325 | 2-0F-06 |  | 3-45 | F29 | ON/OFF | 台15線 KH15 CB |  | adib | B2/P07_D1 | [8 empty] | 台南PS.KH15_CB | KH15(11KV台15線) CB | FEEDER | [5 empty] | 1103 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | L/KH20/T1 |  |  | 0430 |  | 0326 | 2-15-06 |  | 3-46 | F30 | ON/OFF | 台20線 KH20 CB |  | aejb | B2/P07_D1 | [8 empty] | 台南PS.KH20_CB | KH20(11KV台20線) CB | FEEDER | [5 empty] | 1104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | L/KH19/T1 |  |  | 0433 |  | 0327 | 2-16-01 |  | 3-47 | F31 | ON/OFF | 台19線 KH19 CB |  | aeib | B2/P07_D1 | [8 empty] | 台南PS.KH19_CB | KH19(11KV台19線) CB | FEEDER | [5 empty] | 1105 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | L/KH18/T1 |  |  | 0448 |  | 0328 | 2-18-00 |  | 3-48 | F32 | ON/OFF | 台18線 KH18 CB |  | aehb | B2/P07_D1 | [8 empty] | 台南PS.KH18_CB | KH18(11KV台18線) CB | FEEDER | [5 empty] | 1106 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | L/KH17/T1 |  |  | 0451 |  | 0329 | 2-18-03 |  | 3-49 | F33 | ON/OFF | 台17線 KH17 CB |  | aegb | B2/P07_D1 | [8 empty] | 台南PS.KH17_CB | KH17(11KV台17線) CB | FEEDER | [5 empty] | 1107 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1264 |  |  | 2-3F-00 |  |  | 23/11KV | A/N | #5A,6,7,8 DTR 23/11KV CBA（請在轉接箱轉接) |  |  | B1/P07_A1 | [8 empty] | 台南PS.DTR_CBA(3) | #5A-6-7-8DTR-23/11KV-CBA | OTHER | [5 empty] | 1108 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1263 |  |  | 2-3E-15 |  |  | 23/11KV | A/N | #5A,6,7,8 DTR 23/11KV CBF（請在轉接箱轉接) |  |  | B1/P07_A1 | [8 empty] | 台南PS.DTR_CBF(3) | #5A-6-7-8DTR-23/11KV-CBF | OTHER | [5 empty] | 1109 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/8BBus | L/KH16/T1 |  |  | 0454 |  | 0330 | 2-18-06 |  | 3-4A | F34 | ON/OFF | 台16線 KH16 CB |  | aefb | B2/P07_D1 | [8 empty] | 台南PS.KH16_CB | KH16(11KV台16線) CB | FEEDER | [5 empty] | 1110 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | GDA1 |  | INSERT | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | Locate Empty |  |  |  |  | B3/P07_A1 | [8 empty] | 台南PS.310A1_GDA | 11KV M5A1(310A1) 51N RY | OTHER | [5 empty] | 1111 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 310A1 | #5DTR(A)(310A1) |  | GDA2 |  | INSERT | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | Locate Empty |  |  |  |  | B3/P07_A1 | [8 empty] | 台南PS.310A2_GDA | 11KV M5A2(310A2) 51N RY | OTHER | [5 empty] | 1112 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 320 | #5DTR(320) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | Locate Empty |  |  |  |  | B3/P07_A1 | [8 empty] | 台南PS.320_GDA | 11KV M5B(320) 51N RY | OTHER | [5 empty] | 1113 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 330 | #6DTR(330) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | Locate Empty |  |  |  |  | B3/P07_A1 | [8 empty] | 台南PS.330_GDA | 22KV M6(330) 51N RY | OTHER | [5 empty] | 1114 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 350 | #7DTR(350) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | Locate Empty |  |  |  |  | B3/P07_A1 | [8 empty] | 台南PS.350_GDA | 22KV M7(350) 51N RY | OTHER | [5 empty] | 1115 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
P07 | 台南PS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: P07/161/1BUS/V; OPRD2: P07/161/2BUS/V
P07 | 台南PS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: P07/69/1BUS/V; OPRD2: P07/69/2BUS/V
P07 | 台南PS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/P07_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: P07/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: P07/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
P07 | 台南PS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/P07_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_16 | OPRD1: P07/161/1510/MW; OPRD2: P07/161/1520/MW; OPRD3: P07/161/1530/MW; OPRD4: P07/161/1540/MW; OPRD5: P07/161/1550/MW; OPRD6: P07/161/1560/MW; OPRD7: P07/161/1570/MW; OPRD8: P07/69/620/MW; OPRD9: P07/69/630/MW; OPRD10: P07/69/660/MW; OPRD11: P07/69/670/MW; OPRD12: P07/69/710/MW; OPRD13: P07/69/720/MW; OPRD14: P07/69/750/MW; OPRD15: P07/69/760/MW; OPRD16: P07/69/770/MW
P07 | 台南PS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/P07_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: P07/0/CalcPoint/OPRN2_MW
P07 | 台南PS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/P07_A1 | [17 empty] | none
P07 | 台南PS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/P07_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: P07/0/CalcPoint/OPRN1; OPRD2: P07/0/CalcPoint/OPRN2; OPRD3: P07/0/CalcPoint/PRFL_UL
P07 | 台南PS |  |  | 5DTR | 5DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P07/11/310A1/I_R; OPRD2: P07/11/310A2/I_R
P07 | 台南PS |  |  | 5DTR | 5DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P07/11/310A1/I_S; OPRD2: P07/11/310A2/I_S
P07 | 台南PS |  |  | 5DTR | 5DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P07/11/310A1/I_T; OPRD2: P07/11/310A2/I_T
P07 | 台南PS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P07_A1 | [12 empty] | 台南PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P07/69/750/MW; OPRD2: P07/69/750/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P07_A1 | [12 empty] | 台南PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P07/69/760/MW; OPRD2: P07/69/760/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P07_A1 | [12 empty] | 台南PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P07/69/770/MW; OPRD2: P07/69/770/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1510 | 台南～仁德線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1510_AMP | 台南仁德線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P07/161/1510/MW; OPRD2: P07/161/1510/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1520 | 山上～台南海線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1520_AMP | 山上海線 AMP | LINE161 | AMP_CAL | C16R1328 | amp_cal | OPRD1: P07/161/1520/MW; OPRD2: P07/161/1520/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎～台南山線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1530_AMP | 龍崎山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P07/161/1530/MW; OPRD2: P07/161/1530/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎～台南海線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1540_AMP | 龍崎海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P07/161/1540/MW; OPRD2: P07/161/1540/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1550_AMP | 台南延平線 AMP | LINE161 | AMP_CAL | C20R1200 | amp_cal | OPRD1: P07/161/1550/MW; OPRD2: P07/161/1550/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1560 | 台南～忠孝二路(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1560_AMP | 台南忠孝二路 AMP | LINE161 | AMP_CAL | C20R1001 | amp_cal | OPRD1: P07/161/1560/MW; OPRD2: P07/161/1560/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 161 | 161kV | 1570 | 台南～忠孝一路(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.1570_AMP | 台南忠孝一路 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: P07/161/1570/MW; OPRD2: P07/161/1570/MVAR; OPRD3: P07/0/CalcPoint/Vbs4
P07 | 台南PS | 69 | 69kV | 620 | 台南～保安線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.620_AMP | 保安線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P07/69/620/MW; OPRD2: P07/69/620/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 69 | 69kV | 630 | 台南～光洲線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.630_AMP | 台南光洲線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: P07/69/630/MW; OPRD2: P07/69/630/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 69 | 69kV | 660 | 台南～後甲海線(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.660_AMP | 台南後甲海線 AMP | LINE69 | AMP_CAL | C12R0947 | amp_cal | OPRD1: P07/69/660/MW; OPRD2: P07/69/660/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.670_AMP | 台南大灣一路 AMP | LINE69 | AMP_CAL | C12R0878 | amp_cal | OPRD1: P07/69/670/MW; OPRD2: P07/69/670/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 69 | 69kV | 710 | 台南～太子、南仁、新視代線(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.710_AMP | 南仁線 AMP | LINE69 | AMP_CAL | C12R0641 | amp_cal | OPRD1: P07/69/710/MW; OPRD2: P07/69/710/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.720_AMP | 台南大灣二路 AMP | LINE69 | AMP_CAL | C12R0878 | amp_cal | OPRD1: P07/69/720/MW; OPRD2: P07/69/720/MVAR; OPRD3: P07/0/CalcPoint/Vbs2
P07 | 台南PS | 11 | 11kV | 5A1BUS | #5A1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/11/5A1BUS/V
P07 | 台南PS | 11 | 11kV | 5A2BUS | #5A2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/11/5A2BUS/V
P07 | 台南PS | 11 | 11kV | 5BBUS | #5BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/11/5BBUS/V
P07 | 台南PS | 11 | 11kV | 8ABUS | #8ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/11/8ABUS/V
P07 | 台南PS | 11 | 11kV | 8BBUS | #8BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/11/8BBUS/V
P07 | 台南PS | 22 | 22kV | 6BUS | #6BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/22/6BUS/V
P07 | 台南PS | 22 | 22kV | 7BUS | #7BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P07/22/7BUS/V
P07 | 台南PS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P07_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 台南PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P07/69/750/MW; OPRD2: P07/69/750/MVAR
P07 | 台南PS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P07_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 台南PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P07/69/760/MW; OPRD2: P07/69/760/MVAR
P07 | 台南PS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P07_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 台南PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P07/69/770/MW; OPRD2: P07/69/770/MVAR
P07 | 台南PS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#1MTR_LOAD | #1MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P07//1MTR/MVA; OPRD2: 0
P07 | 台南PS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#2MTR_LOAD | #2MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P07//2MTR/MVA; OPRD2: 0
P07 | 台南PS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#3MTR_LOAD | #3MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P07//3MTR/MVA; OPRD2: 0
P07 | 台南PS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#1MTR_PF | #1MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P07/69/750/MW; OPRD2: P07/69/750/MVAR
P07 | 台南PS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#2MTR_PF | #2MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P07/69/760/MW; OPRD2: P07/69/760/MVAR
P07 | 台南PS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#3MTR_PF | #3MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P07/69/770/MW; OPRD2: P07/69/770/MVAR
P07 | 台南PS |  |  | 5DTR(A) | #5DTR(A) |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#5DTR(A)_PERM | #5DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//5DTR(A)/SupLocal; OPRD2: P07//5DTR(A)/Tap Chan
P07 | 台南PS |  |  | 5DTR(B) | #5DTR(B) |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#5DTR(B)_PERM | #5DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//5DTR(B)/SupLocal; OPRD2: P07//5DTR(B)/Tap Chan
P07 | 台南PS |  |  | 6DTR | #6DTR |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#6DTR_PERM | #6DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//6DTR/SupLocal; OPRD2: P07//6DTR/Tap Chan
P07 | 台南PS |  |  | 7DTR | #7DTR |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#7DTR_PERM | #7DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//7DTR/SupLocal; OPRD2: P07//7DTR/Tap Chan
P07 | 台南PS |  |  | 8DTR(A) | #8DTR(A) |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#8DTR(A)_PERM | #8DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//8DTR(A)/SupLocal; OPRD2: P07//8DTR(A)/Tap Chan
P07 | 台南PS |  |  | 8DTR(B) | #8DTR(B) |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#8DTR(B)_PERM | #8DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P07//8DTR(B)/SupLocal; OPRD2: P07//8DTR(B)/Tap Chan
P07 | 台南PS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P07//1MTR/SupLocal; OPRD2: P07//1MTR/Tap Chan; OPRD3: P07//1MTR/M_F_I
P07 | 台南PS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P07//2MTR/SupLocal; OPRD2: P07//2MTR/Tap Chan; OPRD3: P07//2MTR/M_F_I
P07 | 台南PS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/P07_A1 | [12 empty] | 台南PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P07//3MTR/SupLocal; OPRD2: P07//3MTR/Tap Chan; OPRD3: P07//3MTR/M_F_I
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8ABUS/V; OPRD2: P07/11/KH11/I_R; OPRD3: P07/11/KH11/I_S; OPRD4: P07/11/KH11/I_T
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8ABUS/V; OPRD2: P07/11/KH12/I_R; OPRD3: P07/11/KH12/I_S; OPRD4: P07/11/KH12/I_T
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8ABUS/V; OPRD2: P07/11/KH13/I_R; OPRD3: P07/11/KH13/I_S; OPRD4: P07/11/KH13/I_T
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8ABUS/V; OPRD2: P07/11/KH14/I_R; OPRD3: P07/11/KH14/I_S; OPRD4: P07/11/KH14/I_T
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8ABUS/V; OPRD2: P07/11/KH15/I_R; OPRD3: P07/11/KH15/I_S; OPRD4: P07/11/KH15/I_T
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8BBUS/V; OPRD2: P07/11/KH16/I_R; OPRD3: P07/11/KH16/I_S; OPRD4: P07/11/KH16/I_T
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8BBUS/V; OPRD2: P07/11/KH17/I_R; OPRD3: P07/11/KH17/I_S; OPRD4: P07/11/KH17/I_T
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8BBUS/V; OPRD2: P07/11/KH18/I_R; OPRD3: P07/11/KH18/I_S; OPRD4: P07/11/KH18/I_T
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8BBUS/V; OPRD2: P07/11/KH19/I_R; OPRD3: P07/11/KH19/I_S; OPRD4: P07/11/KH19/I_T
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/8BBUS/V; OPRD2: P07/11/KH20/I_R; OPRD3: P07/11/KH20/I_S; OPRD4: P07/11/KH20/I_T
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A1BUS/V; OPRD2: P07/11/KH31/I_R; OPRD3: P07/11/KH31/I_S; OPRD4: P07/11/KH31/I_T
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A1BUS/V; OPRD2: P07/11/KH32/I_R; OPRD3: P07/11/KH32/I_S; OPRD4: P07/11/KH32/I_T
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A1BUS/V; OPRD2: P07/11/KH33/I_R; OPRD3: P07/11/KH33/I_S; OPRD4: P07/11/KH33/I_T
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A2BUS/V; OPRD2: P07/11/KH36/I_R; OPRD3: P07/11/KH36/I_S; OPRD4: P07/11/KH36/I_T
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A2BUS/V; OPRD2: P07/11/KH37/I_R; OPRD3: P07/11/KH37/I_S; OPRD4: P07/11/KH37/I_T
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5A2BUS/V; OPRD2: P07/11/KH38/I_R; OPRD3: P07/11/KH38/I_S; OPRD4: P07/11/KH38/I_T
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH41/I_R; OPRD3: P07/11/KH41/I_S; OPRD4: P07/11/KH41/I_T
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH42/I_R; OPRD3: P07/11/KH42/I_S; OPRD4: P07/11/KH42/I_T
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH43/I_R; OPRD3: P07/11/KH43/I_S; OPRD4: P07/11/KH43/I_T
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH44/I_R; OPRD3: P07/11/KH44/I_S; OPRD4: P07/11/KH44/I_T
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH45/I_R; OPRD3: P07/11/KH45/I_S; OPRD4: P07/11/KH45/I_T
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/11/5BBUS/V; OPRD2: P07/11/KH46/I_R; OPRD3: P07/11/KH46/I_S; OPRD4: P07/11/KH46/I_T
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH61/I_R; OPRD3: P07/22/KH61/I_S; OPRD4: P07/22/KH61/I_T
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH62/I_R; OPRD3: P07/22/KH62/I_S; OPRD4: P07/22/KH62/I_T
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH63/I_R; OPRD3: P07/22/KH63/I_S; OPRD4: P07/22/KH63/I_T
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH64/I_R; OPRD3: P07/22/KH64/I_S; OPRD4: P07/22/KH64/I_T
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH65/I_R; OPRD3: P07/22/KH65/I_S; OPRD4: P07/22/KH65/I_T
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/6BUS/V; OPRD2: P07/22/KH66/I_R; OPRD3: P07/22/KH66/I_S; OPRD4: P07/22/KH66/I_T
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH71/I_R; OPRD3: P07/22/KH71/I_S; OPRD4: P07/22/KH71/I_T
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH72/I_R; OPRD3: P07/22/KH72/I_S; OPRD4: P07/22/KH72/I_T
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH73/I_R; OPRD3: P07/22/KH73/I_S; OPRD4: P07/22/KH73/I_T
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH74/I_R; OPRD3: P07/22/KH74/I_S; OPRD4: P07/22/KH74/I_T
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH75/I_R; OPRD3: P07/22/KH75/I_S; OPRD4: P07/22/KH75/I_T
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P07/22/7BUS/V; OPRD2: P07/22/KH76/I_R; OPRD3: P07/22/KH76/I_S; OPRD4: P07/22/KH76/I_T
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH11/kVA; OPRD2: P07/11/KH11/KVAR
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH12/kVA; OPRD2: P07/11/KH12/KVAR
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH13/kVA; OPRD2: P07/11/KH13/KVAR
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH14/kVA; OPRD2: P07/11/KH14/KVAR
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH15/kVA; OPRD2: P07/11/KH15/KVAR
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH16/kVA; OPRD2: P07/11/KH16/KVAR
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH17/kVA; OPRD2: P07/11/KH17/KVAR
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH18/kVA; OPRD2: P07/11/KH18/KVAR
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH19/kVA; OPRD2: P07/11/KH19/KVAR
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH20/kVA; OPRD2: P07/11/KH20/KVAR
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH31/kVA; OPRD2: P07/11/KH31/KVAR
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH32/kVA; OPRD2: P07/11/KH32/KVAR
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH33/kVA; OPRD2: P07/11/KH33/KVAR
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH36/kVA; OPRD2: P07/11/KH36/KVAR
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH37/kVA; OPRD2: P07/11/KH37/KVAR
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH38/kVA; OPRD2: P07/11/KH38/KVAR
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH41/kVA; OPRD2: P07/11/KH41/KVAR
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH42/kVA; OPRD2: P07/11/KH42/KVAR
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH43/kVA; OPRD2: P07/11/KH43/KVAR
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH44/kVA; OPRD2: P07/11/KH44/KVAR
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH45/kVA; OPRD2: P07/11/KH45/KVAR
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/11/KH46/kVA; OPRD2: P07/11/KH46/KVAR
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH61/kVA; OPRD2: P07/22/KH61/KVAR
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH62/kVA; OPRD2: P07/22/KH62/KVAR
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH63/kVA; OPRD2: P07/22/KH63/KVAR
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH64/kVA; OPRD2: P07/22/KH64/KVAR
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH65/kVA; OPRD2: P07/22/KH65/KVAR
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH66/kVA; OPRD2: P07/22/KH66/KVAR
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH71/kVA; OPRD2: P07/22/KH71/KVAR
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH72/kVA; OPRD2: P07/22/KH72/KVAR
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH73/kVA; OPRD2: P07/22/KH73/KVAR
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH74/kVA; OPRD2: P07/22/KH74/KVAR
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH75/kVA; OPRD2: P07/22/KH75/KVAR
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P07/22/KH76/kVA; OPRD2: P07/22/KH76/KVAR
P07 | 台南PS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/P07_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P07/69/750/MW; OPRD2: P07/69/760/MW; OPRD3: P07/69/770/MW
P07 | 台南PS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/P07_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P07/69/750/MVAR; OPRD2: P07/69/760/MVAR; OPRD3: P07/69/770/MVAR
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/210/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/220/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/230/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.410_SC_MVAR | 11KV#11SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/410/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.420_SC_MVAR | 11KV#12SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/420/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.430_SC_MVAR | 11KV#13SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/430/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.440_SC_MVAR | 11KV#14SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P07/11/440/CB; OPRD2: 6.9; OPRD3: 0
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P07/22/240/CB; OPRD2: 13.8; OPRD3: 0
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P07/22/250/CB; OPRD2: 13.8; OPRD3: 0
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P07/22/260/CB; OPRD2: 13.8; OPRD3: 0
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P07_A1 | [12 empty] | 台南PS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P07/22/270/CB; OPRD2: 13.8; OPRD3: 0
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P07/69/810/CB; OPRD2: 69; OPRD3: 0
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.820_SC_MVAR | 69KV#2SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P07/69/820/CB; OPRD2: 69; OPRD3: 0
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P07_A1 | [12 empty] | 台南PS.830_SC_MVAR | 69KV#3SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P07/69/830/CB; OPRD2: 69; OPRD3: 0
P07 | 台南PS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/P07_A1 | [12 empty] | 台南PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_32 |  | com_alarm_77 | P07//1MTR/PHA | P07//1MTR/87A | P07//1MTR/GDA | P07//1MTR/51ZA | P07//1MTR/96PA | P07//1MTR/63Q | P07//1MTR/96D | P07//1MTR/TRA | P07//2MTR/96D | P07//2MTR/GDA | P07//2MTR/96B1 | P07//2MTR/63Q | P07//2MTR/TRA | P07//2MTR/87A | P07//2MTR/96PA | P07//2MTR/96B2 | P07//2MTR/51ZA | P07//2MTR/PHA | P07//3MTR/GDA | P07//3MTR/87A | P07//3MTR/PHA | P07//3MTR/63Q | P07//3MTR/96PA | P07//3MTR/96D | P07//3MTR/TRA | P07//3MTR/51ZA | P07//5DTR/96B2 | P07//5DTR/96PA | P07//5DTR/87A | P07//5DTR/96D | P07//5DTR/63Q | P07//5DTR/51ZA | P07//5DTR/96B1 | P07//5DTR/TRA | P07//5DTR/PHA | P07//5DTR/GDA | P07//6DTR/51ZA | P07//6DTR/PHA | P07//6DTR/87A | P07//6DTR/TRA | P07//6DTR/96PA | P07//6DTR/63Q | P07//6DTR/96D | P07//6DTR/96B1 | P07//6DTR/GDA | P07//6DTR/96B2 | P07//7DTR/96D | P07//7DTR/87A | P07//7DTR/51ZA | P07//7DTR/TRA
P07 | 台南PS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/P07_A1 | [12 empty] | 台南PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_7 |  | com_alarm_7 | OPRD1: P07//1MTR/TRF; OPRD2: P07//2MTR/TRF; OPRD3: P07//3MTR/TRF; OPRD4: P07//5DTR/TRF; OPRD5: P07//6DTR/TRF; OPRD6: P07//7DTR/TRF; OPRD7: P07//8DTR/TRF
P07 | 台南PS | 161 | 161kV | 1750_D1 | #5DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/161/1750/CB
P07 | 台南PS | 11 | 11kV | 310A1_D1 | #5DTR(A)(310A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/11/310A1/CB
P07 | 台南PS | 11 | 11kV | 310A2_D1 | #5DTR(A)(310A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/11/310A2/CB
P07 | 台南PS | 161 | 161kV | 1760_D1 | #6DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/161/1760/CB
P07 | 台南PS | 22 | 22kV | 330_D1 | #6DTR(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/22/330/CB
P07 | 台南PS | 161 | 161kV | 1770_D1 | #7DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/161/1770/CB
P07 | 台南PS | 22 | 22kV | 350_D1 | #7DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/22/350/CB
P07 | 台南PS | 161 | 161kV | 1780_D1 | #8DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/161/1780/CB
P07 | 台南PS | 11 | 11kV | 370_D1 | #8DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/11/370/CB
P07 | 台南PS | 11 | 11kV | 380_D1 | #8DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/11/380/CB
P07 | 台南PS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/0/RTU/RTU_R_L
P07 | 台南PS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/0/StaDev/DCA
P07 | 台南PS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/0/StaDev/STUV
P07 | 台南PS | 161 | 161kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/161/ComPoint/ABS_89A
P07 | 台南PS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/0/StaDev/DCE
P07 | 台南PS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/69/ComPoint/ABS_89A
P07 | 台南PS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/0/StaDev/PMA
P07 | 台南PS | 11 | 11kV | 320_D1 | #5DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P07_D1 | [17 empty] | lamp2CC | OPRD1: P07/11/320/CB

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P07 | 台南PS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 台南PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | P07/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
P07 | 台南PS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 台南PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | P07/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1510_AMP | 台南仁德線 AMP | LINE161 | P07/161/1510/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1520_AMP | 山上海線 AMP | LINE161 | P07/161/1520/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C16R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 1600.000000 | 2.780000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1530_AMP | 龍崎山線 AMP | LINE161 | P07/161/1530/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1540_AMP | 龍崎海線 AMP | LINE161 | P07/161/1540/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1550_AMP | 台南延平線 AMP | LINE161 | P07/161/1550/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1560_AMP | 台南忠孝二路 AMP | LINE161 | P07/161/1560/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1001 | 900.000000 | 900.000000 | 1001.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.620_AMP | 保安線 AMP | LINE69 | P07/69/620/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.630_AMP | 台南光洲線 AMP | LINE69 | P07/69/630/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.640_AMP | 備用線 AMP | LINE69 |  |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C12R0859 | 773.099976 | 773.099976 | 859.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.660_AMP | 台南後甲海線 AMP | LINE69 | P07/69/660/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C12R0947 | 852.299988 | 852.299988 | 947.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.670_AMP | 台南大灣一路 AMP | LINE69 | P07/69/670/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C12R0878 | 790.200012 | 790.200012 | 878.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.680_AMP | 金榮線 AMP | LINE69 |  |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C04R0399 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.710_AMP | 南仁線 AMP | LINE69 | P07/69/710/I |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C12R0641 | 576.900024 | 576.900024 | 641.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.720_AMP | 台南大灣二路 AMP | LINE69 | P07/69/720/I |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C12R0878 | 790.200012 | 790.200012 | 878.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | P07//1MTR/MVA |  | MVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_LOAD | #1MTR 負載率 | MTR | P07//1MTR/Loading |  | TR_LOAD_200 |  |  | 19 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_PF | #1MTR 功率因素 | MTR | P07//1MTR/PF |  | RPDC_PF_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | P07//1MTR/I |  | AMP_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P07 | 台南PS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | P07//2MTR/MVA |  | MVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_LOAD | #2MTR 負載率 | MTR | P07//2MTR/Loading |  | TR_LOAD_200 |  |  | 23 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_PF | #2MTR 功率因素 | MTR | P07//2MTR/PF |  | RPDC_PF_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | P07//2MTR/I |  | AMP_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P07 | 台南PS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | P07//3MTR/MVA |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_LOAD | #3MTR 負載率 | MTR | P07//3MTR/Loading |  | TR_LOAD_200 |  |  | 27 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_PF | #3MTR 功率因素 | MTR | P07//3MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | P07//3MTR/I |  | AMP_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P07 | 台南PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MW) |  | MW | [25 empty] | ADCS_S | [8 empty] | 台南PS.RPDC_MTR_MW | SUM(161/69KV MTR MW) | MTR |  |  | RPDC_3MTR_MW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MVAR) |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.RPDC_MTR_MVAR | SUM(161/69KV MTR MVAR) | MTR |  |  | RPDC_3MTR_MVAR_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | RPDC_MTR | RPDC |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.RPDC_MTR_PF | RPDC MTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_MVA | #5DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_LOAD | #5DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 34 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_PF | #5DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_MVA | #5DTR二次側(A2) MVA |  |  |  | MVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR(A2) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_LOAD | #5DTR(A2) 負載率 |  |  |  | TR_LOAD_30 |  |  | 37 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR(A2) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_PF | #5DTR(A2) 功率因素 |  |  |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_MVA | #5DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_LOAD | #5DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 40 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_PF | #5DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_MVA | #6DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_LOAD | #6DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 43 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_PF | #6DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_MVA | #7DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_LOAD | #7DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_PF | #7DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_MW | #5DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_MVAR | #5DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 5DTR | #5DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_MVA | #5DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_LOAD | #5DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 51 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.210_SC_MVAR | 11KV#1SC MVAR | SC | P07/11/210/MVAR |  | SC_CAL_11 |  |  | 52 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 410_SC | #11SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.410_SC_MVAR | 11KV#11SC MVAR | SC | P07/11/410/MVAR |  | SC_CAL_11 |  |  | 53 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 420_SC | #12SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.420_SC_MVAR | 11KV#12SC MVAR | SC | P07/11/420/MVAR |  | SC_CAL_11 |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 430_SC | #13SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.430_SC_MVAR | 11KV#13SC MVAR | SC | P07/11/430/MVAR |  | SC_CAL_11 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 440_SC | #14SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.440_SC_MVAR | 11KV#14SC MVAR | SC | P07/11/440/MVAR |  | SC_CAL_11 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 810_SC | #1SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.810_SC_MVAR | 69KV#1SC MVAR | SC | P07/69/810/MVAR |  | SC_CAL_69 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.820_SC_MVAR | 69KV#2SC MVAR | SC | P07/69/820/MVAR |  | SC_CAL_69 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.830_SC_MVAR | 69KV#3SC MVAR | SC | P07/69/830/MVAR |  | SC_CAL_69 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | TRTOT | 台南主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 台南PS.TRTOT_MW | 台南主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_7 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | TRTOT | 台南主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 台南PS.TRTOT_MVAR | 台南主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_7 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台61線KVA | 23KV台61線KVA | FEEDER |  |  | KVA_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台61線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台61線KW | 23KV台61線KW | FEEDER |  |  | KW_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台62線KVA | 23KV台62線KVA | FEEDER |  |  | KVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台62線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台62線KW | 23KV台62線KW | FEEDER |  |  | KW_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台63線KVA | 23KV台63線KVA | FEEDER |  |  | KVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台63線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台63線KW | 23KV台63線KW | FEEDER |  |  | KW_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台64線KVA | 23KV台64線KVA | FEEDER |  |  | KVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台64線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台64線KW | 23KV台64線KW | FEEDER |  |  | KW_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台65線KVA | 23KV台65線KVA | FEEDER |  |  | KVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台65線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台65線KW | 23KV台65線KW | FEEDER |  |  | KW_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台66線KVA | 23KV台66線KVA | FEEDER |  |  | KVA_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台66線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台66線KW | 23KV台66線KW | FEEDER |  |  | KW_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台71線KVA | 23KV台71線KVA | FEEDER |  |  | KVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台71線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台71線KW | 23KV台71線KW | FEEDER |  |  | KW_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台72線KVA | 23KV台72線KVA | FEEDER |  |  | KVA_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台72線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台72線KW | 23KV台72線KW | FEEDER |  |  | KW_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台73線KVA | 23KV台73線KVA | FEEDER |  |  | KVA_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台73線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台73線KW | 23KV台73線KW | FEEDER |  |  | KW_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台74線KVA | 23KV台74線KVA | FEEDER |  |  | KVA_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台74線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台74線KW | 23KV台74線KW | FEEDER |  |  | KW_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台75線KVA | 23KV台75線KVA | FEEDER |  |  | KVA_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台75線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台75線KW | 23KV台75線KW | FEEDER |  |  | KW_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台31線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台31線KVA | 11KV台31線KVA | FEEDER |  |  | KVA_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台31線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台31線KW | 11KV台31線KW | FEEDER |  |  | KW_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台32線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台32線KVA | 11KV台32線KVA | FEEDER |  |  | KVA_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台32線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台32線KW | 11KV台32線KW | FEEDER |  |  | KW_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台33線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台33線KVA | 11KV台33線KVA | FEEDER |  |  | KVA_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台33線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台33線KW | 11KV台33線KW | FEEDER |  |  | KW_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台36線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台36線KVA | 11KV台36線KVA | FEEDER |  |  | KVA_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台36線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台36線KW | 11KV台36線KW | FEEDER |  |  | KW_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台37線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台37線KVA | 11KV台37線KVA | FEEDER |  |  | KVA_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台37線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台37線KW | 11KV台37線KW | FEEDER |  |  | KW_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台38線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台38線KVA | 11KV台38線KVA | FEEDER |  |  | KVA_CAL |  |  | 94 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台38線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台38線KW | 11KV台38線KW | FEEDER |  |  | KW_CAL |  |  | 95 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台41線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台41線KVA | 11KV台41線KVA | FEEDER |  |  | KVA_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台41線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台41線KW | 11KV台41線KW | FEEDER |  |  | KW_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台42線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台42線KVA | 11KV台42線KVA | FEEDER |  |  | KVA_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台42線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台42線KW | 11KV台42線KW | FEEDER |  |  | KW_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台43線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台43線KVA | 11KV台43線KVA | FEEDER |  |  | KVA_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台43線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台43線KW | 11KV台43線KW | FEEDER |  |  | KW_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台44線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台44線KVA | 11KV台44線KVA | FEEDER |  |  | KVA_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台44線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台44線KW | 11KV台44線KW | FEEDER |  |  | KW_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台76線KVA | 23KV台76線KVA | FEEDER |  |  | KVA_CAL |  |  | 104 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台76線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台76線KW | 23KV台76線KW | FEEDER |  |  | KW_CAL |  |  | 105 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台45線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台45線KVA | 11KV台45線KVA | FEEDER |  |  | KVA_CAL |  |  | 106 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台45線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台45線KW | 11KV台45線KW | FEEDER |  |  | KW_CAL |  |  | 107 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台46線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台46線KVA | 11KV台46線KVA | FEEDER |  |  | KVA_CAL |  |  | 108 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台46線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台46線KW | 11KV台46線KW | FEEDER |  |  | KW_CAL |  |  | 109 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.220_SC_MVAR | 11KV#2SC MVAR | SC | P07/11/220/MVAR |  | SC_CAL_11 |  |  | 110 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.250_SC_MVAR | 23KV#5SC MVAR | SC | P07/22/250/MVAR |  | SC_CAL_23 |  |  | 111 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.260_SC_MVAR | 23KV#6SC MVAR | SC | P07/22/260/MVAR |  | SC_CAL_23 |  |  | 112 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 270_SC | #7SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.270_SC_MVAR | 23KV#7SC MVAR | SC | P07/22/270/MVAR |  | SC_CAL_23 |  |  | 113 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | MTR_TOT | 台南MTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 台南PS.MTR_TOT_MW | 台南MTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 114 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | DTR_TOT | 台南DTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 台南PS.DTR_TOT_MW | 台南DTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 115 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台11線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台11線KVA | 11KV台11線KVA | FEEDER |  |  | KVA_CAL |  |  | 116 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台11線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台11線KW | 11KV台11線KW | FEEDER |  |  | KW_CAL |  |  | 117 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台12線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台12線KVA | 11KV台12線KVA | FEEDER |  |  | KVA_CAL |  |  | 118 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台12線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台12線KW | 11KV台12線KW | FEEDER |  |  | KW_CAL |  |  | 119 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台13線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台13線KVA | 11KV台13線KVA | FEEDER |  |  | KVA_CAL |  |  | 120 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台13線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台13線KW | 11KV台13線KW | FEEDER |  |  | KW_CAL |  |  | 121 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台14線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台14線KVA | 11KV台14線KVA | FEEDER |  |  | KVA_CAL |  |  | 122 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台14線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台14線KW | 11KV台14線KW | FEEDER |  |  | KW_CAL |  |  | 123 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台15線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台15線KVA | 11KV台15線KVA | FEEDER |  |  | KVA_CAL |  |  | 124 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台15線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台15線KW | 11KV台15線KW | FEEDER |  |  | KW_CAL |  |  | 125 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台16線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台16線KVA | 11KV台16線KVA | FEEDER |  |  | KVA_CAL |  |  | 126 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台16線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台16線KW | 11KV台16線KW | FEEDER |  |  | KW_CAL |  |  | 127 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台17線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台17線KVA | 11KV台17線KVA | FEEDER |  |  | KVA_CAL |  |  | 128 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台17線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台17線KW | 11KV台17線KW | FEEDER |  |  | KW_CAL |  |  | 129 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台18線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台18線KVA | 11KV台18線KVA | FEEDER |  |  | KVA_CAL |  |  | 130 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台18線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台18線KW | 11KV台18線KW | FEEDER |  |  | KW_CAL |  |  | 131 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台19線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台19線KVA | 11KV台19線KVA | FEEDER |  |  | KVA_CAL |  |  | 132 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台19線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台19線KW | 11KV台19線KW | FEEDER |  |  | KW_CAL |  |  | 133 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台20線KVA | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台20線KVA | 11KV台20線KVA | FEEDER |  |  | KVA_CAL |  |  | 134 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  |  |  |  | 台20線KW | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.台20線KW | 11KV台20線KW | FEEDER |  |  | KW_CAL |  |  | 135 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_MVA | #8DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 136 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_LOAD | #8DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 137 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_PF | #8DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 138 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_MVA | #8DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 139 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_LOAD | #8DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 140 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_PF | #8DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 141 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_MW | #8DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 142 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_MVAR | #8DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 143 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 8DTR | #8DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_MVA | #8DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 144 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_LOAD | #8DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 145 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P07 | 台南PS | 11 | 11kV | 5ABUS | #5ABUS |  | V | [25 empty] | ADCS_S | [8 empty] | 台南PS.11KV#5ABUS_KV | 11KV #5ABUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 146 | CalcAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | 5DTR(C) | #3DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 台南PS.#5DTR(C)_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 147 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 5DTR(C) | #3DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 台南PS.#5DTR(C)_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 148 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | 5DTR(C) | #5DTR(C) |  | PF | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(C)_PF | #5DTR(C) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 149 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P07 | 台南PS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.230_SC_MVAR | 11KV#3SC MVAR | SC | P07/11/230/MVAR |  | SC_CAL_11 |  |  | 150 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 台南PS.240_SC_MVAR | 23KV#4SC MVAR | SC | P07/22/240/MVAR |  | SC_CAL_23 |  |  | 151 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 台南PS.1570_AMP | 台南忠孝一路 AMP | LINE161 | P07/161/1570/I |  | AMP_CAL |  |  | 152 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P07 | 台南PS | 69 | 69kV | 620_CB | 保安線(620_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.620_CB_4 | 620(保安線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 153 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 630_CB | 台南光洲線(630_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.630_CB_4 | 630(台南光洲線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 154 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 640_CB | 備用線(640_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.640_CB_4 | 640(備用線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 155 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 660_CB | 台南後甲海線(660_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.660_CB_4 | 660(台南後甲海線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 156 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 670_CB | 台南大灣一路(670_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.670_CB_4 | 670(台南大灣一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 157 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 720_CB | 台南大灣二路(720_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.720_CB_4 | 720(台南大灣二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 158 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 159 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 160 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 161 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | MTR | MTR |  | A_M | [25 empty] | RPDC_AD | [8 empty] | 台南PS.MTR_A/M | MTR OLTC A/M | MTR |  |  | LCP_3PTR |  |  | 162 | CalcDIPoint | [38 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 1750_CB | #5DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.1750_CB_4 | 1750(#5DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 163 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 330_CB | #6DTR(330_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.330_CB_4 | 330(#6DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 164 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 350_CB | #7DTR(350_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.350_CB_4 | 350(#7DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 165 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 1760_CB | #6DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.1760_CB_4 | 1760(#6DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 166 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 1770_CB | #7DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.1770_CB_4 | 1770(#7DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 167 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 370_CB | #8DTR(370_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.370_CB_4 | 370(#8DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 168 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 410_CB | #11SC(410_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.410_CB_4 | 410(11KV #11SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 169 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 420_CB | #12SC(420_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.420_CB_4 | 420(11KV #12SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 170 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 430_CB | #13SC(430_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.430_CB_4 | 430(11KV #13SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 171 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 440_CB | #14SC(440_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.440_CB_4 | 440(11KV #14SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 172 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 173 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | _OSCA | 示波器啟動警報 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.69KV_OSCA_4 | 69KV示波器啟動警報 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 174 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | DTR_CBA(2) | DTR_CBA(2) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.DTR_CBA(2)_4 | #5BDTR-11KV-CBA(D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 175 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | DTR_CBA(3) | #5A-6-7-8DTR-23/-CBA(DTR_CBA(3)) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.DTR_CBA(3)_4 | #5A-6-7-8DTR-23/11KV-CBA (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 176 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | DTR_CBF(2) | #5B-DTR--CBF(DTR_CBF(2)) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.DTR_CBF(2)_4 | #5B-DTR-11KV-CBF (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 177 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | DTR_CBF(3) | #5A-6-7-8DTR-23/-CBF(DTR_CBF(3)) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.DTR_CBF(3)_4 | #5A-6-7-8DTR-23/11KV-CBF (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 178 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 179 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P07 | 台南PS | 0 |  | TEST_CB | TEST(TEST_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.TEST_CB_4 | TEST CB (D4) | OTHER |  |  | AD_LAMP_DD_1 |  |  | 180 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 台南PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | P07/0/CalcPoint/SUBA |  | STATION_FAULT_32 |  |  | 181 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 台南PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | P07/0/CalcPoint/SUBF |  | STATION_FAULT_7 |  |  | 182 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 183 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 184 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510_AMP | 台南仁德線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1510_AMP_A | 台南仁德線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 185 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 161 | 161kV | 1520_AMP | 山上海線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1520_AMP_A | 山上海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 186 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 161 | 161kV | 1530_AMP | 龍崎山線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1530_AMP_A | 龍崎山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 187 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 161 | 161kV | 1540_AMP | 龍崎海線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1540_AMP_A | 龍崎海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 188 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 161 | 161kV | 1550_AMP | 台南延平線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1550_AMP_A | 台南延平線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 189 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 161 | 161kV | 1560_AMP | 台南忠孝二路 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1560_AMP_A | 台南忠孝二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 190 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 620_AMP | 保安線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.620_AMP_A | 保安線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 191 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 620_AMP | 保安線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.620_AMP_4 | 保安線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 192 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 630_AMP | 台南光洲線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.630_AMP_A | 台南光洲線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 193 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 630_AMP | 台南光洲線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.630_AMP_4 | 台南光洲線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 194 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 640_AMP | 備用線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.640_AMP_A | 備用線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 195 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 640_AMP | 備用線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.640_AMP_4 | 備用線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 196 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 660_AMP | 台南後甲海線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.660_AMP_A | 台南後甲海線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 197 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 660_AMP | 台南後甲海線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.660_AMP_4 | 台南後甲海線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 198 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 670_AMP | 台南大灣一路 | [27 empty] | ADCS_S | [8 empty] | 台南PS.670_AMP_A | 台南大灣一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 199 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 670_AMP | 台南大灣一路 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.670_AMP_4 | 台南大灣一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 200 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 680_AMP | 金榮線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.680_AMP_A | 金榮線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 201 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 710_AMP | 南仁線 | [27 empty] | ADCS_S | [8 empty] | 台南PS.710_AMP_A | 南仁線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 202 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 710_AMP | 南仁線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.710_AMP_4 | 南仁線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 203 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 69 | 69kV | 720_AMP | 台南大灣二路 | [27 empty] | ADCS_S | [8 empty] | 台南PS.720_AMP_A | 台南大灣二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 204 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_MVA_A | #1MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 205 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | P07//1MTR/TR_PERM |  | MTR_PERM |  |  | 206 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_MVA_A | #2MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 207 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | P07//2MTR/TR_PERM |  | MTR_PERM |  |  | 208 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_MVA_A | #3MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 209 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | P07//3MTR/TR_PERM |  | MTR_PERM |  |  | 210 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_PERM | #5DTR(A) TAP PERMISSION POINT | MTR | P07//5DTR(A)/TR_PERM |  | DTR_PERM |  |  | 211 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_PERM | #5DTR TAP PERMISSION POINT | MTR | P07//5DTR(B)/TR_PERM |  | DTR_PERM |  |  | 212 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_PERM | #6DTR TAP PERMISSION POINT | MTR | P07//6DTR/TR_PERM |  | DTR_PERM |  |  | 213 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_PERM | #7DTR TAP PERMISSION POINT | MTR | P07//7DTR/TR_PERM |  | DTR_PERM |  |  | 214 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5DTR_MVA | #5DTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_MVA_A | #5DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 215 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5DTR_MVA | #5DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.#5DTR_MVA_4 | #5DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 216 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5DTR_MVA | #5DTR |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.#5DTR_MVA_5 | #5DTR MVA 點燈 (D4) |  |  |  | MAP_SET |  |  | 217 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 6DTR_MVA | #6DTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_MVA_A | #6DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 218 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 6DTR_MVA | #6DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.#6DTR_MVA_4 | #6DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 219 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 7DTR_MVA | #7DTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_MVA_A | #7DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 220 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 7DTR_MVA | #7DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.#7DTR_MVA_4 | #7DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 221 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 台南PS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 222 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 223 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 224 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 225 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.270_CB_4 | 270(23KV #7SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 226 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310A1_CB | #5DTR(310A1_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.310A1_CB_4 | 310A1(#5DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 227 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310A2_CB | #5DTR(310A2_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.310A2_CB_4 | 310A2(#5DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 228 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 320_CB | #5DTR(320_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.320_CB_4 | 320(#5DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 229 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 400_CB | 400(400_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.400_CB_4 | 400 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 230 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 1780_CB | #8DTR(1780_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.1780_CB_4 | 1780(#8DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 231 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 380_CB | #8DTR(380_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.380_CB_4 | 380(#8DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 232 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_PERM | #8DTR(A) TAP PERMISSION POINT | MTR | P07//8DTR(A)/TR_PERM |  | DTR_PERM |  |  | 233 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_PERM | #8DTR TAP PERMISSION POINT | MTR | P07//8DTR(B)/TR_PERM |  | DTR_PERM |  |  | 234 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 8DTR_MVA | #8DTR | [27 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_MVA_A | #8DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 235 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 8DTR_MVA | #8DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.#8DTR_MVA_4 | #8DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 236 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 8ABUS | #8ABUS |  | 11KV#8ABUSC | [25 empty] | CDCS | [8 empty] | 台南PS.11KV#8ABUSC | #8ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 237 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 8BBUS | #8BBUS |  | 11KV#8BBUSC | [25 empty] | CDCS | [8 empty] | 台南PS.11KV#8BBUSC | #8BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 238 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5A1BUS | #5A1BUS |  | 11KV#5A1BUSC | [25 empty] | CDCS | [8 empty] | 台南PS.11KV#5A1BUSC | #5A1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 239 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5A2BUS | #5A2BUS |  | 11KV#5A2BUSC | [25 empty] | CDCS | [8 empty] | 台南PS.11KV#5A2BUSC | #5A2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 240 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5BBUS | #5BBUS |  | 11KV#5BBUSC | [25 empty] | CDCS | [8 empty] | 台南PS.11KV#5BBUSC | #5BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 241 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 6BUS | #6BUS |  | 23KV#6BUSC | [25 empty] | CDCS | [8 empty] | 台南PS.23KV#6BUSC | #6BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 242 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 7BUS | #7BUS |  | 23KV#7BUSC | [25 empty] | CDCS | [8 empty] | 台南PS.23KV#7BUSC | #7BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 243 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 台南PS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 244 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 台南PS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B7 |  |  | 245 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 台南PS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 246 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 247 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 台南PS.240_CB_4 | 240(23KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 248 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1570_AMP | 台南忠孝一路 | [27 empty] | ADCS_S | [8 empty] | 台南PS.1570_AMP_A | 台南忠孝一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 249 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P07 | 台南PS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 台南PS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 250 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | P07/0/RTU/ADCH1 |  |  |  | CDC | 251 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | P07/0/RTU/ADCH2 |  |  |  | CDC | 252 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | P07/0/RTU/ADCH3 |  |  |  | CDC | 253 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | P07/0/RTU/ADCH4 |  |  |  | CDC | 254 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | P07/0/RTU/ADCH5 |  |  |  | CDC | 255 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | P07/0/RTU/ADCL1 |  |  |  | CDC | 256 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | P07/0/RTU/ADCL2 |  |  |  | CDC | 257 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | P07/0/RTU/ADCL3 |  |  |  | CDC | 258 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | P07/0/RTU/ADCL4 |  |  |  | CDC | 259 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | P07/0/RTU/ADCL5 |  |  |  | CDC | 260 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | P07/161/1BUS/V |  |  |  | CDC | 261 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | P07/161/2BUS/V |  |  |  | CDC | 262 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P07 | 台南PS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-B6 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | P07/69/1BUS/V |  |  |  | CDC | 263 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P07 | 台南PS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-B7 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | P07/69/2BUS/V |  |  |  | CDC | 264 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P07 | 台南PS | 11 | 11kV | 5A1BUS | #5A1BUS |  | V | [17 empty] | 2-88 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV#5A1BUS_KV | 11KV #5A1BUS KV | BUS | P07/11/5A1BUS/V |  |  |  | CDC | 265 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 5A2BUS | #5A2BUS |  | V | [17 empty] | 2-A6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV#5A2BUS_KV | 11KV #5A2BUS KV | BUS | P07/11/5A2BUS/V |  |  |  | CDC | 266 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 5BBUS | #5BBUS |  | V | [17 empty] | 3-82 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV#5BBUS_KV | 11KV #5BBUS KV | BUS | P07/11/5BBUS/V |  |  |  | CDC | 267 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 22 | 22kV | 6BUS | #6BUS |  | V | [17 empty] | 1-E0 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.23KV#6BUS_KV | 23KV #6BUS KV | BUS | P07/22/6BUS/V |  |  |  | CDC | 268 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P07 | 台南PS | 22 | 22kV | 7BUS | #7BUS |  | V | [17 empty] | 2-AC | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.23KV#7BUS_KV | 23KV #7BUS KV | BUS | P07/22/7BUS/V |  |  |  | CDC | 269 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1510_MW | 台南仁德線 MW | LINE161 | P07/161/1510/MW |  |  |  | CDC | 270 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1510_MVAR | 台南仁德線 MVAR | LINE161 | P07/161/1510/MVAR |  |  |  | CDC | 271 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510LPD | 台南仁德線(1510) |  | V | [17 empty] | 1-FE | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1510LPD_KV | 台南仁德線(1510) LPD KV | LINE161 | P07/161/1510/V |  |  |  | CDC | 272 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1520_MW | 山上海線 MW | LINE161 | P07/161/1520/MW |  |  |  | CDC | 273 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1520_MVAR | 山上海線 MVAR | LINE161 | P07/161/1520/MVAR |  |  |  | CDC | 274 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1520LPD | 山上海線(1520) |  | V | [17 empty] | 1-FF | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1520LPD_KV | 山上海線(1520) LPD KV | LINE161 | P07/161/1520/V |  |  |  | CDC | 275 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1530_MW | 龍崎山線 MW | LINE161 | P07/161/1530/MW |  |  |  | CDC | 276 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1530_MVAR | 龍崎山線 MVAR | LINE161 | P07/161/1530/MVAR |  |  |  | CDC | 277 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1530LPD | 龍崎山線(1530) |  | V | [17 empty] | 1-DE | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1530LPD_KV | 龍崎山線(1530) LPD KV | LINE161 | P07/161/1530/V |  |  |  | CDC | 278 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1540_MW | 龍崎海線 MW | LINE161 | P07/161/1540/MW |  |  |  | CDC | 279 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1540_MVAR | 龍崎海線 MVAR | LINE161 | P07/161/1540/MVAR |  |  |  | CDC | 280 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1540LPD | 龍崎海線(1540) |  | V | [17 empty] | 1-DF | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1540LPD_KV | 龍崎海線(1540) LPD KV | LINE161 | P07/161/1540/V |  |  |  | CDC | 281 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1550_MW | 台南延平線 MW | LINE161 | P07/161/1550/MW |  |  |  | CDC | 282 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1550_MVAR | 台南延平線 MVAR | LINE161 | P07/161/1550/MVAR |  |  |  | CDC | 283 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1560_MW | 台南忠孝二路 MW | LINE161 | P07/161/1560/MW |  |  |  | CDC | 284 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1560_MVAR | 台南忠孝二路 MVAR | LINE161 | P07/161/1560/MVAR |  |  |  | CDC | 285 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | MW | [17 empty] | 1-CE | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.620_MW | 保安線 MW | LINE69 | P07/69/620/MW |  |  |  | CDC | 286 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | MVAR | [17 empty] | 1-CF | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.620_MVAR | 保安線 MVAR | LINE69 | P07/69/620/MVAR |  |  |  | CDC | 287 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.630_MW | 台南光洲線 MW | LINE69 | P07/69/630/MW |  |  |  | CDC | 288 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.630_MVAR | 台南光洲線 MVAR | LINE69 | P07/69/630/MVAR |  |  |  | CDC | 289 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | MW | [17 empty] | 1-CA | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.640_MW | 備用線 MW | LINE69 |  |  |  |  | CDC | 290 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | MVAR | [17 empty] | 1-CB | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.640_MVAR | 備用線 MVAR | LINE69 |  |  |  |  | CDC | 291 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | MW | [17 empty] | 1-C6 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.660_MW | 台南後甲海線 MW | LINE69 | P07/69/660/MW |  |  |  | CDC | 292 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | MVAR | [17 empty] | 1-C7 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.660_MVAR | 台南後甲海線 MVAR | LINE69 | P07/69/660/MVAR |  |  |  | CDC | 293 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | MW | [17 empty] | 1-C4 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.670_MW | 台南大灣一路 MW | LINE69 | P07/69/670/MW |  |  |  | CDC | 294 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | MVAR | [17 empty] | 1-C5 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.670_MVAR | 台南大灣一路 MVAR | LINE69 | P07/69/670/MVAR |  |  |  | CDC | 295 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | MW | [17 empty] | 1-BE | [5 empty] | MW_-48_48(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.680_MW | 金榮線 MW | LINE69 |  |  |  |  | CDC | 296 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | MVAR | [17 empty] | 1-BF | [5 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.680_MVAR | 金榮線 MVAR | LINE69 |  |  |  |  | CDC | 297 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | MW | [17 empty] | 1-BC | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.710_MW | 南仁線 MW | LINE69 | P07/69/710/MW |  |  |  | CDC | 298 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | MVAR | [17 empty] | 1-BD | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.710_MVAR | 南仁線 MVAR | LINE69 | P07/69/710/MVAR |  |  |  | CDC | 299 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | MW | [17 empty] | 1-BA | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.720_MW | 台南大灣二路 MW | LINE69 | P07/69/720/MW |  |  |  | CDC | 300 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | MVAR | [17 empty] | 1-BB | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.720_MVAR | 台南大灣二路 MVAR | LINE69 | P07/69/720/MVAR |  |  |  | CDC | 301 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P07 | 台南PS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1500TIE_AMP | 1500TIE AMP | TIE | P07/161/1500/I_R |  |  |  | CDC | 302 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-D6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.600TIE_AMP | 600TIE AMP | TIE | P07/69/600/I_R |  |  |  | CDC | 303 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-D8 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#1MTR_MW | #1MTR二次側 MW | MTR | P07/69/750/MW |  |  |  | CDC | 304 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-D9 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | P07/69/750/MVAR |  |  |  | CDC | 305 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-95 |  | 1-29 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | P07//1MTR/TapPosMv |  |  |  | CDC | 306 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-96 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#1MTR_OIL | #1MTR 油溫 | MTR | P07//1MTR/OilTemp |  |  |  | CDC | 307 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-97 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#1MTR_COIL | #1MTR 線溫 | MTR | P07//1MTR/CoilTemp |  |  |  | CDC | 308 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-DA | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#2MTR_MW | #2MTR二次側 MW | MTR | P07/69/760/MW |  |  |  | CDC | 309 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-DB | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | P07/69/760/MVAR |  |  |  | CDC | 310 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-98 |  | 1-2D |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | P07//2MTR/TapPosMv |  |  |  | CDC | 311 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#2MTR_OIL | #2MTR 油溫 | MTR | P07//2MTR/OilTemp |  |  |  | CDC | 312 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#2MTR_COIL | #2MTR 線溫 | MTR | P07//2MTR/CoilTemp |  |  |  | CDC | 313 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-DC | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#3MTR_MW | #3MTR二次側 MW | MTR | P07/69/770/MW |  |  |  | CDC | 314 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P07 | 台南PS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-DD | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | P07/69/770/MVAR |  |  |  | CDC | 315 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-31 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | P07//3MTR/TapPosMv |  |  |  | CDC | 316 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-9C | [5 empty] | OIL_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#3MTR_OIL | #3MTR 油溫 | MTR | P07//3MTR/OilTemp |  |  |  | CDC | 317 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.300000
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-9D | [5 empty] | COIL_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#3MTR_COIL | #3MTR 線溫 | MTR | P07//3MTR/CoilTemp |  |  |  | CDC | 318 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.300000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | MW | [17 empty] | 2-89 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_MW | #5DTR二次側(A) MW | MTR | P07/11/310A1/KW |  |  |  | CDC | 319 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | MVAR | [17 empty] | 2-8A | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_MVAR | #5DTR二次側(A) MVAR | MTR | P07/11/310A1/KVAR |  |  |  | CDC | 320 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | I_R | [17 empty] | 2-8B | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_A1 | #5DTR二次側(A) R相AMP | MTR | P07/11/310A1/I_R |  |  |  | CDC | 321 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | I_S | [17 empty] | 2-8C | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_A2 | #5DTR二次側(A) S相AMP | MTR | P07/11/310A1/I_S |  |  |  | CDC | 322 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR二次側(A) |  | I_T | [17 empty] | 2-8D | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_A3 | #5DTR二次側(A) T相AMP | MTR | P07/11/310A1/I_T |  |  |  | CDC | 323 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | OilTemp | [17 empty] | 1-A0 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR_OIL | #5DTR 油溫 | MTR | P07//5DTR/OilTemp |  |  |  | CDC | 324 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | CoilTemp | [17 empty] | 1-A1 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_COIL | #5DTR(A) 線溫 | MTR | P07//5DTR(A)/CoilTemp |  |  |  | CDC | 325 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | TapPosMv | [17 empty] | 1-A3 |  | 1-39 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_TAP | #5DTR(A) OLTC TAP | MTR | P07//5DTR(A)/TapPosMv |  |  |  | CDC | 326 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | MW | [17 empty] | 2-A7 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_MW | #5DTR二次側(A2) MW | MTR | P07/11/310A2/KW |  |  |  | CDC | 327 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | MVAR | [17 empty] | 2-A8 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_MVAR | #5DTR二次側(A2) MVAR | MTR | P07/11/310A2/KVAR |  |  |  | CDC | 328 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | I_R | [17 empty] | 2-A9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_A1 | #5DTR二次側(A2) R相AMP | MTR | P07/11/310A2/I_R |  |  |  | CDC | 329 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | I_S | [17 empty] | 2-AA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_A2 | #5DTR二次側(A2) S相AMP | MTR | P07/11/310A2/I_S |  |  |  | CDC | 330 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(A2) | #5DTR二次側(A2) |  | I_T | [17 empty] | 2-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(A2)_A3 | #5DTR二次側(A2) T相AMP | MTR | P07/11/310A2/I_T |  |  |  | CDC | 331 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | MW | [17 empty] | 3-83 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_MW | #5DTR二次側(B) MW | MTR | P07/11/320/KW |  |  |  | CDC | 332 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | MVAR | [17 empty] | 3-84 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_MVAR | #5DTR二次側(B) MVAR | MTR | P07/11/320/KVAR |  |  |  | CDC | 333 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | I_R | [17 empty] | 3-85 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_A1 | #5DTR二次側(B) R相AMP | MTR | P07/11/320/I_R |  |  |  | CDC | 334 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | I_S | [17 empty] | 3-86 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_A2 | #5DTR二次側(B) S相AMP | MTR | P07/11/320/I_S |  |  |  | CDC | 335 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR二次側(B) |  | I_T | [17 empty] | 3-87 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_A3 | #5DTR二次側(B) T相AMP | MTR | P07/11/320/I_T |  |  |  | CDC | 336 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | CoilTemp | [17 empty] | 1-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_COIL | #5DTR(B) 線溫 | MTR | P07//5DTR(B)/CoilTemp |  |  |  | CDC | 337 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | TapPosMv | [17 empty] | 1-A4 |  | 1-3B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_TAP | #5DTR(B) OLTC TAP | MTR | P07//5DTR(B)/TapPosMv |  |  |  | CDC | 338 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | MW | [17 empty] | 1-E1 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_MW | #6DTR二次側 MW | MTR | P07/22/330/KW |  |  |  | CDC | 339 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | MVAR | [17 empty] | 1-E2 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_MVAR | #6DTR二次側 MVAR | MTR | P07/22/330/KVAR |  |  |  | CDC | 340 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | I_R | [17 empty] | 1-E3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_A1 | #6DTR二次側 R相AMP | MTR | P07/22/330/I_R |  |  |  | CDC | 341 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | I_S | [17 empty] | 1-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_A2 | #6DTR二次側 S相AMP | MTR | P07/22/330/I_S |  |  |  | CDC | 342 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 6DTR | #6DTR二次側 |  | I_T | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_A3 | #6DTR二次側 T相AMP | MTR | P07/22/330/I_T |  |  |  | CDC | 343 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | OilTemp | [17 empty] | 1-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_OIL | #6DTR 油溫 | MTR | P07//6DTR/OilTemp |  |  |  | CDC | 344 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | CoilTemp | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_COIL | #6DTR 線溫 | MTR | P07//6DTR/CoilTemp |  |  |  | CDC | 345 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | TapPosMv | [17 empty] | 1-A9 |  | 1-3D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#6DTR_TAP | #6DTR OLTC TAP | MTR | P07//6DTR/TapPosMv |  |  |  | CDC | 346 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | MW | [17 empty] | 2-AD | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_MW | #7DTR二次側 MW | MTR | P07/22/350/KW |  |  |  | CDC | 347 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | MVAR | [17 empty] | 2-AE | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_MVAR | #7DTR二次側 MVAR | MTR | P07/22/350/KVAR |  |  |  | CDC | 348 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | I_R | [17 empty] | 2-AF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_A1 | #7DTR二次側 R相AMP | MTR | P07/22/350/I_R |  |  |  | CDC | 349 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | I_S | [17 empty] | 2-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_A2 | #7DTR二次側 S相AMP | MTR | P07/22/350/I_S |  |  |  | CDC | 350 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 7DTR | #7DTR二次側 |  | I_T | [17 empty] | 2-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_A3 | #7DTR二次側 T相AMP | MTR | P07/22/350/I_T |  |  |  | CDC | 351 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | OilTemp | [17 empty] | 1-AB | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_OIL | #7DTR 油溫 | MTR | P07//7DTR/OilTemp |  |  |  | CDC | 352 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | CoilTemp | [17 empty] | 1-AC | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_COIL | #7DTR 線溫 | MTR | P07//7DTR/CoilTemp |  |  |  | CDC | 353 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | TapPosMv | [17 empty] | 1-AE |  | 1-41 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#7DTR_TAP | #7DTR OLTC TAP | MTR | P07//7DTR/TapPosMv |  |  |  | CDC | 354 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-D5 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.直流N電源電壓 | 直流N電源電壓 | OTHER | P07/0/StaDev/DCV_N |  |  |  | CDC | 355 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P07 | 台南PS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-D4 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.直流P電源電壓 | 直流P電源電壓 | OTHER | P07/0/StaDev/DCV_P |  |  |  | CDC | 356 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台61線 | 台61線 |  | 台61線KVAR | [17 empty] | 1-E6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台61線KVAR | 23KV台61線 KVAR | FEEDER | P07/22/KH61/KVAR |  |  |  | CDC | 357 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台61線 | 台61線 |  | 台61線A1 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台61線A1 | 23KV台61線 R相AMP | FEEDER | P07/22/KH61/I_R |  |  |  | CDC | 358 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台61線 | 台61線 |  | 台61線A2 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台61線A2 | 23KV台61線 S相AMP | FEEDER | P07/22/KH61/I_S |  |  |  | CDC | 359 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台61線 | 台61線 |  | 台61線A3 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台61線A3 | 23KV台61線 T相AMP | FEEDER | P07/22/KH61/I_T |  |  |  | CDC | 360 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台62線 | 台62線 |  | 台62線KVAR | [17 empty] | 1-EA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台62線KVAR | 23KV台62線 KVAR | FEEDER | P07/22/KH62/KVAR |  |  |  | CDC | 361 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台62線 | 台62線 |  | 台62線A1 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台62線A1 | 23KV台62線 R相AMP | FEEDER | P07/22/KH62/I_R |  |  |  | CDC | 362 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台62線 | 台62線 |  | 台62線A2 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台62線A2 | 23KV台62線 S相AMP | FEEDER | P07/22/KH62/I_S |  |  |  | CDC | 363 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台62線 | 台62線 |  | 台62線A3 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台62線A3 | 23KV台62線 T相AMP | FEEDER | P07/22/KH62/I_T |  |  |  | CDC | 364 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台63線 | 台63線 |  | 台63線KVAR | [17 empty] | 1-EE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台63線KVAR | 23KV台63線 KVAR | FEEDER | P07/22/KH63/KVAR |  |  |  | CDC | 365 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台63線 | 台63線 |  | 台63線A1 | [17 empty] | 1-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台63線A1 | 23KV台63線 R相AMP | FEEDER | P07/22/KH63/I_R |  |  |  | CDC | 366 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台63線 | 台63線 |  | 台63線A2 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台63線A2 | 23KV台63線 S相AMP | FEEDER | P07/22/KH63/I_S |  |  |  | CDC | 367 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台63線 | 台63線 |  | 台63線A3 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台63線A3 | 23KV台63線 T相AMP | FEEDER | P07/22/KH63/I_T |  |  |  | CDC | 368 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台64線 | 台64線 |  | 台64線KVAR | [17 empty] | 1-F2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台64線KVAR | 23KV台64線 KVAR | FEEDER | P07/22/KH64/KVAR |  |  |  | CDC | 369 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台64線 | 台64線 |  | 台64線A1 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台64線A1 | 23KV台64線 R相AMP | FEEDER | P07/22/KH64/I_R |  |  |  | CDC | 370 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台64線 | 台64線 |  | 台64線A2 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台64線A2 | 23KV台64線 S相AMP | FEEDER | P07/22/KH64/I_S |  |  |  | CDC | 371 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台64線 | 台64線 |  | 台64線A3 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台64線A3 | 23KV台64線 T相AMP | FEEDER | P07/22/KH64/I_T |  |  |  | CDC | 372 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台65線 | 台65線 |  | 台65線KVAR | [17 empty] | 1-F6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台65線KVAR | 23KV台65線 KVAR | FEEDER | P07/22/KH65/KVAR |  |  |  | CDC | 373 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台65線 | 台65線 |  | 台65線A1 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台65線A1 | 23KV台65線 R相AMP | FEEDER | P07/22/KH65/I_R |  |  |  | CDC | 374 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台65線 | 台65線 |  | 台65線A2 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台65線A2 | 23KV台65線 S相AMP | FEEDER | P07/22/KH65/I_S |  |  |  | CDC | 375 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台65線 | 台65線 |  | 台65線A3 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台65線A3 | 23KV台65線 T相AMP | FEEDER | P07/22/KH65/I_T |  |  |  | CDC | 376 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台66線 | 台66線 |  | 台66線KVAR | [17 empty] | 1-FA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台66線KVAR | 23KV台66線 KVAR | FEEDER | P07/22/KH66/KVAR |  |  |  | CDC | 377 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台66線 | 台66線 |  | 台66線A1 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台66線A1 | 23KV台66線 R相AMP | FEEDER | P07/22/KH66/I_R |  |  |  | CDC | 378 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台66線 | 台66線 |  | 台66線A2 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台66線A2 | 23KV台66線 S相AMP | FEEDER | P07/22/KH66/I_S |  |  |  | CDC | 379 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台66線 | 台66線 |  | 台66線A3 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台66線A3 | 23KV台66線 T相AMP | FEEDER | P07/22/KH66/I_T |  |  |  | CDC | 380 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台71線 | 台71線 |  | 台71線KVAR | [17 empty] | 2-B2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台71線KVAR | 23KV台71線 KVAR | FEEDER | P07/22/KH71/KVAR |  |  |  | CDC | 381 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台71線 | 台71線 |  | 台71線A1 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台71線A1 | 23KV台71線 R相AMP | FEEDER | P07/22/KH71/I_R |  |  |  | CDC | 382 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台71線 | 台71線 |  | 台71線A2 | [17 empty] | 2-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台71線A2 | 23KV台71線 S相AMP | FEEDER | P07/22/KH71/I_S |  |  |  | CDC | 383 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台71線 | 台71線 |  | 台71線A3 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台71線A3 | 23KV台71線 T相AMP | FEEDER | P07/22/KH71/I_T |  |  |  | CDC | 384 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台72線 | 台72線 |  | 台72線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台72線KVAR | 23KV台72線 KVAR | FEEDER | P07/22/KH72/KVAR |  |  |  | CDC | 385 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台72線 | 台72線 |  | 台72線A1 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台72線A1 | 23KV台72線 R相AMP | FEEDER | P07/22/KH72/I_R |  |  |  | CDC | 386 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台72線 | 台72線 |  | 台72線A2 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台72線A2 | 23KV台72線 S相AMP | FEEDER | P07/22/KH72/I_S |  |  |  | CDC | 387 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台72線 | 台72線 |  | 台72線A3 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台72線A3 | 23KV台72線 T相AMP | FEEDER | P07/22/KH72/I_T |  |  |  | CDC | 388 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台73線 | 台73線 |  | 台73線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台73線KVAR | 23KV台73線 KVAR | FEEDER | P07/22/KH73/KVAR |  |  |  | CDC | 389 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台73線 | 台73線 |  | 台73線A1 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台73線A1 | 23KV台73線 R相AMP | FEEDER | P07/22/KH73/I_R |  |  |  | CDC | 390 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台73線 | 台73線 |  | 台73線A2 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台73線A2 | 23KV台73線 S相AMP | FEEDER | P07/22/KH73/I_S |  |  |  | CDC | 391 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台73線 | 台73線 |  | 台73線A3 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台73線A3 | 23KV台73線 T相AMP | FEEDER | P07/22/KH73/I_T |  |  |  | CDC | 392 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台74線 | 台74線 |  | 台74線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台74線KVAR | 23KV台74線 KVAR | FEEDER | P07/22/KH74/KVAR |  |  |  | CDC | 393 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台74線 | 台74線 |  | 台74線A1 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台74線A1 | 23KV台74線 R相AMP | FEEDER | P07/22/KH74/I_R |  |  |  | CDC | 394 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台74線 | 台74線 |  | 台74線A2 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台74線A2 | 23KV台74線 S相AMP | FEEDER | P07/22/KH74/I_S |  |  |  | CDC | 395 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台74線 | 台74線 |  | 台74線A3 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台74線A3 | 23KV台74線 T相AMP | FEEDER | P07/22/KH74/I_T |  |  |  | CDC | 396 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台75線 | 台75線 |  | 台75線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台75線KVAR | 23KV台75線 KVAR | FEEDER | P07/22/KH75/KVAR |  |  |  | CDC | 397 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台75線 | 台75線 |  | 台75線A1 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台75線A1 | 23KV台75線 R相AMP | FEEDER | P07/22/KH75/I_R |  |  |  | CDC | 398 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台75線 | 台75線 |  | 台75線A2 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台75線A2 | 23KV台75線 S相AMP | FEEDER | P07/22/KH75/I_S |  |  |  | CDC | 399 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台75線 | 台75線 |  | 台75線A3 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台75線A3 | 23KV台75線 T相AMP | FEEDER | P07/22/KH75/I_T |  |  |  | CDC | 400 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台31線 | 台31線 |  | 台31線KVAR | [17 empty] | 2-8E | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台31線KVAR | 11KV台31線 KVAR | FEEDER | P07/11/KH31/KVAR |  |  |  | CDC | 401 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台31線 | 台31線 |  | 台31線A1 | [17 empty] | 2-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台31線A1 | 11KV台31線 R相AMP | FEEDER | P07/11/KH31/I_R |  |  |  | CDC | 402 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台31線 | 台31線 |  | 台31線A2 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台31線A2 | 11KV台31線 S相AMP | FEEDER | P07/11/KH31/I_S |  |  |  | CDC | 403 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台31線 | 台31線 |  | 台31線A3 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台31線A3 | 11KV台31線 T相AMP | FEEDER | P07/11/KH31/I_T |  |  |  | CDC | 404 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台32線 | 台32線 |  | 台32線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台32線KVAR | 11KV台32線 KVAR | FEEDER | P07/11/KH32/KVAR |  |  |  | CDC | 405 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台32線 | 台32線 |  | 台32線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台32線A1 | 11KV台32線 R相AMP | FEEDER | P07/11/KH32/I_R |  |  |  | CDC | 406 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台32線 | 台32線 |  | 台32線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台32線A2 | 11KV台32線 S相AMP | FEEDER | P07/11/KH32/I_S |  |  |  | CDC | 407 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台32線 | 台32線 |  | 台32線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台32線A3 | 11KV台32線 T相AMP | FEEDER | P07/11/KH32/I_T |  |  |  | CDC | 408 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台33線 | 台33線 |  | 台33線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台33線KVAR | 11KV台33線 KVAR | FEEDER | P07/11/KH33/KVAR |  |  |  | CDC | 409 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台33線 | 台33線 |  | 台33線A1 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台33線A1 | 11KV台33線 R相AMP | FEEDER | P07/11/KH33/I_R |  |  |  | CDC | 410 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台33線 | 台33線 |  | 台33線A2 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台33線A2 | 11KV台33線 S相AMP | FEEDER | P07/11/KH33/I_S |  |  |  | CDC | 411 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台33線 | 台33線 |  | 台33線A3 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台33線A3 | 11KV台33線 T相AMP | FEEDER | P07/11/KH33/I_T |  |  |  | CDC | 412 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台36線 | 台36線 |  | 台36線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台36線KVAR | 11KV台36線 KVAR | FEEDER | P07/11/KH36/KVAR |  |  |  | CDC | 413 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台36線 | 台36線 |  | 台36線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台36線A1 | 11KV台36線 R相AMP | FEEDER | P07/11/KH36/I_R |  |  |  | CDC | 414 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台36線 | 台36線 |  | 台36線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台36線A2 | 11KV台36線 S相AMP | FEEDER | P07/11/KH36/I_S |  |  |  | CDC | 415 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台36線 | 台36線 |  | 台36線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台36線A3 | 11KV台36線 T相AMP | FEEDER | P07/11/KH36/I_T |  |  |  | CDC | 416 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台37線 | 台37線 |  | 台37線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台37線KVAR | 11KV台37線 KVAR | FEEDER | P07/11/KH37/KVAR |  |  |  | CDC | 417 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台37線 | 台37線 |  | 台37線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台37線A1 | 11KV台37線 R相AMP | FEEDER | P07/11/KH37/I_R |  |  |  | CDC | 418 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台37線 | 台37線 |  | 台37線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台37線A2 | 11KV台37線 S相AMP | FEEDER | P07/11/KH37/I_S |  |  |  | CDC | 419 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台37線 | 台37線 |  | 台37線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台37線A3 | 11KV台37線 T相AMP | FEEDER | P07/11/KH37/I_T |  |  |  | CDC | 420 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台38線 | 台38線 |  | 台38線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台38線KVAR | 11KV台38線 KVAR | FEEDER | P07/11/KH38/KVAR |  |  |  | CDC | 421 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台38線 | 台38線 |  | 台38線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台38線A1 | 11KV台38線 R相AMP | FEEDER | P07/11/KH38/I_R |  |  |  | CDC | 422 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台38線 | 台38線 |  | 台38線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台38線A2 | 11KV台38線 S相AMP | FEEDER | P07/11/KH38/I_S |  |  |  | CDC | 423 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台38線 | 台38線 |  | 台38線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台38線A3 | 11KV台38線 T相AMP | FEEDER | P07/11/KH38/I_T |  |  |  | CDC | 424 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台41線 | 台41線 |  | 台41線KVAR | [17 empty] | 3-88 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台41線KVAR | 11KV台41線 KVAR | FEEDER | P07/11/KH41/KVAR |  |  |  | CDC | 425 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台41線 | 台41線 |  | 台41線A1 | [17 empty] | 3-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台41線A1 | 11KV台41線 R相AMP | FEEDER | P07/11/KH41/I_R |  |  |  | CDC | 426 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台41線 | 台41線 |  | 台41線A2 | [17 empty] | 3-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台41線A2 | 11KV台41線 S相AMP | FEEDER | P07/11/KH41/I_S |  |  |  | CDC | 427 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台41線 | 台41線 |  | 台41線A3 | [17 empty] | 3-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台41線A3 | 11KV台41線 T相AMP | FEEDER | P07/11/KH41/I_T |  |  |  | CDC | 428 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台41線 | 台41線 |  | 台41線A0 | [17 empty] | 3-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台41線A0 | 11KV台41線 N相AMP | FEEDER | P07/11/KH41/I_N |  |  |  | CDC | 429 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台42線 | 台42線 |  | 台42線KVAR | [17 empty] | 3-8D | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台42線KVAR | 11KV台42線 KVAR | FEEDER | P07/11/KH42/KVAR |  |  |  | CDC | 430 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台42線 | 台42線 |  | 台42線A1 | [17 empty] | 3-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台42線A1 | 11KV台42線 R相AMP | FEEDER | P07/11/KH42/I_R |  |  |  | CDC | 431 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台42線 | 台42線 |  | 台42線A2 | [17 empty] | 3-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台42線A2 | 11KV台42線 S相AMP | FEEDER | P07/11/KH42/I_S |  |  |  | CDC | 432 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台42線 | 台42線 |  | 台42線A3 | [17 empty] | 3-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台42線A3 | 11KV台42線 T相AMP | FEEDER | P07/11/KH42/I_T |  |  |  | CDC | 433 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台42線 | 台42線 |  | 台42線A0 | [17 empty] | 3-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台42線A0 | 11KV台42線 N相AMP | FEEDER | P07/11/KH42/I_N |  |  |  | CDC | 434 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台43線 | 台43線 |  | 台43線KVAR | [17 empty] | 3-92 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台43線KVAR | 11KV台43線 KVAR | FEEDER | P07/11/KH43/KVAR |  |  |  | CDC | 435 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台43線 | 台43線 |  | 台43線A1 | [17 empty] | 3-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台43線A1 | 11KV台43線 R相AMP | FEEDER | P07/11/KH43/I_R |  |  |  | CDC | 436 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台43線 | 台43線 |  | 台43線A2 | [17 empty] | 3-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台43線A2 | 11KV台43線 S相AMP | FEEDER | P07/11/KH43/I_S |  |  |  | CDC | 437 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台43線 | 台43線 |  | 台43線A3 | [17 empty] | 3-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台43線A3 | 11KV台43線 T相AMP | FEEDER | P07/11/KH43/I_T |  |  |  | CDC | 438 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台43線 | 台43線 |  | 台43線A0 | [17 empty] | 3-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台43線A0 | 11KV台43線 N相AMP | FEEDER | P07/11/KH43/I_N |  |  |  | CDC | 439 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台44線 | 台44線 |  | 台44線KVAR | [17 empty] | 3-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台44線KVAR | 11KV台44線 KVAR | FEEDER | P07/11/KH44/KVAR |  |  |  | CDC | 440 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台44線 | 台44線 |  | 台44線A1 | [17 empty] | 3-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台44線A1 | 11KV台44線 R相AMP | FEEDER | P07/11/KH44/I_R |  |  |  | CDC | 441 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台44線 | 台44線 |  | 台44線A2 | [17 empty] | 3-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台44線A2 | 11KV台44線 S相AMP | FEEDER | P07/11/KH44/I_S |  |  |  | CDC | 442 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台44線 | 台44線 |  | 台44線A3 | [17 empty] | 3-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台44線A3 | 11KV台44線 T相AMP | FEEDER | P07/11/KH44/I_T |  |  |  | CDC | 443 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台44線 | 台44線 |  | 台44線A0 | [17 empty] | 3-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台44線A0 | 11KV台44線 N相AMP | FEEDER | P07/11/KH44/I_N |  |  |  | CDC | 444 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台76線 | 台76線 |  | 台76線KVAR | [17 empty] | 2-C8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台76線KVAR | 23KV台76線 KVAR | FEEDER | P07/22/KH76/KVAR |  |  |  | CDC | 445 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台76線 | 台76線 |  | 台76線A1 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台76線A1 | 23KV台76線 R相AMP | FEEDER | P07/22/KH76/I_R |  |  |  | CDC | 446 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台76線 | 台76線 |  | 台76線A2 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台76線A2 | 23KV台76線 S相AMP | FEEDER | P07/22/KH76/I_S |  |  |  | CDC | 447 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台76線 | 台76線 |  | 台76線A3 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台76線A3 | 23KV台76線 T相AMP | FEEDER | P07/22/KH76/I_T |  |  |  | CDC | 448 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台45線 | 台45線 |  | 台45線KVAR | [17 empty] | 3-9C | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台45線KVAR | 11KV台45線 KVAR | FEEDER | P07/11/KH45/KVAR |  |  |  | CDC | 449 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台45線 | 台45線 |  | 台45線A1 | [17 empty] | 3-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台45線A1 | 11KV台45線 R相AMP | FEEDER | P07/11/KH45/I_R |  |  |  | CDC | 450 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台45線 | 台45線 |  | 台45線A2 | [17 empty] | 3-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台45線A2 | 11KV台45線 S相AMP | FEEDER | P07/11/KH45/I_S |  |  |  | CDC | 451 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台45線 | 台45線 |  | 台45線A3 | [17 empty] | 3-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台45線A3 | 11KV台45線 T相AMP | FEEDER | P07/11/KH45/I_T |  |  |  | CDC | 452 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台45線 | 台45線 |  | 台45線A0 | [17 empty] | 3-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台45線A0 | 11KV台45線 N相AMP | FEEDER | P07/11/KH45/I_N |  |  |  | CDC | 453 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台46線 | 台46線 |  | 台46線KVAR | [17 empty] | 3-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台46線KVAR | 11KV台46線 KVAR | FEEDER | P07/11/KH46/KVAR |  |  |  | CDC | 454 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台46線 | 台46線 |  | 台46線A1 | [17 empty] | 3-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台46線A1 | 11KV台46線 R相AMP | FEEDER | P07/11/KH46/I_R |  |  |  | CDC | 455 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台46線 | 台46線 |  | 台46線A2 | [17 empty] | 3-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台46線A2 | 11KV台46線 S相AMP | FEEDER | P07/11/KH46/I_S |  |  |  | CDC | 456 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台46線 | 台46線 |  | 台46線A3 | [17 empty] | 3-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台46線A3 | 11KV台46線 T相AMP | FEEDER | P07/11/KH46/I_T |  |  |  | CDC | 457 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台46線 | 台46線 |  | 台46線A0 | [17 empty] | 3-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台46線A0 | 11KV台46線 N相AMP | FEEDER | P07/11/KH46/I_N |  |  |  | CDC | 458 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 2-85 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | P07/11/100/I_R |  |  |  | CDC | 459 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 2-86 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | P07/11/100/I_S |  |  |  | CDC | 460 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 2-87 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | P07/11/100/I_T |  |  |  | CDC | 461 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.23KV_200_A1 | 23KV 200 R相AMP | TIE | P07/22/200/I_R |  |  |  | CDC | 462 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.23KV_200_A2 | 23KV 200 S相AMP | TIE | P07/22/200/I_S |  |  |  | CDC | 463 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.23KV_200_A3 | 23KV 200 T相AMP | TIE | P07/22/200/I_T |  |  |  | CDC | 464 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台11線 | 台11線 |  | 台11線KVAR | [17 empty] | 3-AC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台11線KVAR | 11KV台11線 KVAR | FEEDER | P07/11/KH11/KVAR |  |  |  | CDC | 465 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A1 | [17 empty] | 3-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台11線A1 | 11KV台11線 R相AMP | FEEDER | P07/11/KH11/I_R |  |  |  | CDC | 466 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A2 | [17 empty] | 3-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台11線A2 | 11KV台11線 S相AMP | FEEDER | P07/11/KH11/I_S |  |  |  | CDC | 467 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A3 | [17 empty] | 3-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台11線A3 | 11KV台11線 T相AMP | FEEDER | P07/11/KH11/I_T |  |  |  | CDC | 468 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A0 | [17 empty] | 3-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台11線A0 | 11KV台11線 N相AMP | FEEDER | P07/11/KH11/I_N |  |  |  | CDC | 469 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台12線 | 台12線 |  | 台12線KVAR | [17 empty] | 3-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台12線KVAR | 11KV台12線 KVAR | FEEDER | P07/11/KH12/KVAR |  |  |  | CDC | 470 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A1 | [17 empty] | 3-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台12線A1 | 11KV台12線 R相AMP | FEEDER | P07/11/KH12/I_R |  |  |  | CDC | 471 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A2 | [17 empty] | 3-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台12線A2 | 11KV台12線 S相AMP | FEEDER | P07/11/KH12/I_S |  |  |  | CDC | 472 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A3 | [17 empty] | 3-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台12線A3 | 11KV台12線 T相AMP | FEEDER | P07/11/KH12/I_T |  |  |  | CDC | 473 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A0 | [17 empty] | 3-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台12線A0 | 11KV台12線 N相AMP | FEEDER | P07/11/KH12/I_N |  |  |  | CDC | 474 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台13線 | 台13線 |  | 台13線KVAR | [17 empty] | 3-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台13線KVAR | 11KV台13線 KVAR | FEEDER | P07/11/KH13/KVAR |  |  |  | CDC | 475 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A1 | [17 empty] | 3-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台13線A1 | 11KV台13線 R相AMP | FEEDER | P07/11/KH13/I_R |  |  |  | CDC | 476 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A2 | [17 empty] | 3-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台13線A2 | 11KV台13線 S相AMP | FEEDER | P07/11/KH13/I_S |  |  |  | CDC | 477 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A3 | [17 empty] | 3-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台13線A3 | 11KV台13線 T相AMP | FEEDER | P07/11/KH13/I_T |  |  |  | CDC | 478 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A0 | [17 empty] | 3-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台13線A0 | 11KV台13線 N相AMP | FEEDER | P07/11/KH13/I_N |  |  |  | CDC | 479 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台14線 | 台14線 |  | 台14線KVAR | [17 empty] | 3-BB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台14線KVAR | 11KV台14線 KVAR | FEEDER | P07/11/KH14/KVAR |  |  |  | CDC | 480 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A1 | [17 empty] | 3-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台14線A1 | 11KV台14線 R相AMP | FEEDER | P07/11/KH14/I_R |  |  |  | CDC | 481 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A2 | [17 empty] | 3-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台14線A2 | 11KV台14線 S相AMP | FEEDER | P07/11/KH14/I_S |  |  |  | CDC | 482 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A3 | [17 empty] | 3-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台14線A3 | 11KV台14線 T相AMP | FEEDER | P07/11/KH14/I_T |  |  |  | CDC | 483 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A0 | [17 empty] | 3-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台14線A0 | 11KV台14線 N相AMP | FEEDER | P07/11/KH14/I_N |  |  |  | CDC | 484 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台15線 | 台15線 |  | 台15線KVAR | [17 empty] | 3-C2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台15線KVAR | 11KV台15線 KVAR | FEEDER | P07/11/KH15/KVAR |  |  |  | CDC | 485 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A1 | [17 empty] | 3-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台15線A1 | 11KV台15線 R相AMP | FEEDER | P07/11/KH15/I_R |  |  |  | CDC | 486 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A2 | [17 empty] | 3-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台15線A2 | 11KV台15線 S相AMP | FEEDER | P07/11/KH15/I_S |  |  |  | CDC | 487 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A3 | [17 empty] | 3-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台15線A3 | 11KV台15線 T相AMP | FEEDER | P07/11/KH15/I_T |  |  |  | CDC | 488 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A0 | [17 empty] | 3-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台15線A0 | 11KV台15線 N相AMP | FEEDER | P07/11/KH15/I_N |  |  |  | CDC | 489 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台16線 | 台16線 |  | 台16線KVAR | [17 empty] | 3-E4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台16線KVAR | 11KV台16線 KVAR | FEEDER | P07/11/KH16/KVAR |  |  |  | CDC | 490 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A1 | [17 empty] | 3-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台16線A1 | 11KV台16線 R相AMP | FEEDER | P07/11/KH16/I_R |  |  |  | CDC | 491 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A2 | [17 empty] | 3-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台16線A2 | 11KV台16線 S相AMP | FEEDER | P07/11/KH16/I_S |  |  |  | CDC | 492 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A3 | [17 empty] | 3-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台16線A3 | 11KV台16線 T相AMP | FEEDER | P07/11/KH16/I_T |  |  |  | CDC | 493 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A0 | [17 empty] | 3-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台16線A0 | 11KV台16線 N相AMP | FEEDER | P07/11/KH16/I_N |  |  |  | CDC | 494 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台17線 | 台17線 |  | 台17線KVAR | [17 empty] | 3-DF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台17線KVAR | 11KV台17線 KVAR | FEEDER | P07/11/KH17/KVAR |  |  |  | CDC | 495 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A1 | [17 empty] | 3-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台17線A1 | 11KV台17線 R相AMP | FEEDER | P07/11/KH17/I_R |  |  |  | CDC | 496 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A2 | [17 empty] | 3-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台17線A2 | 11KV台17線 S相AMP | FEEDER | P07/11/KH17/I_S |  |  |  | CDC | 497 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A3 | [17 empty] | 3-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台17線A3 | 11KV台17線 T相AMP | FEEDER | P07/11/KH17/I_T |  |  |  | CDC | 498 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A0 | [17 empty] | 3-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台17線A0 | 11KV台17線 N相AMP | FEEDER | P07/11/KH17/I_N |  |  |  | CDC | 499 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台18線 | 台18線 |  | 台18線KVAR | [17 empty] | 3-DA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台18線KVAR | 11KV台18線 KVAR | FEEDER | P07/11/KH18/KVAR |  |  |  | CDC | 500 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A1 | [17 empty] | 3-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台18線A1 | 11KV台18線 R相AMP | FEEDER | P07/11/KH18/I_R |  |  |  | CDC | 501 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A2 | [17 empty] | 3-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台18線A2 | 11KV台18線 S相AMP | FEEDER | P07/11/KH18/I_S |  |  |  | CDC | 502 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A3 | [17 empty] | 3-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台18線A3 | 11KV台18線 T相AMP | FEEDER | P07/11/KH18/I_T |  |  |  | CDC | 503 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A0 | [17 empty] | 3-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台18線A0 | 11KV台18線 N相AMP | FEEDER | P07/11/KH18/I_N |  |  |  | CDC | 504 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台19線 | 台19線 |  | 台19線KVAR | [17 empty] | 3-D5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台19線KVAR | 11KV台19線 KVAR | FEEDER | P07/11/KH19/KVAR |  |  |  | CDC | 505 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A1 | [17 empty] | 3-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台19線A1 | 11KV台19線 R相AMP | FEEDER | P07/11/KH19/I_R |  |  |  | CDC | 506 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A2 | [17 empty] | 3-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台19線A2 | 11KV台19線 S相AMP | FEEDER | P07/11/KH19/I_S |  |  |  | CDC | 507 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A3 | [17 empty] | 3-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台19線A3 | 11KV台19線 T相AMP | FEEDER | P07/11/KH19/I_T |  |  |  | CDC | 508 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A0 | [17 empty] | 3-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台19線A0 | 11KV台19線 N相AMP | FEEDER | P07/11/KH19/I_N |  |  |  | CDC | 509 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台20線 | 台20線 |  | 台20線KVAR | [17 empty] | 3-D0 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台20線KVAR | 11KV台20線 KVAR | FEEDER | P07/11/KH20/KVAR |  |  |  | CDC | 510 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A1 | [17 empty] | 3-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台20線A1 | 11KV台20線 R相AMP | FEEDER | P07/11/KH20/I_R |  |  |  | CDC | 511 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A2 | [17 empty] | 3-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台20線A2 | 11KV台20線 S相AMP | FEEDER | P07/11/KH20/I_S |  |  |  | CDC | 512 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A3 | [17 empty] | 3-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台20線A3 | 11KV台20線 T相AMP | FEEDER | P07/11/KH20/I_T |  |  |  | CDC | 513 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A0 | [17 empty] | 3-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台20線A0 | 11KV台20線 N相AMP | FEEDER | P07/11/KH20/I_N |  |  |  | CDC | 514 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _300 | 300 |  | I_R | [17 empty] | 3-C7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_300_A1 | 11KV 300 R相AMP | TIE | P07/11/300/I_R |  |  |  | CDC | 515 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _300 | 300 |  | I_S | [17 empty] | 3-C8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_300_A2 | 11KV 300 S相AMP | TIE | P07/11/300/I_S |  |  |  | CDC | 516 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _300 | 300 |  | I_T | [17 empty] | 3-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_300_A3 | 11KV 300 T相AMP | TIE | P07/11/300/I_T |  |  |  | CDC | 517 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _400 | 400 |  | I_R | [17 empty] | 3-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_400_A1 | 11KV 400 R相AMP | TIE | P07/11/400/I_R |  |  |  | CDC | 518 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _400 | 400 |  | I_S | [17 empty] | 3-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_400_A2 | 11KV 400 S相AMP | TIE | P07/11/400/I_S |  |  |  | CDC | 519 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | _400 | 400 |  | I_T | [17 empty] | 3-EB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV_400_A3 | 11KV 400 T相AMP | TIE | P07/11/400/I_T |  |  |  | CDC | 520 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | MW | [17 empty] | 3-A7 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_MW | #8DTR二次側(A) MW | MTR | P07/11/370/KW |  |  |  | CDC | 521 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | MVAR | [17 empty] | 3-A8 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_MVAR | #8DTR二次側(A) MVAR | MTR | P07/11/370/KVAR |  |  |  | CDC | 522 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | I_R | [17 empty] | 3-A9 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_A1 | #8DTR二次側(A) R相AMP | MTR | P07/11/370/I_R |  |  |  | CDC | 523 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | I_S | [17 empty] | 3-AA | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_A2 | #8DTR二次側(A) S相AMP | MTR | P07/11/370/I_S |  |  |  | CDC | 524 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR二次側(A) |  | I_T | [17 empty] | 3-AB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_A3 | #8DTR二次側(A) T相AMP | MTR | P07/11/370/I_T |  |  |  | CDC | 525 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | OilTemp | [17 empty] | 1-A5 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR_OIL | #8DTR 油溫 | MTR | P07//8DTR/OilTemp |  |  |  | CDC | 526 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | CoilTemp | [17 empty] | 1-A8 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_COIL | #8DTR(A) 線溫 | MTR | P07//8DTR(A)/CoilTemp |  |  |  | CDC | 527 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | TapPosMv | [17 empty] | 1-AD |  | 1-3F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_TAP | #8DTR(A) OLTC TAP | MTR | P07//8DTR(A)/TapPosMv |  |  |  | CDC | 528 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | MW | [17 empty] | 3-CB | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_MW | #8DTR二次側(B) MW | MTR | P07/11/380/KW |  |  |  | CDC | 529 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | MVAR | [17 empty] | 3-CC | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_MVAR | #8DTR二次側(B) MVAR | MTR | P07/11/380/KVAR |  |  |  | CDC | 530 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | I_R | [17 empty] | 3-CD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_A1 | #8DTR二次側(B) R相AMP | MTR | P07/11/380/I_R |  |  |  | CDC | 531 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | I_S | [17 empty] | 3-CE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_A2 | #8DTR二次側(B) S相AMP | MTR | P07/11/380/I_S |  |  |  | CDC | 532 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR二次側(B) |  | I_T | [17 empty] | 3-CF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_A3 | #8DTR二次側(B) T相AMP | MTR | P07/11/380/I_T |  |  |  | CDC | 533 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | CoilTemp | [17 empty] | 1-AA | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_COIL | #8DTR(B) 線溫 | MTR | P07//8DTR(B)/CoilTemp |  |  |  | CDC | 534 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | TapPosMv | [17 empty] | 1-AF |  | 1-43 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_TAP | #8DTR(B) OLTC TAP | MTR | P07//8DTR(B)/TapPosMv |  |  |  | CDC | 535 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P07 | 台南PS | 11 | 11kV | 8ABUS | #8ABUS |  | V | [17 empty] | 3-A6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV#8ABUS_KV | 11KV #8ABUS KV | BUS | P07/11/8ABUS/V |  |  |  | CDC | 536 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 8BBUS | #8BBUS |  | V | [17 empty] | 3-CA | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.11KV#8BBUS_KV | 11KV #8BBUS KV | BUS | P07/11/8BBUS/V |  |  |  | CDC | 537 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P07 | 台南PS | 11 | 11kV | 台31線 | 台31線 |  | 台31線A0 | [17 empty] | 3-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台31線A0 | 11KV台31線 N相AMP | FEEDER | P07/11/KH31/I_N |  |  |  | CDC | 538 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台32線 | 台32線 |  | 台32線A0 | [17 empty] | 3-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台32線A0 | 11KV台32線 N相AMP | FEEDER | P07/11/KH32/I_N |  |  |  | CDC | 539 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台33線 | 台33線 |  | 台33線A0 | [17 empty] | 3-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台33線A0 | 11KV台33線 N相AMP | FEEDER | P07/11/KH33/I_N |  |  |  | CDC | 540 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台36線 | 台36線 |  | 台36線A0 | [17 empty] | 3-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台36線A0 | 11KV台36線 N相AMP | FEEDER | P07/11/KH36/I_N |  |  |  | CDC | 541 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台37線 | 台37線 |  | 台37線A0 | [17 empty] | 3-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台37線A0 | 11KV台37線 N相AMP | FEEDER | P07/11/KH37/I_N |  |  |  | CDC | 542 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台38線 | 台38線 |  | 台38線A0 | [17 empty] | 3-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台38線A0 | 11KV台38線 N相AMP | FEEDER | P07/11/KH38/I_N |  |  |  | CDC | 543 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台61線 | 台61線 |  | 台61線A0 | [17 empty] | 3-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台61線A0 | 23KV台61線 N相AMP | FEEDER | P07/22/KH61/I_N |  |  |  | CDC | 544 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台62線 | 台62線 |  | 台62線A0 | [17 empty] | 3-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台62線A0 | 23KV台62線 N相AMP | FEEDER | P07/22/KH62/I_N |  |  |  | CDC | 545 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台63線 | 台63線 |  | 台63線A0 | [17 empty] | 3-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台63線A0 | 23KV台63線 N相AMP | FEEDER | P07/22/KH63/I_N |  |  |  | CDC | 546 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台64線 | 台64線 |  | 台64線A0 | [17 empty] | 3-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台64線A0 | 23KV台64線 N相AMP | FEEDER | P07/22/KH64/I_N |  |  |  | CDC | 547 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台65線 | 台65線 |  | 台65線A0 | [17 empty] | 3-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台65線A0 | 23KV台65線 N相AMP | FEEDER | P07/22/KH65/I_N |  |  |  | CDC | 548 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台66線 | 台66線 |  | 台66線A0 | [17 empty] | 3-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台66線A0 | 23KV台66線 N相AMP | FEEDER | P07/22/KH66/I_N |  |  |  | CDC | 549 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台71線 | 台71線 |  | 台71線A0 | [17 empty] | 3-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台71線A0 | 23KV台71線 N相AMP | FEEDER | P07/22/KH71/I_N |  |  |  | CDC | 550 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台72線 | 台72線 |  | 台72線A0 | [17 empty] | 3-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台72線A0 | 23KV台72線 N相AMP | FEEDER | P07/22/KH72/I_N |  |  |  | CDC | 551 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台73線 | 台73線 |  | 台73線A0 | [17 empty] | 3-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台73線A0 | 23KV台73線 N相AMP | FEEDER | P07/22/KH73/I_N |  |  |  | CDC | 552 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台74線 | 台74線 |  | 台74線A0 | [17 empty] | 3-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台74線A0 | 23KV台74線 N相AMP | FEEDER | P07/22/KH74/I_N |  |  |  | CDC | 553 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台75線 | 台75線 |  | 台75線A0 | [17 empty] | 3-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台75線A0 | 23KV台75線 N相AMP | FEEDER | P07/22/KH75/I_N |  |  |  | CDC | 554 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 22 | 22kV | 台76線 | 台76線 |  | 台76線A0 | [17 empty] | 3-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台76線A0 | 23KV台76線 N相AMP | FEEDER | P07/22/KH76/I_N |  |  |  | CDC | 555 | GENERICAIPoint | PS011_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1570_MW | 台南忠孝一路 MW | LINE161 | P07/161/1570/MW |  |  |  | CDC | 556 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1570_MVAR | 台南忠孝一路 MVAR | LINE161 | P07/161/1570/MVAR |  |  |  | CDC | 557 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P07 | 台南PS | 0 |  | 1550_OF | 台南延平線 |  | R | [17 empty] | 1-D0 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1550_OF_R | 台南延平線 R相 油壓 | OTHER | P07/161/1550/OilPreR |  |  |  | CDC | 558 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1550_OF | 台南延平線 |  | S | [17 empty] | 1-D1 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1550_OF_S | 台南延平線 S相 油壓 | OTHER | P07/161/1550/OilPreS |  |  |  | CDC | 559 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1550_OF | 台南延平線 |  | T | [17 empty] | 1-D2 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1550_OF_T | 台南延平線 T相 油壓 | OTHER | P07/161/1550/OilPreT |  |  |  | CDC | 560 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1560_OF | 台南忠孝二路 |  | R | [17 empty] | 1-9E | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1560_OF_R | 台南忠孝二路 R相 油壓 | OTHER | P07/161/1560/OilPreR |  |  |  | CDC | 561 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1560_OF | 台南忠孝二路 |  | S | [17 empty] | 1-9F | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1560_OF_S | 台南忠孝二路 S相 油壓 | OTHER | P07/161/1560/OilPreS |  |  |  | CDC | 562 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 1560_OF | 台南忠孝二路 |  | T | [17 empty] | 1-B2 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 台南PS.1560_OF_T | 台南忠孝二路 T相 油壓 | OTHER | P07/161/1560/OilPreT |  |  |  | CDC | 563 | GENERICAIPoint | PS011_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台南紡織(KH38) | 台南紡織(KH38) |  | 台南紡織KVAR | [17 empty] | 2-D1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織KVAR | 11KV台南紡織(KH38) KVAR | FEEDER |  |  |  |  | CDC | 564 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 5.400000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台南紡織(KH38) | 台南紡織(KH38) |  | 台南紡織A1 | [17 empty] | 2-D2 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織A1 | 11KV台南紡織(KH38) R相AMP | FEEDER |  |  |  |  | CDC | 565 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台南紡織(KH38) | 台南紡織(KH38) |  | 台南紡織A2 | [17 empty] | 2-D3 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織A2 | 11KV台南紡織(KH38) S相AMP | FEEDER |  |  |  |  | CDC | 566 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 11 | 11kV | 台南紡織(KH38) | 台南紡織(KH38) |  | 台南紡織A3 | [17 empty] | 2-D4 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織A3 | 11KV台南紡織(KH38) T相AMP | FEEDER |  |  |  |  | CDC | 567 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P07 | 台南PS | 0 |  | 台南紡織 | 11V台南紡織(KH38) |  | KV1 | [17 empty] | 2-D5 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織_KV1 | 11V台南紡織(KH38) R相KV | OTHER |  |  |  |  | CDC | 568 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 2.000000 | 1.500000
P07 | 台南PS | 0 |  | 台南紡織 | 11V台南紡織(KH38) |  | KV2 | [17 empty] | 2-D6 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織_KV2 | 11V台南紡織(KH38) S相KV | OTHER |  |  |  |  | CDC | 569 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 2.000000 | 1.500000
P07 | 台南PS | 0 |  | 台南紡織 | 11V台南紡織(KH38) |  | KV3 | [17 empty] | 2-D7 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織_KV3 | 11V台南紡織(KH38) T相KV | OTHER |  |  |  |  | CDC | 570 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 2.000000 | 1.500000
P07 | 台南PS | 0 |  | 台南紡織 | 11V台南紡織(KH38) |  | KW | [17 empty] | 2-D0 | [5 empty] | KW_-9000_9000(-2000_2000) |  | DDCS4_1 | [8 empty] | 台南PS.台南紡織_KW | 11V台南紡織(KH38) KW | OTHER |  |  |  |  | CDC | 571 | GENERICAIPoint | PS011_L2 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.700000 | 0.010000
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | GDA | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1510_GDA | 台南仁德線(1510) 接地RY | LINE161 | P07/161/1510/GDA |  |  |  | CDC | 572 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | CB | [17 empty] | 1-01-00 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1510_CB | 1510(台南仁德線) CB | LINE161 | P07/161/1510/CB |  |  |  | CDC | 573 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | 79UL | [17 empty] | 1-32-02 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1510_79UL | 台南仁德線(1510) 79RY U/L | LINE161 | P07/161/1510/79UL |  |  |  | CDC | 574 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | ABS1 | 1511 | [16 empty] | 1-37-00 | 1-37-01 | 1-4F | [5 empty] | ADCS_S | [8 empty] | 台南PS.1511_ABS | 1511(台南仁德線) ABS | LINE161 | P07/161/1510/ABS1 |  |  |  | CDC | 575 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | ABS2 | 1512 | [16 empty] | 1-37-02 | 1-37-03 | 1-50 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1512_ABS | 1512(台南仁德線) ABS | LINE161 | P07/161/1510/ABS2 |  |  |  | CDC | 576 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | ABS3 | 1513 | [16 empty] | 1-37-04 | 1-37-05 | 1-51 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1513_ABS | 1513(台南仁德線) ABS | LINE161 | P07/161/1510/ABS3 |  |  |  | CDC | 577 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | E3 | 1513E | [16 empty] | 1-37-06 | 1-37-07 | 1-52 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1513E_ES | 1513E(台南仁德線) ES | LINE161 | P07/161/1510/E3 |  |  |  | CDC | 578 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1520_GDA | 山上海線(1520) 接地RY | LINE161 | P07/161/1520/GDA |  |  |  | CDC | 579 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | 21A | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1520_21A | 山上海線(1520) 21RY | LINE161 | P07/161/1520/PHA |  |  |  | CDC | 580 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | CB | [17 empty] | 1-00-04 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1520_CB | 1520(山上海線) CB | LINE161 | P07/161/1520/CB |  |  |  | CDC | 581 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | 79UL | [17 empty] | 1-31-15 |  | 1-1E | [5 empty] | ADCS_S | [8 empty] | 台南PS.1520_79UL | 山上海線(1520) 79RY U/L | LINE161 | P07/161/1520/79UL |  |  |  | CDC | 582 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | ABS1 | 1521 | [16 empty] | 1-36-08 | 1-36-09 | 1-4B | [5 empty] | ADCS_S | [8 empty] | 台南PS.1521_ABS | 1521(山上海線) ABS | LINE161 | P07/161/1520/ABS1 |  |  |  | CDC | 583 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | ABS2 | 1522 | [16 empty] | 1-36-10 | 1-36-11 | 1-4C | [5 empty] | ADCS_S | [8 empty] | 台南PS.1522_ABS | 1522(山上海線) ABS | LINE161 | P07/161/1520/ABS2 |  |  |  | CDC | 584 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | ABS3 | 1523 | [16 empty] | 1-36-12 | 1-36-13 | 1-4D | [5 empty] | ADCS_S | [8 empty] | 台南PS.1523_ABS | 1523(山上海線) ABS | LINE161 | P07/161/1520/ABS3 |  |  |  | CDC | 585 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | E3 | 1523E | [16 empty] | 1-36-14 | 1-36-15 | 1-4E | [5 empty] | ADCS_S | [8 empty] | 台南PS.1523E_ES | 1523E(山上海線) ES | LINE161 | P07/161/1520/E3 |  |  |  | CDC | 586 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | GDA | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1530_GDA | 龍崎山線(1530) 接地RY | LINE161 | P07/161/1530/GDA |  |  |  | CDC | 587 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | CB | [17 empty] | 1-02-04 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1530_CB | 1530(龍崎山線) CB | LINE161 | P07/161/1530/CB |  |  |  | CDC | 588 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | 79UL | [17 empty] | 1-32-11 |  | 1-26 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1530_79UL | 龍崎山線(1530) 79RY U/L | LINE161 | P07/161/1530/79UL |  |  |  | CDC | 589 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | ABS1 | 1531 | [16 empty] | 1-38-08 | 1-38-09 | 1-5B | [5 empty] | ADCS_S | [8 empty] | 台南PS.1531_ABS | 1531(龍崎山線) ABS | LINE161 | P07/161/1530/ABS1 |  |  |  | CDC | 590 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | ABS2 | 1532 | [16 empty] | 1-38-10 | 1-38-11 | 1-5C | [5 empty] | ADCS_S | [8 empty] | 台南PS.1532_ABS | 1532(龍崎山線) ABS | LINE161 | P07/161/1530/ABS2 |  |  |  | CDC | 591 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | ABS3 | 1533 | [16 empty] | 1-38-12 | 1-38-13 | 1-5D | [5 empty] | ADCS_S | [8 empty] | 台南PS.1533_ABS | 1533(龍崎山線) ABS | LINE161 | P07/161/1530/ABS3 |  |  |  | CDC | 592 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | E3 | 1533E | [16 empty] | 1-38-14 | 1-38-15 | 1-5E | [5 empty] | ADCS_S | [8 empty] | 台南PS.1533E_ES | 1533E(龍崎山線) ES | LINE161 | P07/161/1530/E3 |  |  |  | CDC | 593 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | GDA | [17 empty] | 1-03-03 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1540_GDA | 龍崎海線(1540) 接地RY | LINE161 | P07/161/1540/GDA |  |  |  | CDC | 594 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | CB | [17 empty] | 1-03-00 |  | 1-07 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1540_CB | 1540(龍崎海線) CB | LINE161 | P07/161/1540/CB |  |  |  | CDC | 595 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | 79UL | [17 empty] | 1-32-14 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1540_79UL | 龍崎海線(1540) 79RY U/L | LINE161 | P07/161/1540/79UL |  |  |  | CDC | 596 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | ABS1 | 1541 | [16 empty] | 1-39-00 | 1-39-01 | 1-5F | [5 empty] | ADCS_S | [8 empty] | 台南PS.1541_ABS | 1541(龍崎海線) ABS | LINE161 | P07/161/1540/ABS1 |  |  |  | CDC | 597 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | ABS2 | 1542 | [16 empty] | 1-39-02 | 1-39-03 | 1-60 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1542_ABS | 1542(龍崎海線) ABS | LINE161 | P07/161/1540/ABS2 |  |  |  | CDC | 598 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | ABS3 | 1543 | [16 empty] | 1-39-04 | 1-39-05 | 1-61 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1543_ABS | 1543(龍崎海線) ABS | LINE161 | P07/161/1540/ABS3 |  |  |  | CDC | 599 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | E3 | 1543E | [16 empty] | 1-39-06 | 1-39-07 | 1-62 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1543E_ES | 1543E(龍崎海線) ES | LINE161 | P07/161/1540/E3 |  |  |  | CDC | 600 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1550_GDA | 台南延平線(1550) 接地RY | LINE161 | P07/161/1550/GDA |  |  |  | CDC | 601 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | CB | [17 empty] | 1-02-00 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1550_CB | 1550(台南延平線) CB | LINE161 | P07/161/1550/CB |  |  |  | CDC | 602 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 79UL | [17 empty] | 1-32-08 |  | 1-24 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1550_79UL | 台南延平線(1550) 79RY U/L | LINE161 | P07/161/1550/79UL |  |  |  | CDC | 603 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | ABS1 | 1551 | [16 empty] | 1-38-00 | 1-38-01 | 1-57 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1551_ABS | 1551(台南延平線) ABS | LINE161 | P07/161/1550/ABS1 |  |  |  | CDC | 604 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | ABS2 | 1552 | [16 empty] | 1-38-02 | 1-38-03 | 1-58 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1552_ABS | 1552(台南延平線) ABS | LINE161 | P07/161/1550/ABS2 |  |  |  | CDC | 605 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | ABS3 | 1553 | [16 empty] | 1-38-04 | 1-38-05 | 1-59 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1553_ABS | 1553(台南延平線) ABS | LINE161 | P07/161/1550/ABS3 |  |  |  | CDC | 606 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | E3 | 1553E | [16 empty] | 1-38-06 | 1-38-07 | 1-5A | [5 empty] | ADCS_S | [8 empty] | 台南PS.1553E_ES | 1553E(台南延平線) ES | LINE161 | P07/161/1550/E3 |  |  |  | CDC | 607 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | GDA | [17 empty] | 1-01-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1560_GDA | 台南忠孝二路(1560) 接地RY | LINE161 | P07/161/1560/GDA |  |  |  | CDC | 608 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | CB | [17 empty] | 1-01-04 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1560_CB | 1560(台南忠孝二路) CB | LINE161 | P07/161/1560/CB |  |  |  | CDC | 609 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | 79UL | [17 empty] | 1-32-05 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1560_79UL | 台南忠孝二路(1560) 79RY U/L | LINE161 | P07/161/1560/79UL |  |  |  | CDC | 610 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | ABS1 | 1561 | [16 empty] | 1-37-08 | 1-37-09 | 1-53 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1561_ABS | 1561(台南忠孝二路) ABS | LINE161 | P07/161/1560/ABS1 |  |  |  | CDC | 611 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | ABS2 | 1562 | [16 empty] | 1-37-10 | 1-37-11 | 1-54 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1562_ABS | 1562(台南忠孝二路) ABS | LINE161 | P07/161/1560/ABS2 |  |  |  | CDC | 612 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | ABS3 | 1563 | [16 empty] | 1-37-12 | 1-37-13 | 1-55 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1563_ABS | 1563(台南忠孝二路) ABS | LINE161 | P07/161/1560/ABS3 |  |  |  | CDC | 613 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | E3 | 1563E | [16 empty] | 1-37-14 | 1-37-15 | 1-56 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1563E_ES | 1563E(台南忠孝二路) ES | LINE161 | P07/161/1560/E3 |  |  |  | CDC | 614 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | PHA | [17 empty] | 1-1D-02 | [7 empty] | 69KV_S | [8 empty] | 台南PS.620_PHA | 保安線(620) 相間RY | LINE69 | P07/69/620/PHA |  |  |  | CDC | 615 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | GDA | [17 empty] | 1-1D-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.620_GDA | 保安線(620) 接地RY | LINE69 | P07/69/620/GDA |  |  |  | CDC | 616 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | CB | [17 empty] | 1-1D-00 |  | 1-73 | [5 empty] | 69KV_S | [8 empty] | 台南PS.620_CB | 620(保安線) CB | LINE69 | P07/69/620/CB |  |  |  | CDC | 617 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | ABS1 | 621 | [16 empty] | 2-37-12 | 2-37-13 | 2-4E | [5 empty] | ADCS_S | [8 empty] | 台南PS.621_ABS | 621(保安線) ABS | LINE69 | P07/69/620/ABS1 |  |  |  | CDC | 618 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | ABS2 | 622 | [16 empty] | 2-37-14 | 2-37-15 | 2-4F | [5 empty] | ADCS_S | [8 empty] | 台南PS.622_ABS | 622(保安線) ABS | LINE69 | P07/69/620/ABS2 |  |  |  | CDC | 619 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | ABS3 | 623 | [16 empty] | 2-38-00 | 2-38-01 | 2-50 | [5 empty] | ADCS_S | [8 empty] | 台南PS.623_ABS | 623(保安線) ABS | LINE69 | P07/69/620/ABS3 |  |  |  | CDC | 620 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | E3 | 623E | [16 empty] | 2-38-02 | 2-38-03 | 2-51 | [5 empty] | ADCS_S | [8 empty] | 台南PS.623E_ES | 623E(保安線) ES | LINE69 | P07/69/620/E3 |  |  |  | CDC | 621 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | 69KV_S | [8 empty] | 台南PS.630_PHA | 台南光洲線(630) 相間RY | LINE69 | P07/69/630/PHA |  |  |  | CDC | 622 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | 69KV_S | [8 empty] | 台南PS.630_GDA | 台南光洲線(630) 接地RY | LINE69 | P07/69/630/GDA |  |  |  | CDC | 623 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | CB | [17 empty] | 1-1C-04 |  | 1-72 | [5 empty] | 69KV_S | [8 empty] | 台南PS.630_CB | 630(台南光洲線) CB | LINE69 | P07/69/630/CB |  |  |  | CDC | 624 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | ABS1 | 631 | [16 empty] | 2-37-04 | 2-37-05 | 2-4A | [5 empty] | ADCS_S | [8 empty] | 台南PS.631_ABS | 631(台南光洲線) ABS | LINE69 | P07/69/630/ABS1 |  |  |  | CDC | 625 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | ABS2 | 632 | [16 empty] | 2-37-06 | 2-37-07 | 2-4B | [5 empty] | ADCS_S | [8 empty] | 台南PS.632_ABS | 632(台南光洲線) ABS | LINE69 | P07/69/630/ABS2 |  |  |  | CDC | 626 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | ABS3 | 633 | [16 empty] | 2-37-08 | 2-37-09 | 2-4C | [5 empty] | ADCS_S | [8 empty] | 台南PS.633_ABS | 633(台南光洲線) ABS | LINE69 | P07/69/630/ABS3 |  |  |  | CDC | 627 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | E3 | 633E | [16 empty] | 2-37-10 | 2-37-11 | 2-4D | [5 empty] | ADCS_S | [8 empty] | 台南PS.633E_ES | 633E(台南光洲線) ES | LINE69 | P07/69/630/E3 |  |  |  | CDC | 628 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | PHA | [17 empty] | 1-1C-02 | [7 empty] | 69KV_S | [8 empty] | 台南PS.640_PHA | 備用線(640) 相間RY | LINE69 |  |  |  |  | CDC | 629 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | GDA | [17 empty] | 1-1C-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.640_GDA | 備用線(640) 接地RY | LINE69 |  |  |  |  | CDC | 630 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | 85A | [17 empty] | 1-1C-01 | [7 empty] | 69KV_S | [8 empty] | 台南PS.640_85A | 備用線(640) 85RY | LINE69 |  |  |  |  | CDC | 631 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | 74A | [17 empty] | 2-3D-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.640_74A | 備用線(640) 74RY | LINE69 |  |  |  |  | CDC | 632 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | 85UL | [17 empty] | 2-3D-00 |  | 2-1E | [5 empty] | ADCS_S | [8 empty] | 台南PS.640_85UL | 備用線(640) 85RY U/L | LINE69 |  |  |  |  | CDC | 633 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | CB | [17 empty] | 1-1C-00 |  | 1-71 | [5 empty] | 69KV_S | [8 empty] | 台南PS.640_CB | 640(備用線) CB | LINE69 |  |  |  |  | CDC | 634 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | ABS1 | 641 | [16 empty] | 2-36-12 | 2-36-13 | 2-46 | [5 empty] | ADCS_S | [8 empty] | 台南PS.641_ABS | 641(備用線) ABS | LINE69 |  |  |  |  | CDC | 635 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | ABS2 | 642 | [16 empty] | 2-36-14 | 2-36-15 | 2-47 | [5 empty] | ADCS_S | [8 empty] | 台南PS.642_ABS | 642(備用線) ABS | LINE69 |  |  |  |  | CDC | 636 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | ABS3 | 643 | [16 empty] | 2-37-00 | 2-37-01 | 2-48 | [5 empty] | ADCS_S | [8 empty] | 台南PS.643_ABS | 643(備用線) ABS | LINE69 |  |  |  |  | CDC | 637 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | E3 | 643E | [16 empty] | 2-37-02 | 2-37-03 | 2-49 | [5 empty] | ADCS_S | [8 empty] | 台南PS.643E_ES | 643E(備用線) ES | LINE69 |  |  |  |  | CDC | 638 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | PHA | [17 empty] | 1-1B-02 | [7 empty] | 69KV_S | [8 empty] | 台南PS.660_PHA | 台南後甲海線(660) 相間RY | LINE69 | P07/69/660/PHA |  |  |  | CDC | 639 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | GDA | [17 empty] | 1-1B-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.660_GDA | 台南後甲海線(660) 接地RY | LINE69 | P07/69/660/GDA |  |  |  | CDC | 640 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | CB | [17 empty] | 1-1B-00 |  | 1-6F | [5 empty] | 69KV_S | [8 empty] | 台南PS.660_CB | 660(台南後甲海線) CB | LINE69 | P07/69/660/CB |  |  |  | CDC | 641 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | ABS1 | 661 | [16 empty] | 2-35-12 | 2-35-13 | 2-3E | [5 empty] | ADCS_S | [8 empty] | 台南PS.661_ABS | 661(台南後甲海線) ABS | LINE69 | P07/69/660/ABS1 |  |  |  | CDC | 642 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | ABS2 | 662 | [16 empty] | 2-35-14 | 2-35-15 | 2-3F | [5 empty] | ADCS_S | [8 empty] | 台南PS.662_ABS | 662(台南後甲海線) ABS | LINE69 | P07/69/660/ABS2 |  |  |  | CDC | 643 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | ABS3 | 663 | [16 empty] | 2-36-00 | 2-36-01 | 2-40 | [5 empty] | ADCS_S | [8 empty] | 台南PS.663_ABS | 663(台南後甲海線) ABS | LINE69 | P07/69/660/ABS3 |  |  |  | CDC | 644 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | E3 | 663E | [16 empty] | 2-36-02 | 2-36-03 | 2-41 | [5 empty] | ADCS_S | [8 empty] | 台南PS.663E_ES | 663E(台南後甲海線) ES | LINE69 | P07/69/660/E3 |  |  |  | CDC | 645 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PHA | [17 empty] | 1-1A-06 | [7 empty] | 69KV_S | [8 empty] | 台南PS.670_PHA | 台南大灣一路(670) 相間RY | LINE69 | P07/69/670/PHA |  |  |  | CDC | 646 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | GDA | [17 empty] | 1-1A-07 | [7 empty] | 69KV_S | [8 empty] | 台南PS.670_GDA | 台南大灣一路(670) 接地RY | LINE69 | P07/69/670/GDA |  |  |  | CDC | 647 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | CB | [17 empty] | 1-1A-04 |  | 1-6E | [5 empty] | 69KV_S | [8 empty] | 台南PS.670_CB | 670(台南大灣一路) CB | LINE69 | P07/69/670/CB |  |  |  | CDC | 648 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | ABS1 | 671 | [16 empty] | 2-35-04 | 2-35-05 | 2-3A | [5 empty] | ADCS_S | [8 empty] | 台南PS.671_ABS | 671(台南大灣一路) ABS | LINE69 | P07/69/670/ABS1 |  |  |  | CDC | 649 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | ABS2 | 672 | [16 empty] | 2-35-06 | 2-35-07 | 2-3B | [5 empty] | ADCS_S | [8 empty] | 台南PS.672_ABS | 672(台南大灣一路) ABS | LINE69 | P07/69/670/ABS2 |  |  |  | CDC | 650 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | ABS3 | 673 | [16 empty] | 2-35-08 | 2-35-09 | 2-3C | [5 empty] | ADCS_S | [8 empty] | 台南PS.673_ABS | 673(台南大灣一路) ABS | LINE69 | P07/69/670/ABS3 |  |  |  | CDC | 651 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | E3 | 673E | [16 empty] | 2-35-10 | 2-35-11 | 2-3D | [5 empty] | ADCS_S | [8 empty] | 台南PS.673E_ES | 673E(台南大灣一路) ES | LINE69 | P07/69/670/E3 |  |  |  | CDC | 652 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | PHA | [17 empty] | 1-19-06 | [7 empty] | 69KV_S | [8 empty] | 台南PS.680_PHA | 金榮線(680) 相間RY | LINE69 |  |  |  |  | CDC | 653 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | GDA | [17 empty] | 1-19-07 | [7 empty] | 69KV_S | [8 empty] | 台南PS.680_GDA | 金榮線(680) 接地RY | LINE69 |  |  |  |  | CDC | 654 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | 85A | [17 empty] | 1-19-05 | [7 empty] | 69KV_S | [8 empty] | 台南PS.680_85A | 金榮線(680) 85RY | LINE69 |  |  |  |  | CDC | 655 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | 74A | [17 empty] | 2-3C-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.680_74A | 金榮線(680) 74RY | LINE69 |  |  |  |  | CDC | 656 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | CB | [17 empty] | 1-19-04 |  | 1-6C | [5 empty] | 69KV_S | [8 empty] | 台南PS.680_CB | 680(金榮線) CB | LINE69 |  |  |  |  | CDC | 657 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | 81AS | [17 empty] | 1-0E-01 | [7 empty] | 69KV_S | [8 empty] | 台南PS.680_81A/S | (680) 81RY A/S | LINE69 |  |  |  |  | CDC | 658 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | 81UL | [17 empty] | 2-3D-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.680_81UL | (680) 81RY U/L | LINE69 |  |  |  |  | CDC | 659 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | ABS1 | 681 | [16 empty] | 2-34-04 | 2-34-05 | 2-32 | [5 empty] | ADCS_S | [8 empty] | 台南PS.681_ABS | 681(金榮線) ABS | LINE69 |  |  |  |  | CDC | 660 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | ABS2 | 682 | [16 empty] | 2-34-06 | 2-34-07 | 2-33 | [5 empty] | ADCS_S | [8 empty] | 台南PS.682_ABS | 682(金榮線) ABS | LINE69 |  |  |  |  | CDC | 661 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | ABS3 | 683 | [16 empty] | 2-34-08 | 2-34-09 | 2-34 | [5 empty] | ADCS_S | [8 empty] | 台南PS.683_ABS | 683(金榮線) ABS | LINE69 |  |  |  |  | CDC | 662 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | E3 | 683E | [16 empty] | 2-34-10 | 2-34-11 | 2-35 | [5 empty] | ADCS_S | [8 empty] | 台南PS.683E_ES | 683E(金榮線) ES | LINE69 |  |  |  |  | CDC | 663 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | PHA | [17 empty] | 1-19-02 | [7 empty] | 69KV_S | [8 empty] | 台南PS.710_PHA | 南仁線(710) 相間RY | LINE69 | P07/69/710/PHA |  |  |  | CDC | 664 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | GDA | [17 empty] | 1-19-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.710_GDA | 南仁線(710) 接地RY | LINE69 | P07/69/710/GDA |  |  |  | CDC | 665 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | CB | [17 empty] | 1-19-00 |  | 1-6B | [5 empty] | 69KV_S | [8 empty] | 台南PS.710_CB | 710(南仁線) CB | LINE69 | P07/69/710/CB |  |  |  | CDC | 666 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | 81AS | [17 empty] | 1-0E-00 | [7 empty] | 69KV_S | [8 empty] | 台南PS.710_81A/S | (710) 81RY A/S | LINE69 | P07/69/710/81A |  |  |  | CDC | 667 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | 81UL | [17 empty] | 2-3D-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.710_81UL | (710) 81RY U/L | LINE69 | P07/69/710/81UL |  |  |  | CDC | 668 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | ABS1 | 711 | [16 empty] | 2-33-12 | 2-33-13 | 2-2E | [5 empty] | ADCS_S | [8 empty] | 台南PS.711_ABS | 711(南仁線) ABS | LINE69 | P07/69/710/ABS1 |  |  |  | CDC | 669 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | ABS2 | 712 | [16 empty] | 2-33-14 | 2-33-15 | 2-2F | [5 empty] | ADCS_S | [8 empty] | 台南PS.712_ABS | 712(南仁線) ABS | LINE69 | P07/69/710/ABS2 |  |  |  | CDC | 670 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | ABS3 | 713 | [16 empty] | 2-34-00 | 2-34-01 | 2-30 | [5 empty] | ADCS_S | [8 empty] | 台南PS.713_ABS | 713(南仁線) ABS | LINE69 | P07/69/710/ABS3 |  |  |  | CDC | 671 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | E3 | 713E | [16 empty] | 2-34-02 | 2-34-03 | 2-31 | [5 empty] | ADCS_S | [8 empty] | 台南PS.713E_ES | 713E(南仁線) ES | LINE69 | P07/69/710/E3 |  |  |  | CDC | 672 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | 69KV_S | [8 empty] | 台南PS.720_PHA | 台南大灣二路(720) 相間RY | LINE69 | P07/69/720/PHA |  |  |  | CDC | 673 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | 69KV_S | [8 empty] | 台南PS.720_GDA | 台南大灣二路(720) 接地RY | LINE69 | P07/69/720/GDA |  |  |  | CDC | 674 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | CB | [17 empty] | 1-18-04 |  | 1-6A | [5 empty] | 69KV_S | [8 empty] | 台南PS.720_CB | 720(台南大灣二路) CB | LINE69 | P07/69/720/CB |  |  |  | CDC | 675 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | ABS1 | 721 | [16 empty] | 2-33-04 | 2-33-05 | 2-2A | [5 empty] | ADCS_S | [8 empty] | 台南PS.721_ABS | 721(台南大灣二路) ABS | LINE69 | P07/69/720/ABS1 |  |  |  | CDC | 676 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | ABS2 | 722 | [16 empty] | 2-33-06 | 2-33-07 | 2-2B | [5 empty] | ADCS_S | [8 empty] | 台南PS.722_ABS | 722(台南大灣二路) ABS | LINE69 | P07/69/720/ABS2 |  |  |  | CDC | 677 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | ABS3 | 723 | [16 empty] | 2-33-08 | 2-33-09 | 2-2C | [5 empty] | ADCS_S | [8 empty] | 台南PS.723_ABS | 723(台南大灣二路) ABS | LINE69 | P07/69/720/ABS3 |  |  |  | CDC | 678 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | E3 | 723E | [16 empty] | 2-33-10 | 2-33-11 | 2-2D | [5 empty] | ADCS_S | [8 empty] | 台南PS.723E_ES | 723E(台南大灣二路) ES | LINE69 | P07/69/720/E3 |  |  |  | CDC | 679 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-0A-07 |  | 3-31 | [5 empty] | ADCS_S | [8 empty] | 台南PS.230_CB | 230(11KV #3SC) CB | SC | P07/11/230/CB |  |  |  | CDC | 680 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-01-07 |  | 2-6C | [5 empty] | ADCS_S | [8 empty] | 台南PS.240_CB | 240(23KV #4SC) CB | SC | P07/22/240/CB |  |  |  | CDC | 681 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | PHA | [17 empty] | 2-06-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_PHA | 11KV台31線(KH31) 相間RY | FEEDER | P07/11/KH31/51A |  |  |  | CDC | 682 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) |  | GDA | [17 empty] | 2-06-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_GDA | 11KV台31線(KH31) 接地RY | FEEDER | P07/11/KH31/51NA |  |  |  | CDC | 683 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) 79RY |  | 79UL | [17 empty] | 3-30-08 |  | 3-0B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_79UL | 11KV台31線(KH31) 79RY U/L | FEEDER | P07/11/KH31/79UL |  |  |  | CDC | 684 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH31 | 台31線(KH31) LCO分流器 |  | ADJ | [17 empty] | 3-33-04 |  | 3-24 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_ADJ | 11KV台31線(KH31) LCO分流器 U/L | FEEDER | P07/11/KH31/ADJ |  |  |  | CDC | 685 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH31 | KH31(11KV台31線) |  | CB | [17 empty] | 2-02-02 |  | 2-6F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_CB | KH31(11KV台31線) CB | FEEDER | P07/11/KH31/CB |  |  |  | CDC | 686 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | PHA | [17 empty] | 2-06-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_PHA | 11KV台32線(KH32) 相間RY | FEEDER | P07/11/KH32/51A |  |  |  | CDC | 687 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) |  | GDA | [17 empty] | 2-07-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_GDA | 11KV台32線(KH32) 接地RY | FEEDER | P07/11/KH32/51NA |  |  |  | CDC | 688 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) 79RY |  | 79UL | [17 empty] | 3-30-09 |  | 3-0C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_79UL | 11KV台32線(KH32) 79RY U/L | FEEDER | P07/11/KH32/79UL |  |  |  | CDC | 689 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH32 | 台32線(KH32) LCO分流器 |  | ADJ | [17 empty] | 3-33-05 |  | 3-25 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_ADJ | 11KV台32線(KH32) LCO分流器 U/L | FEEDER | P07/11/KH32/ADJ |  |  |  | CDC | 690 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH32 | KH32(11KV台32線) |  | CB | [17 empty] | 2-02-03 |  | 2-70 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_CB | KH32(11KV台32線) CB | FEEDER | P07/11/KH32/CB |  |  |  | CDC | 691 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | PHA | [17 empty] | 2-07-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_PHA | 11KV台33線(KH33) 相間RY | FEEDER | P07/11/KH33/51A |  |  |  | CDC | 692 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) |  | GDA | [17 empty] | 2-07-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_GDA | 11KV台33線(KH33) 接地RY | FEEDER | P07/11/KH33/51NA |  |  |  | CDC | 693 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) 79RY |  | 79UL | [17 empty] | 3-30-10 |  | 3-0D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_79UL | 11KV台33線(KH33) 79RY U/L | FEEDER | P07/11/KH33/79UL |  |  |  | CDC | 694 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH33 | 台33線(KH33) LCO分流器 |  | ADJ | [17 empty] | 3-33-06 |  | 3-26 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_ADJ | 11KV台33線(KH33) LCO分流器 U/L | FEEDER | P07/11/KH33/ADJ |  |  |  | CDC | 695 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH33 | KH33(11KV台33線) |  | CB | [17 empty] | 2-02-04 |  | 2-71 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_CB | KH33(11KV台33線) CB | FEEDER | P07/11/KH33/CB |  |  |  | CDC | 696 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | PHA | [17 empty] | 2-07-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_PHA | 11KV台36線(KH36) 相間RY | FEEDER | P07/11/KH36/51A |  |  |  | CDC | 697 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) |  | GDA | [17 empty] | 2-07-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_GDA | 11KV台36線(KH36) 接地RY | FEEDER | P07/11/KH36/51NA |  |  |  | CDC | 698 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) 79RY |  | 79UL | [17 empty] | 3-30-11 |  | 3-0E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_79UL | 11KV台36線(KH36) 79RY U/L | FEEDER | P07/11/KH36/79UL |  |  |  | CDC | 699 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH36 | 台36線(KH36) LCO分流器 |  | ADJ | [17 empty] | 3-33-07 |  | 3-27 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_ADJ | 11KV台36線(KH36) LCO分流器 U/L | FEEDER | P07/11/KH36/ADJ |  |  |  | CDC | 700 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH36 | KH36(11KV台36線) |  | CB | [17 empty] | 2-02-06 |  | 2-72 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_CB | KH36(11KV台36線) CB | FEEDER | P07/11/KH36/CB |  |  |  | CDC | 701 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_PHA | 11KV台37線(KH37) 相間RY | FEEDER | P07/11/KH37/51A |  |  |  | CDC | 702 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_GDA | 11KV台37線(KH37) 接地RY | FEEDER | P07/11/KH37/51NA |  |  |  | CDC | 703 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) 79RY |  | 79UL | [17 empty] | 3-30-12 |  | 3-0F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_79UL | 11KV台37線(KH37) 79RY U/L | FEEDER | P07/11/KH37/79UL |  |  |  | CDC | 704 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH37 | 台37線(KH37) LCO分流器 |  | ADJ | [17 empty] | 3-33-08 |  | 3-28 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_ADJ | 11KV台37線(KH37) LCO分流器 U/L | FEEDER | P07/11/KH37/ADJ |  |  |  | CDC | 705 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH37 | KH37(11KV台37線) |  | CB | [17 empty] | 2-02-07 |  | 2-73 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_CB | KH37(11KV台37線) CB | FEEDER | P07/11/KH37/CB |  |  |  | CDC | 706 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | PHA | [17 empty] | 2-07-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_PHA | 11KV台38線(KH38) 相間RY | FEEDER | P07/11/KH38/51A |  |  |  | CDC | 707 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) |  | GDA | [17 empty] | 2-08-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_GDA | 11KV台38線(KH38) 接地RY | FEEDER | P07/11/KH38/51NA |  |  |  | CDC | 708 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) 79RY |  | 79UL | [17 empty] | 3-30-13 |  | 3-10 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_79UL | 11KV台38線(KH38) 79RY U/L | FEEDER | P07/11/KH38/79UL |  |  |  | CDC | 709 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH38 | 台38線(KH38) LCO分流器 |  | ADJ | [17 empty] | 3-33-09 |  | 3-29 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_ADJ | 11KV台38線(KH38) LCO分流器 U/L | FEEDER | P07/11/KH38/ADJ |  |  |  | CDC | 710 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH38 | KH38(11KV台38線) |  | CB | [17 empty] | 2-03-00 |  | 2-74 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_CB | KH38(11KV台38線) CB | FEEDER | P07/11/KH38/CB |  |  |  | CDC | 711 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | PHA | [17 empty] | 2-0C-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_PHA | 11KV台41線(KH41) 相間RY | FEEDER | P07/11/KH41/51A |  |  |  | CDC | 712 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) |  | GDA | [17 empty] | 2-0C-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_GDA | 11KV台41線(KH41) 接地RY | FEEDER | P07/11/KH41/51NA |  |  |  | CDC | 713 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) 79RY |  | 79UL | [17 empty] | 3-3C-01 |  | 3-39 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_79UL | 11KV台41線(KH41) 79RY U/L | FEEDER |  |  |  |  | CDC | 714 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH41 | KH41(11KV台41線) |  | CB | [17 empty] | 2-0B-00 |  | 3-32 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_CB | KH41(11KV台41線) CB | FEEDER | P07/11/KH41/CB |  |  |  | CDC | 715 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | PHA | [17 empty] | 2-0C-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_PHA | 11KV台42線(KH42) 相間RY | FEEDER | P07/11/KH42/51A |  |  |  | CDC | 716 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) |  | GDA | [17 empty] | 2-0C-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_GDA | 11KV台42線(KH42) 接地RY | FEEDER | P07/11/KH42/51NA |  |  |  | CDC | 717 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) 79RY |  | 79UL | [17 empty] | 3-3C-02 |  | 3-3A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_79UL | 11KV台42線(KH42) 79RY U/L | FEEDER |  |  |  |  | CDC | 718 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH42 | KH42(11KV台42線) |  | CB | [17 empty] | 2-0B-01 |  | 3-33 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_CB | KH42(11KV台42線) CB | FEEDER | P07/11/KH42/CB |  |  |  | CDC | 719 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | PHA | [17 empty] | 2-0C-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_PHA | 11KV台43線(KH43) 相間RY | FEEDER | P07/11/KH43/51A |  |  |  | CDC | 720 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) |  | GDA | [17 empty] | 2-0C-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_GDA | 11KV台43線(KH43) 接地RY | FEEDER | P07/11/KH43/51NA |  |  |  | CDC | 721 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) 79RY |  | 79UL | [17 empty] | 3-3C-03 |  | 3-3B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_79UL | 11KV台43線(KH43) 79RY U/L | FEEDER |  |  |  |  | CDC | 722 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH43 | KH43(11KV台43線) |  | CB | [17 empty] | 2-0B-02 |  | 3-34 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_CB | KH43(11KV台43線) CB | FEEDER | P07/11/KH43/CB |  |  |  | CDC | 723 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | PHA | [17 empty] | 2-0C-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_PHA | 11KV台44線(KH44) 相間RY | FEEDER | P07/11/KH44/51A |  |  |  | CDC | 724 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) |  | GDA | [17 empty] | 2-0C-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_GDA | 11KV台44線(KH44) 接地RY | FEEDER | P07/11/KH44/51NA |  |  |  | CDC | 725 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) 79RY |  | 79UL | [17 empty] | 3-3C-04 |  | 3-3C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_79UL | 11KV台44線(KH44) 79RY U/L | FEEDER |  |  |  |  | CDC | 726 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH44 | KH44(11KV台44線) |  | CB | [17 empty] | 2-0B-03 |  | 3-35 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_CB | KH44(11KV台44線) CB | FEEDER | P07/11/KH44/CB |  |  |  | CDC | 727 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | PHA | [17 empty] | 2-0D-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_PHA | 11KV台45線(KH45) 相間RY | FEEDER | P07/11/KH45/51A |  |  |  | CDC | 728 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) |  | GDA | [17 empty] | 2-0D-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_GDA | 11KV台45線(KH45) 接地RY | FEEDER | P07/11/KH45/51NA |  |  |  | CDC | 729 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) 79RY |  | 79UL | [17 empty] | 3-3C-05 |  | 3-3D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_79UL | 11KV台45線(KH45) 79RY U/L | FEEDER |  |  |  |  | CDC | 730 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH45 | KH45(11KV台45線) |  | CB | [17 empty] | 2-0B-04 |  | 3-36 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_CB | KH45(11KV台45線) CB | FEEDER | P07/11/KH45/CB |  |  |  | CDC | 731 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | PHA | [17 empty] | 2-0D-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_PHA | 11KV台46線(KH46) 相間RY | FEEDER | P07/11/KH46/51A |  |  |  | CDC | 732 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) |  | GDA | [17 empty] | 2-0D-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_GDA | 11KV台46線(KH46) 接地RY | FEEDER | P07/11/KH46/51NA |  |  |  | CDC | 733 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) 79RY |  | 79UL | [17 empty] | 3-3C-06 |  | 3-3E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_79UL | 11KV台46線(KH46) 79RY U/L | FEEDER |  |  |  |  | CDC | 734 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH46 | KH46(11KV台46線) |  | CB | [17 empty] | 2-0B-05 |  | 3-37 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_CB | KH46(11KV台46線) CB | FEEDER | P07/11/KH46/CB |  |  |  | CDC | 735 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | PHA | [17 empty] | 2-04-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_PHA | 23KV台61線(KH61) 相間RY | FEEDER | P07/22/KH61/51A |  |  |  | CDC | 736 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) |  | GDA | [17 empty] | 2-04-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_GDA | 23KV台61線(KH61) 接地RY | FEEDER | P07/22/KH61/51NA |  |  |  | CDC | 737 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) 79RY |  | 79UL | [17 empty] | 3-30-00 |  | 3-03 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_79UL | 23KV台61線(KH61) 79RY U/L | FEEDER | P07/22/KH61/79UL |  |  |  | CDC | 738 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH61 | 台61線(KH61) LCO分流器 |  | ADJ | [17 empty] | 3-32-14 |  | 3-1E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_ADJ | 23KV台61線(KH61) LCO分流器 U/L | FEEDER | P07/22/KH61/ADJ |  |  |  | CDC | 739 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH61 | KH61(23KV台61線) |  | CB | [17 empty] | 2-01-01 |  | 2-66 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_CB | KH61(23KV台61線) CB | FEEDER | P07/22/KH61/CB |  |  |  | CDC | 740 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | PHA | [17 empty] | 2-04-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_PHA | 23KV台62線(KH62) 相間RY | FEEDER | P07/22/KH62/51A |  |  |  | CDC | 741 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) |  | GDA | [17 empty] | 2-04-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_GDA | 23KV台62線(KH62) 接地RY | FEEDER | P07/22/KH62/51NA |  |  |  | CDC | 742 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) 79RY |  | 79UL | [17 empty] | 3-30-01 |  | 3-04 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_79UL | 23KV台62線(KH62) 79RY U/L | FEEDER | P07/22/KH62/79UL |  |  |  | CDC | 743 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH62 | 台62線(KH62) LCO分流器 |  | ADJ | [17 empty] | 3-32-15 |  | 3-1F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_ADJ | 23KV台62線(KH62) LCO分流器 U/L | FEEDER | P07/22/KH62/ADJ |  |  |  | CDC | 744 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH62 | KH62(23KV台62線) |  | CB | [17 empty] | 2-01-02 |  | 2-67 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_CB | KH62(23KV台62線) CB | FEEDER | P07/22/KH62/CB |  |  |  | CDC | 745 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | PHA | [17 empty] | 2-04-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_PHA | 23KV台63線(KH63) 相間RY | FEEDER | P07/22/KH63/51A |  |  |  | CDC | 746 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) |  | GDA | [17 empty] | 2-05-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_GDA | 23KV台63線(KH63) 接地RY | FEEDER | P07/22/KH63/51NA |  |  |  | CDC | 747 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) 79RY |  | 79UL | [17 empty] | 3-30-02 |  | 3-05 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_79UL | 23KV台63線(KH63) 79RY U/L | FEEDER | P07/22/KH63/79UL |  |  |  | CDC | 748 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH63 | 台63線(KH63) LCO分流器 |  | ADJ | [17 empty] | 3-33-00 |  | 3-20 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_ADJ | 23KV台63線(KH63) LCO分流器 U/L | FEEDER | P07/22/KH63/ADJ |  |  |  | CDC | 749 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH63 | KH63(23KV台63線) |  | CB | [17 empty] | 2-01-03 |  | 2-68 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_CB | KH63(23KV台63線) CB | FEEDER | P07/22/KH63/CB |  |  |  | CDC | 750 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | PHA | [17 empty] | 2-05-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_PHA | 23KV台64線(KH64) 相間RY | FEEDER | P07/22/KH64/51A |  |  |  | CDC | 751 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) |  | GDA | [17 empty] | 2-05-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_GDA | 23KV台64線(KH64) 接地RY | FEEDER | P07/22/KH64/51NA |  |  |  | CDC | 752 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) 79RY |  | 79UL | [17 empty] | 3-30-03 |  | 3-06 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_79UL | 23KV台64線(KH64) 79RY U/L | FEEDER | P07/22/KH64/79UL |  |  |  | CDC | 753 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH64 | 台64線(KH64) LCO分流器 |  | ADJ | [17 empty] | 3-33-01 |  | 3-21 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_ADJ | 23KV台64線(KH64) LCO分流器 U/L | FEEDER | P07/22/KH64/ADJ |  |  |  | CDC | 754 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH64 | KH64(23KV台64線) |  | CB | [17 empty] | 2-01-04 |  | 2-69 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_CB | KH64(23KV台64線) CB | FEEDER | P07/22/KH64/CB |  |  |  | CDC | 755 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_PHA | 23KV台65線(KH65) 相間RY | FEEDER | P07/22/KH65/51A |  |  |  | CDC | 756 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_GDA | 23KV台65線(KH65) 接地RY | FEEDER | P07/22/KH65/51NA |  |  |  | CDC | 757 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) 79RY |  | 79UL | [17 empty] | 3-30-04 |  | 3-07 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_79UL | 23KV台65線(KH65) 79RY U/L | FEEDER | P07/22/KH65/79UL |  |  |  | CDC | 758 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH65 | 台65線(KH65) LCO分流器 |  | ADJ | [17 empty] | 3-33-02 |  | 3-22 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_ADJ | 23KV台65線(KH65) LCO分流器 U/L | FEEDER | P07/22/KH65/ADJ |  |  |  | CDC | 759 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH65 | KH65(23KV台65線) |  | CB | [17 empty] | 2-01-05 |  | 2-6A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_CB | KH65(23KV台65線) CB | FEEDER | P07/22/KH65/CB |  |  |  | CDC | 760 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | PHA | [17 empty] | 2-05-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_PHA | 23KV台66線(KH66) 相間RY | FEEDER | P07/22/KH66/51A |  |  |  | CDC | 761 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) |  | GDA | [17 empty] | 2-05-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_GDA | 23KV台66線(KH66) 接地RY | FEEDER | P07/22/KH66/51NA |  |  |  | CDC | 762 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) 79RY |  | 79UL | [17 empty] | 3-30-05 |  | 3-08 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_79UL | 23KV台66線(KH66) 79RY U/L | FEEDER | P07/22/KH66/79UL |  |  |  | CDC | 763 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH66 | 台66線(KH66) LCO分流器 |  | ADJ | [17 empty] | 3-33-03 |  | 3-23 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_ADJ | 23KV台66線(KH66) LCO分流器 U/L | FEEDER | P07/22/KH66/ADJ |  |  |  | CDC | 764 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH66 | KH66(23KV台66線) |  | CB | [17 empty] | 2-01-06 |  | 2-6B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_CB | KH66(23KV台66線) CB | FEEDER | P07/22/KH66/CB |  |  |  | CDC | 765 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | PHA | [17 empty] | 2-09-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_PHA | 23KV台71線(KH71) 相間RY | FEEDER | P07/22/KH71/51A |  |  |  | CDC | 766 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) |  | GDA | [17 empty] | 2-09-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_GDA | 23KV台71線(KH71) 接地RY | FEEDER | P07/22/KH71/51NA |  |  |  | CDC | 767 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) 79RY |  | 79UL | [17 empty] | 3-31-02 |  | 3-15 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_79UL | 23KV台71線(KH71) 79RY U/L | FEEDER | P07/22/KH71/79UL |  |  |  | CDC | 768 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH71 | 台71線(KH71) LCO分流器 |  | ADJ | [17 empty] | 3-33-10 |  | 3-2A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_ADJ | 23KV台71線(KH71) LCO分流器 U/L | FEEDER | P07/22/KH71/ADJ |  |  |  | CDC | 769 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH71 | KH71(23KV台71線) |  | CB | [17 empty] | 2-03-05 |  | 2-7A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_CB | KH71(23KV台71線) CB | FEEDER | P07/22/KH71/CB |  |  |  | CDC | 770 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | PHA | [17 empty] | 2-09-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_PHA | 23KV台72線(KH72) 相間RY | FEEDER | P07/22/KH72/51A |  |  |  | CDC | 771 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) |  | GDA | [17 empty] | 2-09-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_GDA | 23KV台72線(KH72) 接地RY | FEEDER | P07/22/KH72/51NA |  |  |  | CDC | 772 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) 79RY |  | 79UL | [17 empty] | 3-31-03 |  | 3-16 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_79UL | 23KV台72線(KH72) 79RY U/L | FEEDER | P07/22/KH72/79UL |  |  |  | CDC | 773 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH72 | 台72線(KH72) LCO分流器 |  | ADJ | [17 empty] | 3-33-11 |  | 3-2B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_ADJ | 23KV台72線(KH72) LCO分流器 U/L | FEEDER | P07/22/KH72/ADJ |  |  |  | CDC | 774 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH72 | KH72(23KV台72線) |  | CB | [17 empty] | 2-03-06 |  | 2-7B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_CB | KH72(23KV台72線) CB | FEEDER | P07/22/KH72/CB |  |  |  | CDC | 775 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_PHA | 23KV台73線(KH73) 相間RY | FEEDER | P07/22/KH73/51A |  |  |  | CDC | 776 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_GDA | 23KV台73線(KH73) 接地RY | FEEDER | P07/22/KH73/51NA |  |  |  | CDC | 777 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) 79RY |  | 79UL | [17 empty] | 3-31-04 |  | 3-17 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_79UL | 23KV台73線(KH73) 79RY U/L | FEEDER | P07/22/KH73/79UL |  |  |  | CDC | 778 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH73 | 台73線(KH73) LCO分流器 |  | ADJ | [17 empty] | 3-33-12 |  | 3-2C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_ADJ | 23KV台73線(KH73) LCO分流器 U/L | FEEDER | P07/22/KH73/ADJ |  |  |  | CDC | 779 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH73 | KH73(23KV台73線) |  | CB | [17 empty] | 2-03-07 |  | 2-7C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_CB | KH73(23KV台73線) CB | FEEDER | P07/22/KH73/CB |  |  |  | CDC | 780 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | PHA | [17 empty] | 2-0A-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_PHA | 23KV台74線(KH74) 相間RY | FEEDER | P07/22/KH74/51A |  |  |  | CDC | 781 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) |  | GDA | [17 empty] | 2-0A-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_GDA | 23KV台74線(KH74) 接地RY | FEEDER | P07/22/KH74/51NA |  |  |  | CDC | 782 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) 79RY |  | 79UL | [17 empty] | 3-31-05 |  | 3-18 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_79UL | 23KV台74線(KH74) 79RY U/L | FEEDER | P07/22/KH74/79UL |  |  |  | CDC | 783 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH74 | 台74線(KH74) LCO分流器 |  | ADJ | [17 empty] | 3-33-13 |  | 3-2D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_ADJ | 23KV台74線(KH74) LCO分流器 U/L | FEEDER | P07/22/KH74/ADJ |  |  |  | CDC | 784 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH74 | KH74(23KV台74線) |  | CB | [17 empty] | 2-04-00 |  | 2-7D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_CB | KH74(23KV台74線) CB | FEEDER | P07/22/KH74/CB |  |  |  | CDC | 785 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | PHA | [17 empty] | 2-0A-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_PHA | 23KV台75線(KH75) 相間RY | FEEDER | P07/22/KH75/51A |  |  |  | CDC | 786 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) |  | GDA | [17 empty] | 2-0A-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_GDA | 23KV台75線(KH75) 接地RY | FEEDER | P07/22/KH75/51NA |  |  |  | CDC | 787 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) 79RY |  | 79UL | [17 empty] | 3-31-06 |  | 3-19 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_79UL | 23KV台75線(KH75) 79RY U/L | FEEDER | P07/22/KH75/79UL |  |  |  | CDC | 788 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH75 | 台75線(KH75) LCO分流器 |  | ADJ | [17 empty] | 3-33-14 |  | 3-2E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_ADJ | 23KV台75線(KH75) LCO分流器 U/L | FEEDER | P07/22/KH75/ADJ |  |  |  | CDC | 789 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH75 | KH75(23KV台75線) |  | CB | [17 empty] | 2-04-01 |  | 2-7E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_CB | KH75(23KV台75線) CB | FEEDER | P07/22/KH75/CB |  |  |  | CDC | 790 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-03-02 |  | 2-77 | [5 empty] | ADCS_S | [8 empty] | 台南PS.100_CB | 100(TIE) CB | TIE | P07/11/100/CB |  |  |  | CDC | 791 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-08-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.100_51A | 11KV TIE(100) 51RY | TIE | P07/11/100/51A |  |  |  | CDC | 792 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-08-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.100_51NA | 11KV TIE(100) 51N RY | TIE | P07/11/100/51NA |  |  |  | CDC | 793 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-03-04 |  | 1-08 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1500_CB | 1500(TIE) CB | TIE | P07/161/1500/CB |  |  |  | CDC | 794 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1500_50A | 161KV TIE(1500) 50RY | TIE | P07/161/1500/PHA |  |  |  | CDC | 795 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-02-01 |  | 2-6E | [5 empty] | ADCS_S | [8 empty] | 台南PS.200_CB | 200(TIE) CB | TIE | P07/22/200/CB |  |  |  | CDC | 796 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-06-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.200_51A | 23KV TIE(200) 51RY | TIE | P07/22/200/51A |  |  |  | CDC | 797 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-06-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.200_51NA | 23KV TIE(200) 51N RY | TIE | P07/22/200/51NA |  |  |  | CDC | 798 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-15-00 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 台南PS.300_CB | 300(TIE) CB | TIE | P07/11/300/CB |  |  |  | CDC | 799 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-15-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.300_51A | 11KV TIE(300) 51RY | TIE | P07/11/300/51A |  |  |  | CDC | 800 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-15-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.300_51NA | 11KV TIE(300) 51N RY | TIE | P07/11/300/51NA |  |  |  | CDC | 801 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-06-00 |  | 1-09 | [5 empty] | 69KV_S | [8 empty] | 台南PS.600_CB | 600(TIE) CB | TIE | P07/69/600/CB |  |  |  | CDC | 802 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | [16 empty] | 2-3A-08 | 2-3A-09 | 2-64 | [5 empty] | ADCS_S | [8 empty] | 台南PS.601_ABS | 601(TIE) ABS | TIE | P07/69/600/ABS1 |  |  |  | CDC | 803 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | [16 empty] | 2-3A-10 | 2-3A-11 | 2-65 | [5 empty] | ADCS_S | [8 empty] | 台南PS.602_ABS | 602(TIE) ABS | TIE | P07/69/600/ABS2 |  |  |  | CDC | 804 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | [17 empty] | 1-06-05 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 台南PS.1650_CB | 1650(#1MTR) CB | MTR | P07/161/1650/CB |  |  |  | CDC | 805 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-06-06 |  | 1-0B | [5 empty] | 69KV_S | [8 empty] | 台南PS.750_CB | 750(#1MTR) CB | MTR | P07/69/750/CB |  |  |  | CDC | 806 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | P07//1MTR/51ZA |  |  |  | CDC | 807 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#1MTR_87A | #1MTR 87RY | MTR | P07//1MTR/87A |  |  |  | CDC | 808 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-06-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | P07//1MTR/96PA |  |  |  | CDC | 809 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_96D | #1MTR 96D RY | MTR | P07//1MTR/96D |  |  |  | CDC | 810 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_96P | #1MTR 96P RY | MTR | P07//1MTR/96P |  |  |  | CDC | 811 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-35-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_63Q | #1MTR 63Q RY | MTR | P07//1MTR/63Q |  |  |  | CDC | 812 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-35-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | P07//1MTR/3A5Other |  |  |  | CDC | 813 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_TRA | #1MTR 重故障 | MTR | P07//1MTR/TRA |  |  |  | CDC | 814 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_TRF | #1MTR 輕故障 | MTR | P07//1MTR/TRF |  |  |  | CDC | 815 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | P07//1MTR/SupLocal |  |  |  | CDC | 816 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-04 |  | 1-2A | [5 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | P07//1MTR/Tap Chan |  |  |  | CDC | 817 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | M/F/I | [17 empty] | 1-39-12 | 1-39-13 | 1-2B | [5 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | P07//1MTR/M_F_I |  |  |  | CDC | 818 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS1 | 1651 | [16 empty] | 2-30-00 | 2-30-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1651_ABS | 1651(#1MTR) ABS | MTR | P07/161/1650/ABS1 |  |  |  | CDC | 819 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | ABS2 | 1652 | [16 empty] | 2-30-02 | 2-30-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1652_ABS | 1652(#1MTR) ABS | MTR | P07/161/1650/ABS2 |  |  |  | CDC | 820 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 2-30-04 | 2-30-05 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 台南PS.751_ABS | 751(#1MTR) ABS | MTR | P07/69/750/ABS1 |  |  |  | CDC | 821 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | ABS2 | 752 | [16 empty] | 2-30-06 | 2-30-07 | 2-03 | [5 empty] | ADCS_S | [8 empty] | 台南PS.752_ABS | 752(#1MTR) ABS | MTR | P07/69/750/ABS2 |  |  |  | CDC | 822 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | [17 empty] | 1-07-05 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 台南PS.1660_CB | 1660(#2MTR) CB | MTR | P07/161/1660/CB |  |  |  | CDC | 823 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-07-06 |  | 1-0D | [5 empty] | 69KV_S | [8 empty] | 台南PS.760_CB | 760(#2MTR) CB | MTR | P07/69/760/CB |  |  |  | CDC | 824 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-08-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | P07//2MTR/51ZA |  |  |  | CDC | 825 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-08-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#2MTR_87A | #2MTR 87RY | MTR | P07//2MTR/87A |  |  |  | CDC | 826 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-07-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | P07//2MTR/96PA |  |  |  | CDC | 827 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_96D | #2MTR 96D RY | MTR | P07//2MTR/96D |  |  |  | CDC | 828 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_96P | #2MTR 96P RY | MTR | P07//2MTR/96P |  |  |  | CDC | 829 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-31-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_63Q | #2MTR 63Q RY | MTR | P07//2MTR/63Q |  |  |  | CDC | 830 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-31-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | P07//2MTR/96B1 |  |  |  | CDC | 831 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | P07//2MTR/96B2 |  |  |  | CDC | 832 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-33-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_TRA | #2MTR 重故障 | MTR | P07//2MTR/TRA |  |  |  | CDC | 833 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-33-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_TRF | #2MTR 輕故障 | MTR | P07//2MTR/TRF |  |  |  | CDC | 834 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | P07//2MTR/SupLocal |  |  |  | CDC | 835 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-33-10 |  | 1-2E | [5 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | P07//2MTR/Tap Chan |  |  |  | CDC | 836 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | M/F/I | [17 empty] | 1-39-14 | 1-39-15 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | P07//2MTR/M_F_I |  |  |  | CDC | 837 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | [16 empty] | 2-30-08 | 2-30-09 | 2-04 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1661_ABS | 1661(#2MTR) ABS | MTR | P07/161/1660/ABS1 |  |  |  | CDC | 838 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | [16 empty] | 2-30-10 | 2-30-11 | 2-05 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1662_ABS | 1662(#2MTR) ABS | MTR | P07/161/1660/ABS2 |  |  |  | CDC | 839 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 2-30-12 | 2-30-13 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 台南PS.761_ABS | 761(#2MTR) ABS | MTR | P07/69/760/ABS1 |  |  |  | CDC | 840 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | [16 empty] | 2-30-14 | 2-30-15 | 2-07 | [5 empty] | ADCS_S | [8 empty] | 台南PS.762_ABS | 762(#2MTR) ABS | MTR | P07/69/760/ABS2 |  |  |  | CDC | 841 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB | [17 empty] | 1-08-05 |  | 1-0E | [5 empty] | 161KV_S | [8 empty] | 台南PS.1670_CB | 1670(#3MTR) CB | MTR | P07/161/1670/CB |  |  |  | CDC | 842 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-08-06 |  | 1-0F | [5 empty] | 69KV_S | [8 empty] | 台南PS.770_CB | 770(#3MTR) CB | MTR | P07/69/770/CB |  |  |  | CDC | 843 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-09-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | P07//3MTR/51ZA |  |  |  | CDC | 844 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-09-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#3MTR_87A | #3MTR 87RY | MTR | P07//3MTR/87A |  |  |  | CDC | 845 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-08-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | P07//3MTR/96PA |  |  |  | CDC | 846 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-34-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_96D | #3MTR 96D RY | MTR | P07//3MTR/96D |  |  |  | CDC | 847 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-34-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_96P | #3MTR 96P RY | MTR | P07//3MTR/96P |  |  |  | CDC | 848 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_63Q | #3MTR 63Q RY | MTR | P07//3MTR/63Q |  |  |  | CDC | 849 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | P07//3MTR/3A5Other |  |  |  | CDC | 850 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-34-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_TRA | #3MTR 重故障 | MTR | P07//3MTR/TRA |  |  |  | CDC | 851 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-34-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_TRF | #3MTR 輕故障 | MTR | P07//3MTR/TRF |  |  |  | CDC | 852 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-34-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | P07//3MTR/SupLocal |  |  |  | CDC | 853 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-34-00 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | P07//3MTR/Tap Chan |  |  |  | CDC | 854 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | M/F/I | [17 empty] | 1-3A-00 | 1-3A-01 | 1-33 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | P07//3MTR/M_F_I |  |  |  | CDC | 855 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | [16 empty] | 2-31-00 | 2-31-01 | 2-08 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1671_ABS | 1671(#3MTR) ABS | MTR | P07/161/1670/ABS1 |  |  |  | CDC | 856 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | [16 empty] | 2-31-02 | 2-31-03 | 2-09 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1672_ABS | 1672(#3MTR) ABS | MTR | P07/161/1670/ABS2 |  |  |  | CDC | 857 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 2-31-04 | 2-31-05 | 2-0A | [5 empty] | ADCS_S | [8 empty] | 台南PS.771_ABS | 771(#3MTR) ABS | MTR | P07/69/770/ABS1 |  |  |  | CDC | 858 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | [16 empty] | 2-31-06 | 2-31-07 | 2-0B | [5 empty] | ADCS_S | [8 empty] | 台南PS.772_ABS | 772(#3MTR) ABS | MTR | P07/69/770/ABS2 |  |  |  | CDC | 859 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | CB | [17 empty] | 1-0A-06 |  | 1-12 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1750_CB | 1750(#5DTR) CB | MTR | P07/161/1750/CB |  |  |  | CDC | 860 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 330 | #6DTR(330) |  | CB | [17 empty] | 1-0B-06 |  | 1-16 | [5 empty] | ADCS_S | [8 empty] | 台南PS.330_CB | 330(#6DTR) CB | MTR | P07/22/330/CB |  |  |  | CDC | 861 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 350 | #7DTR(350) |  | CB | [17 empty] | 1-0C-06 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 台南PS.350_CB | 350(#7DTR) CB | MTR | P07/22/350/CB |  |  |  | CDC | 862 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 51ZA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#5DTR_51ZA | #5DTR 51Z RY | MTR | P07//5DTR/51ZA |  |  |  | CDC | 863 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 87A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#5DTR_87A | #5DTR 87RY | MTR | P07//5DTR/87A |  |  |  | CDC | 864 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 330 | #6DTR(330) |  | 51A | [17 empty] | 1-0C-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.330_51A | #6DTR二次側(330) 51RY | MTR | P07/22/330/51A |  |  |  | CDC | 865 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 350 | #7DTR(350) |  | 51A | [17 empty] | 1-0D-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.350_51A | #7DTR二次側(350) 51RY | MTR | P07/22/350/51A |  |  |  | CDC | 866 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 96PA | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#5DTR_96PA | #5DTR 機械保護動作 | MTR | P07//5DTR/96PA |  |  |  | CDC | 867 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 96D | [17 empty] | 1-3D-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_96D | #5DTR 96D RY | MTR | P07//5DTR/96D |  |  |  | CDC | 868 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 96P | [17 empty] | 1-3D-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_96P | #5DTR 96P RY | MTR | P07//5DTR/96P |  |  |  | CDC | 869 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 63Q | [17 empty] | 1-3D-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_63Q | #5DTR 63Q RY | MTR | P07//5DTR/63Q |  |  |  | CDC | 870 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 96B1 | [17 empty] | 1-3D-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_96B1 | #5DTR 96B1 RY | MTR | P07//5DTR/96B1 |  |  |  | CDC | 871 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 96B2 | [17 empty] | 1-3D-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_96B2 | #5DTR 96B2 RY | MTR | P07//5DTR/96B2 |  |  |  | CDC | 872 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | TRA | [17 empty] | 1-35-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_TRA | #5DTR 重故障 | MTR | P07//5DTR/TRA |  |  |  | CDC | 873 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | TRF | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_TRF | #5DTR 輕故障 | MTR | P07//5DTR/TRF |  |  |  | CDC | 874 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | SupLocal | [17 empty] | 1-34-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_S/L | #5DTR(A) OLTC S/L | MTR | P07//5DTR(A)/SupLocal |  |  |  | CDC | 875 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 5DTR(A) | #5DTR(A) |  | A_M | [17 empty] | 1-34-12 |  | 1-3A | [5 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(A)_A/M | #5DTR(A) OLTC A/M | MTR | P07//5DTR(A)/Tap Chan |  |  |  | CDC | 876 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | SupLocal | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_S/L | #5DTR(B) OLTC S/L | MTR | P07//5DTR(B)/SupLocal |  |  |  | CDC | 877 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 5DTR(B) | #5DTR(B) |  | A_M | [17 empty] | 1-34-14 |  | 1-3C | [5 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR(B)_A/M | #5DTR(B) OLTC A/M | MTR | P07//5DTR(B)/Tap Chan |  |  |  | CDC | 878 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | ABS1 | 1751 | [16 empty] | 2-32-00 | 2-32-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1751_ABS | 1751(#5DTR) ABS | MTR | P07/161/1750/ABS1 |  |  |  | CDC | 879 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | ABS2 | 1752 | [16 empty] | 2-32-02 | 2-32-03 | 2-11 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1752_ABS | 1752(#5DTR) ABS | MTR | P07/161/1750/ABS2 |  |  |  | CDC | 880 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | CB | [17 empty] | 1-0B-05 |  | 1-15 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1760_CB | 1760(#6DTR) CB | MTR | P07/161/1760/CB |  |  |  | CDC | 881 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 51ZA | [17 empty] | 1-0C-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#6DTR_51ZA | #6DTR 51Z RY | MTR | P07//6DTR/51ZA |  |  |  | CDC | 882 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 87A | [17 empty] | 1-0C-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#6DTR_87A | #6DTR 87RY | MTR | P07//6DTR/87A |  |  |  | CDC | 883 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 96PA | [17 empty] | 1-0B-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#6DTR_96PA | #6DTR 機械保護動作 | MTR | P07//6DTR/96PA |  |  |  | CDC | 884 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 96D | [17 empty] | 1-3D-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_96D | #6DTR 96D RY | MTR | P07//6DTR/96D |  |  |  | CDC | 885 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 96P | [17 empty] | 1-3D-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_96P | #6DTR 96P RY | MTR | P07//6DTR/96P |  |  |  | CDC | 886 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 63Q | [17 empty] | 1-3D-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_63Q | #6DTR 63Q RY | MTR | P07//6DTR/63Q |  |  |  | CDC | 887 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 96B1 | [17 empty] | 1-3D-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_96B1 | #6DTR 96B1 RY | MTR | P07//6DTR/96B1 |  |  |  | CDC | 888 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 96B2 | [17 empty] | 1-3D-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_96B2 | #6DTR 96B2 RY | MTR | P07//6DTR/96B2 |  |  |  | CDC | 889 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | TRA | [17 empty] | 1-35-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_TRA | #6DTR 重故障 | MTR | P07//6DTR/TRA |  |  |  | CDC | 890 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | TRF | [17 empty] | 1-35-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_TRF | #6DTR 輕故障 | MTR | P07//6DTR/TRF |  |  |  | CDC | 891 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | SupLocal | [17 empty] | 1-35-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_S/L | #6DTR OLTC S/L | MTR | P07//6DTR/SupLocal |  |  |  | CDC | 892 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | A_M | [17 empty] | 1-35-04 |  | 1-3E | [5 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_A/M | #6DTR OLTC A/M | MTR | P07//6DTR/Tap Chan |  |  |  | CDC | 893 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS1 | 1761 | [16 empty] | 2-32-04 | 2-32-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1761_ABS | 1761(#6DTR) ABS | MTR | P07/161/1760/ABS1 |  |  |  | CDC | 894 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | ABS2 | 1762 | [16 empty] | 2-32-06 | 2-32-07 | 2-13 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1762_ABS | 1762(#6DTR) ABS | MTR | P07/161/1760/ABS2 |  |  |  | CDC | 895 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | CB | [17 empty] | 1-0C-05 |  | 1-18 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1770_CB | 1770(#7DTR) CB | MTR | P07/161/1770/CB |  |  |  | CDC | 896 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 370 | #8DTR(370) |  | CB | [17 empty] | 1-0F-04 |  | 1-1B | [5 empty] | ADCS_S | [8 empty] | 台南PS.370_CB | 370(#8DTR) CB | MTR | P07/11/370/CB |  |  |  | CDC | 897 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 51ZA | [17 empty] | 1-0D-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#7DTR_51ZA | #7DTR 51Z RY | MTR | P07//7DTR/51ZA |  |  |  | CDC | 898 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 87A | [17 empty] | 1-0D-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#7DTR_87A | #7DTR 87RY | MTR | P07//7DTR/87A |  |  |  | CDC | 899 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 370 | #8DTR(370) |  | 51A | [17 empty] | 1-0F-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.370_51A | #8DTR二次側(370) 51RY | MTR | P07/11/370/51A |  |  |  | CDC | 900 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 96PA | [17 empty] | 1-0C-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#7DTR_96PA | #7DTR 機械保護動作 | MTR | P07//7DTR/96PA |  |  |  | CDC | 901 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 96D | [17 empty] | 1-3D-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_96D | #7DTR 96D RY | MTR | P07//7DTR/96D |  |  |  | CDC | 902 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 96P | [17 empty] | 1-3D-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_96P | #7DTR 96P RY | MTR | P07//7DTR/96P |  |  |  | CDC | 903 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 63Q | [17 empty] | 1-3D-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_63Q | #7DTR 63Q RY | MTR | P07//7DTR/63Q |  |  |  | CDC | 904 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 96B1 | [17 empty] | 1-3D-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_96B1 | #7DTR 96B1 RY | MTR | P07//7DTR/96B1 |  |  |  | CDC | 905 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 96B2 | [17 empty] | 1-3D-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_96B2 | #7DTR 96B2 RY | MTR | P07//7DTR/96B2 |  |  |  | CDC | 906 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | TRA | [17 empty] | 1-35-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_TRA | #7DTR 重故障 | MTR | P07//7DTR/TRA |  |  |  | CDC | 907 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | TRF | [17 empty] | 1-35-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_TRF | #7DTR 輕故障 | MTR | P07//7DTR/TRF |  |  |  | CDC | 908 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | SupLocal | [17 empty] | 1-35-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_S/L | #7DTR OLTC S/L | MTR | P07//7DTR/SupLocal |  |  |  | CDC | 909 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | A_M | [17 empty] | 1-35-12 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_A/M | #7DTR OLTC A/M | MTR | P07//7DTR/Tap Chan |  |  |  | CDC | 910 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | ABS1 | 1771 | [16 empty] | 2-32-08 | 2-32-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1771_ABS | 1771(#7DTR) ABS | MTR | P07/161/1770/ABS1 |  |  |  | CDC | 911 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | ABS2 | 1772 | [16 empty] | 2-32-10 | 2-32-11 | 2-15 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1772_ABS | 1772(#7DTR) ABS | MTR | P07/161/1770/ABS2 |  |  |  | CDC | 912 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | CB | [17 empty] | 2-0D-04 |  | 1-47 | [5 empty] | ADCS_S | [8 empty] | 台南PS.410_CB | 410(11KV #11SC) CB | SC | P07/11/410/CB |  |  |  | CDC | 913 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | SCA | [17 empty] | 2-0D-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.410_SCA | 11KV #11SC 51,51N RY | SC | P07/11/410/SCA |  |  |  | CDC | 914 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 410 | #11SC(410) |  | UVA | [17 empty] | 2-0D-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.410_UVA | 11KV #11SC 27RY(欠壓) | SC | P07/11/410/UVA |  |  |  | CDC | 915 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | CB | [17 empty] | 2-0D-07 |  | 1-48 | [5 empty] | ADCS_S | [8 empty] | 台南PS.420_CB | 420(11KV #12SC) CB | SC | P07/11/420/CB |  |  |  | CDC | 916 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | SCA | [17 empty] | 2-0E-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.420_SCA | 11KV #12SC 51,51N RY | SC | P07/11/420/SCA |  |  |  | CDC | 917 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 420 | #12SC(420) |  | UVA | [17 empty] | 2-0E-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.420_UVA | 11KV #12SC 27RY(欠壓) | SC | P07/11/420/UVA |  |  |  | CDC | 918 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | CB | [17 empty] | 2-19-04 |  | 1-4A | [5 empty] | ADCS_S | [8 empty] | 台南PS.430_CB | 430(11KV #13SC) CB | SC | P07/11/430/CB |  |  |  | CDC | 919 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | SCA | [17 empty] | 2-19-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.430_SCA | 11KV #13SC 51,51N RY | SC | P07/11/430/SCA |  |  |  | CDC | 920 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 430 | #13SC(430) |  | UVA | [17 empty] | 2-19-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.430_UVA | 11KV #13SC 27RY(欠壓) | SC | P07/11/430/UVA |  |  |  | CDC | 921 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | CB | [17 empty] | 2-19-01 |  | 1-49 | [5 empty] | ADCS_S | [8 empty] | 台南PS.440_CB | 440(11KV #14SC) CB | SC | P07/11/440/CB |  |  |  | CDC | 922 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | SCA | [17 empty] | 2-19-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.440_SCA | 11KV #14SC 51,51N RY | SC | P07/11/440/SCA |  |  |  | CDC | 923 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 440 | #14SC(440) |  | UVA | [17 empty] | 2-19-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.440_UVA | 11KV #14SC 27RY(欠壓) | SC | P07/11/440/UVA |  |  |  | CDC | 924 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 2-02-05 |  | 2-75 | [5 empty] | ADCS_S | [8 empty] | 台南PS.210_CB | 210(11KV #1SC) CB | SC | P07/11/210/CB |  |  |  | CDC | 925 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 2-08-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.210_SCA | 11KV #1SC 51,51N RY | SC | P07/11/210/SCA |  |  |  | CDC | 926 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 2-08-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | P07/11/210/UVA |  |  |  | CDC | 927 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-1F-01 |  | 1-78 | [5 empty] | 69KV_S | [8 empty] | 台南PS.810_CB | 810(69KV #1SC) CB | SC | P07/69/810/CB |  |  |  | CDC | 928 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 2-3A-00 | 2-3A-01 | 2-60 | [5 empty] | ADCS_S | [8 empty] | 台南PS.811_ABS | 811(69KV #1SC) ABS | SC | P07/69/810/ABS1 |  |  |  | CDC | 929 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | ABS2 | 812 | [16 empty] | 2-3A-02 | 2-3A-03 | 2-61 | [5 empty] | ADCS_S | [8 empty] | 台南PS.812_ABS | 812(69KV #1SC) ABS | SC | P07/69/810/ABS2 |  |  |  | CDC | 930 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 2-00-00 | [7 empty] | 69KV_S | [8 empty] | 台南PS.810_SCA | 69KV #1SC 51,51N RY | SC | P07/69/810/SCA |  |  |  | CDC | 931 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 2-00-01 | [7 empty] | 69KV_S | [8 empty] | 台南PS.810_OUVA | 69KV #1SC 27,59RY | SC | P07/69/810/UVA |  |  |  | CDC | 932 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 810 | #1SC(810) |  | NCA | [17 empty] | 2-3F-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.810_NCA | 69KV #1SC NCT RY | SC | P07/0/1SC/NCA |  |  |  | CDC | 933 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | CB | [17 empty] | 1-1F-00 |  | 1-77 | [5 empty] | 69KV_S | [8 empty] | 台南PS.820_CB | 820(69KV #2SC) CB | SC | P07/69/820/CB |  |  |  | CDC | 934 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | [16 empty] | 2-39-12 | 2-39-13 | 2-5E | [5 empty] | ADCS_S | [8 empty] | 台南PS.821_ABS | 821(69KV #2SC) ABS | SC | P07/69/820/ABS1 |  |  |  | CDC | 935 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | [16 empty] | 2-39-14 | 2-39-15 | 2-5F | [5 empty] | ADCS_S | [8 empty] | 台南PS.822_ABS | 822(69KV #2SC) ABS | SC | P07/69/820/ABS2 |  |  |  | CDC | 936 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | SCA | [17 empty] | 2-00-02 | [7 empty] | 69KV_S | [8 empty] | 台南PS.820_SCA | 69KV #2SC 51,51N RY | SC | P07/69/820/SCA |  |  |  | CDC | 937 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | UVA | [17 empty] | 2-00-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.820_OUVA | 69KV #2SC 27,59RY | SC | P07/69/820/UVA |  |  |  | CDC | 938 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 820 | #2SC(820) |  | NCA | [17 empty] | 2-3F-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.820_NCA | 69KV #2SC NCT RY | SC | P07/0/2SC/NCA |  |  |  | CDC | 939 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | CB | [17 empty] | 1-1F-02 |  | 1-79 | [5 empty] | 69KV_S | [8 empty] | 台南PS.830_CB | 830(69KV #3SC) CB | SC | P07/69/830/CB |  |  |  | CDC | 940 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | [16 empty] | 2-3A-04 | 2-3A-05 | 2-62 | [5 empty] | ADCS_S | [8 empty] | 台南PS.831_ABS | 831(69KV #3SC) ABS | SC | P07/69/830/ABS1 |  |  |  | CDC | 941 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | [16 empty] | 2-3A-06 | 2-3A-07 | 2-63 | [5 empty] | ADCS_S | [8 empty] | 台南PS.832_ABS | 832(69KV #3SC) ABS | SC | P07/69/830/ABS2 |  |  |  | CDC | 942 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | SCA | [17 empty] | 2-00-04 | [7 empty] | 69KV_S | [8 empty] | 台南PS.830_SCA | 69KV #3SC 51,51N RY | SC | P07/69/830/SCA |  |  |  | CDC | 943 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | UVA | [17 empty] | 2-00-05 | [7 empty] | 69KV_S | [8 empty] | 台南PS.830_OUVA | 69KV #3SC 27,59RY | SC | P07/69/830/UVA |  |  |  | CDC | 944 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 830 | #3SC(830) |  | NCA | [17 empty] | 2-3F-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.830_NCA | 69KV #3SC NCT RY | SC | P07/0/3SC/NCA |  |  |  | CDC | 945 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-30-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | P07/161/1BUS/BUS_VUA |  |  |  | CDC | 946 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-03-06 | [7 empty] | 161KV_S | [8 empty] | 台南PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | P07/161/1BUS/87A |  |  |  | CDC | 947 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-30-02 |  | 2-36 | [5 empty] | ADCS_S | [8 empty] | 台南PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | P07/161/1BUS/87UL |  |  |  | CDC | 948 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-30-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | P07/161/2BUS/BUS_VUA |  |  |  | CDC | 949 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-03-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | P07/161/2BUS/87A |  |  |  | CDC | 950 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-30-03 |  | 2-37 | [5 empty] | ADCS_S | [8 empty] | 台南PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | P07/161/2BUS/87UL |  |  |  | CDC | 951 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | P07/69/1BUS/BUS_VUA |  |  |  | CDC | 952 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-06-03 | [7 empty] | 69KV_S | [8 empty] | 台南PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | P07/69/1BUS/87A |  |  |  | CDC | 953 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 1-30-04 |  | 2-5B | [5 empty] | ADCS_S | [8 empty] | 台南PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | P07/69/1BUS/87UL |  |  |  | CDC | 954 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | P07/69/2BUS/BUS_VUA |  |  |  | CDC | 955 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 69KV_S | [8 empty] | 台南PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | P07/69/2BUS/87A |  |  |  | CDC | 956 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 1-30-05 |  | 3-1D | [5 empty] | ADCS_S | [8 empty] | 台南PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | P07/69/2BUS/87UL |  |  |  | CDC | 957 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | P07/161/ComPoint/ABS_89A |  |  |  | CDC | 958 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-30-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_CBA | 161KV斷路器重故障 | OTHER | P07/161/ComPoint/CBA |  |  |  | CDC | 959 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-30-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | P07/161/ComPoint/CBF |  |  |  | CDC | 960 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-0D-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | P07/161/ComPoint/OSCA |  |  |  | CDC | 961 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0D-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | P07/161/ComPoint/RCA |  |  |  | CDC | 962 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-30-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | P07/161/ComPoint/COMT |  |  |  | CDC | 963 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-3F-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | P07/69/ComPoint/ABS_89A |  |  |  | CDC | 964 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV |  |  |  | CBA | [17 empty] | 2-3E-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_CBA | 69KV斷路器重故障 | OTHER | P07/69/ComPoint/CBA |  |  |  | CDC | 965 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV |  |  |  | CBF | [17 empty] | 2-3E-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | P07/69/ComPoint/CBF |  |  |  | CDC | 966 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV |  |  |  | OSCA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | P07/69/ComPoint/OSCA |  |  |  | CDC | 967 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV |  |  |  | COMT | [17 empty] | 2-3E-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | P07/69/ComPoint/COMT |  |  |  | CDC | 968 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | DTR | DTR |  | CBA(2) | [17 empty] | 3-3C-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.DTR_CBA(2) | #5B-DTR-11KV-CBA | OTHER |  |  |  |  | CDC | 969 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | DTR | DTR |  | CBA(3) | [17 empty] | 2-3F-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.DTR_CBA(3) | #5A-6-7-8DTR-23/11KV-CBA | OTHER | P07//5DTR(A)/CBA |  |  |  | CDC | 970 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | DTR | DTR |  | CBF(2) | [17 empty] | 3-3C-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.DTR_CBF(2) | #5B-DTR-11KV-CBF | OTHER |  |  |  |  | CDC | 971 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | DTR | DTR |  | CBF(3) | [17 empty] | 2-3E-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.DTR_CBF(3) | #5A-6-7-8DTR-23/11KV-CBF | OTHER | P07//5DTR(A)/CBF |  |  |  | CDC | 972 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | P07/0/RTU/RTU_R_L |  |  |  | CDC | 973 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P07 | 台南PS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 台南PS.TEST_CB | TEST CB | OTHER | P07/0/RTU/Test_CB |  |  |  | CDC | 974 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  |  |  |  | Fire1 | [17 empty] | 3-32-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | P07/0/StaDev/Fire1 |  |  |  | CDC | 975 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | Fire2 | [17 empty] | 3-32-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | P07/0/StaDev/Fire2 |  |  |  | CDC | 976 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | Fire3 | [17 empty] | 3-32-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.火災警報(3) | 火災警報(3)全區保全系統 | OTHER | P07/0/StaDev/Fire3 |  |  |  | CDC | 977 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 火災警報(4)-2MTR | 火災警報(4)-#2MTR |  | Fire4 | [17 empty] | 3-32-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.火災警報(4) | 火災警報(4)-#2MTR CO2 | OTHER | P07/0/StaDev/Fire4 |  |  |  | CDC | 978 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | OPA | [17 empty] | 2-3E-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | P07/0/ComPoint/OPA |  |  |  | CDC | 979 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 25PFA | [17 empty] | 1-30-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | P07/0/ComPoint/25PFA |  |  |  | CDC | 980 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 25TA | [17 empty] | 1-30-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | P07/0/ComPoint/25TA |  |  |  | CDC | 981 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | SUBA | [17 empty] | 2-3F-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.其他重故障 | 161線路復閉壓力不足 | OTHER | P07/0/StaDev/PSA |  |  |  | CDC | 982 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | ACB1 | [17 empty] | 3-31-10 |  | 3-00 | [5 empty] | ADCS_S | [8 empty] | 台南PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | P07/0/StaDev/ACB1 |  |  |  | CDC | 983 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P07 | 台南PS | 0 |  |  |  |  | ACB2 | [17 empty] | 3-31-12 |  | 3-02 | [5 empty] | ADCS_S | [8 empty] | 台南PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | P07/0/StaDev/ACB2 |  |  |  | CDC | 984 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P07 | 台南PS | 0 |  |  |  |  | ACBA | [17 empty] | 2-3E-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.所內電源ACBA | 所內電源故障警報 | OTHER | P07/0/StaDev/ACBA |  |  |  | CDC | 985 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 3-31-11 |  | 3-01 | [5 empty] | ADCS_S | [8 empty] | 台南PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | P07/0/StaDev/ACBT |  |  |  | CDC | 986 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P07 | 台南PS | 0 |  |  |  |  | STUV | [17 empty] | 1-31-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | P07/0/StaDev/STUV |  |  |  | CDC | 987 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-3E-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | P07/0/StaDev/CHG1 |  |  |  | CDC | 988 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.直流電源DCA | 直流電源故障警報 | OTHER | P07/0/StaDev/DCA |  |  |  | CDC | 989 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | DCE | [17 empty] | 2-3E-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.直流電源DCE | 直流電源接地故障警報 | OTHER | P07/0/StaDev/DCE |  |  |  | CDC | 990 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | OilLeak | [17 empty] | 2-3E-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.洩油池水位警報 | 洩油池水位警報 | OTHER | P07/0/StaDev/5A5Other |  |  |  | CDC | 991 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-3E-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | P07/0/StaDev/CHG2 |  |  |  | CDC | 992 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | CommACF | [17 empty] | 2-3E-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | P07/0/StaDev/CommACF |  |  |  | CDC | 993 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | Burglar1 | [17 empty] | 3-32-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | P07/0/StaDev/Burglar1 |  |  |  | CDC | 994 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | Burglar2 | [17 empty] | 3-32-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.無人化防盜(2) | 無人化防盜(2) | OTHER | P07/0/StaDev/Burglar2 |  |  |  | CDC | 995 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | Door1 | [17 empty] | 3-32-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.無人化門禁(1) | 無人化門禁(1)變電所大小門 | OTHER | P07/0/StaDev/Door1 |  |  |  | CDC | 996 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  |  |  |  | Door2 | [17 empty] | 3-32-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | P07/0/StaDev/Door2 |  |  |  | CDC | 997 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  |  |  |  | Door3 | [17 empty] | 3-32-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.無人化門禁(3) | 無人化門禁(3)sp | OTHER | P07/0/StaDev/Door3 |  |  |  | CDC | 998 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  |  |  |  | Lights1 | [17 empty] | 3-31-08 |  | 3-1B | [5 empty] | ADCS_S | [8 empty] | 台南PS.開關場照明(A) | 161KV開關場照明 | OTHER | P07/0/StaDev/Lights1 |  |  |  | CDC | 999 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P07 | 台南PS | 0 |  |  |  |  | Lights2 | [17 empty] | 3-31-09 |  | 3-1C | [5 empty] | ADCS_S | [8 empty] | 台南PS.開關場照明(B) | 69KV開關場照明 | OTHER | P07/0/StaDev/Lights2 |  |  |  | CDC | 1000 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P07 | 台南PS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | P07/161/ComPoint/OSCF |  |  |  | CDC | 1001 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV |  |  |  | OSCF | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | P07/69/ComPoint/OSCF |  |  |  | CDC | 1002 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 3-32-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | P07/0/StaDev/AIRCON |  |  |  | CDC | 1003 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P07 | 台南PS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 3-32-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.23KV_SC_60A | 23/11KV SC 60A | OTHER | P07/0/ComPoint/60A |  |  |  | CDC | 1004 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 3-31-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.水位警報(1) | 地下室水位警報(1) | OTHER | P07/0/StaDev/Water1 |  |  |  | CDC | 1005 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 3-31-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.水位警報(2) | 地下室水位警報(2) | OTHER | P07/0/StaDev/Water2 |  |  |  | CDC | 1006 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH41 | 台41線(KH41) LCO分流器 |  | ADJ | [17 empty] | 3-3C-09 |  | 3-3F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_ADJ | 11KV台41線(KH41) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1007 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH42 | 台42線(KH42) LCO分流器 |  | ADJ | [17 empty] | 3-3C-10 |  | 3-40 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_ADJ | 11KV台42線(KH42) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1008 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH43 | 台43線(KH43) LCO分流器 |  | ADJ | [17 empty] | 3-3C-11 |  | 3-41 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_ADJ | 11KV台43線(KH43) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1009 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH44 | 台44線(KH44) LCO分流器 |  | ADJ | [17 empty] | 3-3C-12 |  | 3-42 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_ADJ | 11KV台44線(KH44) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1010 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH45 | 台45線(KH45) LCO分流器 |  | ADJ | [17 empty] | 3-3C-13 |  | 3-43 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_ADJ | 11KV台45線(KH45) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1011 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH46 | 台46線(KH46) LCO分流器 |  | ADJ | [17 empty] | 3-3C-14 |  | 3-44 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_ADJ | 11KV台46線(KH46) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1012 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | PHA | [17 empty] | 2-0A-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_PHA | 23KV台76線(KH76) 相間RY | FEEDER | P07/22/KH76/51A |  |  |  | CDC | 1013 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) |  | GDA | [17 empty] | 2-0A-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_GDA | 23KV台76線(KH76) 接地RY | FEEDER | P07/22/KH76/51NA |  |  |  | CDC | 1014 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) 79RY |  | 79UL | [17 empty] | 3-31-07 |  | 3-1A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_79UL | 23KV台76線(KH76) 79RY U/L | FEEDER |  |  |  |  | CDC | 1015 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 22 | 22kV | KH76 | 台76線(KH76) LCO分流器 |  | ADJ | [17 empty] | 3-33-15 |  | 3-2F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_ADJ | 23KV台76線(KH76) LCO分流器 U/L | FEEDER | P07/22/KH76/ADJ |  |  |  | CDC | 1016 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 22 | 22kV | KH76 | KH76(23KV台76線) |  | CB | [17 empty] | 2-04-02 |  | 2-7F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_CB | KH76(23KV台76線) CB | FEEDER | P07/22/KH76/CB |  |  |  | CDC | 1017 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | PHA | [17 empty] | 1-01-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1510_PHA | 台南仁德線(1510) 相間RY | LINE161 | P07/161/1510/PHA |  |  |  | CDC | 1018 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-3D-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | P07/161/1500/50SA |  |  |  | CDC | 1019 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 710 | 南仁線(710) |  | MDARF | [17 empty] | 1-36-07 | [7 empty] | 69KV_S | [8 empty] | 台南PS.710_MDARF | 710 MDAR RY故障警報 | OTHER | P07/69/710/4A5Other |  |  |  | CDC | 1020 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | 87A | [17 empty] | 1-00-05 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1520_87A | 山上海線(1520) 87RY | LINE161 | P07/161/1520/87A |  |  |  | CDC | 1021 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | 87UL | [17 empty] | 1-31-14 |  | 1-1D | [5 empty] | ADCS_S | [8 empty] | 台南PS.1520_87UL | 山上海線(1520) 87RY U/L | LINE161 | P07/161/1520/87UL |  |  |  | CDC | 1022 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-3E-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.通信機房溫度 | 通信機房溫度警報 | OTHER | P07/0/StaDev/R_Temp |  |  |  | CDC | 1023 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 3-30-14 |  | 3-11 | [5 empty] | ADCS_S | [8 empty] | 台南PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | P07/11/210/SC_A_M |  |  |  | CDC | 1024 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 2-03-01 |  | 2-76 | [5 empty] | ADCS_S | [8 empty] | 台南PS.220_CB | 220(11KV #2SC) CB | SC | P07/11/220/CB |  |  |  | CDC | 1025 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 3-30-15 |  | 3-12 | [5 empty] | ADCS_S | [8 empty] | 台南PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | P07/11/220/SC_A_M |  |  |  | CDC | 1026 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 2-08-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.220_SCA | 11KV #2SC 51,51N RY | SC | P07/11/220/SCA |  |  |  | CDC | 1027 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 2-08-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | P07/11/220/UVA |  |  |  | CDC | 1028 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-02-00 |  | 2-6D | [5 empty] | ADCS_S | [8 empty] | 台南PS.250_CB | 250(23KV #5SC) CB | SC | P07/22/250/CB |  |  |  | CDC | 1029 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 3-30-07 |  | 3-0A | [5 empty] | ADCS_S | [8 empty] | 台南PS.250_A/M | 23KV #5SC 乏控器 A/M | SC | P07/22/250/SC_A_M |  |  |  | CDC | 1030 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-06-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.250_SCA | 23KV #5SC 51,51N RY | SC | P07/22/250/SCA |  |  |  | CDC | 1031 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-06-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | P07/22/250/UVA |  |  |  | CDC | 1032 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-03-04 |  | 2-79 | [5 empty] | ADCS_S | [8 empty] | 台南PS.260_CB | 260(23KV #6SC) CB | SC | P07/22/260/CB |  |  |  | CDC | 1033 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 3-31-01 |  | 3-14 | [5 empty] | ADCS_S | [8 empty] | 台南PS.260_A/M | 23KV #6SC 乏控器 A/M | SC | P07/22/260/SC_A_M |  |  |  | CDC | 1034 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-09-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.260_SCA | 23KV #6SC 51,51N RY | SC | P07/22/260/SCA |  |  |  | CDC | 1035 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-09-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | P07/22/260/UVA |  |  |  | CDC | 1036 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 2-03-03 |  | 2-78 | [5 empty] | ADCS_S | [8 empty] | 台南PS.270_CB | 270(23KV #7SC) CB | SC | P07/22/270/CB |  |  |  | CDC | 1037 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M | [17 empty] | 3-31-00 |  | 3-13 | [5 empty] | ADCS_S | [8 empty] | 台南PS.270_A/M | 23KV #7SC 乏控器 A/M | SC | P07/22/270/SC_A_M |  |  |  | CDC | 1038 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 2-08-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.270_SCA | 23KV #7SC 51,51N RY | SC | P07/22/270/SCA |  |  |  | CDC | 1039 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 2-09-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | P07/22/270/UVA |  |  |  | CDC | 1040 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 310A1 | #5DTR |  | CB | [17 empty] | 1-14-00 |  | 1-13 | [5 empty] | ADCS_S | [8 empty] | 台南PS.310A1_CB | 310A1(#5DTR) CB | MTR | P07/11/310A1/CB |  |  |  | CDC | 1041 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310A2 | #5DTR |  | CB | [17 empty] | 1-14-02 |  | 1-14 | [5 empty] | ADCS_S | [8 empty] | 台南PS.310A2_CB | 310A2(#5DTR) CB | MTR | P07/11/310A2/CB |  |  |  | CDC | 1042 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 320 | #5DTR(320) |  | CB | [17 empty] | 1-0E-04 |  | 3-30 | [5 empty] | ADCS_S | [8 empty] | 台南PS.320_CB | 320(#5DTR) CB | MTR | P07/11/320/CB |  |  |  | CDC | 1043 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310A1 | #5DTR二次側(310A1) |  | 51A | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.310A1_51A | #5DTR二次側(310A1) 51RY | MTR | P07/11/310A1/51A |  |  |  | CDC | 1044 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 310A2 | #5DTR二次側(310A2) |  | 51A | [17 empty] | 1-14-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.310A2_51A | #5DTR二次側(310A2) 51RY | MTR | P07/11/310A2/51A |  |  |  | CDC | 1045 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 320 | #5DTR(320) |  | 51A | [17 empty] | 1-0E-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.320_51A | #5DTR二次側(320) 51RY | MTR | P07/11/320/51A |  |  |  | CDC | 1046 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | PHA | [17 empty] | 1-02-06 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1530_PHA | 龍崎山線(1530) 相間RY | LINE161 | P07/161/1530/PHA |  |  |  | CDC | 1047 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | 87A | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1530_87A | 龍崎山線(1530) 87RY | LINE161 | P07/161/1530/87A |  |  |  | CDC | 1048 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | 87UL | [17 empty] | 1-32-10 |  | 1-25 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1530_87UL | 龍崎山線(1530) 87RY U/L | LINE161 | P07/161/1530/87UL |  |  |  | CDC | 1049 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1530 | 龍崎山線(1530) |  | DTTA | [17 empty] | 2-3C-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1530_DTTA | 龍崎台南山線(1530) 遠方遙跳 | OTHER | P07/161/1530/DTTA |  |  |  | CDC | 1050 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | PHA | [17 empty] | 1-03-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1540_PHA | 龍崎海線(1540) 相間RY | LINE161 | P07/161/1540/PHA |  |  |  | CDC | 1051 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | 87A | [17 empty] | 1-03-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1540_87A | 龍崎海線(1540) 87RY | LINE161 | P07/161/1540/87A |  |  |  | CDC | 1052 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | 87UL | [17 empty] | 1-32-13 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1540_87UL | 龍崎海線(1540) 87RY U/L | LINE161 | P07/161/1540/87UL |  |  |  | CDC | 1053 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1540 | 龍崎海線(1540) |  | DTTA | [17 empty] | 2-3C-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1540_DTTA | 龍崎台南海線(1540) 遠方遙跳 | OTHER | P07/161/1540/DTTA |  |  |  | CDC | 1054 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | PHA | [17 empty] | 2-0E-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_PHA | 11KV台11線(KH11) 相間RY | FEEDER | P07/11/KH11/51A |  |  |  | CDC | 1055 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) |  | GDA | [17 empty] | 2-0E-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_GDA | 11KV台11線(KH11) 接地RY | FEEDER | P07/11/KH11/51NA |  |  |  | CDC | 1056 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) 79RY |  | 79UL | [17 empty] | 3-3C-15 |  | 3-4B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_79UL | 11KV台11線(KH11) 79RY U/L | FEEDER |  |  |  |  | CDC | 1057 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH11 | 台11線(KH11) LCO分流器 |  | ADJ | [17 empty] | 3-3D-09 |  | 3-55 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_ADJ | 11KV台11線(KH11) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1058 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH11 | KH(11KV台11線) |  | CB | [17 empty] | 2-0E-02 |  | 2-42 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_CB | KH11(11KV台11線) CB | FEEDER | P07/11/KH11/CB |  |  |  | CDC | 1059 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | PHA | [17 empty] | 2-0E-06 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_PHA | 11KV台12線(KH12) 相間RY | FEEDER | P07/11/KH12/51A |  |  |  | CDC | 1060 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) |  | GDA | [17 empty] | 2-0E-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_GDA | 11KV台12線(KH12) 接地RY | FEEDER | P07/11/KH12/51NA |  |  |  | CDC | 1061 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) 79RY |  | 79UL | [17 empty] | 3-3D-00 |  | 3-4C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_79UL | 11KV台12線(KH12) 79RY U/L | FEEDER |  |  |  |  | CDC | 1062 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH12 | 台12線(KH12) LCO分流器 |  | ADJ | [17 empty] | 3-3D-10 |  | 3-56 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_ADJ | 11KV台12線(KH12) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1063 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH12 | KH12(11KV台12線) |  | CB | [17 empty] | 2-0E-05 |  | 2-43 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_CB | KH12(11KV台12線) CB | FEEDER | P07/11/KH12/CB |  |  |  | CDC | 1064 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | PHA | [17 empty] | 2-0F-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_PHA | 11KV台13線(KH13) 相間RY | FEEDER | P07/11/KH13/51A |  |  |  | CDC | 1065 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) |  | GDA | [17 empty] | 2-0F-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_GDA | 11KV台13線(KH13) 接地RY | FEEDER | P07/11/KH13/51NA |  |  |  | CDC | 1066 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) 79RY |  | 79UL | [17 empty] | 3-3D-01 |  | 3-4D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_79UL | 11KV台13線(KH13) 79RY U/L | FEEDER |  |  |  |  | CDC | 1067 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH13 | 台13線(KH13) LCO分流器 |  | ADJ | [17 empty] | 3-3D-11 |  | 3-57 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_ADJ | 11KV台13線(KH13) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1068 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH13 | KH13(11KV台13線) |  | CB | [17 empty] | 2-0F-00 |  | 2-44 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_CB | KH13(11KV台13線) CB | FEEDER | P07/11/KH13/CB |  |  |  | CDC | 1069 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | PHA | [17 empty] | 2-0F-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_PHA | 11KV台14線(KH14) 相間RY | FEEDER | P07/11/KH14/51A |  |  |  | CDC | 1070 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) |  | GDA | [17 empty] | 2-0F-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_GDA | 11KV台14線(KH14) 接地RY | FEEDER | P07/11/KH14/51NA |  |  |  | CDC | 1071 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) 79RY |  | 79UL | [17 empty] | 3-3D-02 |  | 3-4E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_79UL | 11KV台14線(KH14) 79RY U/L | FEEDER |  |  |  |  | CDC | 1072 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH14 | 台14線(KH14) LCO分流器 |  | ADJ | [17 empty] | 3-3D-12 |  | 3-58 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_ADJ | 11KV台14線(KH14) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1073 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH14 | KH14(11KV台14線) |  | CB | [17 empty] | 2-0F-03 |  | 2-45 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_CB | KH14(11KV台14線) CB | FEEDER | P07/11/KH14/CB |  |  |  | CDC | 1074 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | PHA | [17 empty] | 2-0F-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_PHA | 11KV台15線(KH15) 相間RY | FEEDER | P07/11/KH15/51A |  |  |  | CDC | 1075 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) |  | GDA | [17 empty] | 2-14-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_GDA | 11KV台15線(KH15) 接地RY | FEEDER | P07/11/KH15/51NA |  |  |  | CDC | 1076 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) 79RY |  | 79UL | [17 empty] | 3-3D-03 |  | 3-4F | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_79UL | 11KV台15線(KH15) 79RY U/L | FEEDER |  |  |  |  | CDC | 1077 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH15 | 台15線(KH15) LCO分流器 |  | ADJ | [17 empty] | 3-3D-13 |  | 3-59 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_ADJ | 11KV台15線(KH15) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1078 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH15 | KH15(11KV台15線) |  | CB | [17 empty] | 2-0F-06 |  | 3-45 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_CB | KH15(11KV台15線) CB | FEEDER | P07/11/KH15/CB |  |  |  | CDC | 1079 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | PHA | [17 empty] | 2-18-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_PHA | 11KV台16線(KH16) 相間RY | FEEDER | P07/11/KH16/51A |  |  |  | CDC | 1080 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) |  | GDA | [17 empty] | 2-19-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_GDA | 11KV台16線(KH16) 接地RY | FEEDER | P07/11/KH16/51NA |  |  |  | CDC | 1081 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) 79RY |  | 79UL | [17 empty] | 3-3D-08 |  | 3-54 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_79UL | 11KV台16線(KH16) 79RY U/L | FEEDER |  |  |  |  | CDC | 1082 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH16 | 台16線(KH16) LCO分流器 |  | ADJ | [17 empty] | 3-3E-02 |  | 3-5E | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_ADJ | 11KV台16線(KH16) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1083 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH16 | KH16(11KV台16線) |  | CB | [17 empty] | 2-18-06 |  | 3-4A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_CB | KH16(11KV台16線) CB | FEEDER | P07/11/KH16/CB |  |  |  | CDC | 1084 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | PHA | [17 empty] | 2-18-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_PHA | 11KV台17線(KH17) 相間RY | FEEDER | P07/11/KH17/51A |  |  |  | CDC | 1085 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) |  | GDA | [17 empty] | 2-18-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_GDA | 11KV台17線(KH17) 接地RY | FEEDER | P07/11/KH17/51NA |  |  |  | CDC | 1086 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) 79RY |  | 79UL | [17 empty] | 3-3D-07 |  | 3-53 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_79UL | 11KV台17線(KH17) 79RY U/L | FEEDER |  |  |  |  | CDC | 1087 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH17 | 台17線(KH17) LCO分流器 |  | ADJ | [17 empty] | 3-3E-01 |  | 3-5D | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_ADJ | 11KV台17線(KH17) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1088 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH17 | KH17(11KV台17線) |  | CB | [17 empty] | 2-18-03 |  | 3-49 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_CB | KH17(11KV台17線) CB | FEEDER | P07/11/KH17/CB |  |  |  | CDC | 1089 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | PHA | [17 empty] | 2-18-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_PHA | 11KV台18線(KH18) 相間RY | FEEDER | P07/11/KH18/51A |  |  |  | CDC | 1090 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) |  | GDA | [17 empty] | 2-18-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_GDA | 11KV台18線(KH18) 接地RY | FEEDER | P07/11/KH18/51NA |  |  |  | CDC | 1091 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) 79RY |  | 79UL | [17 empty] | 3-3D-06 |  | 3-52 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_79UL | 11KV台18線(KH18) 79RY U/L | FEEDER |  |  |  |  | CDC | 1092 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH18 | 台18線(KH18) LCO分流器 |  | ADJ | [17 empty] | 3-3E-00 |  | 3-5C | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_ADJ | 11KV台18線(KH18) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1093 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH18 | KH18(11KV台18線) |  | CB | [17 empty] | 2-18-00 |  | 3-48 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_CB | KH18(11KV台18線) CB | FEEDER | P07/11/KH18/CB |  |  |  | CDC | 1094 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | PHA | [17 empty] | 2-16-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_PHA | 11KV台19線(KH19) 相間RY | FEEDER | P07/11/KH19/51A |  |  |  | CDC | 1095 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) |  | GDA | [17 empty] | 2-16-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_GDA | 11KV台19線(KH19) 接地RY | FEEDER | P07/11/KH19/51NA |  |  |  | CDC | 1096 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) 79RY |  | 79UL | [17 empty] | 3-3D-05 |  | 3-51 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_79UL | 11KV台19線(KH19) 79RY U/L | FEEDER |  |  |  |  | CDC | 1097 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH19 | 台19線(KH19) LCO分流器 |  | ADJ | [17 empty] | 3-3D-15 |  | 3-5B | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_ADJ | 11KV台19線(KH19) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1098 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH19 | KH19(11KV台19線) |  | CB | [17 empty] | 2-16-01 |  | 3-47 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_CB | KH19(11KV台19線) CB | FEEDER | P07/11/KH19/CB |  |  |  | CDC | 1099 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | PHA | [17 empty] | 2-15-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_PHA | 11KV台20線(KH20) 相間RY | FEEDER | P07/11/KH20/51A |  |  |  | CDC | 1100 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) |  | GDA | [17 empty] | 2-16-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_GDA | 11KV台20線(KH20) 接地RY | FEEDER | P07/11/KH20/51NA |  |  |  | CDC | 1101 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) 79RY |  | 79UL | [17 empty] | 3-3D-04 |  | 3-50 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_79UL | 11KV台20線(KH20) 79RY U/L | FEEDER |  |  |  |  | CDC | 1102 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 11 | 11kV | KH20 | 台20線(KH20) LCO分流器 |  | ADJ | [17 empty] | 3-3D-14 |  | 3-5A | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_ADJ | 11KV台20線(KH20) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 1103 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P07 | 台南PS | 11 | 11kV | KH20 | KH20(11KV台20線) |  | CB | [17 empty] | 2-15-06 |  | 3-46 | [5 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_CB | KH20(11KV台20線) CB | FEEDER | P07/11/KH20/CB |  |  |  | CDC | 1104 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 2-19-07 |  | 1-11 | [5 empty] | ADCS_S | [8 empty] | 台南PS.400_CB | 400(TIE) CB | TIE | P07/11/400/CB |  |  |  | CDC | 1105 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 2-1A-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.400_51A | 11KV TIE(400) 51RY | TIE | P07/11/400/51A |  |  |  | CDC | 1106 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 2-1A-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.400_51NA | 11KV TIE(400) 51N RY | TIE | P07/11/400/51NA |  |  |  | CDC | 1107 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 390 | #3SSTR(390) |  | CB | [17 empty] | 2-15-03 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 台南PS.390_CB | 390(#3SSTR) CB | OTHER | P07/11/390/CB |  |  |  | CDC | 1108 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 2-15-04 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#3SSTR_51A | #3SSTR 51RY | OTHER | P07/11/390/PHA |  |  |  | CDC | 1109 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 2-15-05 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | P07/11/390/GDA |  |  |  | CDC | 1110 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | CB | [17 empty] | 1-0E-06 |  | 1-1A | [5 empty] | 161KV_S | [8 empty] | 台南PS.1780_CB | 1780(#8DTR) CB | MTR | P07/161/1780/CB |  |  |  | CDC | 1111 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 380 | #8DTR(380) |  | CB | [17 empty] | 1-10-00 |  | 1-1C | [5 empty] | ADCS_S | [8 empty] | 台南PS.380_CB | 380(#8DTR) CB | MTR | P07/11/380/CB |  |  |  | CDC | 1112 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 51ZA | [17 empty] | 1-0F-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#8DTR_51ZA | #8DTR 51Z RY | MTR | P07//8DTR/51ZA |  |  |  | CDC | 1113 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 87A | [17 empty] | 1-0E-07 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#8DTR_87A | #8DTR 87RY | MTR | P07//8DTR/87A |  |  |  | CDC | 1114 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 380 | #8DTR(380) |  | 51A | [17 empty] | 1-10-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.380_51A | #8DTR二次側(380) 51RY | MTR | P07/11/380/51A |  |  |  | CDC | 1115 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 96PA | [17 empty] | 1-0F-00 | [7 empty] | 161KV_S | [8 empty] | 台南PS.#8DTR_96PA | #8DTR 機械保護動作 | MTR | P07//8DTR/96PA |  |  |  | CDC | 1116 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 96D | [17 empty] | 1-3C-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_96D | #8DTR 96D RY | MTR | P07//8DTR/96D |  |  |  | CDC | 1117 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 96P | [17 empty] | 1-3C-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_96P | #8DTR 96P RY | MTR | P07//8DTR/96P |  |  |  | CDC | 1118 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 63Q | [17 empty] | 1-3C-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_63Q | #8DTR 63Q RY | MTR | P07//8DTR/63Q |  |  |  | CDC | 1119 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 96B1 | [17 empty] | 1-3C-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_96B1 | #8DTR 96B1 RY | MTR | P07//8DTR/96B1 |  |  |  | CDC | 1120 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 96B2 | [17 empty] | 1-3C-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_96B2 | #8DTR 96B2 RY | MTR | P07//8DTR/96B2 |  |  |  | CDC | 1121 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | TRA | [17 empty] | 1-36-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_TRA | #8DTR 重故障 | MTR | P07//8DTR/TRA |  |  |  | CDC | 1122 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | TRF | [17 empty] | 1-36-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_TRF | #8DTR 輕故障 | MTR | P07//8DTR/TRF |  |  |  | CDC | 1123 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | SupLocal | [17 empty] | 1-36-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_S/L | #8DTR(A) OLTC S/L | MTR | P07//8DTR(A)/SupLocal |  |  |  | CDC | 1124 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 8DTR(A) | #8DTR(A) |  | A_M | [17 empty] | 1-36-01 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(A)_A/M | #8DTR(A) OLTC A/M | MTR | P07//8DTR(A)/Tap Chan |  |  |  | CDC | 1125 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | SupLocal | [17 empty] | 1-36-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_S/L | #8DTR(B) OLTC S/L | MTR | P07//8DTR(B)/SupLocal |  |  |  | CDC | 1126 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P07 | 台南PS | 0 |  | 8DTR(B) | #8DTR(B) |  | A_M | [17 empty] | 1-36-03 |  | 1-44 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR(B)_A/M | #8DTR(B) OLTC A/M | MTR | P07//8DTR(B)/Tap Chan |  |  |  | CDC | 1127 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | ABS1 | 1781 | [16 empty] | 2-32-12 | 2-32-13 | 2-5C | [5 empty] | ADCS_S | [8 empty] | 台南PS.1781_ABS | 1781(#8DTR) ABS | MTR | P07/161/1780/ABS1 |  |  |  | CDC | 1128 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | ABS2 | 1782 | [16 empty] | 2-32-14 | 2-32-15 | 2-5D | [5 empty] | ADCS_S | [8 empty] | 台南PS.1782_ABS | 1782(#8DTR) ABS | MTR | P07/161/1780/ABS2 |  |  |  | CDC | 1129 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 0 |  | 370 | #8DTR(370) |  | GDA | [17 empty] | 1-0F-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.370_GDA | 370開關箱IED RY GDA | OTHER | P07/11/370/GDA |  |  |  | CDC | 1130 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 370 | #8DTR(370) |  | PHA2 | [17 empty] | 1-0F-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.370_PHA2 | 370開關箱IED RY PHA | OTHER | P07/11/370/PHA |  |  |  | CDC | 1131 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 380 | #8DTR(380) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.380_GDA | 380開關箱IED RY GDA | OTHER | P07/11/380/GDA |  |  |  | CDC | 1132 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 380 | #8DTR(380) |  | PHA2 | [17 empty] | 1-10-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.380_PHA2 | 380開關箱IED RY PHA | OTHER | P07/11/380/PHA |  |  |  | CDC | 1133 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | PMA | [17 empty] | 3-32-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.PMA | 電力量測表計故障 | OTHER | P07/0/StaDev/PMA |  |  |  | CDC | 1134 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1520 | 山上海線(1520) |  | 87CFA | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1520_87CFA | 山上海線(1520)87RY通訊故障 | OTHER | P07/161/1520/87CFA |  |  |  | CDC | 1135 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1520 | 山上海線(1520) |  | RYFA | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1520_RYFA | 山上海線(1520)數位電驛故障 | OTHER | P07/161/1520/RYFA |  |  |  | CDC | 1136 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1530 | 龍崎山線(1530) |  | 87CFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1530_87CFA | 龍崎台南山線(1530)87RY通訊故障 | OTHER | P07/161/1530/87CFA |  |  |  | CDC | 1137 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1530 | 龍崎山線(1530) |  | RYFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1530_RYFA | 龍崎台南山線(1530)數位電驛故障 | OTHER | P07/161/1530/RYFA |  |  |  | CDC | 1138 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1540 | 龍崎海線(1540) |  | 87CFA | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1540_87CFA | 龍崎台南海線(1540)87RY通訊故障 | OTHER | P07/161/1540/87CFA |  |  |  | CDC | 1139 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1540 | 龍崎海線(1540) |  | RYFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1540_RYFA | 龍崎台南海線(1540)數位電驛故障 | OTHER | P07/161/1540/RYFA |  |  |  | CDC | 1140 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1550_PHA | 台南延平線(1550) 相間RY | LINE161 | P07/161/1550/PHA |  |  |  | CDC | 1141 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 87A | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1550_87A | 台南延平線(1550) 87RY | LINE161 | P07/161/1550/87A |  |  |  | CDC | 1142 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 87UL | [17 empty] | 1-32-07 |  | 1-23 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1550_87UL | 台南延平線(1550) 87RY U/L | LINE161 | P07/161/1550/87UL |  |  |  | CDC | 1143 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1550 | 台南延平線(1550) |  | 87CFA | [17 empty] | 1-31-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1550_87CFA | 台南延平線(1550)87RY通訊故障 | OTHER | P07/161/1550/87CFA |  |  |  | CDC | 1144 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1550 | 台南延平線(1550) |  | RYFA | [17 empty] | 1-31-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1550_RYFA | 台南延平線(1550)數位電驛故障 | OTHER | P07/161/1550/RYFA |  |  |  | CDC | 1145 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | PHA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1560_PHA | 台南忠孝二路(1560) 相間RY | LINE161 | P07/161/1560/PHA |  |  |  | CDC | 1146 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | 87CFA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1560_87CFA | 台南忠孝二路(1560)87RY通訊故障 | OTHER | P07/161/1560/87CFA |  |  |  | CDC | 1147 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | RYFA | [17 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1560_RYFA | 台南忠孝二路(1560)數位電驛故障 | OTHER | P07/161/1560/RYFA |  |  |  | CDC | 1148 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | 87A | [17 empty] | 1-18-05 | [7 empty] | 69KV_S | [8 empty] | 台南PS.720_87A | 台南大灣二路(720) 87RY | LINE69 | P07/69/720/87A |  |  |  | CDC | 1149 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | 87UL | [17 empty] | 2-3C-02 |  | 2-17 | [5 empty] | ADCS_S | [8 empty] | 台南PS.720_87UL | 台南大灣二路(720) 87RY U/L | LINE69 | P07/69/720/87UL |  |  |  | CDC | 1150 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | 79UL | [17 empty] | 2-3C-03 |  | 2-16 | [5 empty] | ADCS_S | [8 empty] | 台南PS.720_79UL | 台南大灣二路(720) 79RY U/L | LINE69 | P07/69/720/79UL |  |  |  | CDC | 1151 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 720 | 台南大灣二路(720) |  | 87CFA | [17 empty] | 2-3C-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.720_87CFA | 台南大灣二路(720)87RY通訊故障 | OTHER | P07/69/720/87CFA |  |  |  | CDC | 1152 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 720 | 台南大灣二路(720) |  | RYFA | [17 empty] | 2-3C-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.720_RYFA | 台南大灣二路(720)數位電驛故障 | OTHER | P07/69/720/RYFA |  |  |  | CDC | 1153 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | IEDA | [17 empty] | 3-32-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.IEDA | 變壓器資產管理監視IED故障 | OTHER | P07//1MTR/IRFA |  |  |  | CDC | 1154 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | 87A | [17 empty] | 1-1B-01 | [7 empty] | 69KV_S | [8 empty] | 台南PS.660_87A | 台南後甲海線(660) 87RY | LINE69 | P07/69/660/87A |  |  |  | CDC | 1155 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | 87UL | [17 empty] | 2-3C-12 |  | 2-1C | [5 empty] | ADCS_S | [8 empty] | 台南PS.660_87UL | 台南後甲海線(660) 87RY U/L | LINE69 | P07/69/660/87UL |  |  |  | CDC | 1156 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 660 | 台南後甲海線(660) |  | 87CFA | [17 empty] | 2-3C-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.660_87CFA | 台南後甲海線(660)87RY通訊故障 | OTHER | P07/69/660/87CFA |  |  |  | CDC | 1157 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 660 | 台南後甲海線(660) |  | RYFA | [17 empty] | 2-3C-15 | [7 empty] | ADCS_S | [8 empty] | 台南PS.660_RYFA | 台南後甲海線(660)數位電驛故障 | OTHER | P07/69/660/RYFA |  |  |  | CDC | 1158 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | 87A | [17 empty] | 1-1C-05 | [7 empty] | 69KV_S | [8 empty] | 台南PS.630_87A | 台南光洲線(630) 87RY | LINE69 | P07/69/630/87A |  |  |  | CDC | 1159 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | 87UL | [17 empty] | 2-3D-02 |  | 2-1F | [5 empty] | ADCS_S | [8 empty] | 台南PS.630_87UL | 台南光洲線(630) 87RY U/L | LINE69 | P07/69/630/87UL |  |  |  | CDC | 1160 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 630 | 台南光洲線(630) |  | 87CFA | [17 empty] | 2-3D-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.630_87CFA | 台南光洲線(630)87RY通訊故障 | OTHER | P07/69/630/87CFA |  |  |  | CDC | 1161 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 630 | 台南光洲線(630) |  | RYFA | [17 empty] | 2-3C-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.630_RYFA | 台南光洲線(630)數位電驛故障 | OTHER | P07/69/630/RYFA |  |  |  | CDC | 1162 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 3-3C-00 |  | 3-38 | [5 empty] | ADCS_S | [8 empty] | 台南PS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 1163 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-0B-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.230_SCA | 11KV #3SC 51,51N RY | SC | P07/11/230/SCA |  |  |  | CDC | 1164 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-0B-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | P07/11/230/UVA |  |  |  | CDC | 1165 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 3-30-06 |  | 3-09 | [5 empty] | ADCS_S | [8 empty] | 台南PS.240_A/M | 23KV #4SC 乏控器 A/M | SC | P07/22/240/SC_A_M |  |  |  | CDC | 1166 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-05-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.240_SCA | 23KV #4SC 51,51N RY | SC | P07/22/240/SCA |  |  |  | CDC | 1167 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-06-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | P07/22/240/UVA |  |  |  | CDC | 1168 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | 81RYFA | [17 empty] | 2-3D-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.81RYFA | 低頻電驛故障 | OTHER | P07/69/710/RYFA |  |  |  | CDC | 1169 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-3D-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | P07/0/ComPoint/GRZ100 |  |  |  | CDC | 1170 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-39-08 | 1-39-09 | 1-63 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1501_DS | 1501(TIE) DS | OTHER | P07/161/1500/DS1 |  |  |  | CDC | 1171 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-39-10 | 1-39-11 | 1-64 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1502_DS | 1502(TIE) DS | OTHER | P07/161/1500/DS2 |  |  |  | CDC | 1172 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 22 | 22kV | 11_ | 11/ 79RY |  | LOA | [17 empty] | 3-31-13 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.11/23KV_LOA | 11/23KV 79RY 饋線復閉失敗 | OTHER | P07/0/ComPoint/LOA |  |  |  | CDC | 1173 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | 87A | [17 empty] | 1-1D-01 | [7 empty] | 69KV_S | [8 empty] | 台南PS.620_87A | 保安線(620) 87RY | LINE69 | P07/69/620/87A |  |  |  | CDC | 1174 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | 87UL | [17 empty] | 2-3D-04 |  | 2-20 | [5 empty] | ADCS_S | [8 empty] | 台南PS.620_87UL | 保安線(620) 87RY U/L | LINE69 | P07/69/620/87UL |  |  |  | CDC | 1175 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 620 | 保安線(620) |  | 87CFA | [17 empty] | 2-3D-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.620_87CFA | 台南保安線(620)87RY通訊故障 | OTHER | P07/69/620/87CFA |  |  |  | CDC | 1176 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 620 | 保安線(620) |  | RYFA | [17 empty] | 2-3D-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.620_RYFA | 台南保安線(620)數位電驛故障 | OTHER | P07/69/620/RYFA |  |  |  | CDC | 1177 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | 87A | [17 empty] | 1-1A-05 | [7 empty] | 69KV_S | [8 empty] | 台南PS.670_87A | 台南大灣一路(670) 87RY | LINE69 | P07/69/670/87A |  |  |  | CDC | 1178 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | 87UL | [17 empty] | 2-3C-10 |  | 2-1B | [5 empty] | ADCS_S | [8 empty] | 台南PS.670_87UL | 台南大灣一路(670) 87RY U/L | LINE69 | P07/69/670/87UL |  |  |  | CDC | 1179 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 670 | 台南大灣一路(670) |  | 87CFA | [17 empty] | 2-3C-11 | [7 empty] | ADCS_S | [8 empty] | 台南PS.670_87CFA | 台南大灣ㄧ路(670)87RY通訊故障 | OTHER | P07/69/670/87CFA |  |  |  | CDC | 1180 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 670 | 台南大灣一路(670) |  | RYFA | [17 empty] | 2-3D-09 | [7 empty] | ADCS_S | [8 empty] | 台南PS.670_RYFA | 台南大灣ㄧ路(670)數位電驛故障 | OTHER | P07/69/670/RYFA |  |  |  | CDC | 1181 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  |  |  |  | GEN | [17 empty] | 3-32-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.GEN | 緊急發電機運轉 | OTHER | P07/0/StaDev/6A5Other |  |  |  | CDC | 1182 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1570_PHA | 台南忠孝一路(1570) 相間RY | LINE161 | P07/161/1570/PHA |  |  |  | CDC | 1183 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 台南PS.1570_GDA | 台南忠孝一路(1570) 接地RY | LINE161 | P07/161/1570/GDA |  |  |  | CDC | 1184 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | CB | [17 empty] | 1-00-00 |  | 1-17 | [5 empty] | 161KV_S | [8 empty] | 台南PS.1570_CB | 1570(台南忠孝一路) CB | LINE161 | P07/161/1570/CB |  |  |  | CDC | 1185 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | 79UL | [17 empty] | 1-3A-04 |  | 1-46 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1570_79UL | 台南忠孝一路(1570) 79RY U/L | LINE161 | P07/161/1570/79UL |  |  |  | CDC | 1186 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | DS1 | 1571 | [16 empty] | 2-36-04 | 2-36-05 | 1-35 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1571_DS | 1571(台南忠孝一路) DS | LINE161 | P07/161/1570/DS1 |  |  |  | CDC | 1187 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | DS2 | 1572 | [16 empty] | 2-36-06 | 2-36-07 | 1-36 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1572_DS | 1572(台南忠孝一路) DS | LINE161 | P07/161/1570/DS2 |  |  |  | CDC | 1188 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | DS3 | 1573 | [16 empty] | 2-36-08 | 2-36-09 | 1-37 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1573_DS | 1573(台南忠孝一路) DS | LINE161 | P07/161/1570/DS3 |  |  |  | CDC | 1189 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | E3 | 1573E | [16 empty] | 2-36-10 | 2-36-11 | 1-38 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1573E_ES | 1573E(台南忠孝一路) ES | LINE161 | P07/161/1570/E3 |  |  |  | CDC | 1190 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | 87A1 | [17 empty] | 1-00-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1570_87A1 | 台南忠孝一路(1570)第一套87RY | OTHER | P07/161/1570/87A1 |  |  |  | CDC | 1191 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | 87A2 | [17 empty] | 1-04-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1570_87A2 | 台南忠孝一路(1570)第二套87RY | OTHER | P07/161/1570/87A2 |  |  |  | CDC | 1192 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | 87CFA | [17 empty] | 1-3A-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1570_87CFA | 台南忠孝一路(1570)87RY通訊故障 | OTHER | P07/161/1570/87CFA |  |  |  | CDC | 1193 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | 1_87UL1 | [17 empty] | 1-3A-02 |  | 1-45 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1570_87UL1 | 台南忠孝一路(1570)#1 87RY U/L | OTHER | P07/161/1570/1_87UL1 |  |  |  | CDC | 1194 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | 1_87UL2 | [17 empty] | 1-3A-03 |  | 1-66 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1570_87UL2 | 台南忠孝一路(1570)#2 87RY U/L | OTHER | P07/161/1570/1_87UL2 |  |  |  | CDC | 1195 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1570 | 台南忠孝一路(1570) |  | RYFA | [17 empty] | 1-3A-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1570_RYFA | 台南忠孝一路(1570)數位電驛故障 | OTHER | P07/161/1570/RYFA |  |  |  | CDC | 1196 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | 87A1 | [17 empty] | 1-01-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1510_87A1 | 台南仁德線(1510)第一套87RY | OTHER | P07/161/1510/87A1 |  |  |  | CDC | 1197 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | 87A2 | [17 empty] | 1-04-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1510_87A2 | 台南仁德線(1510)第二套87RY | OTHER | P07/161/1510/87A2 |  |  |  | CDC | 1198 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | 87CFA | [17 empty] | 1-31-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1510_87CFA | 台南仁德線(1510)87RY通訊故障 | OTHER | P07/161/1510/87CFA |  |  |  | CDC | 1199 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | 1_87UL1 | [17 empty] | 1-32-01 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 台南PS.1510_87UL1 | 台南仁德線(1510)#1 87RY U/L | OTHER | P07/161/1510/1_87UL1 |  |  |  | CDC | 1200 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | 1_87UL2 | [17 empty] | 1-3A-07 |  | 1-6D | [5 empty] | ADCS_S | [8 empty] | 台南PS.1510_87UL2 | 台南仁德線(1510)#2 87RY U/L | OTHER | P07/161/1510/1_87UL2 |  |  |  | CDC | 1201 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1510 | 台南仁德線(1510) |  | RYFA | [17 empty] | 1-31-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1510_RYFA | 台南仁德線(1510)數位電驛故障 | OTHER | P07/161/1510/RYFA |  |  |  | CDC | 1202 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | 87A1 | [17 empty] | 1-01-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1560_87A1 | 台南忠孝二路(1560)第一套87RY | OTHER | P07/161/1560/87A1 |  |  |  | CDC | 1203 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | 87A2 | [17 empty] | 1-04-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.1560_87A2 | 台南忠孝二路(1560)第二套87RY | OTHER | P07/161/1560/87A2 |  |  |  | CDC | 1204 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | 1_87UL1 | [17 empty] | 1-32-04 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1560_87UL1 | 台南忠孝二路(1560)#1 87RY U/L | OTHER | P07/161/1560/1_87UL1 |  |  |  | CDC | 1205 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1560 | 台南忠孝二路(1560) |  | 1_87UL2 | [17 empty] | 1-32-09 |  | 1-70 | [5 empty] | ADCS_S | [8 empty] | 台南PS.1560_87UL2 | 台南忠孝二路(1560)#2 87RY U/L | OTHER | P07/161/1560/1_87UL2 |  |  |  | CDC | 1206 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 3-3E-05 |  | 2-1D | [5 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1207 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-10-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_86A | #1MTR 86RY | OTHER | P07//1MTR/MTR_86A |  |  |  | CDC | 1208 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 |  | 2-19 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | P07//1MTR/87UL |  |  |  | CDC | 1209 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 3-3E-03 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1210 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | GDA | [17 empty] | 1-10-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_GDA | #1MTR GDA | OTHER | P07//1MTR/GDA |  |  |  | CDC | 1211 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | PHA | [17 empty] | 1-07-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_PHA | #1MTR PHA | OTHER | P07//1MTR/PHA |  |  |  | CDC | 1212 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 3-3E-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1213 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 3-3E-08 |  | 2-23 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1214 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-11-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_86A | #2MTR 86RY | OTHER | P07//2MTR/MTR_86A |  |  |  | CDC | 1215 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-33-09 |  | 2-21 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | P07//2MTR/87UL |  |  |  | CDC | 1216 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 3-3E-06 |  | 2-22 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1217 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 1-10-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_GDA | #2MTR GDA | OTHER | P07//2MTR/GDA |  |  |  | CDC | 1218 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | PHA | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_PHA | #2MTR PHA | OTHER | P07//2MTR/PHA |  |  |  | CDC | 1219 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 3-3E-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1220 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 3-3E-11 |  | 2-26 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1221 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-11-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_86A | #3MTR 86RY | OTHER | P07//3MTR/MTR_86A |  |  |  | CDC | 1222 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 1-33-15 |  | 2-24 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | P07//3MTR/87UL |  |  |  | CDC | 1223 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 3-3E-09 |  | 2-25 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1224 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | GDA | [17 empty] | 1-11-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_GDA | #3MTR GDA | OTHER | P07//3MTR/GDA |  |  |  | CDC | 1225 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | PHA | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_PHA | #3MTR PHA | OTHER | P07//3MTR/PHA |  |  |  | CDC | 1226 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 3-3E-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1227 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 51Z_UL | [17 empty] | 3-3F-04 |  | 2-57 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_51ZUL | #7DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1228 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | DTR_86A | [17 empty] | 1-11-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_86A | #7DTR 86RY | OTHER | P07//7DTR/DTR_86A |  |  |  | CDC | 1229 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 1_87UL1 | [17 empty] | 1-35-11 |  | 2-55 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_87UL1 | #7DTR #1 87RY U/L | OTHER |  |  |  |  | CDC | 1230 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | 1_87UL2 | [17 empty] | 3-3F-02 |  | 2-56 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_87UL2 | #7DTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1231 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | GDA | [17 empty] | 1-0D-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_GDA | #7DTR GDA | OTHER | P07//7DTR/GDA |  |  |  | CDC | 1232 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | PHA | [17 empty] | 1-0D-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_PHA | #7DTR PHA | OTHER | P07//7DTR/PHA |  |  |  | CDC | 1233 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 7DTR | #7DTR |  | RYFA | [17 empty] | 3-3F-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#7DTR_RYFA | #7DTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1234 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 51Z_UL | [17 empty] | 3-3F-01 |  | 2-54 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_51ZUL | #6DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1235 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | DTR_86A | [17 empty] | 1-11-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_86A | #6DTR 86RY | OTHER | P07//6DTR/DTR_86A |  |  |  | CDC | 1236 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 1_87UL1 | [17 empty] | 1-35-03 |  | 2-52 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_87UL1 | #6DTR #1 87RY U/L | OTHER | P07//6DTR/87UL |  |  |  | CDC | 1237 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | 1_87UL2 | [17 empty] | 3-3E-15 |  | 2-53 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_87UL2 | #6DTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1238 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | GDA | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_GDA | #6DTR GDA | OTHER | P07//6DTR/GDA |  |  |  | CDC | 1239 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | PHA | [17 empty] | 1-0C-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_PHA | #6DTR PHA | OTHER | P07//6DTR/PHA |  |  |  | CDC | 1240 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 6DTR | #6DTR |  | RYFA | [17 empty] | 3-3F-00 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#6DTR_RYFA | #6DTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1241 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 51Z_UL | [17 empty] | 3-3E-14 |  | 2-29 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_51ZUL | #5DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1242 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | DTR_86A | [17 empty] | 1-11-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_86A | #5DTR 86RY | OTHER | P07//5DTR/DTR_86A |  |  |  | CDC | 1243 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 1_87UL1 | [17 empty] | 1-34-11 |  | 2-27 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_87UL1 | #5DTR #1 87RY U/L | OTHER | P07//5DTR/87UL |  |  |  | CDC | 1244 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | 1_87UL2 | [17 empty] | 3-3E-12 |  | 2-28 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_87UL2 | #5DTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1245 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | GDA | [17 empty] | 1-0B-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_GDA | #5DTR GDA | OTHER | P07//5DTR/GDA |  |  |  | CDC | 1246 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | PHA | [17 empty] | 1-0B-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_PHA | #5DTR PHA | OTHER | P07//5DTR/PHA |  |  |  | CDC | 1247 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 5DTR | #5DTR |  | RYFA | [17 empty] | 3-3E-13 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#5DTR_RYFA | #5DTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1248 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 51Z_UL | [17 empty] | 3-3F-07 |  | 2-5A | [5 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_51ZUL | #8DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1249 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | DTR_86A | [17 empty] | 1-11-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_86A | #8DTR 86RY | OTHER | P07//8DTR/DTR_86A |  |  |  | CDC | 1250 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 1_87UL1 | [17 empty] | 1-36-00 |  | 2-58 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_87UL1 | #8DTR #1 87RY U/L | OTHER | P07//8DTR/87UL |  |  |  | CDC | 1251 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | 1_87UL2 | [17 empty] | 3-3F-05 |  | 2-59 | [5 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_87UL2 | #8DTR #2 87RY U/L | OTHER |  |  |  |  | CDC | 1252 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | GDA | [17 empty] | 1-0F-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_GDA | #8DTR GDA | OTHER | P07//8DTR/GDA |  |  |  | CDC | 1253 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | PHA | [17 empty] | 1-0F-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_PHA | #8DTR PHA | OTHER | P07//8DTR/PHA |  |  |  | CDC | 1254 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 8DTR | #8DTR |  | RYFA | [17 empty] | 3-3F-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.#8DTR_RYFA | #8DTR數位電驛故障 | OTHER |  |  |  |  | CDC | 1255 | GENERICDIPoint | PS011_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 | [17 empty] | 1-06-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | P07/69/600/GDA1 |  |  |  | CDC | 1256 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 台南PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | P07/69/600/GDA2 |  |  |  | CDC | 1257 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 | [17 empty] | 1-06-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | P07/69/600/PHA1 |  |  |  | CDC | 1258 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 台南PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | P07/69/600/PHA2 |  |  |  | CDC | 1259 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | RYFA | [17 empty] | 2-3D-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | P07/69/600/RYFA |  |  |  | CDC | 1260 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-33-14 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | P07/69/ComPoint/12B_CTFA |  |  |  | CDC | 1261 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-33-08 | [7 empty] | ADCS_S | [8 empty] | 台南PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | P07/69/ComPoint/BUS_RYFA |  |  |  | CDC | 1262 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-3B-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | P07/161/ComPoint/12B_CTFA |  |  |  | CDC | 1263 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-3B-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | P07/161/ComPoint/BUS_RYFA |  |  |  | CDC | 1264 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P07 | 台南PS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 台南PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | P07/0/ComPoint/OLTC_A |  |  |  | CDC | 1265 | GENERICDIPoint | PS011_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 310A1 | 310A1 |  | GDA | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 台南PS.310A1_GDA | 11KV M5A1(310A1) 51N RY | OTHER | P07/11/310A1/GDA1 |  |  |  | CDC | 1266 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 310A2 | 310A2 |  | GDA | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 台南PS.310A2_GDA | 11KV M5A2(310A2) 51N RY | OTHER | P07/11/310A1/GDA2 |  |  |  | CDC | 1267 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 320 | #5DTR(320) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_S | [8 empty] | 台南PS.320_GDA | 11KV M5B(320) 51N RY | OTHER | P07/11/320/GDA |  |  |  | CDC | 1268 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 330 | #6DTR(330) |  | GDA | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 台南PS.330_GDA | 22KV M6(330) 51N RY | OTHER | P07/22/330/GDA |  |  |  | CDC | 1269 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 0 |  | 350 | #7DTR(350) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 台南PS.350_GDA | 22KV M7(350) 51N RY | OTHER | P07/22/350/GDA |  |  |  | CDC | 1270 | GENERICDIPoint | PS011_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | PV台南紡織 | 台南紡織(KH38) |  | CB | [17 empty] | 2-1B-00 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.PV台南紡織_CB | 11KV台南紡織(KH38) CB | OTHER |  |  |  |  | CDC | 1271 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 11 | 11kV | PV台南紡織 | 台南紡織(KH38) |  | DS1 | PV台南紡織 | [16 empty] | 2-3B-00 | 2-3B-01 | [6 empty] | DDCS4_1 | [8 empty] | 台南PS.PV台南紡織_DS | 11KV台南紡織(KH38) DS | OTHER |  |  |  |  | CDC | 1272 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | 59V0 | [17 empty] | 2-1B-02 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_59V0 | 11KV台南紡織(KH38) 59V0 | OTHER |  |  |  |  | CDC | 1273 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | 81A | [17 empty] | 2-1B-05 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_81A | 11KV台南紡織(KH38) 81A | OTHER |  |  |  |  | CDC | 1274 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | CFA | [17 empty] | 2-3B-07 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_CFA | 11KV台南紡織(KH38) 通訊故障 | OTHER |  |  |  |  | CDC | 1275 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | GDA | [17 empty] | 2-1B-04 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_GDA | 11KV台南紡織(KH38) GDA | OTHER |  |  |  |  | CDC | 1276 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | LBS | [17 empty] | 2-3B-02 | 2-3B-03 | [6 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_LBS | 11KV台南紡織(KH38) LBS | OTHER |  |  |  |  | CDC | 1277 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | PHA | [17 empty] | 2-1B-03 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_PHA | 11KV台南紡織(KH38) PHA | OTHER |  |  |  |  | CDC | 1278 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | PTDS | [17 empty] | 2-3B-04 | 2-3B-05 | [6 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_PTDS | 11KV台南紡織(KH38) PTDS | OTHER |  |  |  |  | CDC | 1279 | GENERICDIPoint | PS011_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P07 | 台南PS | 11 | 11kV | 台南紡織 | 台南紡織(KH38) |  | RYFA | [17 empty] | 2-1B-01 | [7 empty] | DDCS4_1 | [8 empty] | 台南PS.台南紡織_RYA | 11KV台南紡織(KH38) 27/59A | OTHER |  |  |  |  | CDC | 1280 | GENERICDIPoint | PS011_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P07 | 台南PS | 11 | 11kV | 410_SC | #11SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.410_SC_CAP | 11KV#11SC 容量 | SC | [5 empty] | 1281 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 420_SC | #12SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.420_SC_CAP | 11KV#12SC 容量 | SC | [5 empty] | 1282 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 430_SC | #13SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.430_SC_CAP | 11KV#13SC 容量 | SC | [5 empty] | 1283 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 440_SC | #14SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.440_SC_CAP | 11KV#14SC 容量 | SC | [5 empty] | 1284 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 810_SC | #1SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 1285 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.820_SC_CAP | 69KV#2SC 容量 | SC | [5 empty] | 1286 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.830_SC_CAP | 69KV#3SC 容量 | SC | [5 empty] | 1287 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 043 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_043 | 台南PS NT 69KV_Hi_Limit | [6 empty] | 1288 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 044 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_044 | 台南PS NT 69KV_Lo_Limit | [6 empty] | 1289 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 045 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_045 | 台南PS NT #5ADTR 11KV_Hi_Limit | [6 empty] | 1290 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 046 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_046 | 台南PS NT #5ADTR 11KV_Lo_Limit | [6 empty] | 1291 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 047 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_047 | 台南PS NT #5BDTR 11KV_Hi_Limit | [6 empty] | 1292 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 048 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_048 | 台南PS NT #5BDTR 11KV_Lo_Limit | [6 empty] | 1293 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 049 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_049 | 台南PS NT #2DTR 11KV_Hi_Limit | [6 empty] | 1294 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 050 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_050 | 台南PS NT #2DTR 11KV_Lo_Limit | [6 empty] | 1295 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 051 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_051 | 台南PS NT #1DTR 11KV_Hi_Limit | [6 empty] | 1296 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 052 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_052 | 台南PS NT #1DTR 11KV_Lo_Limit | [6 empty] | 1297 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 053 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_053 | 台南PS NT #7DTR 23KV_Hi_Limit | [6 empty] | 1298 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 054 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_054 | 台南PS NT #7DTR 23KV_Lo_Limit | [6 empty] | 1299 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 055 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_055 | 台南PS NT #6DTR 23KV_Hi_Limit | [6 empty] | 1300 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P07 | 台南PS | 0 |  | TRD | 台南PS |  | 056 | [25 empty] | TRAIN_AD | [8 empty] | 台南PS.TRD_056 | 台南PS NT #6DTR 23KV_Lo_Limit | [6 empty] | 1301 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P07 | 台南PS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 1302 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 1303 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 1304 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 1305 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 270_SC | #7SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 1306 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 1307 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 22 | 22kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 台南PS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 1308 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1510LE | 1510LE (非取樣點) | LINE161 | P07/161/1510/LE0 |  |  |  |  | 1309 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1510 | 台南仁德線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1510BE | 1510BE (非取樣點) | LINE161 | P07/161/1510/BE0 |  |  |  |  | 1310 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1520LE | 1520LE (非取樣點) | LINE161 | P07/161/1520/LE0 |  |  |  |  | 1311 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1520 | 山上海線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1520BE | 1520BE (非取樣點) | LINE161 | P07/161/1520/BE0 |  |  |  |  | 1312 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1530LE | 1530LE (非取樣點) | LINE161 | P07/161/1530/LE0 |  |  |  |  | 1313 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1530 | 龍崎山線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1530BE | 1530BE (非取樣點) | LINE161 | P07/161/1530/BE0 |  |  |  |  | 1314 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1540LE | 1540LE (非取樣點) | LINE161 | P07/161/1540/LE0 |  |  |  |  | 1315 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1540 | 龍崎海線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1540BE | 1540BE (非取樣點) | LINE161 | P07/161/1540/BE0 |  |  |  |  | 1316 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1550LE | 1550LE (非取樣點) | LINE161 | P07/161/1550/LE0 |  |  |  |  | 1317 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1550 | 台南延平線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1550BE | 1550BE (非取樣點) | LINE161 | P07/161/1550/BE0 |  |  |  |  | 1318 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1560LE | 1560LE (非取樣點) | LINE161 | P07/161/1560/LE0 |  |  |  |  | 1319 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1560 | 台南忠孝二路(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1560BE | 1560BE (非取樣點) | LINE161 | P07/161/1560/BE0 |  |  |  |  | 1320 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.620LE | 620LE (非取樣點) | LINE69 | P07/69/620/LE0 |  |  |  |  | 1321 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | BE0 | 620BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.620BE | 620BE (非取樣點) | LINE69 | P07/69/620/BE0 |  |  |  |  | 1322 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.630LE | 630LE (非取樣點) | LINE69 | P07/69/630/LE0 |  |  |  |  | 1323 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | BE0 | 630BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.630BE | 630BE (非取樣點) | LINE69 | P07/69/630/BE0 |  |  |  |  | 1324 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | LE0 | 640LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 1325 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | BE0 | 640BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 1326 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | LE0 | 660LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.660LE | 660LE (非取樣點) | LINE69 | P07/69/660/LE0 |  |  |  |  | 1327 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | BE0 | 660BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.660BE | 660BE (非取樣點) | LINE69 | P07/69/660/BE0 |  |  |  |  | 1328 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | LE0 | 670LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.670LE | 670LE (非取樣點) | LINE69 | P07/69/670/LE0 |  |  |  |  | 1329 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | BE0 | 670BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.670BE | 670BE (非取樣點) | LINE69 | P07/69/670/BE0 |  |  |  |  | 1330 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | LE0 | 680LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.680LE | 680LE (非取樣點) | LINE69 | [5 empty] | 1331 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 680 | 金榮線(680) |  | BE0 | 680BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.680BE | 680BE (非取樣點) | LINE69 | [5 empty] | 1332 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | LE0 | 710LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.710LE | 710LE (非取樣點) | LINE69 | P07/69/710/LE0 |  |  |  |  | 1333 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 710 | 南仁線(710) |  | BE0 | 710BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.710BE | 710BE (非取樣點) | LINE69 | P07/69/710/BE0 |  |  |  |  | 1334 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | LE0 | 720LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.720LE | 720LE (非取樣點) | LINE69 | P07/69/720/LE0 |  |  |  |  | 1335 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.720BE | 720BE (非取樣點) | LINE69 | P07/69/720/BE0 |  |  |  |  | 1336 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.230_ES | 230_ES (非取樣點) | SC | P07/11/230/BE0 |  |  |  |  | 1337 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.240_ES | 240_ES (非取樣點) | SC | P07/22/240/BE0 |  |  |  |  | 1338 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH31 | KH31_DS |  | DS1 | KH31_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_DS | KH31_DS (非取樣點) | FEEDER | P07/11/KH31/DS1 |  |  |  |  | 1339 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH31 | KH31_ES |  | LE0 | KH31_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH31_ES | KH31_ES (非取樣點) | FEEDER | P07/11/KH31/E1 |  |  |  |  | 1340 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH32 | KH32_DS |  | DS1 | KH32_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_DS | KH32_DS (非取樣點) | FEEDER | P07/11/KH32/DS1 |  |  |  |  | 1341 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH32 | KH32_ES |  | LE0 | KH32_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH32_ES | KH32_ES (非取樣點) | FEEDER | P07/11/KH32/E1 |  |  |  |  | 1342 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH33 | KH33_DS |  | DS1 | KH33_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_DS | KH33_DS (非取樣點) | FEEDER | P07/11/KH33/DS1 |  |  |  |  | 1343 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH33 | KH33_ES |  | LE0 | KH33_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH33_ES | KH33_ES (非取樣點) | FEEDER | P07/11/KH33/E1 |  |  |  |  | 1344 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH36 | KH36_DS |  | DS1 | KH36_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_DS | KH36_DS (非取樣點) | FEEDER | P07/11/KH36/DS1 |  |  |  |  | 1345 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH36 | KH36_ES |  | LE0 | KH36_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH36_ES | KH36_ES (非取樣點) | FEEDER | P07/11/KH36/E1 |  |  |  |  | 1346 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH37 | KH37_DS |  | DS1 | KH37_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_DS | KH37_DS (非取樣點) | FEEDER | P07/11/KH37/DS1 |  |  |  |  | 1347 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH37 | KH37_ES |  | LE0 | KH37_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH37_ES | KH37_ES (非取樣點) | FEEDER | P07/11/KH37/E1 |  |  |  |  | 1348 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH38 | KH38_DS |  | DS1 | KH38_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_DS | KH38_DS (非取樣點) | FEEDER | P07/11/KH38/DS1 |  |  |  |  | 1349 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH38 | KH38_ES |  | LE0 | KH38_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH38_ES | KH38_ES (非取樣點) | FEEDER | P07/11/KH38/E1 |  |  |  |  | 1350 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH41 | KH41_DS |  | DS1 | KH41_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_DS | KH41_DS (非取樣點) | FEEDER | P07/11/KH41/DS1 |  |  |  |  | 1351 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH41 | KH41_ES |  | LE0 | KH41_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH41_ES | KH41_ES (非取樣點) | FEEDER | P07/11/KH41/E1 |  |  |  |  | 1352 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH42 | KH42_DS |  | DS1 | KH42_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_DS | KH42_DS (非取樣點) | FEEDER | P07/11/KH42/DS1 |  |  |  |  | 1353 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH42 | KH42_ES |  | LE0 | KH42_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH42_ES | KH42_ES (非取樣點) | FEEDER | P07/11/KH42/E1 |  |  |  |  | 1354 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH43 | KH43_DS |  | DS1 | KH43_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_DS | KH43_DS (非取樣點) | FEEDER | P07/11/KH43/DS1 |  |  |  |  | 1355 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH43 | KH43_ES |  | LE0 | KH43_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH43_ES | KH43_ES (非取樣點) | FEEDER | P07/11/KH43/E1 |  |  |  |  | 1356 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH44 | KH44_DS |  | DS1 | KH44_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_DS | KH44_DS (非取樣點) | FEEDER | P07/11/KH44/DS1 |  |  |  |  | 1357 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH44 | KH44_ES |  | LE0 | KH44_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH44_ES | KH44_ES (非取樣點) | FEEDER | P07/11/KH44/E1 |  |  |  |  | 1358 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH45 | KH45_DS |  | DS1 | KH45_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_DS | KH45_DS (非取樣點) | FEEDER | P07/11/KH45/DS1 |  |  |  |  | 1359 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH45 | KH45_ES |  | LE0 | KH45_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH45_ES | KH45_ES (非取樣點) | FEEDER | P07/11/KH45/E1 |  |  |  |  | 1360 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH46 | KH46_DS |  | DS1 | KH46_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_DS | KH46_DS (非取樣點) | FEEDER | P07/11/KH46/DS1 |  |  |  |  | 1361 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH46 | KH46_ES |  | LE0 | KH46_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH46_ES | KH46_ES (非取樣點) | FEEDER | P07/11/KH46/E1 |  |  |  |  | 1362 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH61 | KH61_DS |  | DS1 | KH61_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_DS | KH61_DS (非取樣點) | FEEDER | P07/22/KH61/DS1 |  |  |  |  | 1363 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH61 | KH61_ES |  | LE0 | KH61_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH61_ES | KH61_ES (非取樣點) | FEEDER | P07/22/KH61/E1 |  |  |  |  | 1364 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH62 | KH62_DS |  | DS1 | KH62_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_DS | KH62_DS (非取樣點) | FEEDER | P07/22/KH62/DS1 |  |  |  |  | 1365 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH62 | KH62_ES |  | LE0 | KH62_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH62_ES | KH62_ES (非取樣點) | FEEDER | P07/22/KH62/E1 |  |  |  |  | 1366 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH63 | KH63_DS |  | DS1 | KH63_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_DS | KH63_DS (非取樣點) | FEEDER | P07/22/KH63/DS1 |  |  |  |  | 1367 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH63 | KH63_ES |  | LE0 | KH63_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH63_ES | KH63_ES (非取樣點) | FEEDER | P07/22/KH63/E1 |  |  |  |  | 1368 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH64 | KH64_DS |  | DS1 | KH64_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_DS | KH64_DS (非取樣點) | FEEDER | P07/22/KH64/DS1 |  |  |  |  | 1369 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH64 | KH64_ES |  | LE0 | KH64_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH64_ES | KH64_ES (非取樣點) | FEEDER | P07/22/KH64/E1 |  |  |  |  | 1370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH65 | KH65_DS |  | DS1 | KH65_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_DS | KH65_DS (非取樣點) | FEEDER | P07/22/KH65/DS1 |  |  |  |  | 1371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH65 | KH65_ES |  | LE0 | KH65_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH65_ES | KH65_ES (非取樣點) | FEEDER | P07/22/KH65/E1 |  |  |  |  | 1372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH66 | KH66_DS |  | DS1 | KH66_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_DS | KH66_DS (非取樣點) | FEEDER | P07/22/KH66/DS1 |  |  |  |  | 1373 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH66 | KH66_ES |  | LE0 | KH66_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH66_ES | KH66_ES (非取樣點) | FEEDER | P07/22/KH66/E1 |  |  |  |  | 1374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH71 | KH71_DS |  | DS1 | KH71_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_DS | KH71_DS (非取樣點) | FEEDER | P07/22/KH71/DS1 |  |  |  |  | 1375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH71 | KH71_ES |  | LE0 | KH71_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH71_ES | KH71_ES (非取樣點) | FEEDER | P07/22/KH71/E1 |  |  |  |  | 1376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH72 | KH72_DS |  | DS1 | KH72_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_DS | KH72_DS (非取樣點) | FEEDER | P07/22/KH72/DS1 |  |  |  |  | 1377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH72 | KH72_ES |  | LE0 | KH72_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH72_ES | KH72_ES (非取樣點) | FEEDER | P07/22/KH72/E1 |  |  |  |  | 1378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH73 | KH73_DS |  | DS1 | KH73_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_DS | KH73_DS (非取樣點) | FEEDER | P07/22/KH73/DS1 |  |  |  |  | 1379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH73 | KH73_ES |  | LE0 | KH73_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH73_ES | KH73_ES (非取樣點) | FEEDER | P07/22/KH73/E1 |  |  |  |  | 1380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH74 | KH74_DS |  | DS1 | KH74_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_DS | KH74_DS (非取樣點) | FEEDER | P07/22/KH74/DS1 |  |  |  |  | 1381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH74 | KH74_ES |  | LE0 | KH74_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH74_ES | KH74_ES (非取樣點) | FEEDER | P07/22/KH74/E1 |  |  |  |  | 1382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH75 | KH75_DS |  | DS1 | KH75_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_DS | KH75_DS (非取樣點) | FEEDER | P07/22/KH75/DS1 |  |  |  |  | 1383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH75 | KH75_ES |  | LE0 | KH75_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH75_ES | KH75_ES (非取樣點) | FEEDER | P07/22/KH75/E1 |  |  |  |  | 1384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.100_DS | 100_DS (非取樣點) | TIE | P07/11/100/DS1 |  |  |  |  | 1385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 台南PS.1501E | 1501E (非取樣點) | TIE | P07/161/1500/E1 |  |  |  |  | 1386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 台南PS.1502E | 1502E (非取樣點) | TIE | P07/161/1500/E2 |  |  |  |  | 1387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.200_DS | 200_DS (非取樣點) | TIE | P07/22/200/DS1 |  |  |  |  | 1388 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_S | [8 empty] | 台南PS.601E | 601E (非取樣點) | TIE | P07/69/600/E1 |  |  |  |  | 1389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_S | [8 empty] | 台南PS.602E | 602E (非取樣點) | TIE | P07/69/600/E2 |  |  |  |  | 1390 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1650TE | 1650TE (非取樣點) | MTR | P07/161/1650/TE0 |  |  |  |  | 1391 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.750TE | 750TE (非取樣點) | MTR | P07/69/750/TE0 |  |  |  |  | 1392 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | NE0 | 1651N | [24 empty] | ADCS_S | [8 empty] | 台南PS.1651N | 1651N (非取樣點) | MTR | P07/161/1650/NE0 |  |  |  |  | 1393 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1650BE | 1650BE (非取樣點) | MTR | P07/161/1650/BE0 |  |  |  |  | 1394 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.750BE | 750BE (非取樣點) | MTR | P07/69/750/BE0 |  |  |  |  | 1395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1660TE | 1660TE (非取樣點) | MTR | P07/161/1660/TE0 |  |  |  |  | 1396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.760TE | 760TE (非取樣點) | MTR | P07/69/760/TE0 |  |  |  |  | 1397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | NE0 | 1661N | [24 empty] | ADCS_S | [8 empty] | 台南PS.1661N | 1661N (非取樣點) | MTR | P07/161/1660/NE0 |  |  |  |  | 1398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1660BE | 1660BE (非取樣點) | MTR | P07/161/1660/BE0 |  |  |  |  | 1399 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.760BE | 760BE (非取樣點) | MTR | P07/69/760/BE0 |  |  |  |  | 1400 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | 1670TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1670TE | 1670TE (非取樣點) | MTR | P07/161/1670/TE0 |  |  |  |  | 1401 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.770TE | 770TE (非取樣點) | MTR | P07/69/770/TE0 |  |  |  |  | 1402 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | NE0 | 1671N | [24 empty] | ADCS_S | [8 empty] | 台南PS.1671N | 1671N (非取樣點) | MTR | P07/161/1670/NE0 |  |  |  |  | 1403 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | 1670BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1670BE | 1670BE (非取樣點) | MTR | P07/161/1670/BE0 |  |  |  |  | 1404 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.770BE | 770BE (非取樣點) | MTR | P07/69/770/BE0 |  |  |  |  | 1405 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1750TE | 1750TE (非取樣點) | MTR | P07/161/1750/TE0 |  |  |  |  | 1406 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1750 | #5DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1750BE | 1750BE (非取樣點) | MTR | P07/161/1750/BE0 |  |  |  |  | 1407 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 330 | #6DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.330_DS | 330_DS (非取樣點) | MTR | P07/22/330/DS1 |  |  |  |  | 1408 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 330 | #6DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.330_ES | 330_ES (非取樣點) | MTR | P07/22/330/TE0 |  |  |  |  | 1409 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 350 | #7DTR(350) |  | DS1 | 350_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.350_DS | 350_DS (非取樣點) | MTR | P07/22/350/DS1 |  |  |  |  | 1410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 350 | #7DTR(350) |  | LE0 | 350_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.350_ES | 350_ES (非取樣點) | MTR | P07/22/350/TE0 |  |  |  |  | 1411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1760TE | 1760TE (非取樣點) | MTR | P07/161/1760/TE0 |  |  |  |  | 1412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1760 | #6DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1760BE | 1760BE (非取樣點) | MTR | P07/161/1760/BE0 |  |  |  |  | 1413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1770TE | 1770TE (非取樣點) | MTR | P07/161/1770/TE0 |  |  |  |  | 1414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1770 | #7DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1770BE | 1770BE (非取樣點) | MTR | P07/161/1770/BE0 |  |  |  |  | 1415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 410 | #11SC(410) |  | SC0 | 410SC | [24 empty] | ADCS_S | [8 empty] | 台南PS.410SC_ES | 410SC_ES (非取樣點) | SC | [5 empty] | 1416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 420 | #12SC(420) |  | SC0 | 420SC | [24 empty] | ADCS_S | [8 empty] | 台南PS.420SC_ES | 420SC_ES (非取樣點) | SC | [5 empty] | 1417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 430 | #13SC(430) |  | SC0 | 430SC | [24 empty] | ADCS_S | [8 empty] | 台南PS.430SC_ES | 430SC_ES (非取樣點) | SC | [5 empty] | 1418 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 440 | #14SC(440) |  | SC0 | 440SC | [24 empty] | ADCS_S | [8 empty] | 台南PS.440SC_ES | 440SC_ES (非取樣點) | SC | [5 empty] | 1419 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.210_ES | 210_ES (非取樣點) | SC | P07/11/210/BE0 |  |  |  |  | 1420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.210_DS | 210_DS (非取樣點) | SC | P07/11/210/DS1 |  |  |  |  | 1421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.810BE | 810BE (非取樣點) | SC | P07/69/810/BE0 |  |  |  |  | 1422 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 810CE | 810CE |  | 810CE | 810CE | [24 empty] | ADCS_S | [8 empty] | 台南PS.810CE | 810CE (非取樣點) | SC | P07/69/810/CE0 |  |  |  |  | 1423 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 820BE | 820BE |  | 820BE | 820BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.820BE | 820BE (非取樣點) | SC | P07/69/820/BE0 |  |  |  |  | 1424 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 820CE | 820CE |  | 820CE | 820CE | [24 empty] | ADCS_S | [8 empty] | 台南PS.820CE | 820CE (非取樣點) | SC | P07/69/820/CE0 |  |  |  |  | 1425 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 830BE | 830BE |  | 830BE | 830BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.830BE | 830BE (非取樣點) | SC | P07/69/830/BE0 |  |  |  |  | 1426 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 830CE | 830CE |  | 830CE | 830CE | [24 empty] | ADCS_S | [8 empty] | 台南PS.830CE | 830CE (非取樣點) | SC | P07/69/830/CE0 |  |  |  |  | 1427 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_S | [8 empty] | 台南PS.161B1E | 161B1E (非取樣點) | BUS | P07/161/161B1E/BE1 |  |  |  |  | 1428 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_S | [8 empty] | 台南PS.161B2E | 161B2E (非取樣點) | BUS | P07/161/161B2E/BE2 |  |  |  |  | 1429 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 台南PS.69B1E | 69B1E (非取樣點) | BUS | P07/69/69B1E/BE1 |  |  |  |  | 1430 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_S | [8 empty] | 台南PS.69B2E | 69B2E (非取樣點) | BUS | P07/69/69B2E/BE2 |  |  |  |  | 1431 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 台南PS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1432 | NotelDIPoint | [38 empty] | START/STOP | STOP
P07 | 台南PS | 69 | 69kV | 1550 | 台南延平線(1550) |  | PW1UL | 1550_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1550_PW1UL | 延平紅線(1550)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1433 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 1550 | 台南延平線(1550) |  | PW2UL | 1550_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1550_PW2UL | 延平紅線(1550)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1434 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 1550 | 台南延平線(1550) |  | HCBUL | 1550_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1550_HCBUL | 延平紅線(1550)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1435 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 1560 | 台南忠孝二路(1560) |  | PW1UL | 1560_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1560_PW1UL | 延平白線(1560)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1436 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 1560 | 台南忠孝二路(1560) |  | PW2UL | 1560_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1560_PW2UL | 延平白線(1560)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1437 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 1560 | 台南忠孝二路(1560) |  | HCBUL | 1560_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.1560_HCBUL | 延平白線(1560)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1438 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.620_PW1UL | 保安線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1439 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.620_PW2UL | 保安線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1440 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 620 | 保安線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.620_HCBUL | 保安線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1441 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | PW1UL | 630_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.630_PW1UL | 光洲線(630)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1442 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | PW2UL | 630_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.630_PW2UL | 光洲線(630)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1443 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 630 | 台南光洲線(630) |  | HCBUL | 630_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.630_HCBUL | 光洲線(630)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1444 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | PW1UL | 640_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.640_PW1UL | 忠孝海線(640)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1445 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | PW2UL | 640_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.640_PW2UL | 忠孝海線(640)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1446 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 640 | 備用線(640) |  | HCBUL | 640_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.640_HCBUL | 忠孝海線(640)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1447 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | PW1UL | 660_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.660_PW1UL | 后甲海線(660)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1448 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | PW2UL | 660_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.660_PW2UL | 后甲海線(660)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1449 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 660 | 台南後甲海線(660) |  | HCBUL | 660_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.660_HCBUL | 后甲海線(660)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1450 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PW1UL | 670_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.670_PW1UL | 大灣線(670)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1451 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PW2UL | 670_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.670_PW2UL | 大灣線(670)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1452 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 670 | 台南大灣一路(670) |  | HCBUL | 670_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.670_HCBUL | 大灣線(670)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1453 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | PW1UL | 720_PW1UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.720_PW1UL | 永康線(720)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1454 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | PW2UL | 720_PW2UL | [24 empty] | ADCS_S | [8 empty] | 台南PS.720_PW2UL | 永康線(720)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1455 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P07 | 台南PS | 69 | 69kV | 720 | 台南大灣二路(720) |  | HCBUL | 720_HCBUL | [24 empty] | ADCS_S | [8 empty] | 台南PS.720_HCBUL | 永康線(720)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1456 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P07 | 台南PS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 台南PS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 1457 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 台南PS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 1458 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH76 | KH76_DS |  | DS1 | KH76_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_DS | KH76_DS (非取樣點) | FEEDER | P07/22/KH76/DS1 |  |  |  |  | 1459 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH76 | KH76_ES |  | LE0 | KH76_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH76_ES | KH76_ES (非取樣點) | FEEDER | P07/22/KH76/E1 |  |  |  |  | 1460 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.220_ES | 220_ES (非取樣點) | SC | P07/11/220/BE0 |  |  |  |  | 1461 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.220_DS | 220_DS (非取樣點) | SC | P07/11/220/DS1 |  |  |  |  | 1462 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.250_ES | 250_ES (非取樣點) | SC | P07/22/250/BE0 |  |  |  |  | 1463 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.250_DS | 250_DS (非取樣點) | SC | P07/22/250/DS1 |  |  |  |  | 1464 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.260_ES | 260_ES (非取樣點) | SC | P07/22/260/BE0 |  |  |  |  | 1465 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.260_DS | 260_DS (非取樣點) | SC | P07/22/260/DS1 |  |  |  |  | 1466 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 270 | #7SC(270) |  | LE0 | 270_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.270_ES | 270_ES (非取樣點) | SC | P07/22/270/BE0 |  |  |  |  | 1467 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 270 | #7SC(270) |  | DS1 | 270_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.270_DS | 270_DS (非取樣點) | SC | P07/22/270/DS1 |  |  |  |  | 1468 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310 | 310A1_DS |  | DS1 | 310A1 | [24 empty] | ADCS_S | [8 empty] | 台南PS.310A1_DS | 310A1_DS (非取樣點) | MTR | P07/11/310A1/DS1 |  |  |  |  | 1469 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310 | 310A2_DS |  | DS1 | 310A2 | [24 empty] | ADCS_S | [8 empty] | 台南PS.310A2_DS | 310A2_DS (非取樣點) | MTR | P07/11/310A2/DS1 |  |  |  |  | 1470 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 320 | #5DTR(320) |  | DS1 | 320_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.320_DS | 320_DS (非取樣點) | MTR | P07/11/320/DS1 |  |  |  |  | 1471 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 310 | 310A1 |  | A10 | 310A1 | [24 empty] | ADCS_S | [8 empty] | 台南PS.310A1_ES | 310A1_ES(非取樣點) | MTR | [5 empty] | 1472 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 310 | 310A2 |  | A20 | 310A2 | [24 empty] | ADCS_S | [8 empty] | 台南PS.310A2_ES | 310A2_ES(非取樣點) | MTR | [5 empty] | 1473 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 320 | #5DTR(320) |  | LE0 | 320_ES | [24 empty] | ADCS_S | [8 empty] | 台南PS.320_ES | 320_ES(非取樣點) | MTR | P07/11/320/TE0 |  |  |  |  | 1474 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH11 | KH11_DS |  | DS1 | KH11_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_DS | KH11_DS (非取樣點) | FEEDER | P07/11/KH11/DS1 |  |  |  |  | 1475 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH11 | KH11_ES |  | LE0 | KH11_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH11_ES | KH11_ES (非取樣點) | FEEDER | P07/11/KH11/BE0 |  |  |  |  | 1476 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH12 | KH12_DS |  | DS1 | KH12_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_DS | KH12_DS (非取樣點) | FEEDER | P07/11/KH12/DS1 |  |  |  |  | 1477 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH12 | KH12_ES |  | LE0 | KH12_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH12_ES | KH12_ES (非取樣點) | FEEDER | P07/11/KH12/BE0 |  |  |  |  | 1478 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH13 | KH13_DS |  | DS1 | KH13_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_DS | KH13_DS (非取樣點) | FEEDER | P07/11/KH13/DS1 |  |  |  |  | 1479 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH13 | KH13_ES |  | LE0 | KH13_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH13_ES | KH13_ES (非取樣點) | FEEDER | P07/11/KH13/BE0 |  |  |  |  | 1480 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH14 | KH14_DS |  | DS1 | KH14_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_DS | KH14_DS (非取樣點) | FEEDER | P07/11/KH14/DS1 |  |  |  |  | 1481 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH14 | KH14_ES |  | LE0 | KH14_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH14_ES | KH14_ES (非取樣點) | FEEDER | P07/11/KH14/BE0 |  |  |  |  | 1482 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH15 | KH15_DS |  | DS1 | KH15_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_DS | KH15_DS (非取樣點) | FEEDER | P07/11/KH15/DS1 |  |  |  |  | 1483 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH15 | KH15_ES |  | LE0 | KH15_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH15_ES | KH15_ES (非取樣點) | FEEDER | P07/11/KH15/BE0 |  |  |  |  | 1484 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH16 | KH16_DS |  | DS1 | KH16_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_DS | KH16_DS (非取樣點) | FEEDER | P07/11/KH16/DS1 |  |  |  |  | 1485 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH16 | KH16_ES |  | LE0 | KH16_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH16_ES | KH16_ES (非取樣點) | FEEDER | P07/11/KH16/BE0 |  |  |  |  | 1486 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH17 | KH17_DS |  | DS1 | KH17_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_DS | KH17_DS (非取樣點) | FEEDER | P07/11/KH17/DS1 |  |  |  |  | 1487 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH17 | KH17_ES |  | LE0 | KH17_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH17_ES | KH17_ES (非取樣點) | FEEDER | P07/11/KH17/BE0 |  |  |  |  | 1488 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH18 | KH18_DS |  | DS1 | KH18_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_DS | KH18_DS (非取樣點) | FEEDER | P07/11/KH18/DS1 |  |  |  |  | 1489 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH18 | KH18_ES |  | LE0 | KH18_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH18_ES | KH18_ES (非取樣點) | FEEDER | P07/11/KH18/BE0 |  |  |  |  | 1490 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH19 | KH19_DS |  | DS1 | KH19_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_DS | KH19_DS (非取樣點) | FEEDER | P07/11/KH19/DS1 |  |  |  |  | 1491 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH19 | KH19_ES |  | LE0 | KH19_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH19_ES | KH19_ES (非取樣點) | FEEDER | P07/11/KH19/BE0 |  |  |  |  | 1492 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | KH20 | KH20_DS |  | DS1 | KH20_DS | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_DS | KH20_DS (非取樣點) | FEEDER | P07/11/KH20/DS1 |  |  |  |  | 1493 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | KH20 | KH20_ES |  | LE0 | KH20_ES | [24 empty] | DDCS4_1 | [8 empty] | 台南PS.KH20_ES | KH20_ES (非取樣點) | FEEDER | P07/11/KH20/BE0 |  |  |  |  | 1494 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1780TE | 1780TE (非取樣點) | MTR | P07/161/1780/TE0 |  |  |  |  | 1495 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1780 | #8DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1780BE | 1780BE (非取樣點) | MTR | P07/161/1780/BE0 |  |  |  |  | 1496 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 台南PS.301 | 301 (非取樣點) | TIE | P07/11/300/DS1 |  |  |  |  | 1497 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 300 | TIE(300) |  | E1 | 301E | [24 empty] | ADCS_S | [8 empty] | 台南PS.301E | 301E (非取樣點) | TIE | P07/11/300/BE0 |  |  |  |  | 1498 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_S | [8 empty] | 台南PS.401 | 401 (非取樣點) | TIE | P07/11/400/DS1 |  |  |  |  | 1499 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 400 | TIE(400) |  | E1 | 401E | [24 empty] | ADCS_S | [8 empty] | 台南PS.401E | 401E (非取樣點) | TIE | P07/11/400/BE0 |  |  |  |  | 1500 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 台南PS.391 | 391 (非取樣點) | OTHER | P07/11/390/DS1 |  |  |  |  | 1501 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 台南PS.391E | 391E (非取樣點) | OTHER | P07/11/390/BE0 |  |  |  |  | 1502 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_S | [8 empty] | 台南PS.371 | 371 (非取樣點) | MTR | P07/11/370/DS1 |  |  |  |  | 1503 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 370 | #8DTR(370) |  | E1 | 371E | [24 empty] | ADCS_S | [8 empty] | 台南PS.371E | 371E (非取樣點) | MTR | P07/11/370/BE0 |  |  |  |  | 1504 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 381 | 381 |  | 381 | 381 | [24 empty] | ADCS_S | [8 empty] | 台南PS.381 | 381 (非取樣點) | MTR | P07/11/380/DS1 |  |  |  |  | 1505 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 380 | #8DTR(380) |  | E1 | 381E | [24 empty] | ADCS_S | [8 empty] | 台南PS.381E | 381E (非取樣點) | MTR | P07/11/380/BE0 |  |  |  |  | 1506 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 411E | 411E |  | 411E | 411E | [24 empty] | ADCS_S | [8 empty] | 台南PS.411E | 411E (非取樣點) | SC | P07/11/410/BE0 |  |  |  |  | 1507 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 411 | 411 |  | 411 | 411 | [24 empty] | ADCS_S | [8 empty] | 台南PS.411 | 411 (非取樣點) | SC | P07/11/410/DS1 |  |  |  |  | 1508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 421E | 421E |  | 421E | 421E | [24 empty] | ADCS_S | [8 empty] | 台南PS.421E | 421E (非取樣點) | SC | P07/11/420/BE0 |  |  |  |  | 1509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 421 | 421 |  | 421 | 421 | [24 empty] | ADCS_S | [8 empty] | 台南PS.421 | 421 (非取樣點) | SC | P07/11/420/DS1 |  |  |  |  | 1510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 431E | 431E |  | 431E | 431E | [24 empty] | ADCS_S | [8 empty] | 台南PS.431E | 431E (非取樣點) | SC | P07/11/430/BE0 |  |  |  |  | 1511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 431 | 431 |  | 431 | 431 | [24 empty] | ADCS_S | [8 empty] | 台南PS.431 | 431 (非取樣點) | SC | P07/11/430/DS1 |  |  |  |  | 1512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 441E | 441E |  | 441E | 441E | [24 empty] | ADCS_S | [8 empty] | 台南PS.441E | 441E (非取樣點) | SC | P07/11/440/BE0 |  |  |  |  | 1513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 441 | 441 |  | 441 | 441 | [24 empty] | ADCS_S | [8 empty] | 台南PS.441 | 441 (非取樣點) | SC | P07/11/440/DS1 |  |  |  |  | 1514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 8A | #8A |  | BE | #8A_BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.#8A_BE | #8A BE(非取樣點) | OTHER | [5 empty] | 1515 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 8B | #8B |  | BE | #8B_BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.#8B_BE | #8B BE(非取樣點) | OTHER | [5 empty] | 1516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.230_DS | 230_DS (非取樣點) | SC | P07/11/230/DS1 |  |  |  |  | 1517 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_S | [8 empty] | 台南PS.240_DS | 240_DS (非取樣點) | SC | P07/22/240/DS1 |  |  |  |  | 1518 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 210E | 210E |  | 210E | 210E | [24 empty] | ADCS_S | [8 empty] | 台南PS.210E | 210E (非取樣點) | SC | P07/11/210/DS2 |  |  |  |  | 1519 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 220E | 220E |  | 220E | 220E | [24 empty] | ADCS_S | [8 empty] | 台南PS.220E | 220E (非取樣點) | SC | P07/11/220/DS2 |  |  |  |  | 1520 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 230E | 230E |  | 230E | 230E | [24 empty] | ADCS_S | [8 empty] | 台南PS.230E | 230E (非取樣點) | SC | P07/11/230/DS2 |  |  |  |  | 1521 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 240E | 240E |  | 240E | 240E | [24 empty] | ADCS_S | [8 empty] | 台南PS.240E | 240E (非取樣點) | SC | P07/22/240/DS2 |  |  |  |  | 1522 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 250E | 250E |  | 250E | 250E | [24 empty] | ADCS_S | [8 empty] | 台南PS.250E | 250E (非取樣點) | SC | P07/22/250/DS2 |  |  |  |  | 1523 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 260E | 260E |  | 260E | 260E | [24 empty] | ADCS_S | [8 empty] | 台南PS.260E | 260E (非取樣點) | SC | P07/22/260/DS2 |  |  |  |  | 1524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 270E | 270E |  | 270E | 270E | [24 empty] | ADCS_S | [8 empty] | 台南PS.270E | 270E (非取樣點) | SC | P07/22/270/DS2 |  |  |  |  | 1525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1570LE | 1570LE (非取樣點) | LINE161 | P07/161/1570/LE0 |  |  |  |  | 1526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 161 | 161kV | 1570 | 台南忠孝一路(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 台南PS.1570BE | 1570BE (非取樣點) | LINE161 | P07/161/1570/BE0 |  |  |  |  | 1527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 8ABUS | 8ABUS |  | PTE | 8ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 台南PS.8ABUS_PTE | #8ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 8ABUS | 8ABUS |  | PTD | 8ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.8ABUS_PTD | #8ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 8BBUS | 8BBUS |  | PTE | 8BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 台南PS.8BBUS_PTE | #8BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P07 | 台南PS | 0 |  | 8BBUS | 8BBUS |  | PTD | 8BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.8BBUS_PTD | #8BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 5A1BUS | 5A1BUS |  | PTD | 5A1BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.5A1BUS_PTD | #5A1BUS_PTD(非取樣點) | OTHER | [5 empty] | 1532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 5A2BUS | 5A2BUS |  | PTD | 5A2BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.5A2BUS_PTD | #5A2BUS_PTD(非取樣點) | OTHER | [5 empty] | 1533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 5BBUS | 5BBUS |  | PTD | 5BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.5BBUS_PTD | #5BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 6BUS | 6BUS |  | PTD | 6BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.6BUS_PTD | #6BUS_PTD(非取樣點) | OTHER | [5 empty] | 1535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P07 | 台南PS | 0 |  | 7BUS | 7BUS |  | PTD | 7BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 台南PS.7BUS_PTD | #7BUS_PTD(非取樣點) | OTHER | [5 empty] | 1536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo