## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S01 | 雲港SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KVBUS | KV | 69KV#1BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S01_A1 | [8 empty] | 雲港SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S01 | 雲港SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KVBUS | KV | 69KV#2BUS PT | kV_-90_90(-2000_2000) | aab | B2/S01_A1 | [8 empty] | 雲港SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S01 | 雲港SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV#1BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S01_D1 | [8 empty] | 雲港SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S01 | 雲港SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | 11KV#3BUS | KV | 三號 BUS PT | kV_-9_9(-2000_2000) | aba | B2/S01_D1 | [8 empty] | 雲港SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S01 | 雲港SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1BUS | [13 empty] | aaaz | B2/S01_A1 | [8 empty] | 雲港SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA | 衡相監視 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 69KV #1BUS | 87 B1A | 一號87電驛動作警報 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0302 |  | 0106 | 1-32-14 |  | 1-6A | 69KV | 87 B1S | 一號BUS87RY U/L狀態 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.87B1S | 69KV #1BUS差動電驛設定 | OTHER |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/2BUS | [13 empty] | aaaz | B2/S01_A1 | [8 empty] | 雲港SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV #2BUS | UVA | 衡相監視 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 69KV #2BUS | 87 B2A | 二號87電驛動作警報 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0303 |  | 0107 | 1-32-15 |  | 1-6B | 69KV | 87 B2S | 二號BUS87RY U/L狀態 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.87B2S | 69KV #2BUS差動電驛設定 | OTHER |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 710 | MW | 北港雲港一路瓦 | MW_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.710_MW | 北港一路 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 710 | MVAR | 北港雲港一路乏 | MVAR_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.710_MVAR | 北港一路 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 710 | MWH(+) | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 720 | MW | 北港雲港二路瓦 | MW_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.720_MW | 北港二路 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 720 | MVAR | 北港雲港二路乏 | MVAR_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.720_MVAR | 北港二路 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 720 | MWH(+) | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 610 | MW | 雲港萬有線瓦 | MW_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.610_MW | 萬有線 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 610 | MVAR | 雲港萬有線乏 | MVAR_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.610_MVAR | 萬有線 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 610 | MWH(+) | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 660 | MW | 備用線 | MW_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.660_MW | 嘉太線 MW | LINE69 |  |  |  |  | CDC | 23 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 660 | MVAR | 備用線 | MVAR_-144_144(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.660_MVAR | 嘉太線 MVAR | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 660 | MWH(+) | 備用線 |  |  | B2/S01_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 25 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 710 | PHA | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.710_PHA | 北港一路(710) 相間RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 710 | GDA | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.710_GDA | 北港一路(710) 接地RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 710 | L187A | 北港雲港一路87電驛動作 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L187A | 710北港雲港ㄧ路差動電驛動作 | OTHER |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87CFA |  | Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | 710 | L187CFA | 北港雲港一路87RY通訊故障 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L187CFA | 710北港雲港ㄧ路87RY通訊故障 | OTHER |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 720 | PHA | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.720_PHA | 北港二路(720) 相間RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 720 | GDA | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.720_GDA | 北港二路(720) 接地RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 720 | L287A | 北港雲港二路87電驛動作 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L287A | 720北港雲港二路差動電驛動作 | OTHER |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87CFA |  | Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | 720 | L287CFA | 北港雲港二路87RY通訊故障 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L287CFA | 720北港雲港二路87RY通訊故障 | OTHER |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 610 | PHA | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.610_PHA | 萬有線(610) 相間RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 610 | GDA | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.610_GDA | 萬有線(610) 接地RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 610 | 85A | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.610_85A | 萬有線(610) 85RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | 610 | 74 U/L | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.610_74A | 萬有線(610) 74RY | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 660 | PHA | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.660_PHA | 嘉太線(660) 相間RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 660 | GDA | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.660_GDA | 嘉太線(660) 接地RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 660 | 85A | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.660_85A | 嘉太線(660) 85RY | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 660 | 74 U/L | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.660_74A | 嘉太線(660) 74RY | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 710 | L187S | 北港雲港一路87RY U/L |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L187S | 710北港雲港ㄧ路差動電驛設定 | OTHER |  |  |  |  | CDC | 42 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 720 | L287S | 北港雲港二路87RY U/L |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L287S | 720北港雲港二路差動電驛設定 | OTHER |  |  |  |  | CDC | 43 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 610 | 85 U/L | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.610_85UL | 萬有線(610) 85RY U/L | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 660 | 85 U/L | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.660_85UL | 嘉太線(660) 85RY U/L | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/P04S011/T2 |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 710 | CB ON/OFF | 北港雲港一路 |  | aaba | B2/S01_A1 | [8 empty] | 雲港SS.710_CB | 710(北港一路) CB | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/P04S012/T2 |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 720 | CB ON/OFF | 北港雲港二路 |  | aada | B2/S01_A1 | [8 empty] | 雲港SS.720_CB | 720(北港二路) CB | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S01C67/T1 |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 610 | CB ON/OFF | 雲港萬有線 |  | aaga | B2/S01_A1 | [8 empty] | 雲港SS.610_CB | 610(萬有線) CB | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/備用線/T1 |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 660 | CB ON/OFF | 備用線 |  | aaia | B2/S01_A1 | [8 empty] | 雲港SS.660_CB | 660(嘉太線) CB | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | DS1 | 711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0016 | 1-38-00 | 1-38-01 | 1-10 | 711 | ABS ON | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.711_DS | 711(北港一路) DS | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | DS2 | 712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0017 | 1-38-02 | 1-38-03 | 1-11 | 712 | ABS ON | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.712_DS | 712(北港一路) DS | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | DS1 | 721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0020 | 1-38-08 | 1-38-09 | 1-14 | 721 | ABS ON | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.721_DS | 721(北港二路) DS | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | DS2 | 722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0021 | 1-38-10 | 1-38-11 | 1-15 | 722 | ABS ON | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.722_DS | 722(北港二路) DS | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | DS1 | 611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0024 | 1-39-00 | 1-39-01 | 1-18 | 611 | ABS ON | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.611_DS | 611(萬有線) DS | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | DS2 | 612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0402 | 403 | 0025 | 1-39-02 | 1-39-03 | 1-19 | 612 | ABS ON | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.612_DS | 612(萬有線) DS | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS1 | 661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0408 | 409 | 0028 | 1-39-08 | 1-39-09 | 1-1C | 661 | ABS ON | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.661_DS | 661(嘉太線) DS | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS2 | 662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0029 | 1-39-10 | 1-39-11 | 1-1D | 662 | ABS ON | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.662_DS | 662(嘉太線) DS | LINE69 |  |  |  |  | CDC | 57 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | DS3 | 713 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0018 | 1-38-04 | 1-38-05 | 1-12 | 713 | ABS ON | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.713_DS | 713(北港一路) DS | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | E3 | 713E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0390 | 391 | 0019 | 1-38-06 | 1-38-07 | 1-13 | 713E | ABS ON | 北港雲港一路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.713E_ES | 713E(北港一路) ES | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 60 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 61 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | DS3 | 723 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0396 | 397 | 0022 | 1-38-12 | 1-38-13 | 1-16 | 723 | ABS ON | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.723_DS | 723(北港二路) DS | LINE69 |  |  |  |  | CDC | 62 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | E3 | 723E |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [6 empty] | 0398 | 399 | 0023 | 1-38-14 | 1-38-15 | 1-17 | 723E | ABS ON | 北港雲港二路 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.723E_ES | 723E(北港二路) ES | LINE69 |  |  |  |  | CDC | 63 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.720LE | 720LE (非取樣點) | LINE69 | [5 empty] | 64 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 65 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | DS3 | 613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0026 | 1-39-04 | 1-39-05 | 1-1A | 613 | ABS ON | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.613_DS | 613(萬有線) DS | LINE69 |  |  |  |  | CDC | 66 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | E3 | 613E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0406 | 407 | 0027 | 1-39-06 | 1-39-07 | 1-1B | 613E | ABS ON | 雲港萬有線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.613E_ES | 613E(萬有線) ES | LINE69 |  |  |  |  | CDC | 67 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 68 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 69 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS3 | 663 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0030 | 1-39-12 | 1-39-13 | 1-1E | 663 | ABS ON | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.663_DS | 663(嘉太線) DS | LINE69 |  |  |  |  | CDC | 70 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | E3 | 663E |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [6 empty] | 0414 | 415 | 0031 | 1-39-14 | 1-39-15 | 1-1F | 663E | ABS ON | 備用線 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.663E_ES | 663E(嘉太線) ES | LINE69 |  |  |  |  | CDC | 71 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 72 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 73 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | F1 PH RY | PHA | 港一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG21_PHA | 11KV港一線(XG21) 相間RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | F1 GD RY | GDA | 港一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG21_GDA | 11KV港一線(XG21) 接地RY | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0062 | 1-33-06 |  | 1-3E | F1 CB | 79 U/L | 港一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG21_79UL | 11KV港一線(XG21) 79RY U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 港一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG21_ADJ | 11KV港一線(XG21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | F2 PH RY | PHA | 港二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG22_PHA | 11KV港二線(XG22) 相間RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | F2 GD RY | GDA | 港二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG22_GDA | 11KV港二線(XG22) 接地RY | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0063 | 1-33-07 |  | 1-3F | F2 CB | 79 U/L | 港二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG22_79UL | 11KV港二線(XG22) 79RY U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 港二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG22_ADJ | 11KV港二線(XG22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | F3 PH RY | PHA | 港三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG23_PHA | 11KV港三線(XG23) 相間RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | F3 GD RY | GDA | 港三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG23_GDA | 11KV港三線(XG23) 接地RY | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0064 | 1-33-08 |  | 1-40 | F3 CB | 79 U/L | 港三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG23_79UL | 11KV港三線(XG23) 79RY U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 港三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG23_ADJ | 11KV港三線(XG23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F4 PH RY | PHA | 港四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG24_PHA | 11KV港四線(XG24) 相間RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F4 GD RY | GDA | 港四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG24_GDA | 11KV港四線(XG24) 接地RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0065 | 1-33-09 |  | 1-41 | F4 CB | 79 U/L | 港四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG24_79UL | 11KV港四線(XG24) 79RY U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 港四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG24_ADJ | 11KV港四線(XG24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F5 PH RY | PHA | 港五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG25_PHA | 11KV港五線(XG25) 相間RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F5 GD RY | GDA | 港五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG25_GDA | 11KV港五線(XG25) 接地RY | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0066 | 1-33-10 |  | 1-42 | F5 CB | 79 U/L | 港五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG25_79UL | 11KV港五線(XG25) 79RY U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 港五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG25_ADJ | 11KV港五線(XG25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-04 |  |  | F11 PH RY | PHA | 港十一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG31_PHA | 11KV港十一(XG31) 相間RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F11 GD RY | GDA | 港十一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG31_GDA | 11KV港十一(XG31) 接地RY | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0100 | 1-35-06 |  | 1-64 | F11 CB | 79 U/L | 港十一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG31_79UL | 11KV港十一(XG31) 79RY U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | F11 LCO | ADJ(U/L) | 港十一線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG31_ADJ | 11KV港十一(XG31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | F12 PH RY | PHA | 港十二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG32_PHA | 11KV港十二(XG32) 相間RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | F12 GD RY | GDA | 港十二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG32_GDA | 11KV港十二(XG32) 接地RY | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0101 | 1-35-07 |  | 1-65 | F12 CB | 79 U/L | 港十二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG32_79UL | 11KV港十二(XG32) 79RY U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | F12 LCO | ADJ(U/L) | 港十二線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG32_ADJ | 11KV港十二(XG32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | F13 PH RY | PHA | 港十三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG33_PHA | 11KV港十三(XG33) 相間RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | F13 GD RY | GDA | 港十三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG33_GDA | 11KV港十三(XG33) 接地RY | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0102 | 1-35-08 |  | 1-66 | F13 CB | 79 U/L | 港十三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG33_79UL | 11KV港十三(XG33) 79RY U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | F13 LCO | ADJ(U/L) | 港十三線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG33_ADJ | 11KV港十三(XG33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | F14 PH RY | PHA | 港十四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG34_PHA | 11KV港十四(XG34) 相間RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F14 GD RY | GDA | 港十四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG34_GDA | 11KV港十四(XG34) 接地RY | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0103 | 1-35-09 |  | 1-67 | F14 CB | 79 U/L | 港十四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG34_79UL | 11KV港十四(XG34) 79RY U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | F14 LCO | ADJ(U/L) | 港十四線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG34_ADJ | 11KV港十四(XG34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | F15 PH RY | PHA | 港十五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG35_PHA | 11KV港十五(XG35) 相間RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F15 GD RY | GDA | 港十五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG35_GDA | 11KV港十五(XG35) 接地RY | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0104 | 1-35-10 |  | 1-68 | F15 CB | 79 U/L | 港十五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG35_79UL | 11KV港十五(XG35) 79RY U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | F15 LCO | ADJ(U/L) | 港十五線 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.XG35_ADJ | 11KV港十五(XG35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | L/XG21/T1 |  |  | 0095 |  | 0053 | 1-0B-07 |  | 1-35 | F1 CB | CB ON/OFF | 港一線 |  | aabb | B2/S01_D1 | [8 empty] | 雲港SS.XG21_CB | XG21(11KV港一線) CB | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG21_DS | XG21_DS (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG21_ES | XG21_ES (非取樣點) | FEEDER | [5 empty] | 116 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | L/XG22/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F2 CB | CB ON/OFF | 港二線 |  | aacb | B2/S01_D1 | [8 empty] | 雲港SS.XG22_CB | XG22(11KV港二線) CB | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG22_DS | XG22_DS (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG22_ES | XG22_ES (非取樣點) | FEEDER | [5 empty] | 119 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | L/XG23/T1 |  |  | 0101 |  | 0055 | 1-0C-05 |  | 1-37 | F3 CB | CB ON/OFF | 港三線 |  | aadb | B2/S01_D1 | [8 empty] | 雲港SS.XG23_CB | XG23(11KV港三線) CB | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG23_DS | XG23_DS (非取樣點) | FEEDER | [5 empty] | 121 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG23_ES | XG23_ES (非取樣點) | FEEDER | [5 empty] | 122 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | L/XG24/T1 |  |  | 0104 |  | 0056 | 1-0D-00 |  | 1-38 | F4 CB | CB ON/OFF | 港四線 |  | aaeb | B2/S01_D1 | [8 empty] | 雲港SS.XG24_CB | XG24(11KV港四線) CB | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG24_DS | XG24_DS (非取樣點) | FEEDER | [5 empty] | 124 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG24_ES | XG24_ES (非取樣點) | FEEDER | [5 empty] | 125 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | L/XG25/T1 |  |  | 0107 |  | 0057 | 1-0D-03 |  | 1-39 | F5 CB | CB ON/OFF | 港五線 |  | aagb | B2/S01_D1 | [8 empty] | 雲港SS.XG25_CB | XG25(11KV港五線) CB | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG25_DS | XG25_DS (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG25_ES | XG25_ES (非取樣點) | FEEDER | [5 empty] | 128 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | L/XG31/T1 |  |  | 0139 |  | 0092 | 1-11-03 |  | 1-5C | F11 CB | CB ON/OFF | 港十一線 |  | abab | B2/S01_D1 | [8 empty] | 雲港SS.XG31_CB | XG31(11KV港十一) CB | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG31_DS | XG31_DS (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG31_ES | XG31_ES (非取樣點) | FEEDER | [5 empty] | 131 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | L/XG32/T1 |  |  | 0142 |  | 0093 | 1-11-06 |  | 1-5D | F12 CB | CB ON/OFF | 港十二線 |  | abbb | B2/S01_D1 | [8 empty] | 雲港SS.XG32_CB | XG32(11KV港十二) CB | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG32_DS | XG32_DS (非取樣點) | FEEDER | [5 empty] | 133 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG32_ES | XG32_ES (非取樣點) | FEEDER | [5 empty] | 134 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | L/XG33/T1 |  |  | 0145 |  | 0094 | 1-12-01 |  | 1-5E | F13 CB | CB ON/OFF | 港十三線 |  | abcb | B2/S01_D1 | [8 empty] | 雲港SS.XG33_CB | XG33(11KV港十三) CB | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG33_DS | XG33_DS (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG33_ES | XG33_ES (非取樣點) | FEEDER | [5 empty] | 137 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | L/XG34/T1 |  |  | 0148 |  | 0095 | 1-12-04 |  | 1-5F | F14 CB | CB ON/OFF | 港十四線 |  | abeb | B2/S01_D1 | [8 empty] | 雲港SS.XG34_CB | XG34(11KV港十四) CB | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG34_DS | XG34_DS (非取樣點) | FEEDER | [5 empty] | 139 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG34_ES | XG34_ES (非取樣點) | FEEDER | [5 empty] | 140 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | L/XG35/T1 |  |  | 0151 |  | 0096 | 1-12-07 |  | 1-60 | F15 CB | CB ON/OFF | 港十五線 |  | abfb | B2/S01_D1 | [8 empty] | 雲港SS.XG35_CB | XG35(11KV港十五) CB | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG35_DS | XG35_DS (非取樣點) | FEEDER | [5 empty] | 142 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.XG35_ES | XG35_ES (非取樣點) | FEEDER | [5 empty] | 143 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | TIE (600) | A1 | TIE (600) R相電流 | A_-1200_1200(-2000_2000) |  | B2/S01_A1 | [8 empty] | 雲港SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 144 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1000 | 950 | 1000 | 1100 | 1200 | 0.71 | -950 | -1000 | -1100 | -1200 | 1 | 0.01 | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 145 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 146 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 147 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0034 |  | 0007 | 1-04-02 |  | 1-07 | 600 | CB ON/OFF | TIE(600) 69KV |  | aafz | B2/S01_A1 | [8 empty] | 雲港SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 148 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/1BUS | B/3BUS |  |  | 0113 |  | 0058 | 1-0E-01 |  | 1-3A | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | zzzz | B2/S01_D1 | [8 empty] | 雲港SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 149 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #1 TIEPH RY | PHA | #1 TIE CB |  |  | B2/S01_D1 | [8 empty] | 雲港SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 150 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIEGD RY | GDA | #1 TIE CB |  |  | B2/S01_D1 | [8 empty] | 雲港SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 151 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | 433 | 0042 | 1-3B-00 | 1-3B-01 | 1-2A | 601 | ABS ON | 69KV 連絡斷路器 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 152 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0043 | 1-3B-02 | 1-3B-03 | 1-2B | 602 | ABS ON | 69KV 連絡斷路器 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 153 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.601E | 601E (非取樣點) | TIE | [5 empty] | 154 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.602E | 602E (非取樣點) | TIE | [5 empty] | 155 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 156 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | DS1 | TIE1(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/S01_D1 | [16 empty] | 157 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 158 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 159 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 160 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 161 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 162 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3MTR | MW | 三號主變 | MW_-36_36(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 163 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3MTR | MVAR | 三號主變 | MVAR_-36_36(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 164 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3MTR R電流 | A1 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 165 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3MTR S電流 | A2 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 166 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3MTR T電流 | A3 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 167 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 168 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 169 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0059 | 1-9B |  | 1-3B | #1MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 170 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH | 一號主變 |  |  | B1/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 171 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 172 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | OilTemp |  | B3 | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 173 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | CoilTemp |  | B3 | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 174 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | TapPosMv |  | B3 | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 175 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | MWh |  | B3 | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3TR | MWH | 三號主變 |  |  | B1/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 176 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | B3,Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3TR | MVARH(+) | 三號主變 |  |  | B1/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 177 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0001 |  | 0050 | 1-00-01 |  | 1-32 | 750 | CB ON/OFF | 一號主變一次側 |  | aacb | B3/S01_D1 | [8 empty] | 雲港SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 178 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S01_D1 | [8 empty] | 雲港SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 179 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S01_D1 | [8 empty] | 雲港SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 180 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | not found | B3/S01_D1 | [8 empty] | 雲港SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 181 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S01_D1 | [8 empty] | 雲港SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 182 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S01_D1 | [8 empty] | 雲港SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 183 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | T/1MTR |  |  | 0007 |  | 0051 | 1-00-07 |  | 1-33 | 1MT | CB ON/OFF | 一號主變二次側 |  | aafa | B2/S01_D1 | [8 empty] | 雲港SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 184 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | T/2MTR |  |  | 0028 |  | 0089 | 1-03-04 |  | 1-59 | 3MTA | CB ON/OFF | 三號主變二次側(A) |  | abda | B2/S01_D1 | [8 empty] | 雲港SS.3M_CB | 3M(#2MTR) CB | DTR |  |  |  |  | CDC | 185 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 186 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 187 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1MTR | 51Z | 一號主變 51Z RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 188 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1MTR | 87A | 一號主變差動電驛 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 189 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1MTR | 87 LS | 一號 主變87 RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 190 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 191 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 192 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 51ZA |  | B3 | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2MTR | 51Z | 二號主變 51Z RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 193 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2MTR | 87A | 二號主變差動電驛 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 194 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2MTR | 87 LS | 二號 主變87 RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 195 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1MT | PHA | 一號主變二次側 51 RY |  |  | B2/S01_D1 | [8 empty] | 雲港SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 196 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #1MTR | TRA | 一號主變重故障 |  | a | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 197 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1MTR | TRF | 一號主變輕故障 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 198 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1MTR | R/L | 一號主變 OLTC |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 199 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0060 | 1-33-05 |  | 1-3C | #1MTR | A/M | 一號主變 OLTC |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 200 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S01 | 雲港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | 3MTA | PHA | 三號主變二次(A)51 RY |  |  | B2/S01_D1 | [8 empty] | 雲港SS.3M_51A | #2MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 201 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | TRA |  | B3 | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #2MTR | TRA | 二號主變重故障 |  | a | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 202 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | TRF |  | B3 | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2MTR | TRF | 二號主變輕故障 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 203 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2MTR | R/L | 二號主變 OLTC |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 204 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2MTR | A/M | 二號主變 OLTC |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 205 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0368 | 369 | 0044 | 1-37-00 | 1-37-01 | 1-2C | 751 | ABS ON | 一號主變 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 206 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0370 | 371 | 0045 | 1-37-02 | 1-37-03 | 1-2D | 752 | ABS ON | 一號主變 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 207 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0372 | 373 | 0046 | 1-37-04 | 1-37-05 | 1-2E | 761 | ABS ON | 二號主變 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 208 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0374 | 375 | 0047 | 1-37-06 | 1-37-07 | 1-2F | 762 | ABS ON | 二號主變 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 209 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.1M-DS1 | 1M-DS1 (非取樣點) | DTR | [5 empty] | 210 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 211 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1MTR | 96A | 一號主變 96D,63A RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 212 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1MTR | TAPA | 一號主變TAP遲滯 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 213 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | #1MTR | 1ACF | 一號主變AC電源失效 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 214 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.3M-DS1 | 3M-DS1 (非取樣點) | DTR | [5 empty] | 215 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 216 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | B3,Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 217 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | B3,Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2MTR | TAPA | 二號主變TAP遲滯 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 218 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | AC_Fault |  | B3 | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0367 |  |  | 1-36-15 |  |  | #2MTR | 2ACF | 二號主變AC電源失效 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 219 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | C/1SC |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | SC 69KV |  | aaha | B2/S01_A1 | [8 empty] | 雲港SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 220 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 221 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/1BUS | C/1SC |  |  | 0110 |  | 0052 | 1-0D-06 |  | 1-34 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | aaab | B2/S01_D1 | [8 empty] | 雲港SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 222 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0061 | 1-33-11 |  | 1-3D | #1SC | A/M | 一號 SC 乏控器 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 223 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 224 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/3BUS | C/3SC |  |  | 0154 |  | 0091 | 1-13-02 |  | 1-5B | #3 11KV SC | CB ON/OFF | #3 11KV SC |  | abgb | B2/S01_D1 | [8 empty] | 雲港SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 225 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0099 | 1-35-11 |  | 1-63 | #3 SC | A/M | 三號 SC 乏控器 |  |  | B2/S01_D1 | [8 empty] | 雲港SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 226 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.230ES | 230ES (非取樣點) | SC | [5 empty] | 227 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0380 | 381 | 0040 | 1-37-12 | 1-37-13 | 1-28 | 811 | ABS ON | 69KV SC |  |  | B2/S01_A1 | [8 empty] | 雲港SS.811_DS | 811(69KV #1SC) DS | SC |  |  |  |  | CDC | 228 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0382 | 383 | 0041 | 1-37-14 | 1-37-15 | 1-29 | 812 | ABS ON | 69KV SC |  |  | B2/S01_A1 | [8 empty] | 雲港SS.812_DS | 812(69KV #1SC) DS | SC |  |  |  |  | CDC | 229 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 810 | PHA GDA | SC 69KV 51 51N RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 230 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 810 | UVA OVA | SC 69KV 27 59N RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 231 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_A1 | [8 empty] | 雲港SS.810LE | 810LE (非取樣點) | SC | [5 empty] | 232 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | #1SC5151NRY | SCA | #1 11KV SC |  |  | B2/S01_D1 | [8 empty] | 雲港SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 233 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | #1SC2759RY | UVA | #1 11KV SC |  |  | B2/S01_D1 | [8 empty] | 雲港SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 234 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | #3SC5151NRY | SCA | #3 11KV SC |  |  | B2/S01_D1 | [8 empty] | 雲港SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 235 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | #3SC2759RY | UVA | #3 11KV SC |  |  | B2/S01_D1 | [8 empty] | 雲港SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 236 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.210DS | 210DS (非取樣點) | SC | [5 empty] | 237 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S01_D1 | [8 empty] | 雲港SS.230DS | 230DS (非取樣點) | SC | [5 empty] | 238 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 239 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 240 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 241 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 242 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 243 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 244 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 雲港SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | SPARE |  | 其他重故障 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | SPARE | UVA | 其他輕故障 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.直流充電機故障 | 充電機AC故障 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.通訊充電機故障 | 充電機(通訊專用) | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | SPARE | (DOOR) | 無人化門禁(1) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S01 | 雲港SS | 69 | 69kV | ComPoint |  |  | 87CTFA |  | B2,B3,Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 69KV BUS | CTFA RY | CT電驛異常警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.BUSCTFA | 69KV BUS CT異常警報 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | 50UL |  | B2,B3,Element | Status | 50RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | TIE(600) | 50S | 瞬時過電流電驛狀態 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.60050S | 600 TIE瞬時過電流RY(50) | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | SPARE |  | 無人化防盜(1) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | SPARE |  | 無人化防盜(2) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV BUS | 87FA RY | 87電驛故障警報(DC電源失效) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.BUS87BF | 69KV BUS差動電驛故障警報 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0109 | 1-30-06 |  | 1-6D | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 所外路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0110 | 1-30-07 |  | 1-6E | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.開關場照明(B) | 所外路燈照明 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.火災警報(1) | 火警-自行裝設 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | SPARE | (FIRE) | 無人化防火(1) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.火災警報(2) | 二氧化碳(CO2)滅火設備 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | SPARE |  | 無人化防火(2) |  |  | B3/S01_D1 | [8 empty] | 雲港SS.火災警報(3) | 火災警報(3) | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 充油電纜 | OPA | 油壓電力電纜 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.充油電纜OPA | 油壓電力電纜 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | Locate Empty | ACB 1S |  |  |  | B3/S01_D1 | [8 empty] | 雲港SS.所內電源ACB1 | ACB1S | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | Locate Empty | ACB 2S |  |  |  | B3/S01_D1 | [8 empty] | 雲港SS.所內電源ACB2 | ACB2S | OTHER |  |  |  |  | CDC | 264 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | ACBA | ACBA AL | ACBA 警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.所內電源ACBA | 所內電源開關ACB警報 | OTHER |  |  |  |  | CDC | 265 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內用電警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.所內電源欠壓 | 所內用電警報 | OTHER |  |  |  |  | CDC | 266 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 |  | NFB跳脫監視 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.直流電源DCA | 直流電源NFB開關警報 | OTHER |  |  |  |  | CDC | 267 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCA | 直流電源接地故障 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 268 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 269 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 270 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.11KV_CBA | 11KV重故障 | OTHER |  |  |  |  | CDC | 271 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S01_D1 | [8 empty] | 雲港SS.11KV_CBF | 11KV輕故障 | OTHER |  |  |  |  | CDC | 272 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池警報 |  | 洩油池警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.洩油池水位警報 | 洩油池泵警報 | OTHER |  |  |  |  | CDC | 273 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS AL | ABS警報 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.69KV_ABS_89A | 69KVABS警報 | OTHER |  |  |  |  | CDC | 274 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | Locate Empty |  | 通訊設備AC故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 275 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0349 |  |  | 1-35-13 |  |  | Locate Empty |  | 通訊設備光纖主故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.通訊OLTE重故障 | 通訊設備光纖主故障 | OTHER |  |  |  |  | CDC | 276 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0350 |  |  | 1-35-14 |  |  | Locate Empty |  | 通訊設備光纖次故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.通訊OLTE輕故障 | 通訊設備光纖次故障 | OTHER |  |  |  |  | CDC | 277 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊PCM警報 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0351 |  |  | 1-35-15 |  |  | Locate Empty |  | 博碼調變器故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.通訊PCM警報 | 博碼調變器故障 | OTHER |  |  |  |  | CDC | 278 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | 81AS1 | 81RY_A/S(1) | Element | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  | 0067 | 1-0E-04 |  | 1-43 | #1 81 RY | 181A | 一號主變 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.81RY_A/S(1) | 81電驛動作,港五卸載 | OTHER |  |  |  |  | CDC | 279 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 600 | PHA | 69KV TIE(600) 67-1 RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.600PHA(1) | 69KV TIE(600) 67-1 RY | OTHER |  |  |  |  | CDC | 280 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 600 | GDA | 69KV TIE(600) 67-1N RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.600GDA(1) | 69KV TIE(600) 67N-1 RY | OTHER |  |  |  |  | CDC | 281 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 600 | PHA | 69KV TIE(600) 67-2 RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.600PHA(2) | 69KV TIE(600) 67-2 RY | OTHER |  |  |  |  | CDC | 282 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 600 | GDA | 69KV TIE(600) 67-2N RY |  |  | B2/S01_A1 | [8 empty] | 雲港SS.600GDA(2) | 69KV TIE(600) 67N-2 RY | OTHER |  |  |  |  | CDC | 283 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Door | 門禁-自行裝設 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.門禁 | 門禁-自行裝設 | OTHER |  |  |  |  | CDC | 284 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | SPARE | SCA | 安全監控 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 285 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | FDR_60A | #1SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1SC | #1SC 59A |  |  |  | B2/S01_D1 | [8 empty] | 雲港SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER |  |  |  |  | CDC | 286 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | FDR_60A | #3SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | #3SC | #3SC 59A |  |  |  | B2/S01_D1 | [8 empty] | 雲港SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER |  |  |  |  | CDC | 287 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | PMA | 電力量測表計故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | PMA | POWER METER A | (原)全所43RS狀態 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.PMA警報 | PMA警報 | OTHER |  |  |  |  | CDC | 288 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 全所閘刀U/L | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0333 |  |  | 1-34-13 |  |  | 600TIE | 600RYFA | 600TIE 電驛故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.600RYFA | 600TIE電驛故障警報 | OTHER |  |  |  |  | CDC | 289 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報#1 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0334 |  |  | 1-34-14 |  |  | Locate Empty |  | 集油池水位警報 1 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.水位警報#1 | 水位警報#1 | OTHER |  |  |  |  | CDC | 290 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報#2 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0335 |  |  | 1-34-15 |  |  | Locate Empty |  | 集油池水位警報 2 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.水位警報#2 | 水位警報#2 | OTHER |  |  |  |  | CDC | 291 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 港一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港一線KVAR | 11KV港一線 KVAR | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 港一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港一線A1 | 11KV港一線 R相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 港一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港一線A2 | 11KV港一線 S相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 港一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港一線A3 | 11KV港一線 T相AMP | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 港一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港一線A0 | 11KV港一線 N相AMP | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 港二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港二線KVAR | 11KV港二線 KVAR | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 港二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港二線A1 | 11KV港二線 R相AMP | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 港二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港二線A2 | 11KV港二線 S相AMP | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 港二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港二線A3 | 11KV港二線 T相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 港二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港二線A0 | 11KV港二線 N相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 乏 | VAR | 港十一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十一KVAR | 11KV港十一 KVAR | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 R相電流 | A1 | 港十一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十一A1 | 11KV港十一 R相AMP | FEEDER |  |  |  |  | CDC | 303 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F11 S相電流 | A2 | 港十一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十一A2 | 11KV港十一 S相AMP | FEEDER |  |  |  |  | CDC | 304 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F11 T相電流 | A3 | 港十一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十一A3 | 11KV港十一 T相AMP | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F11 N相電流 | AMP | 港十一線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十一A0 | 11KV港十一 N相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 乏 | VAR | 港十二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十二KVAR | 11KV港十二 KVAR | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 R相電流 | A1 | 港十二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十二A1 | 11KV港十二 R相AMP | FEEDER |  |  |  |  | CDC | 308 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 S相電流 | A2 | 港十二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十二A2 | 11KV港十二 S相AMP | FEEDER |  |  |  |  | CDC | 309 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F12 T相電流 | A3 | 港十二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十二A3 | 11KV港十二 T相AMP | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F12 N相電流 | AMP | 港十二線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十二A0 | 11KV港十二 N相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 乏 | VAR | 港十三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十三KVAR | 11KV港十三 KVAR | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 R相電流 | A1 | 港十三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十三A1 | 11KV港十三 R相AMP | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 S相電流 | A2 | 港十三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十三A2 | 11KV港十三 S相AMP | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 T相電流 | A3 | 港十三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十三A3 | 11KV港十三 T相AMP | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F13 N相電流 | AMP | 港十三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十三A0 | 11KV港十三 N相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 乏 | VAR | 港十五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十五KVAR | 11KV港十五 KVAR | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 R相電流 | A1 | 港十五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十五A1 | 11KV港十五 R相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 S相電流 | A2 | 港十五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十五A2 | 11KV港十五 S相AMP | FEEDER |  |  |  |  | CDC | 319 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F15 T相電流 | A3 | 港十五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十五A3 | 11KV港十五 T相AMP | FEEDER |  |  |  |  | CDC | 320 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F15 N相電流 | AMP | 港十五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十五A0 | 11KV港十五 N相AMP | FEEDER |  |  |  |  | CDC | 321 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 乏 | VAR | 港十四線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十四KVAR | 11KV港十四 KVAR | FEEDER |  |  |  |  | CDC | 322 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 R相電流 | A1 | 港十四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十四A1 | 11KV港十四 R相AMP | FEEDER |  |  |  |  | CDC | 323 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F14 S相電流 | A2 | 港十四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十四A2 | 11KV港十四 S相AMP | FEEDER |  |  |  |  | CDC | 324 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F14 T相電流 | A3 | 港十四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十四A3 | 11KV港十四 T相AMP | FEEDER |  |  |  |  | CDC | 325 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F14 N相電流 | AMP | 港十四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港十四A0 | 11KV港十四 N相AMP | FEEDER |  |  |  |  | CDC | 326 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 港三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港三線KVAR | 11KV港三線 KVAR | FEEDER |  |  |  |  | CDC | 327 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 港三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港三線A1 | 11KV港三線 R相AMP | FEEDER |  |  |  |  | CDC | 328 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 港三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港三線A2 | 11KV港三線 S相AMP | FEEDER |  |  |  |  | CDC | 329 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 港三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港三線A3 | 11KV港三線 T相AMP | FEEDER |  |  |  |  | CDC | 330 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 港三線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港三線A0 | 11KV港三線 N相AMP | FEEDER |  |  |  |  | CDC | 331 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 港五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港五線KVAR | 11KV港五線 KVAR | FEEDER |  |  |  |  | CDC | 332 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 港五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港五線A1 | 11KV港五線 R相AMP | FEEDER |  |  |  |  | CDC | 333 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 港五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港五線A2 | 11KV港五線 S相AMP | FEEDER |  |  |  |  | CDC | 334 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 港五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港五線A3 | 11KV港五線 T相AMP | FEEDER |  |  |  |  | CDC | 335 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 港五線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港五線A0 | 11KV港五線 N相AMP | FEEDER |  |  |  |  | CDC | 336 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 港四線 | KVAR_-9000_9000(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港四線KVAR | 11KV港四線 KVAR | FEEDER |  |  |  |  | CDC | 337 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 港四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港四線A1 | 11KV港四線 R相AMP | FEEDER |  |  |  |  | CDC | 338 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 港四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港四線A2 | 11KV港四線 S相AMP | FEEDER |  |  |  |  | CDC | 339 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 港四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港四線A3 | 11KV港四線 T相AMP | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 港四線 | A_-500_500(-2000_2000) |  | B2/S01_D1 | [8 empty] | 雲港SS.港四線A0 | 11KV港四線 N相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-150_150(-2000_2000) |  | B3/S01_D1 | [8 empty] | 雲港SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S01 | 雲港SS | 0 |  | ComPoint |  |  | IRFA | 保護電驛IED故障警報 (#1IEDAL) | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 1-32-09 |  |  | #1 81 RY | IEDAL | #1-IED保護電驛故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#1IEDAL | #1保護電驛IED故障警報 | OTHER | [5 empty] | 343 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1MT | GDA | 一號主變二次側 51N RY |  |  | B2/S01_D1 | [8 empty] | 雲港SS.1M_51NA | #1MTR二次側(1M) 51NRY | OTHER | [5 empty] | 344 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1MTR | #163Q | 一號主變ULTC保護 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#163Q | #1主變ULTC保護警報 | OTHER | [5 empty] | 345 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1MTR | #196B1 | 一號主變撲氣電驛第一段 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#196B1 | #1主變撲氣電驛第ㄧ段警報 | OTHER | [5 empty] | 346 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1MTR | #196B2 | 一號主變撲氣電驛第二段 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#196B2 | #1主變撲氣電驛第二段警報 | OTHER | [5 empty] | 347 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1MTR | #196D | 一號主變放壓裝置 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#196D | #1主變放壓裝置警報 | OTHER | [5 empty] | 348 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1MTR | #196P | 一號主變衝擊油壓 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#196P | #1主變衝擊油壓警報 | OTHER | [5 empty] | 349 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2MTR | #263Q | 二號主變ULTC保護 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#263Q | #2主變ULTC保護警報 | OTHER | [5 empty] | 350 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2MTR | #296B1 | 二號主變撲氣電驛第一段 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#296B1 | #2主變撲氣電驛第ㄧ段警報 | OTHER | [5 empty] | 351 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2MTR | #296B2 | 二號主變撲氣電驛第二段 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#296B2 | #2主變撲氣電驛第二段警報 | OTHER | [5 empty] | 352 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2MTR | #296D | 二號主變放壓裝置 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#296D | #2主變放壓裝置警報 | OTHER | [5 empty] | 353 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2MTR | #296P | 二號主變衝擊油壓 |  |  | B1/S01_D1 | [8 empty] | 雲港SS.#296P | #2主變衝擊油壓警報 | OTHER | [5 empty] | 354 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 1-32-08 |  |  | 710 | L1RYFA | 北港雲港一路電驛故障 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L1RYFA | 710北港雲港ㄧ路電驛故障警報 | OTHER | [5 empty] | 355 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 720 | L2RYFA | 北港雲港二路電驛故障 |  |  | B2/S01_A1 | [8 empty] | 雲港SS.L2RYFA | 720北港雲港二路電驛故障警報 | OTHER | [5 empty] | 356 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | ComPoint | 所內設施 |  | IRFA | 保護電驛IED故障警報 (#3IEDAL) | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | IED | #3-IEDAL | #3-IED保護電驛故障 |  |  | B3/S01_D1 | [8 empty] | 雲港SS.#3IEDAL | #3保護電驛IED故障警報 | OTHER | [5 empty] | 357 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 3MTA | GDA | 三號主變二次(A)51N RY |  |  | B2/S01_D1 | [8 empty] | 雲港SS.3M_51NA | #3MTR二次側(3M) 51NRY | OTHER | [5 empty] | 358 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | 50A |  | INSERT | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | TIE(600) | 50A | 50電驛動作警報(不使用) |  |  | B2/S01_A1 | [8 empty] | 雲港SS.600_50A | 600 TIE 50電驛動作警報 | OTHER | [5 empty] | 359 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 KWH | KWH | 港一線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 360 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 KWH | KWH | 港二線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 361 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 KWH | KWH | 港三線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 362 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 KWH | KWH | 港四線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 363 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 KWH | KWH | 港五線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 364 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F11 KWH | KWH | 港十一線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 365 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F12 KWH | KWH | 港十二線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 366 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F13 KWH | KWH | 港十三線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 367 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F14 KWH | KWH | 港十四線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 368 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F15 KWH | KWH | 港十五線 |  |  | B2/S01_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 369 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S01 | 雲港SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S01_D1 | [12 empty] | 雲港SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S01/69/1BUS/V; OPRD2: S01/69/2BUS/V
S01 | 雲港SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S01_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S01/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S01 | 雲港SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S01_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: S01/11/M1/MW; OPRD2: S01/11/M3/MW; OPRD3: S01/69/610/MW; OPRD4: S01/69/660/MW; OPRD5: S01/69/710/MW; OPRD6: S01/69/720/MW
S01 | 雲港SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S01_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S01/0/CalcPoint/OPRN2_MW
S01 | 雲港SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S01_D1 | [17 empty] | none
S01 | 雲港SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S01_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S01/0/CalcPoint/OPRN1; OPRD2: S01/0/CalcPoint/OPRN2; OPRD3: S01/0/CalcPoint/PRFL_UL
S01 | 雲港SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S01/11/M1/MW; OPRD2: S01/11/M1/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S01/11/M3/MW; OPRD2: S01/11/M3/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS | 69 | 69kV | 610 | 雲港～萬有線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S01_A1 | [12 empty] | 雲港SS.610_AMP | 萬有線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S01/69/610/MW; OPRD2: S01/69/610/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S01_A1 | [12 empty] | 雲港SS.660_AMP | 嘉太線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S01/69/660/MW; OPRD2: S01/69/660/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S01_A1 | [12 empty] | 雲港SS.710_AMP | 北港一路 AMP | LINE69 | AMP_CAL | C12R0945 | amp_cal | OPRD1: S01/69/710/MW; OPRD2: S01/69/710/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S01_A1 | [12 empty] | 雲港SS.720_AMP | 北港二路 AMP | LINE69 | AMP_CAL | C12R0945 | amp_cal | OPRD1: S01/69/720/MW; OPRD2: S01/69/720/MVAR; OPRD3: S01/0/CalcPoint/Vbs2
S01 | 雲港SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S01_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S01/11/1BUS/V
S01 | 雲港SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S01_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S01/11/3BUS/V
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S01_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 雲港SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S01/11/M1/MW; OPRD2: S01/11/M1/MVAR
S01 | 雲港SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S01_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 |  | -23.75 | -27.5 | -31.25 | -50 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S01/11/M3/MW; OPRD2: S01/11/M3/MVAR
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S01_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S01//1MTR/MVA; OPRD2: 0
S01 | 雲港SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S01_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S01//3MTR/MVA; OPRD2: 0
S01 | 雲港SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S01_D1 | [12 empty] | 雲港SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S01/11/M1/MW; OPRD2: S01/11/M1/MVAR
S01 | 雲港SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S01_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S01/11/M3/MW; OPRD2: S01/11/M3/MVAR
S01 | 雲港SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S01_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S01//1MTR/SupLocal; OPRD2: S01//1MTR/Tap Chan; OPRD3: NULL
S01 | 雲港SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S01_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S01//3MTR/SupLocal; OPRD2: S01//3MTR/Tap Chan; OPRD3: NULL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/1BUS/V; OPRD2: S01/11/XG21/I_R; OPRD3: S01/11/XG21/I_S; OPRD4: S01/11/XG21/I_T
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/1BUS/V; OPRD2: S01/11/XG22/I_R; OPRD3: S01/11/XG22/I_S; OPRD4: S01/11/XG22/I_T
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/1BUS/V; OPRD2: S01/11/XG23/I_R; OPRD3: S01/11/XG23/I_S; OPRD4: S01/11/XG23/I_T
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/1BUS/V; OPRD2: S01/11/XG24/I_R; OPRD3: S01/11/XG24/I_S; OPRD4: S01/11/XG24/I_T
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/1BUS/V; OPRD2: S01/11/XG25/I_R; OPRD3: S01/11/XG25/I_S; OPRD4: S01/11/XG25/I_T
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/3BUS/V; OPRD2: S01/11/XG31/I_R; OPRD3: S01/11/XG31/I_S; OPRD4: S01/11/XG31/I_T
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/3BUS/V; OPRD2: S01/11/XG32/I_R; OPRD3: S01/11/XG32/I_S; OPRD4: S01/11/XG32/I_T
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/3BUS/V; OPRD2: S01/11/XG33/I_R; OPRD3: S01/11/XG33/I_S; OPRD4: S01/11/XG33/I_T
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/3BUS/V; OPRD2: S01/11/XG34/I_R; OPRD3: S01/11/XG34/I_S; OPRD4: S01/11/XG34/I_T
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S01/11/3BUS/V; OPRD2: S01/11/XG35/I_R; OPRD3: S01/11/XG35/I_S; OPRD4: S01/11/XG35/I_T
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG21/kVA; OPRD2: S01/11/XG21/KVAR
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG22/kVA; OPRD2: S01/11/XG22/KVAR
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG23/kVA; OPRD2: S01/11/XG23/KVAR
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG24/kVA; OPRD2: S01/11/XG24/KVAR
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG25/kVA; OPRD2: S01/11/XG25/KVAR
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG31/kVA; OPRD2: S01/11/XG31/KVAR
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG32/kVA; OPRD2: S01/11/XG32/KVAR
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG33/kVA; OPRD2: S01/11/XG33/KVAR
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG34/kVA; OPRD2: S01/11/XG34/KVAR
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S01/11/XG35/kVA; OPRD2: S01/11/XG35/KVAR
S01 | 雲港SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S01_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S01/11/M1/MW; OPRD2: S01/11/M3/MW
S01 | 雲港SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S01_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S01/11/M1/MVAR; OPRD2: S01/11/M3/MVAR
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S01_D1 | [12 empty] | 雲港SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S01/11/210/CB; OPRD2: 6.9; OPRD3: 0
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S01_D1 | [12 empty] | 雲港SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S01/11/230/CB; OPRD2: 6.9; OPRD3: 0
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S01_A1 | [12 empty] | 雲港SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S01/69/810/CB; OPRD2: 69; OPRD3: 0
S01 | 雲港SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S01_D1 | [12 empty] | 雲港SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_18 | OPRD1: S01//1MTR/63Q; OPRD2: S01//1MTR/96PA; OPRD3: S01//1MTR/TRA; OPRD4: S01//1MTR/96D; OPRD5: S01//1MTR/96B2; OPRD6: S01//1MTR/96B1; OPRD7: S01//1MTR/87A; OPRD8: S01//1MTR/51ZA; OPRD9: S01//2MTR/63Q; OPRD10: S01//2MTR/96D; OPRD11: S01//2MTR/96B2; OPRD12: S01//2MTR/96B1; OPRD13: S01//3MTR/96PA; OPRD14: S01//3MTR/51ZA; OPRD15: S01//3MTR/TRA; OPRD16: S01//3MTR/87A; OPRD17: S01/69/1BUS/87A; OPRD18: S01/69/2BUS/87A
S01 | 雲港SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S01_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S01//1MTR/TRF; OPRD2: S01//3MTR/TRF
S01 | 雲港SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S01_A1 | [17 empty] | lamp2CC | OPRD1: S01/0/RTU/RTU_R_L
S01 | 雲港SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S01_A1 | [17 empty] | lamp2CC | OPRD1: S01/0/StaDev/PSA
S01 | 雲港SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S01_A1 | [17 empty] | lamp2CC | OPRD1: S01/0/StaDev/PSF
S01 | 雲港SS | 69 | 69kV | ComPoint_D1 |  |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S01_D1 | [17 empty] | lamp2CC | OPRD1: S01/69/ComPoint/87CTFA
S01 | 雲港SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S01_A1 | [17 empty] | lamp2CC | OPRD1: S01/0/StaDev/DCA
S01 | 雲港SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S01_A1 | [17 empty] | lamp2CC | OPRD1: S01/0/StaDev/DCE
S01 | 雲港SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S01_D1 | [17 empty] | lamp2CC | OPRD1: S01/69/ComPoint/CBA
S01 | 雲港SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S01_D1 | [17 empty] | lamp2CC | OPRD1: S01/69/ComPoint/CBF
S01 | 雲港SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S01_D1 | [17 empty] | lamp2CC | OPRD1: S01/69/ComPoint/ABS_89A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S01 | 雲港SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 雲港SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S01/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 雲港SS.610_AMP | 萬有線 AMP | LINE69 | S01/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | I | [25 empty] | ADCS_N | [8 empty] | 雲港SS.710_AMP | 北港一路 AMP | LINE69 | S01/69/710/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0945 | 850.500000 | 850.500000 | 945.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | I | [25 empty] | ADCS_N | [8 empty] | 雲港SS.720_AMP | 北港二路 AMP | LINE69 | S01/69/720/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0945 | 850.500000 | 850.500000 | 945.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S01 | 雲港SS | 0 |  |  |  |  | 港一線KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港一線KVA | 11KV港一線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港一線KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港一線KW | 11KV港一線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港二線KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港二線KVA | 11KV港二線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港二線KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港二線KW | 11KV港二線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十一KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十一KVA | 11KV港十一KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十一KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十一KW | 11KV港十一KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十二KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十二KVA | 11KV港十二KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十二KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十二KW | 11KV港十二KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十三KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十三KVA | 11KV港十三KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十三KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十三KW | 11KV港十三KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十五KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十五KVA | 11KV港十五KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十五KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十五KW | 11KV港十五KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十四KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十四KVA | 11KV港十四KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港十四KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港十四KW | 11KV港十四KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港三線KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港三線KVA | 11KV港三線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港三線KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港三線KW | 11KV港三線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港五線KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港五線KVA | 11KV港五線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港五線KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港五線KW | 11KV港五線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港四線KVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港四線KVA | 11KV港四線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  |  |  |  | 港四線KW | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.港四線KW | 11KV港四線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S01//1MTR/MVA |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_PF | #1MTR 功率因素 | DTR | S01//1MTR/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S01 | 雲港SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S01/11/210/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S01/11/230/MVAR |  | SC_CAL_11 |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S01/69/810/MVAR |  | SC_CAL_69 |  |  | 32 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | I | [25 empty] | ADCS_N | [8 empty] | 雲港SS.660_AMP | 嘉太線 AMP | LINE69 | S01/69/660/I |  | AMP_CAL |  |  | 33 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S01 | 雲港SS | 69 | 69kV | 610_CB | 萬有線(610_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.610_CB_1 | 610(萬有線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 34 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 710_CB | 北港一路(710_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.710_CB_1 | 710(北港一路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 720_CB | 北港二路(720_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.720_CB_1 | 720(北港二路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 600_CB | 600(600_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.600_CB_1 | 600 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 37 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.810_CB_1 | 810(69KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 38 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 雲港SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 雲港SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 40 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 充油電纜OPA | 油壓電力電纜 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.充油電纜OPA_A | 油壓電力電纜 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 41 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 雲港SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S01/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 43 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | STATION_FAULT_2 |  |  | 44 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610_AMP | 萬有線 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.610_AMP_A | 萬有線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 45 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 610_AMP | 萬有線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.610_AMP_1 | 萬有線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 710_AMP | 北港一路 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.710_AMP_A | 北港一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 710_AMP | 北港一路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.710_AMP_1 | 北港一路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 720_AMP | 北港二路 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.720_AMP_A | 北港二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 720_AMP | 北港二路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.720_AMP_1 | 北港二路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | 1MTR_MVA | #1MTR |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_MVA_1 | #1MTR MVA 點燈 (D1) | DTR |  |  | MAP_SET |  |  | 51 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | 2MTR_MVA | #2MTR |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_MVA_1 | #2MTR MVA 點燈 (D1) | DTR |  |  | MAP_SET |  |  | 53 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 54 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 660_AMP | 嘉太線 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.660_AMP_A | 嘉太線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 55 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 660_AMP | 嘉太線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.660_AMP_1 | 嘉太線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 56 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 69 | 69kV | 660_CB | 嘉太線(660_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.660_CB_1 | 660(嘉太線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 57 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | L187A | L187A | [27 empty] | ADCS_N | [8 empty] | 雲港SS.L187A_A | 710北港雲港ㄧ路差動電驛動作AD | OTHER |  |  | AD_LAMP_DD_2 |  |  | 58 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | L187CFA | L187CFA | [27 empty] | ADCS_N | [8 empty] | 雲港SS.L187CFA_A | 710北港雲港ㄧ路87RY通訊故障AD | OTHER |  |  | AD_LAMP_DD_2 |  |  | 59 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | L1RYFA | 710北港雲港ㄧ路電驛故障 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.L1RYFA_A | 710北港雲港ㄧ路電驛故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 60 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | L287A | L287A |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.L287A_1 | 720北港雲港二路差動電驛動作D1 | OTHER |  |  | AD_LAMP_DD_2 |  |  | 61 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | L287CFA | L287CFA |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.L287CFA_1 | 720北港雲港二路87RY通訊故障D1 | OTHER |  |  | AD_LAMP_DD_2 |  |  | 62 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | L2RYFA | L2RYFA |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.L2RYFA_1 | 720北港雲港二路電驛故障D1 | OTHER |  |  | AD_LAMP_DD_2 |  |  | 63 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600RYFA | 600TIE電驛故障警報 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.600RYFA_1 | 600TIE電驛故障警報 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 64 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 60050S | 600 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.60050S_A | 600 TIE瞬時過電流RY(50)(AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 65 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600_50A | 600 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.600_50A_A | 600 TIE 50電驛動作警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 66 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | BUS87BF | BUS差動電驛故障警報 | [27 empty] | ADCS_N | [8 empty] | 雲港SS.BUS87BF_A | 69KV BUS差動電驛故障警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 67 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | BUSCTFA | BUS | [27 empty] | ADCS_N | [8 empty] | 雲港SS.BUSCTFA_A | 69KV BUS CT異常警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 68 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S01/0/RTU/ADCH1 |  |  |  | CDC | 69 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S01/0/RTU/ADCH2 |  |  |  | CDC | 70 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S01/0/RTU/ADCH3 |  |  |  | CDC | 71 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S01/0/RTU/ADCL1 |  |  |  | CDC | 72 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S01/0/RTU/ADCL2 |  |  |  | CDC | 73 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S01/0/RTU/ADCL3 |  |  |  | CDC | 74 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S01/69/1BUS/V |  |  |  | CDC | 75 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S01 | 雲港SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S01/69/2BUS/V |  |  |  | CDC | 76 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S01 | 雲港SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S01/11/1BUS/V |  |  |  | CDC | 77 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S01 | 雲港SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S01/11/3BUS/V |  |  |  | CDC | 78 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.610_MW | 萬有線 MW | LINE69 | S01/69/610/MW |  |  |  | CDC | 79 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.610_MVAR | 萬有線 MVAR | LINE69 | S01/69/610/MVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.710_MW | 北港一路 MW | LINE69 | S01/69/710/MW |  |  |  | CDC | 81 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.710_MVAR | 北港一路 MVAR | LINE69 | S01/69/710/MVAR |  |  |  | CDC | 82 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.720_MW | 北港二路 MW | LINE69 | S01/69/720/MW |  |  |  | CDC | 83 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.720_MVAR | 北港二路 MVAR | LINE69 | S01/69/720/MVAR |  |  |  | CDC | 84 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港一線 | 港一線 |  | 港一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港一線KVAR | 11KV港一線 KVAR | FEEDER | S01/11/XG21/KVAR |  |  |  | CDC | 85 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港一線 | 港一線 |  | 港一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港一線A1 | 11KV港一線 R相AMP | FEEDER | S01/11/XG21/I_R |  |  |  | CDC | 86 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港一線 | 港一線 |  | 港一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港一線A2 | 11KV港一線 S相AMP | FEEDER | S01/11/XG21/I_S |  |  |  | CDC | 87 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港一線 | 港一線 |  | 港一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港一線A3 | 11KV港一線 T相AMP | FEEDER | S01/11/XG21/I_T |  |  |  | CDC | 88 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港一線 | 港一線 |  | 港一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港一線A0 | 11KV港一線 N相AMP | FEEDER | S01/11/XG21/I_N |  |  |  | CDC | 89 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港二線 | 港二線 |  | 港二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港二線KVAR | 11KV港二線 KVAR | FEEDER | S01/11/XG22/KVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港二線 | 港二線 |  | 港二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港二線A1 | 11KV港二線 R相AMP | FEEDER | S01/11/XG22/I_R |  |  |  | CDC | 91 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港二線 | 港二線 |  | 港二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港二線A2 | 11KV港二線 S相AMP | FEEDER | S01/11/XG22/I_S |  |  |  | CDC | 92 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港二線 | 港二線 |  | 港二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港二線A3 | 11KV港二線 T相AMP | FEEDER | S01/11/XG22/I_T |  |  |  | CDC | 93 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港二線 | 港二線 |  | 港二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港二線A0 | 11KV港二線 N相AMP | FEEDER | S01/11/XG22/I_N |  |  |  | CDC | 94 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十一 | 港十一 |  | 港十一KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十一KVAR | 11KV港十一 KVAR | FEEDER | S01/11/XG31/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十一 | 港十一 |  | 港十一A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十一A1 | 11KV港十一 R相AMP | FEEDER | S01/11/XG31/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十一 | 港十一 |  | 港十一A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十一A2 | 11KV港十一 S相AMP | FEEDER | S01/11/XG31/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十一 | 港十一 |  | 港十一A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十一A3 | 11KV港十一 T相AMP | FEEDER | S01/11/XG31/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十一 | 港十一 |  | 港十一A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十一A0 | 11KV港十一 N相AMP | FEEDER | S01/11/XG31/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十二 | 港十二 |  | 港十二KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十二KVAR | 11KV港十二 KVAR | FEEDER | S01/11/XG32/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十二 | 港十二 |  | 港十二A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十二A1 | 11KV港十二 R相AMP | FEEDER | S01/11/XG32/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十二 | 港十二 |  | 港十二A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十二A2 | 11KV港十二 S相AMP | FEEDER | S01/11/XG32/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十二 | 港十二 |  | 港十二A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十二A3 | 11KV港十二 T相AMP | FEEDER | S01/11/XG32/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十二 | 港十二 |  | 港十二A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十二A0 | 11KV港十二 N相AMP | FEEDER | S01/11/XG32/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十三 | 港十三 |  | 港十三KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十三KVAR | 11KV港十三 KVAR | FEEDER | S01/11/XG33/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十三 | 港十三 |  | 港十三A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十三A1 | 11KV港十三 R相AMP | FEEDER | S01/11/XG33/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十三 | 港十三 |  | 港十三A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十三A2 | 11KV港十三 S相AMP | FEEDER | S01/11/XG33/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十三 | 港十三 |  | 港十三A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十三A3 | 11KV港十三 T相AMP | FEEDER | S01/11/XG33/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十三 | 港十三 |  | 港十三A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十三A0 | 11KV港十三 N相AMP | FEEDER | S01/11/XG33/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十五 | 港十五 |  | 港十五KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十五KVAR | 11KV港十五 KVAR | FEEDER | S01/11/XG35/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十五 | 港十五 |  | 港十五A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十五A1 | 11KV港十五 R相AMP | FEEDER | S01/11/XG35/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十五 | 港十五 |  | 港十五A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十五A2 | 11KV港十五 S相AMP | FEEDER | S01/11/XG35/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十五 | 港十五 |  | 港十五A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十五A3 | 11KV港十五 T相AMP | FEEDER | S01/11/XG35/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十五 | 港十五 |  | 港十五A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十五A0 | 11KV港十五 N相AMP | FEEDER | S01/11/XG35/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十四 | 港十四 |  | 港十四KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十四KVAR | 11KV港十四 KVAR | FEEDER | S01/11/XG34/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十四 | 港十四 |  | 港十四A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十四A1 | 11KV港十四 R相AMP | FEEDER | S01/11/XG34/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十四 | 港十四 |  | 港十四A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十四A2 | 11KV港十四 S相AMP | FEEDER | S01/11/XG34/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十四 | 港十四 |  | 港十四A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十四A3 | 11KV港十四 T相AMP | FEEDER | S01/11/XG34/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港十四 | 港十四 |  | 港十四A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港十四A0 | 11KV港十四 N相AMP | FEEDER | S01/11/XG34/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港三線 | 港三線 |  | 港三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港三線KVAR | 11KV港三線 KVAR | FEEDER | S01/11/XG23/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港三線 | 港三線 |  | 港三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港三線A1 | 11KV港三線 R相AMP | FEEDER | S01/11/XG23/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港三線 | 港三線 |  | 港三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港三線A2 | 11KV港三線 S相AMP | FEEDER | S01/11/XG23/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港三線 | 港三線 |  | 港三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港三線A3 | 11KV港三線 T相AMP | FEEDER | S01/11/XG23/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港三線 | 港三線 |  | 港三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港三線A0 | 11KV港三線 N相AMP | FEEDER | S01/11/XG23/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港五線 | 港五線 |  | 港五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港五線KVAR | 11KV港五線 KVAR | FEEDER | S01/11/XG25/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港五線 | 港五線 |  | 港五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港五線A1 | 11KV港五線 R相AMP | FEEDER | S01/11/XG25/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港五線 | 港五線 |  | 港五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港五線A2 | 11KV港五線 S相AMP | FEEDER | S01/11/XG25/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港五線 | 港五線 |  | 港五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港五線A3 | 11KV港五線 T相AMP | FEEDER | S01/11/XG25/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港五線 | 港五線 |  | 港五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港五線A0 | 11KV港五線 N相AMP | FEEDER | S01/11/XG25/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港四線 | 港四線 |  | 港四線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港四線KVAR | 11KV港四線 KVAR | FEEDER | S01/11/XG24/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港四線 | 港四線 |  | 港四線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港四線A1 | 11KV港四線 R相AMP | FEEDER | S01/11/XG24/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港四線 | 港四線 |  | 港四線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港四線A2 | 11KV港四線 S相AMP | FEEDER | S01/11/XG24/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港四線 | 港四線 |  | 港四線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港四線A3 | 11KV港四線 T相AMP | FEEDER | S01/11/XG24/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | 港四線 | 港四線 |  | 港四線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.港四線A0 | 11KV港四線 N相AMP | FEEDER | S01/11/XG24/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-90 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.600TIE_AMP | 600TIE AMP | TIE | S01/69/600/I |  |  |  | CDC | 135 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S01/11/TIE1/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S01/11/TIE1/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S01/11/TIE1/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_MW | #1MTR二次側 MW | DTR | S01/11/M1/MW |  |  |  | CDC | 139 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S01/11/M1/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S01/11/M1/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S01/11/M1/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S01/11/M1/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_OIL | #1MTR 油溫 | DTR | S01//1MTR/OilTemp |  |  |  | CDC | 144 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_COIL | #1MTR 線溫 | DTR | S01//1MTR/CoilTemp |  |  |  | CDC | 145 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-3B |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S01//1MTR/TapPosMv |  |  |  | CDC | 146 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_MW | #2MTR二次側 MW | DTR | S01/11/M3/MW |  |  |  | CDC | 147 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S01/11/M3/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S01/11/M3/I_R |  |  |  | CDC | 149 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S01/11/M3/I_S |  |  |  | CDC | 150 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S01/11/M3/I_T |  |  |  | CDC | 151 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_OIL | #2MTR 油溫 | DTR | S01//3MTR/OilTemp |  |  |  | CDC | 152 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_COIL | #2MTR 線溫 | DTR | S01//3MTR/CoilTemp |  |  |  | CDC | 153 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S01//3MTR/TapPosMv |  |  |  | CDC | 154 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S01 | 雲港SS | 0 |  |  |  |  | DCV | [17 empty] | 2-82 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS1_2 | [8 empty] | 雲港SS.直流電源電壓 | 直流電源電壓 | OTHER | S01/0/StaDev/DCV |  |  |  | CDC | 155 | GENERICAIPoint | SS100_L2 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.660_MW | 嘉太線 MW | LINE69 | S01/69/660/MW |  |  |  | CDC | 156 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 雲港SS.660_MVAR | 嘉太線 MVAR | LINE69 | S01/69/660/MVAR |  |  |  | CDC | 157 | GENERICAIPoint | SS100_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.610_PHA | 萬有線(610) 相間RY | LINE69 | S01/69/610/PHA |  |  |  | CDC | 158 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.610_GDA | 萬有線(610) 接地RY | LINE69 | S01/69/610/GDA |  |  |  | CDC | 159 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | 85A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.610_85A | 萬有線(610) 85RY | LINE69 | S01/69/610/85A |  |  |  | CDC | 160 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | 74A | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 雲港SS.610_74A | 萬有線(610) 74RY | LINE69 | S01/69/610/74A |  |  |  | CDC | 161 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | 85UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 雲港SS.610_85UL | 萬有線(610) 85RY U/L | LINE69 | S01/69/610/85UL |  |  |  | CDC | 162 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.610_CB | 610(萬有線) CB | LINE69 | S01/69/610/CB |  |  |  | CDC | 163 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | DS1 | 611 | [16 empty] | 1-39-00 | 1-39-01 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.611_DS | 611(萬有線) DS | LINE69 | S01/69/610/DS1 |  |  |  | CDC | 164 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | DS2 | 612 | [16 empty] | 1-39-02 | 1-39-03 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.612_DS | 612(萬有線) DS | LINE69 | S01/69/610/DS2 |  |  |  | CDC | 165 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | DS3 | 613 | [16 empty] | 1-39-04 | 1-39-05 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 雲港SS.613_DS | 613(萬有線) DS | LINE69 | S01/69/610/DS3 |  |  |  | CDC | 166 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | E3 | 613E | [16 empty] | 1-39-06 | 1-39-07 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 雲港SS.613E_ES | 613E(萬有線) ES | LINE69 | S01/69/610/E3 |  |  |  | CDC | 167 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.710_PHA | 北港一路(710) 相間RY | LINE69 | S01/69/710/PHA |  |  |  | CDC | 168 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.710_GDA | 北港一路(710) 接地RY | LINE69 | S01/69/710/GDA |  |  |  | CDC | 169 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.710_CB | 710(北港一路) CB | LINE69 | S01/69/710/CB |  |  |  | CDC | 170 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | DS1 | 711 | [16 empty] | 1-38-00 | 1-38-01 | 1-10 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.711_DS | 711(北港一路) DS | LINE69 | S01/69/710/DS1 |  |  |  | CDC | 171 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | DS2 | 712 | [16 empty] | 1-38-02 | 1-38-03 | 1-11 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.712_DS | 712(北港一路) DS | LINE69 | S01/69/710/DS2 |  |  |  | CDC | 172 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | DS3 | 713 | [16 empty] | 1-38-04 | 1-38-05 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.713_DS | 713(北港一路) DS | LINE69 | S01/69/710/DS3 |  |  |  | CDC | 173 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | E3 | 713E | [16 empty] | 1-38-06 | 1-38-07 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.713E_ES | 713E(北港一路) ES | LINE69 | S01/69/710/E3 |  |  |  | CDC | 174 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.720_PHA | 北港二路(720) 相間RY | LINE69 | S01/69/720/PHA |  |  |  | CDC | 175 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.720_GDA | 北港二路(720) 接地RY | LINE69 | S01/69/720/GDA |  |  |  | CDC | 176 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.720_CB | 720(北港二路) CB | LINE69 | S01/69/720/CB |  |  |  | CDC | 177 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | DS1 | 721 | [16 empty] | 1-38-08 | 1-38-09 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.721_DS | 721(北港二路) DS | LINE69 | S01/69/720/DS1 |  |  |  | CDC | 178 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | DS2 | 722 | [16 empty] | 1-38-10 | 1-38-11 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.722_DS | 722(北港二路) DS | LINE69 | S01/69/720/DS2 |  |  |  | CDC | 179 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | DS3 | 723 | [16 empty] | 1-38-12 | 1-38-13 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.723_DS | 723(北港二路) DS | LINE69 | S01/69/720/DS3 |  |  |  | CDC | 180 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | E3 | 723E | [16 empty] | 1-38-14 | 1-38-15 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.723E_ES | 723E(北港二路) ES | LINE69 | S01/69/720/ES |  |  |  | CDC | 181 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | PHA | [17 empty] | 1-0C-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_PHA | 11KV港一線(XG21) 相間RY | FEEDER | S01/11/XG21/PHA |  |  |  | CDC | 182 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) |  | GDA | [17 empty] | 1-0C-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_GDA | 11KV港一線(XG21) 接地RY | FEEDER | S01/11/XG21/GDA |  |  |  | CDC | 183 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) 79RY |  | 79UL | [17 empty] | 1-33-06 |  | 1-3E | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_79UL | 11KV港一線(XG21) 79RY U/L | FEEDER | S01/11/XG21/79UL |  |  |  | CDC | 184 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG21 | 港一線(XG21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_ADJ | 11KV港一線(XG21) LCO分流器 U/L | FEEDER | S01/11/XG21/ADJ |  |  |  | CDC | 185 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG21 | XG21(11KV港一線) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_CB | XG21(11KV港一線) CB | FEEDER | S01/11/XG21/CB |  |  |  | CDC | 186 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_PHA | 11KV港二線(XG22) 相間RY | FEEDER | S01/11/XG22/PHA |  |  |  | CDC | 187 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_GDA | 11KV港二線(XG22) 接地RY | FEEDER | S01/11/XG22/GDA |  |  |  | CDC | 188 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3F | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_79UL | 11KV港二線(XG22) 79RY U/L | FEEDER | S01/11/XG22/79UL |  |  |  | CDC | 189 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG22 | 港二線(XG22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_ADJ | 11KV港二線(XG22) LCO分流器 U/L | FEEDER | S01/11/XG22/ADJ |  |  |  | CDC | 190 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG22 | XG22(11KV港二線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_CB | XG22(11KV港二線) CB | FEEDER | S01/11/XG22/CB |  |  |  | CDC | 191 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_PHA | 11KV港三線(XG23) 相間RY | FEEDER | S01/11/XG23/PHA |  |  |  | CDC | 192 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_GDA | 11KV港三線(XG23) 接地RY | FEEDER | S01/11/XG23/GDA |  |  |  | CDC | 193 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-40 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_79UL | 11KV港三線(XG23) 79RY U/L | FEEDER | S01/11/XG23/79UL |  |  |  | CDC | 194 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG23 | 港三線(XG23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_ADJ | 11KV港三線(XG23) LCO分流器 U/L | FEEDER | S01/11/XG23/ADJ |  |  |  | CDC | 195 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG23 | XG23(11KV港三線) |  | CB | [17 empty] | 1-0C-05 |  | 1-37 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_CB | XG23(11KV港三線) CB | FEEDER | S01/11/XG23/CB |  |  |  | CDC | 196 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_PHA | 11KV港四線(XG24) 相間RY | FEEDER | S01/11/XG24/PHA |  |  |  | CDC | 197 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_GDA | 11KV港四線(XG24) 接地RY | FEEDER | S01/11/XG24/GDA |  |  |  | CDC | 198 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-41 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_79UL | 11KV港四線(XG24) 79RY U/L | FEEDER | S01/11/XG24/79UL |  |  |  | CDC | 199 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG24 | 港四線(XG24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_ADJ | 11KV港四線(XG24) LCO分流器 U/L | FEEDER | S01/11/XG24/ADJ |  |  |  | CDC | 200 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG24 | XG24(11KV港四線) |  | CB | [17 empty] | 1-0D-00 |  | 1-38 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_CB | XG24(11KV港四線) CB | FEEDER | S01/11/XG24/CB |  |  |  | CDC | 201 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_PHA | 11KV港五線(XG25) 相間RY | FEEDER | S01/11/XG25/PHA |  |  |  | CDC | 202 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_GDA | 11KV港五線(XG25) 接地RY | FEEDER | S01/11/XG25/GDA |  |  |  | CDC | 203 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-42 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_79UL | 11KV港五線(XG25) 79RY U/L | FEEDER | S01/11/XG25/79UL |  |  |  | CDC | 204 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG25 | 港五線(XG25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_ADJ | 11KV港五線(XG25) LCO分流器 U/L | FEEDER | S01/11/XG25/ADJ |  |  |  | CDC | 205 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG25 | XG25(11KV港五線) |  | CB | [17 empty] | 1-0D-03 |  | 1-39 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_CB | XG25(11KV港五線) CB | FEEDER | S01/11/XG25/CB |  |  |  | CDC | 206 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | PHA | [17 empty] | 1-11-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_PHA | 11KV港十一(XG31) 相間RY | FEEDER | S01/11/XG31/PHA |  |  |  | CDC | 207 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) |  | GDA | [17 empty] | 1-11-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_GDA | 11KV港十一(XG31) 接地RY | FEEDER | S01/11/XG31/GDA |  |  |  | CDC | 208 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) 79RY |  | 79UL | [17 empty] | 1-35-06 |  | 1-64 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_79UL | 11KV港十一(XG31) 79RY U/L | FEEDER | S01/11/XG31/79UL |  |  |  | CDC | 209 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG31 | 港十一(XG31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_ADJ | 11KV港十一(XG31) LCO分流器 U/L | FEEDER | S01/11/XG31/ADJ |  |  |  | CDC | 210 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG31 | XG31(11KV港十一) |  | CB | [17 empty] | 1-11-03 |  | 1-5C | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_CB | XG31(11KV港十一) CB | FEEDER | S01/11/XG31/CB |  |  |  | CDC | 211 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | PHA | [17 empty] | 1-11-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_PHA | 11KV港十二(XG32) 相間RY | FEEDER | S01/11/XG32/PHA |  |  |  | CDC | 212 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) |  | GDA | [17 empty] | 1-12-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_GDA | 11KV港十二(XG32) 接地RY | FEEDER | S01/11/XG32/GDA |  |  |  | CDC | 213 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-65 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_79UL | 11KV港十二(XG32) 79RY U/L | FEEDER | S01/11/XG32/79UL |  |  |  | CDC | 214 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG32 | 港十二(XG32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_ADJ | 11KV港十二(XG32) LCO分流器 U/L | FEEDER | S01/11/XG32/ADJ |  |  |  | CDC | 215 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG32 | XG32(11KV港十二) |  | CB | [17 empty] | 1-11-06 |  | 1-5D | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_CB | XG32(11KV港十二) CB | FEEDER | S01/11/XG32/CB |  |  |  | CDC | 216 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | PHA | [17 empty] | 1-12-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_PHA | 11KV港十三(XG33) 相間RY | FEEDER | S01/11/XG33/PHA |  |  |  | CDC | 217 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) |  | GDA | [17 empty] | 1-12-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_GDA | 11KV港十三(XG33) 接地RY | FEEDER | S01/11/XG33/GDA |  |  |  | CDC | 218 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-66 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_79UL | 11KV港十三(XG33) 79RY U/L | FEEDER | S01/11/XG33/79UL |  |  |  | CDC | 219 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG33 | 港十三(XG33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_ADJ | 11KV港十三(XG33) LCO分流器 U/L | FEEDER | S01/11/XG33/ADJ |  |  |  | CDC | 220 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG33 | XG33(11KV港十三) |  | CB | [17 empty] | 1-12-01 |  | 1-5E | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_CB | XG33(11KV港十三) CB | FEEDER | S01/11/XG33/CB |  |  |  | CDC | 221 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_PHA | 11KV港十四(XG34) 相間RY | FEEDER | S01/11/XG34/PHA |  |  |  | CDC | 222 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_GDA | 11KV港十四(XG34) 接地RY | FEEDER | S01/11/XG34/GDA |  |  |  | CDC | 223 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-67 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_79UL | 11KV港十四(XG34) 79RY U/L | FEEDER | S01/11/XG34/79UL |  |  |  | CDC | 224 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG34 | 港十四(XG34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_ADJ | 11KV港十四(XG34) LCO分流器 U/L | FEEDER | S01/11/XG34/ADJ |  |  |  | CDC | 225 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG34 | XG34(11KV港十四) |  | CB | [17 empty] | 1-12-04 |  | 1-5F | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_CB | XG34(11KV港十四) CB | FEEDER | S01/11/XG34/CB |  |  |  | CDC | 226 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_PHA | 11KV港十五(XG35) 相間RY | FEEDER | S01/11/XG35/PHA |  |  |  | CDC | 227 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_GDA | 11KV港十五(XG35) 接地RY | FEEDER | S01/11/XG35/GDA |  |  |  | CDC | 228 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-68 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_79UL | 11KV港十五(XG35) 79RY U/L | FEEDER | S01/11/XG35/79UL |  |  |  | CDC | 229 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 11 | 11kV | XG35 | 港十五(XG35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_ADJ | 11KV港十五(XG35) LCO分流器 U/L | FEEDER | S01/11/XG35/ADJ |  |  |  | CDC | 230 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S01 | 雲港SS | 11 | 11kV | XG35 | XG35(11KV港十五) |  | CB | [17 empty] | 1-12-07 |  | 1-60 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_CB | XG35(11KV港十五) CB | FEEDER | S01/11/XG35/CB |  |  |  | CDC | 231 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-02 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.600_CB | 600(TIE) CB | TIE | S01/69/600/CB |  |  |  | CDC | 232 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 雲港SS.601_DS | 601(TIE) DS | TIE | S01/69/600/DS1 |  |  |  | CDC | 233 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 雲港SS.602_DS | 602(TIE) DS | TIE | S01/69/600/DS2 |  |  |  | CDC | 234 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0E-01 |  | 1-3A | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.TIE1_CB | 11KV TIE1 CB | TIE | S01/11/TIE1/CB |  |  |  | CDC | 235 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.TIE1_51A | 11KV TIE1 51RY | TIE | S01/11/TIE1/51A |  |  |  | CDC | 236 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S01/11/TIE1/51NA |  |  |  | CDC | 237 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-32 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.750_CB | 750(#1MTR) CB | DTR | S01/69/750/CB |  |  |  | CDC | 238 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-33 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.1M_CB | 1M(#1MTR) CB | DTR | S01/11/M1/CB |  |  |  | CDC | 239 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_51A | #1MTR 51RY | DTR | S01/69/750/51A |  |  |  | CDC | 240 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_51NA | #1MTR 51N RY | DTR | S01/69/750/51NA |  |  |  | CDC | 241 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S01//1MTR/51ZA |  |  |  | CDC | 242 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_87A | #1MTR 87RY | DTR | S01//1MTR/87A |  |  |  | CDC | 243 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S01//1MTR/87UL |  |  |  | CDC | 244 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S01/11/M1/51A |  |  |  | CDC | 245 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_TRA | #1MTR 重故障 | DTR | S01//1MTR/TRA |  |  |  | CDC | 246 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S01//1MTR/TRF |  |  |  | CDC | 247 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S01//1MTR/SupLocal |  |  |  | CDC | 248 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3C | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S01//1MTR/Tap Chan |  |  |  | CDC | 249 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-37-00 | 1-37-01 | 1-2C | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.751_DS | 751(#1MTR) DS | DTR | S01/69/750/DS1 |  |  |  | CDC | 250 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-37-02 | 1-37-03 | 1-2D | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.752_DS | 752(#1MTR) DS | DTR | S01/69/750/DS2 |  |  |  | CDC | 251 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_96A | #1MTR 96P RY | DTR | S01//1MTR/96PA |  |  |  | CDC | 252 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S01//1MTR/OLTC_DLY |  |  |  | CDC | 253 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S01//1MTR/AC_Fault |  |  |  | CDC | 254 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.760_CB | 760(#2MTR) CB | DTR | S01/69/770/CB |  |  |  | CDC | 255 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 3M | #2MTR |  | CB | [17 empty] | 1-03-04 |  | 1-59 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.3M_CB | 3M(#2MTR) CB | DTR | S01/11/M3/CB |  |  |  | CDC | 256 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_51A | #2MTR 51RY | DTR | S01/69/770/51A |  |  |  | CDC | 257 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_51NA | #2MTR 51N RY | DTR | S01/69/770/51NA |  |  |  | CDC | 258 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S01//3MTR/51ZA |  |  |  | CDC | 259 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_87A | #2MTR 87RY | DTR | S01//3MTR/87A |  |  |  | CDC | 260 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S01//3MTR/87UL |  |  |  | CDC | 261 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 0 |  | 3M | #2MTR二次側(3M) |  | 51A | [17 empty] | 1-03-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.3M_51A | #2MTR二次側(3M) 51RY | DTR | S01/11/M3/51A |  |  |  | CDC | 262 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_TRA | #2MTR 重故障 | DTR | S01//3MTR/TRA |  |  |  | CDC | 263 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S01//3MTR/TRF |  |  |  | CDC | 264 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S01//3MTR/SupLocal |  |  |  | CDC | 265 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S01//3MTR/Tap Chan |  |  |  | CDC | 266 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S01 | 雲港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-37-04 | 1-37-05 | 1-2E | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.761_DS | 761(#2MTR) DS | DTR | S01/69/770/DS1 |  |  |  | CDC | 267 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-37-06 | 1-37-07 | 1-2F | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.762_DS | 762(#2MTR) DS | DTR | S01/69/770/DS2 |  |  |  | CDC | 268 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_96A | #2MTR 96P RY | DTR | S01//3MTR/96PA |  |  |  | CDC | 269 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S01//3MTR/OLTC_DLY |  |  |  | CDC | 270 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-36-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S01//3MTR/AC_Fault |  |  |  | CDC | 271 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0D-06 |  | 1-34 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_CB | 210(11KV #1SC) CB | SC | S01/11/210/CB |  |  |  | CDC | 272 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-11 |  | 1-3D | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S01/11/210/Tap Chan |  |  |  | CDC | 273 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0D-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_SCA | 11KV #1SC 51,51N RY | SC | S01/11/210/SCA |  |  |  | CDC | 274 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0E-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S01/11/210/UVA |  |  |  | CDC | 275 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-13-02 |  | 1-5B | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_CB | 230(11KV #3SC) CB | SC | S01/11/230/CB |  |  |  | CDC | 276 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-11 |  | 1-63 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S01/11/230/Tap Chan |  |  |  | CDC | 277 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-13-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_SCA | 11KV #3SC 51,51N RY | SC | S01/11/230/SCA |  |  |  | CDC | 278 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-13-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S01/11/230/UVA |  |  |  | CDC | 279 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.810_CB | 810(69KV #1SC) CB | SC | S01/69/810/CB |  |  |  | CDC | 280 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 1-37-12 | 1-37-13 | 1-28 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.811_DS | 811(69KV #1SC) DS | SC | S01/69/810/DS1 |  |  |  | CDC | 281 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 1-37-14 | 1-37-15 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.812_DS | 812(69KV #1SC) DS | SC | S01/69/810/DS2 |  |  |  | CDC | 282 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.810_SCA | 69KV #1SC 51,51N RY | SC | S01/69/810/SCA |  |  |  | CDC | 283 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.810_OUVA | 69KV #1SC 27,59RY | SC | S01/69/810/UVA |  |  |  | CDC | 284 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 雲港SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S01/69/1BUS/BUS_VUA |  |  |  | CDC | 285 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S01/69/1BUS/87A |  |  |  | CDC | 286 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 雲港SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S01/69/2BUS/BUS_VUA |  |  |  | CDC | 287 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S01/69/2BUS/87A |  |  |  | CDC | 288 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.11KV_CBA | 11KV重故障 | OTHER | S01/11/ComPoint/CBA |  |  |  | CDC | 289 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.11KV_CBF | 11KV輕故障 | OTHER | S01/11/ComPoint/CBF |  |  |  | CDC | 290 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | _ABS | _ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.69KV_ABS_89A | 69KVABS警報 | OTHER | S01/69/ComPoint/ABS_89A |  |  |  | CDC | 291 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S01/69/ComPoint/CBA |  |  |  | CDC | 292 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S01/69/ComPoint/CBF |  |  |  | CDC | 293 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 1-0E-04 |  | 1-43 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.81RY_A/S(1) | 81電驛動作,港五卸載 | OTHER | S01/0/StaDev/81AS1 |  |  |  | CDC | 294 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S01 | 雲港SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S01/0/RTU/RTU_R_L |  |  |  | CDC | 295 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S01 | 雲港SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.TEST_CB | TEST CB | OTHER | S01/0/RTU/Test_CB |  |  |  | CDC | 296 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.火災警報(1) | 火警-自行裝設 | OTHER | S01/0/StaDev/Fire1 |  |  |  | CDC | 297 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.火災警報(2) | 二氧化碳(CO2)滅火設備 | OTHER | S01/0/StaDev/Fire2 |  |  |  | CDC | 298 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-31-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.火災警報(3) | 火災警報(3) | OTHER | S01/0/StaDev/Fire3 |  |  |  | CDC | 299 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.充油電纜OPA | 油壓電力電纜 | OTHER | S01/0/StaDev/OPA |  |  |  | CDC | 300 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.其他重故障 | 變電所內其他重故障 | OTHER | S01/0/StaDev/PSA |  |  |  | CDC | 301 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S01/0/StaDev/PSF |  |  |  | CDC | 302 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.所內電源ACB1 | ACB1S | OTHER | S01/0/StaDev/ACB1 |  |  |  | CDC | 303 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S01 | 雲港SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.所內電源ACB2 | ACB2S | OTHER | S01/0/StaDev/ACB2 |  |  |  | CDC | 304 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S01 | 雲港SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-31-08 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.所內電源ACBA | 所內電源開關ACB警報 | OTHER | S01/0/StaDev/ACBA |  |  |  | CDC | 305 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.所內電源欠壓 | 所內用電警報 | OTHER | S01/0/StaDev/STUV |  |  |  | CDC | 306 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.直流充電機故障 | 充電機AC故障 | OTHER | S01/0/StaDev/CHG1 |  |  |  | CDC | 307 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.直流電源DCA | 直流電源NFB開關警報 | OTHER | S01/0/StaDev/DCA |  |  |  | CDC | 308 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S01/0/StaDev/DCE |  |  |  | CDC | 309 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.洩油池水位警報 | 洩油池泵警報 | OTHER | S01/0/StaDev/OilLeak |  |  |  | CDC | 310 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-35-13 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.通訊OLTE重故障 | 通訊設備光纖主故障 | OTHER | S01/0/StaDev/3A5Other |  |  |  | CDC | 311 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-35-14 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.通訊OLTE輕故障 | 通訊設備光纖次故障 | OTHER | S01/0/StaDev/4A5Other |  |  |  | CDC | 312 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-35-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.通訊PCM警報 | 博碼調變器故障 | OTHER | S01/0/StaDev/5A5Other |  |  |  | CDC | 313 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.通訊充電機故障 | 充電機(通訊專用) | OTHER | S01/0/StaDev/CHG2 |  |  |  | CDC | 314 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-35-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S01/0/StaDev/CommACF |  |  |  | CDC | 315 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S01/0/StaDev/Burglar1 |  |  |  | CDC | 316 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S01/0/StaDev/Burglar2 |  |  |  | CDC | 317 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S01/0/StaDev/Door1 |  |  |  | CDC | 318 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S01 | 雲港SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-6D | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.開關場照明(A) | 所內開關場照明 | OTHER | S01/0/StaDev/Lights1 |  |  |  | CDC | 319 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S01 | 雲港SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-6E | [5 empty] | DDCS1_2 | [8 empty] | 雲港SS.開關場照明(B) | 所外路燈照明 | OTHER | S01/0/StaDev/Lights2 |  |  |  | CDC | 320 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S01 | 雲港SS | 11 | 11kV | _1SC | #1SC |  | 60A | [17 empty] | 1-33-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER | S01/11/210/FDR_60A |  |  |  | CDC | 321 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | _3SC | #3SC |  | 60A | [17 empty] | 1-33-14 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER | S01/11/230/FDR_60A |  |  |  | CDC | 322 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | 水位警報#1 | [17 empty] | 1-34-14 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.水位警報#1 | 水位警報#1 | OTHER | S01/0/StaDev/Water1 |  |  |  | CDC | 323 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | 水位警報#2 | [17 empty] | 1-34-15 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.水位警報#2 | 水位警報#2 | OTHER | S01/0/StaDev/Water2 |  |  |  | CDC | 324 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.安全監控 | 安全監控 | OTHER | S01/0/StaDev/Burglar |  |  |  | CDC | 325 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.門禁 | 門禁-自行裝設 | OTHER | S01/0/StaDev/Door |  |  |  | CDC | 326 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 600GDA(1) | [17 empty] | 1-04-04 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.600GDA(1) | 69KV TIE(600) 67N-1 RY | OTHER | S01/69/600/GDA1 |  |  |  | CDC | 327 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 600PHA(1) | [17 empty] | 1-04-03 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.600PHA(1) | 69KV TIE(600) 67-1 RY | OTHER | S01/69/600/PHA1 |  |  |  | CDC | 328 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 600GDA(2) | [17 empty] | 1-05-01 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.600GDA(2) | 69KV TIE(600) 67N-2 RY | OTHER | S01/69/600/GDA2 |  |  |  | CDC | 329 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 600PHA(2) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.600PHA(2) | 69KV TIE(600) 67-2 RY | OTHER | S01/69/600/PHA2 |  |  |  | CDC | 330 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.660_PHA | 嘉太線(660) 相間RY | LINE69 | S01/69/660/PHA |  |  |  | CDC | 331 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.660_GDA | 嘉太線(660) 接地RY | LINE69 | S01/69/660/GDA |  |  |  | CDC | 332 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 85A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.660_85A | 嘉太線(660) 85RY | LINE69 | S01/69/660/85A |  |  |  | CDC | 333 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 74A | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 雲港SS.660_74A | 嘉太線(660) 74RY | LINE69 | S01/69/660/74A |  |  |  | CDC | 334 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | 85UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 雲港SS.660_85UL | 嘉太線(660) 85RY U/L | LINE69 | S01/69/660/85UL |  |  |  | CDC | 335 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 雲港SS.660_CB | 660(嘉太線) CB | LINE69 | S01/69/660/CB |  |  |  | CDC | 336 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS1 | 661 | [16 empty] | 1-39-08 | 1-39-09 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 雲港SS.661_DS | 661(嘉太線) DS | LINE69 | S01/69/660/DS1 |  |  |  | CDC | 337 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS2 | 662 | [16 empty] | 1-39-10 | 1-39-11 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 雲港SS.662_DS | 662(嘉太線) DS | LINE69 | S01/69/660/DS2 |  |  |  | CDC | 338 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | DS3 | 663 | [16 empty] | 1-39-12 | 1-39-13 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 雲港SS.663_DS | 663(嘉太線) DS | LINE69 | S01/69/660/DS3 |  |  |  | CDC | 339 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | E3 | 663E | [16 empty] | 1-39-14 | 1-39-15 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 雲港SS.663E_ES | 663E(嘉太線) ES | LINE69 | S01/69/660/ES |  |  |  | CDC | 340 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S01 | 雲港SS | 0 |  |  |  |  | #1IEDAL | [17 empty] | 1-32-09 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#1IEDAL | #1保護電驛IED故障警報 | OTHER | S01/0/ComPoint/IRFA |  |  |  | CDC | 341 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51NA | [17 empty] | 1-01-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.1M_51NA | #1MTR二次側(1M) 51NRY | OTHER | S01/11/M1/51NA |  |  |  | CDC | 342 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #163Q | [17 empty] | 1-18-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#163Q | #1主變ULTC保護警報 | OTHER | S01//1MTR/63Q |  |  |  | CDC | 343 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #196B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#196B1 | #1主變撲氣電驛第ㄧ段警報 | OTHER | S01//1MTR/96B1 |  |  |  | CDC | 344 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #196B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#196B2 | #1主變撲氣電驛第二段警報 | OTHER | S01//1MTR/96B2 |  |  |  | CDC | 345 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #196D | [17 empty] | 1-18-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#196D | #1主變放壓裝置警報 | OTHER | S01//1MTR/96D |  |  |  | CDC | 346 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #196P | [17 empty] | 1-18-03 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#196P | #1主變衝擊油壓警報 | OTHER | S01//1MTR/96P |  |  |  | CDC | 347 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #263Q | [17 empty] | 1-19-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#263Q | #2主變ULTC保護警報 | OTHER | S01//2MTR/63Q |  |  |  | CDC | 348 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #296B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#296B1 | #2主變撲氣電驛第ㄧ段警報 | OTHER | S01//2MTR/96B1 |  |  |  | CDC | 349 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #296B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#296B2 | #2主變撲氣電驛第二段警報 | OTHER | S01//2MTR/96B2 |  |  |  | CDC | 350 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #296D | [17 empty] | 1-18-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#296D | #2主變放壓裝置警報 | OTHER | S01//2MTR/96D |  |  |  | CDC | 351 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #296P | [17 empty] | 1-19-00 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#296P | #2主變衝擊油壓警報 | OTHER | S01//2MTR/96P |  |  |  | CDC | 352 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L187A | [17 empty] | 1-08-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.L187A | 710北港雲港ㄧ路差動電驛動作 | OTHER | S01/69/710/87A |  |  |  | CDC | 353 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L187CFA | [17 empty] | 1-32-01 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.L187CFA | 710北港雲港ㄧ路87RY通訊故障 | OTHER | S01/69/710/87CFA |  |  |  | CDC | 354 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L187S | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 雲港SS.L187S | 710北港雲港ㄧ路差動電驛設定 | OTHER | S01/69/710/87UL |  |  |  | CDC | 355 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 0 |  |  |  |  | L1RYFA | [17 empty] | 1-32-08 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.L1RYFA | 710北港雲港ㄧ路電驛故障警報 | OTHER | S01/69/710/RYFA |  |  |  | CDC | 356 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L287A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.L287A | 720北港雲港二路差動電驛動作 | OTHER | S01/69/720/87A |  |  |  | CDC | 357 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L287CFA | [17 empty] | 1-32-03 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.L287CFA | 720北港雲港二路87RY通訊故障 | OTHER | S01/69/720/87CFA |  |  |  | CDC | 358 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | L287S | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 雲港SS.L287S | 720北港雲港二路差動電驛設定 | OTHER | S01/69/720/87UL |  |  |  | CDC | 359 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 0 |  |  |  |  | L2RYFA | [17 empty] | 1-32-11 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.L2RYFA | 720北港雲港二路電驛故障警報 | OTHER | S01/69/720/RYFA |  |  |  | CDC | 360 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | 600RYFA | [17 empty] | 1-34-13 | [7 empty] | 69KV_N | [8 empty] | 雲港SS.600RYFA | 600TIE電驛故障警報 | OTHER | S01/0/StaDev/2A5Other |  |  |  | CDC | 361 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | #3IEDAL | [17 empty] | 1-33-13 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.#3IEDAL | #3保護電驛IED故障警報 | OTHER | S01/0/ComPoint/1A5Other |  |  |  | CDC | 362 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51NA | [17 empty] | 1-03-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.3M_51NA | #3MTR二次側(3M) 51NRY | OTHER | S01/11/M3/51NA |  |  |  | CDC | 363 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 60050S | [17 empty] | 1-31-07 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.60050S | 600 TIE瞬時過電流RY(50) | OTHER | S01/69/600/50UL |  |  |  | CDC | 364 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  | 600 | TIE(600) |  | 50A | [17 empty] | 1-05-02 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.600_50A | 600 TIE 50電驛動作警報 | OTHER | S01/69/600/50A |  |  |  | CDC | 365 | GENERICDIPoint | SS100_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV |  |  |  | 87UL | [17 empty] | 1-32-14 |  | 1-6A | [5 empty] | ADCS_N | [8 empty] | 雲港SS.87B1S | 69KV #1BUS差動電驛設定 | OTHER | S01/69/1BUS/87UL |  |  |  | CDC | 366 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV |  |  |  | 87UL | [17 empty] | 1-32-15 |  | 1-6B | [5 empty] | ADCS_N | [8 empty] | 雲港SS.87B2S | 69KV #2BUS差動電驛設定 | OTHER | S01/69/2BUS/87UL |  |  |  | CDC | 367 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
S01 | 雲港SS | 69 | 69kV |  |  |  | BUS87BF | [17 empty] | 1-31-04 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.BUS87BF | 69KV BUS差動電驛故障警報 | OTHER | S01/0/StaDev/Burglar3 |  |  |  | CDC | 368 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 69 | 69kV | BUS | BUS |  | BUSCTFA | [17 empty] | 1-31-06 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.BUSCTFA | 69KV BUS CT異常警報 | OTHER | S01/69/ComPoint/87CTFA |  |  |  | CDC | 369 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 0 |  |  |  |  | PMA警報 | [17 empty] | 1-34-12 | [7 empty] | DDCS1_2 | [8 empty] | 雲港SS.PMA警報 | PMA警報 | OTHER | S01/0/StaDev/1A5Other |  |  |  | CDC | 370 | GENERICDIPoint | SS100_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S01 | 雲港SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 371 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 372 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS1_2 | [8 empty] | 雲港SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 373 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.610LE | 610LE (非取樣點) | LINE69 | S01/69/610/LE0 |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 610 | 萬有線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.610BE | 610BE (非取樣點) | LINE69 | S01/69/610/BE0 |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | LE0 | 710LE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.710LE | 710LE (非取樣點) | LINE69 | S01/69/710/LE0 |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 710 | 北港一路(710) |  | BE0 | 710BE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.710BE | 710BE (非取樣點) | LINE69 | S01/69/710/BE0 |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | LE0 | 720LE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.720LE | 720LE (非取樣點) | LINE69 | S01/69/720/LE0 |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 720 | 北港二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.720BE | 720BE (非取樣點) | LINE69 | S01/69/720/BE0 |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG21 | XG21_DS |  | DS1 | XG21_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_DS | XG21_DS (非取樣點) | FEEDER | S01/11/XG21/DS |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG21 | XG21_ES |  | LE0 | XG21_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG21_ES | XG21_ES (非取樣點) | FEEDER | S01/11/XG21/ES |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG22 | XG22_DS |  | DS1 | XG22_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_DS | XG22_DS (非取樣點) | FEEDER | S01/11/XG22/DS |  |  |  |  | 382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG22 | XG22_ES |  | LE0 | XG22_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG22_ES | XG22_ES (非取樣點) | FEEDER | S01/11/XG22/ES |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG23 | XG23_DS |  | DS1 | XG23_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_DS | XG23_DS (非取樣點) | FEEDER | S01/11/XG23/DS |  |  |  |  | 384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG23 | XG23_ES |  | LE0 | XG23_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG23_ES | XG23_ES (非取樣點) | FEEDER | S01/11/XG23/ES |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG24 | XG24_DS |  | DS1 | XG24_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_DS | XG24_DS (非取樣點) | FEEDER | S01/11/XG24/DS |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG24 | XG24_ES |  | LE0 | XG24_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG24_ES | XG24_ES (非取樣點) | FEEDER | S01/11/XG24/ES |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG25 | XG25_DS |  | DS1 | XG25_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_DS | XG25_DS (非取樣點) | FEEDER | S01/11/XG25/DS |  |  |  |  | 388 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG25 | XG25_ES |  | LE0 | XG25_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG25_ES | XG25_ES (非取樣點) | FEEDER | S01/11/XG25/ES |  |  |  |  | 389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG31 | XG31_DS |  | DS1 | XG31_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_DS | XG31_DS (非取樣點) | FEEDER | S01/11/XG31/DS |  |  |  |  | 390 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG31 | XG31_ES |  | LE0 | XG31_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG31_ES | XG31_ES (非取樣點) | FEEDER | S01/11/XG31/ES |  |  |  |  | 391 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG32 | XG32_DS |  | DS1 | XG32_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_DS | XG32_DS (非取樣點) | FEEDER | S01/11/XG32/DS |  |  |  |  | 392 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG32 | XG32_ES |  | LE0 | XG32_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG32_ES | XG32_ES (非取樣點) | FEEDER | S01/11/XG32/ES |  |  |  |  | 393 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG33 | XG33_DS |  | DS1 | XG33_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_DS | XG33_DS (非取樣點) | FEEDER | S01/11/XG33/DS |  |  |  |  | 394 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG33 | XG33_ES |  | LE0 | XG33_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG33_ES | XG33_ES (非取樣點) | FEEDER | S01/11/XG33/ES |  |  |  |  | 395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG34 | XG34_DS |  | DS1 | XG34_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_DS | XG34_DS (非取樣點) | FEEDER | S01/11/XG34/DS |  |  |  |  | 396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG34 | XG34_ES |  | LE0 | XG34_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG34_ES | XG34_ES (非取樣點) | FEEDER | S01/11/XG34/ES |  |  |  |  | 397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | XG35 | XG35_DS |  | DS1 | XG35_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_DS | XG35_DS (非取樣點) | FEEDER | S01/11/XG35/DS |  |  |  |  | 398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | XG35 | XG35_ES |  | LE0 | XG35_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.XG35_ES | XG35_ES (非取樣點) | FEEDER | S01/11/XG35/ES |  |  |  |  | 399 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 雲港SS.601E | 601E (非取樣點) | TIE | S01/69/600/E1 |  |  |  |  | 400 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 雲港SS.602E | 602E (非取樣點) | TIE | S01/69/600/E2 |  |  |  |  | 401 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S01/11/TIE1/DS |  |  |  |  | 402 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.750TE | 750TE (非取樣點) | DTR | S01/69/750/TE0 |  |  |  |  | 403 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.750BE | 750BE (非取樣點) | DTR | S01/69/750/BE0 |  |  |  |  | 404 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 1M-DS1 | 1M-DS1 |  | M-DS10 | 1M-DS1 | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.1M-DS1 | 1M-DS1 (非取樣點) | DTR | S01/11/M1/DS |  |  |  |  | 405 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.1M_ES | 1M_ES (非取樣點) | DTR | S01/11/M1/ES |  |  |  |  | 406 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.760TE | 760TE (非取樣點) | DTR | S01/69/770/TE0 |  |  |  |  | 407 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.760BE | 760BE (非取樣點) | DTR | S01/69/770/BE0 |  |  |  |  | 408 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 3M-DS1 | 3M-DS1 |  | M-DS10 | 3M-DS1 | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.3M-DS1 | 3M-DS1 (非取樣點) | DTR | S01/11/M3/DS |  |  |  |  | 409 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.3M_ES | 3M_ES (非取樣點) | DTR | S01/11/M3/ES |  |  |  |  | 410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.210ES | 210ES (非取樣點) | SC | S01/11/210/ES |  |  |  |  | 411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 210DS | 210DS |  | 210DS | 210DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.210DS | 210DS (非取樣點) | SC | S01/11/210/DS |  |  |  |  | 412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 230ES | 230ES |  | 230ES | 230ES | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.230ES | 230ES (非取樣點) | SC | S01/11/230/ES |  |  |  |  | 413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 230DS | 230DS |  | 230DS | 230DS | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.230DS | 230DS (非取樣點) | SC | S01/11/230/DS |  |  |  |  | 414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S01 | 雲港SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.810BE | 810BE (非取樣點) | SC | S01/69/810/BE0 |  |  |  |  | 415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 810LE | 810LE |  | 810LE | 810LE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.810LE | 810LE (非取樣點) | SC | S01/69/810/LE0 |  |  |  |  | 416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 雲港SS.69B1E | 69B1E (非取樣點) | BUS | S01/69/1BUS/BE1 |  |  |  |  | 417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 雲港SS.69B2E | 69B2E (非取樣點) | BUS | S01/69/2BUS/BE2 |  |  |  |  | 418 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS1_2 | [8 empty] | 雲港SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 419 | NotelDIPoint | [38 empty] | START/STOP | STOP
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | LE0 | 660LE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.660LE | 660LE (非取樣點) | LINE69 | S01/69/660/LE0 |  |  |  |  | 420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S01 | 雲港SS | 69 | 69kV | 660 | 嘉太線(660) |  | BE0 | 660BE | [24 empty] | ADCS_N | [8 empty] | 雲港SS.660BE | 660BE (非取樣點) | LINE69 | S01/69/660/BE0 |  |  |  |  | 421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo