## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S09 | 大美SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KVBUS | KV | 69KVBUS PT | kV_-90_90(-2000_2000) | aaa | B2/S09_A1 | [8 empty] | 大美SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S09 | 大美SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV#1BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | baa | B2/S09_D1 | [8 empty] | 大美SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV#2BUS | KV | 二號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S09_D1 | [8 empty] | 大美SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aagb | B2/S09_A1 | [8 empty] | 大美SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 5 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA | 衡相監視 |  |  | B2/S09_A1 | [8 empty] | 大美SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 6 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 720 | MW | 雲林大美一路 | MW_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.720_MW | 雲林ㄧ路 MW | LINE69 |  |  |  |  | CDC | 7 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 720 | MVAR | 雲林大美一路 | MVAR_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.720_MVAR | 雲林ㄧ路 MVAR | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 720 | MWH(+) | 雲林大美 |  |  | B2/S09_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 9 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 610 | MW | 大美建大 | MW_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.610_MW | 建大線 MW | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 610 | MVAR | 大美建大 | MVAR_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.610_MVAR | 建大線 MVAR | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 610 | MWH(+) | 大美建大 |  |  | B2/S09_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 12 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 640 | MW | 大美濁水 | MW_-96_96(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.640_MW | 濁水線 MW | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 640 | MVAR | 大美濁水 | MVAR_-96_96(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.640_MVAR | 濁水線 MVAR | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 640 | MWH(+) | 濁水大美 |  |  | B2/S09_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 15 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 620 | MW | 雲林大美二路 | MW_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.620_MW | 雲林二路 MW | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 620 | MVAR | 雲林大美二路 | MVAR_-144_144(-2000_2000) |  | B2/S09_A1 | [8 empty] | 大美SS.620_MVAR | 雲林二路 MVAR | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 620 | MWH(+) | 斗六大美 |  |  | B2/S09_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 18 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 720 | PHA | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.720_PHA | 雲林ㄧ路(720) 相間RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 720 | GDA | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.720_GDA | 雲林ㄧ路(720) 接地RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 610 | PHA | 大美建大 |  |  | B2/S09_A1 | [8 empty] | 大美SS.610_PHA | 建大線(610) 相間RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 610 | GDA | 大美建大 |  |  | B2/S09_A1 | [8 empty] | 大美SS.610_GDA | 建大線(610) 接地RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 640 | PHA | 大美濁水 |  |  | B2/S09_A1 | [8 empty] | 大美SS.640_PHA | 濁水線(640) 相間RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 640 | GDA | 大美濁水 |  |  | B2/S09_A1 | [8 empty] | 大美SS.640_GDA | 濁水線(640) 接地RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 620 | PHA | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.620_PHA | 雲林二路(620) 相間RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 620 | GDA | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.620_GDA | 雲林二路(620) 接地RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/P03S091/T2 |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 720 | CB ON/OFF | 雲林大美一路 |  | aaba | B2/S09_A1 | [8 empty] | 大美SS.720_CB | 720(雲林ㄧ路) CB | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/S09TN01/T1 |  |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 610 | CB ON/OFF | 大美建大 |  | aaca | B2/S09_A1 | [8 empty] | 大美SS.610_CB | 610(建大線) CB | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0000 |  | 0017 | 1-00-00 |  | 1-11 | 69KV 81RY | 81A | 低頻率電驛 |  |  | B2/S09_A1 | [8 empty] | 大美SS.610_81A/S | (610) 81RY A/S | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/H04S09/T2 |  |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 640 | CB ON/OFF | 大美濁水 |  | aaea | B2/S09_A1 | [8 empty] | 大美SS.640_CB | 640(濁水線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/P03S092/T2 |  |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 620 | CB ON/OFF | 雲林大美二路 |  | aafa | B2/S09_A1 | [8 empty] | 大美SS.620_CB | 620(雲林二路) CB | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | ABS1 | 721 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0018 | 1-38-08 | 1-38-09 | 1-12 | 721 | ABS ON | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.721_ABS | 721(雲林ㄧ路) ABS | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | ABS2 | 722 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0019 | 1-38-10 | 1-38-11 | 1-13 | 722 | ABS ON | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.722_ABS | 722(雲林ㄧ路) ABS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | ABS1 | 611 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0021 | 1-38-14 | 1-38-15 | 1-15 | 611 | ABS ON | 大美建大 |  |  | B2/S09_A1 | [8 empty] | 大美SS.611_ABS | 611(建大線) ABS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | ABS2 | 612 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0022 | 1-39-00 | 1-39-01 | 1-16 | 612 | ABS ON | 大美建大 |  |  | B2/S09_A1 | [8 empty] | 大美SS.612_ABS | 612(建大線) ABS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | ABS1 | 641 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0024 | 1-39-04 | 1-39-05 | 1-18 | 641 | ABS ON | 濁水大美 |  |  | B2/S09_A1 | [8 empty] | 大美SS.641_ABS | 641(濁水線) ABS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | ABS2 | 642 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0025 | 1-39-06 | 1-39-07 | 1-19 | 642 | ABS ON | 濁水大美 |  |  | B2/S09_A1 | [8 empty] | 大美SS.642_ABS | 642(濁水線) ABS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0027 | 1-39-10 | 1-39-11 | 1-1B | 621 | ABS ON | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.621_ABS | 621(雲林二路) ABS | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0028 | 1-39-12 | 1-39-13 | 1-1C | 622 | ABS ON | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.622_ABS | 622(雲林二路) ABS | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | ES2 | 722E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0396 | 397 | 0020 | 1-38-12 | 1-38-13 | 1-14 | 722E | ABS ON | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.722E_ES | 722E(雲林ㄧ路) ES | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0402 | 403 | 0023 | 1-39-02 | 1-39-03 | 1-17 | 612E | ABS ON | 大美建大 |  |  | B2/S09_A1 | [8 empty] | 大美SS.612E_ES | 612E(建大線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | ES2 | 642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0408 | 409 | 0026 | 1-39-08 | 1-39-09 | 1-1A | 642E | ABS ON | 濁水大美 |  |  | B2/S09_A1 | [8 empty] | 大美SS.642E_ES | 642E(濁水線) ES | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0029 | 1-39-14 | 1-39-15 | 1-1D | 622E | ABS ON | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.622E_ES | 622E(雲林二路) ES | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F1 PH RY | PHA | 美一線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK21_PHA | 11KV美一線(XK21) 相間RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F1 GD RY | GDA | 美一線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK21_GDA | 11KV美一線(XK21) 接地RY | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | F1 CB | 79 U/L | 美一線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK21_79UL | 11KV美一線(XK21) 79RY U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 美一線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK21_ADJ | 11KV美一線(XK21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | F2 PH RY | PHA | 美二線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK22_PHA | 11KV美二線(XK22) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F2 GD RY | GDA | 美二線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK22_GDA | 11KV美二線(XK22) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | F2 CB | 79 U/L | 美二線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK22_79UL | 11KV美二線(XK22) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 美二線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK22_ADJ | 11KV美二線(XK22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F3 PH RY | PHA | 美三線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK23_PHA | 11KV美三線(XK23) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | F3 GD RY | GDA | 美三線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK23_GDA | 11KV美三線(XK23) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | F3 CB | 79 U/L | 美三線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK23_79UL | 11KV美三線(XK23) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 美三線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK23_ADJ | 11KV美三線(XK23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | F4 PH RY | PHA | 美九線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK29_PHA | 11KV美九線(XK29) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | F4 GD RY | GDA | 美九線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK29_GDA | 11KV美九線(XK29) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | F4 CB | 79 U/L | 美九線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK29_79UL | 11KV美九線(XK29) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 美九線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK29_ADJ | 11KV美九線(XK29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | F5 PH RY | PHA | 美十線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK30_PHA | 11KV美十線(XK30) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | F5 GD RY | GDA | 美十線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK30_GDA | 11KV美十線(XK30) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | F5 CB | 79 U/L | 美十線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK30_79UL | 11KV美十線(XK30) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 美十線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK30_ADJ | 11KV美十線(XK30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | F6 PH RY | PHA | 美四線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK24_PHA | 11KV美四線(XK24) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | F6 GD RY | GDA | 美四線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK24_GDA | 11KV美四線(XK24) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | F6 CB | 79 U/L | 美四線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK24_79UL | 11KV美四線(XK24) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | F6 LCO | ADJ(U/L) | 美四線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK24_ADJ | 11KV美四線(XK24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F7 PH RY | PHA | 美五線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK25_PHA | 11KV美五線(XK25) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F7 GD RY | GDA | 美五線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK25_GDA | 11KV美五線(XK25) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | F7 CB | 79 U/L | 美五線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK25_79UL | 11KV美五線(XK25) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | F7 LCO | ADJ(U/L) | 美五線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK25_ADJ | 11KV美五線(XK25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | F8 PH RY | PHA | 美六線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK26_PHA | 11KV美六線(XK26) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F8 GD RY | GDA | 美六線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK26_GDA | 11KV美六線(XK26) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | F8 CB | 79 U/L | 美六線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK26_79UL | 11KV美六線(XK26) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | F8 LCO | ADJ(U/L) | 美六線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK26_ADJ | 11KV美六線(XK26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F9 PH RY | PHA | 美七線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK27_PHA | 11KV美七線(XK27) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | F9 GD RY | GDA | 美七線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK27_GDA | 11KV美七線(XK27) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | F9 CB | 79 U/L | 美七線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK27_79UL | 11KV美七線(XK27) 79RY U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | F9 LCO | ADJ(U/L) | 美七線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK27_ADJ | 11KV美七線(XK27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F10 PH RY | PHA | 美八線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK28_PHA | 11KV美八線(XK28) 相間RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F10 GD RY | GDA | 美八線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK28_GDA | 11KV美八線(XK28) 接地RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | F10 CB | 79 U/L | 美八線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK28_79UL | 11KV美八線(XK28) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | F10 LCO | ADJ(U/L) | 美八線 |  |  | B2/S09_D1 | [8 empty] | 大美SS.XK28_ADJ | 11KV美八線(XK28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/XK21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | F1 CB | CB ON/OFF | 美一線 |  | badb | B2/S09_D1 | [8 empty] | 大美SS.XK21_CB | XK21(11KV美一線) CB | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK21_DS | XK21_DS (非取樣點) | FEEDER | [5 empty] | 85 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK21_ES | XK21_ES (非取樣點) | FEEDER | [5 empty] | 86 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/XK22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | F2 CB | CB ON/OFF | 美二線 |  | baeb | B2/S09_D1 | [8 empty] | 大美SS.XK22_CB | XK22(11KV美二線) CB | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK22_DS | XK22_DS (非取樣點) | FEEDER | [5 empty] | 88 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK22_ES | XK22_ES (非取樣點) | FEEDER | [5 empty] | 89 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/XK23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F3 CB | CB ON/OFF | 美三線 |  | bafb | B2/S09_D1 | [8 empty] | 大美SS.XK23_CB | XK23(11KV美三線) CB | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK23_DS | XK23_DS (非取樣點) | FEEDER | [5 empty] | 91 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK23_ES | XK23_ES (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/XK29/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | F4 CB | CB ON/OFF | 美九線 |  | bagb | B2/S09_D1 | [8 empty] | 大美SS.XK29_CB | XK29(11KV美九線) CB | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK29_DS | XK29_DS (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK29_ES | XK29_ES (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/XK30/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | F5 CB | CB ON/OFF | 美十線 |  | bahb | B2/S09_D1 | [8 empty] | 大美SS.XK30_CB | XK30(11KV美十線) CB | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK30_DS | XK30_DS (非取樣點) | FEEDER | [5 empty] | 97 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK30_ES | XK30_ES (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | L/XK24/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | F6 CB | CB ON/OFF | 美四線 |  | aacb | B2/S09_D1 | [8 empty] | 大美SS.XK24_CB | XK24(11KV美四線) CB | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK24_DS | XK24_DS (非取樣點) | FEEDER | [5 empty] | 100 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK24_ES | XK24_ES (非取樣點) | FEEDER | [5 empty] | 101 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | L/XK25/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | F7 CB | CB ON/OFF | 美五線 |  | aadb | B2/S09_D1 | [8 empty] | 大美SS.XK25_CB | XK25(11KV美五線) CB | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK25_DS | XK25_DS (非取樣點) | FEEDER | [5 empty] | 103 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK25_ES | XK25_ES (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | L/XK26/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | F8 CB | CB ON/OFF | 美六線 |  | aafb | B2/S09_D1 | [8 empty] | 大美SS.XK26_CB | XK26(11KV美六線) CB | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK26_DS | XK26_DS (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK26_ES | XK26_ES (非取樣點) | FEEDER | [5 empty] | 107 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | L/XK27/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | F9 CB | CB ON/OFF | 美七線 |  | aagb | B2/S09_D1 | [8 empty] | 大美SS.XK27_CB | XK27(11KV美七線) CB | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK27_DS | XK27_DS (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK27_ES | XK27_ES (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | L/XK28/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | F10 CB | CB ON/OFF | 美八線 |  | aahb | B2/S09_D1 | [8 empty] | 大美SS.XK28_CB | XK28(11KV美八線) CB | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK28_DS | XK28_DS (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.XK28_ES | XK28_ES (非取樣點) | FEEDER | [5 empty] | 113 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 114 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 115 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 116 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  | N2為實線 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | B/2BUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | aaab | B2/S09_D1 | [8 empty] | 大美SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 117 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIEPH RY | PHA | #1 TIE CB |  |  | B2/S09_D1 | [8 empty] | 大美SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 118 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1 TIEGD RY | GDA | #1 TIE CB |  |  | B2/S09_D1 | [8 empty] | 大美SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 119 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.TIE1DS1 | TIE1DS1 (非取樣點) | TIE | [5 empty] | 120 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 121 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 122 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 123 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 124 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 125 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2MTR | MW | 二號主變 | MW_-36_36(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 126 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2MTR | MVAR | 二號主變 | MVAR_-36_36(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 127 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2MTR R電流 | A1 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 128 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2MTR S電流 | A2 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 129 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2MTR T電流 | A3 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 130 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 131 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 132 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 133 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH | 一號主變 |  |  | B1/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 134 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 135 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 136 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 137 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 138 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S09 | 大美SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2TR | MWH | 二號主變 |  |  | B1/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 139 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2TR | MVARH(+) | 二號主變 |  |  | B1/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 140 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aaab | B3/S09_D1 | [8 empty] | 大美SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 141 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S09_D1 | [8 empty] | 大美SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 142 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S09_D1 | [8 empty] | 大美SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 143 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aadb | B3/S09_D1 | [8 empty] | 大美SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 144 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S09_D1 | [8 empty] | 大美SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 145 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S09_D1 | [8 empty] | 大美SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 146 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | 1MT | CB ON/OFF | 一號主變二次側 |  | baba | B2/S09_D1 | [8 empty] | 大美SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 147 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2MA | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | 2MTA | CB ON/OFF | 二號主變二次側(A) |  | aaea | B2/S09_D1 | [8 empty] | 大美SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 148 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S09_D1 | [8 empty] | 大美SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 149 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S09_D1 | [8 empty] | 大美SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 150 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1MTR | 51Z | 一號主變 51Z RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 151 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1MTR | 87A | 一號主變差動電驛 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 152 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1MTR | 87 LS | 一號 主變87 RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 153 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S09_D1 | [8 empty] | 大美SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 154 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S09_D1 | [8 empty] | 大美SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 155 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2MTR | 51Z | 二號主變 51Z RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 156 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2MTR | 87A | 二號主變差動電驛 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 157 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2MTR | 87 LS | 二號 主變87 RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 158 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1MT | PHA | 一號主變二次側 51 RY |  |  | B2/S09_D1 | [8 empty] | 大美SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 159 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #1MTR | TRA | 一號主變重故障 |  | a | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 160 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1MTR | TRF | 一號主變輕故障 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 161 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1MTR | R/L | 一號主變 OLTC |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 162 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S09 | 大美SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1MTR | A/M | 一號主變 OLTC |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 163 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S09 | 大美SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 2MTA | PHA | 二號主變二次(A)51 RY |  |  | B2/S09_D1 | [8 empty] | 大美SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 164 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #2MTR | TRA | 二號主變重故障 |  | a | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 165 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2MTR | TRF | 二號主變輕故障 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 166 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2MTR | R/L | 二號主變 OLTC |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 167 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S09 | 大美SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2MTR | A/M | 二號主變 OLTC |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 168 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | 一號主變 |  |  | B3/S09_D1 | [8 empty] | 大美SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 169 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | 二號主變 |  |  | B3/S09_D1 | [8 empty] | 大美SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 170 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M(非取樣點) | ADD | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 171 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1MTR | 96A | 一號主變 96D,63A RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 172 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1MTR | TAPA | 一號主變TAP遲滯 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 173 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1MTR | 1ACF | 一號主變AC電源失效 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 174 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | 2MA(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 175 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 176 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2MTR | TAPA | 二號主變TAP遲滯 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 177 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2MTR | 2ACF | 二號主變AC電源失效 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 178 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | bacb | B2/S09_D1 | [8 empty] | 大美SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 179 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1SC | A/M | 一號 SC 乏控器 |  |  | B2/S09_D1 | [8 empty] | 大美SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 180 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 181 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbV | B/2BUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC | CB ON/OFF | #2 11KV SC |  | aabb | B2/S09_D1 | [8 empty] | 大美SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 182 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2 SC | A/M | 二號 SC 乏控器 |  |  | B2/S09_D1 | [8 empty] | 大美SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 183 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.220ES | 220ES (非取樣點) | SC | [5 empty] | 184 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1SC5151NRY | SCA | #1 11KV SC |  |  | B2/S09_D1 | [8 empty] | 大美SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 185 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1SC2759RY | UVA | #1 11KV SC |  |  | B2/S09_D1 | [8 empty] | 大美SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 186 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2SC5151NRY | SCA | #2 11KV SC |  |  | B2/S09_D1 | [8 empty] | 大美SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 187 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2SC2759RY | UVA | #2 11KV SC |  |  | B2/S09_D1 | [8 empty] | 大美SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 188 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.210DS | 210DS (非取樣點) | SC | [5 empty] | 189 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.220DS | 220DS (非取樣點) | SC | [5 empty] | 190 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 191 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 192 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 193 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 194 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 195 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 196 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 大美SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 197 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 198 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | SPARE |  | 其他重故障 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 199 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | SPARE | UVA | 其他輕故障 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 200 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 201 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 202 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | SPARE |  | 無人化門禁(1) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 203 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | SPARE |  | 無人化門禁(2) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 204 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | SPARE |  | 無人化門禁(3) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 205 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | SPARE |  | 無人化防盜(1) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 206 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | SPARE |  | 無人化防盜(2) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 207 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | SPARE |  | 無人化防盜(3) |  |  | B3/S09_D1 | [8 empty] | 大美SS.無人化防盜(3) | 無人化防盜(3) | OTHER |  |  |  |  | CDC | 208 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S09_D1 | [8 empty] | 大美SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 209 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S09_D1 | [8 empty] | 大美SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 210 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S09_D1 | [8 empty] | 大美SS.火災警報(1) | 火警-自行裝設 | OTHER |  |  |  |  | CDC | 211 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | SPARE |  | 無人化防火(1) |  |  | B3/S09_D1 | [8 empty] | 大美SS.火災警報(2) | 煙烙燼氣體自動滅火系統警報 | OTHER |  |  |  |  | CDC | 212 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | SPARE |  | 無人化防火(2) |  |  | B3/S09_D1 | [8 empty] | 大美SS.火災警報(3) | 水氣霧自動滅火系統警報 | OTHER |  |  |  |  | CDC | 213 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.火災警報(4) | MCSG空氣取樣警報 | OTHER |  |  |  |  | CDC | 214 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內用電警報 |  |  | B3/S09_D1 | [8 empty] | 大美SS.所內電源ACBA | 所內電源開關ACB警報 | OTHER |  |  |  |  | CDC | 215 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 |  | NFB跳脫監視 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.直流電源DCA | 直流電源NFB開關警報 | OTHER |  |  |  |  | CDC | 216 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCA | 直流電源接地故障 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 217 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 218 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 219 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 220 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S09_D1 | [8 empty] | 大美SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 221 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池警報 |  | 洩油池警報 |  |  | B3/S09_D1 | [8 empty] | 大美SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 222 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS AL | ABS警報 |  |  | B3/S09_D1 | [8 empty] | 大美SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 223 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-37-00 |  |  | SPARE |  | 通訊設備AC故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 224 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 1-37-01 |  |  | SPARE |  | 通訊設備光纖主故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 225 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-37-02 |  |  | SPARE |  | 通訊設備光纖次故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 226 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊PCM警報 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0371 |  |  | 1-37-03 |  |  | SPARE |  | 博碼調變器故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 227 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 81AS1 |  | Element | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0065 | 1-0C-06 |  | 1-41 | #1 81 RY | 181A | 一號主變 |  |  | B3/S09_D1 | [8 empty] | 大美SS.81RY_A/S(1) | 81電驛動作,美二,三,六卸載 | OTHER |  |  |  |  | CDC | 228 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Door | 門禁-自行裝設 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S09_D1 | [8 empty] | 大美SS.門禁 | 門禁-自行裝設 | OTHER |  |  |  |  | CDC | 229 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 全所43RS狀態 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0349 |  |  | 1-35-13 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.全所43RS狀態 | 全所43RS狀態 | OTHER |  |  |  |  | CDC | 230 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 全所閘刀U/L | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0350 |  |  | 1-35-14 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.全所閘刀U/L | 全所閘刀U/L | OTHER |  |  |  |  | CDC | 231 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | SPARE | SCA | 安全監控 |  |  | B3/S09_D1 | [8 empty] | 大美SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 232 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報#1 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0334 |  |  | 1-34-14 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.水位警報#1 | 水位警報#1 | OTHER |  |  |  |  | CDC | 233 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報#2 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0335 |  |  | 1-34-15 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.水位警報#2 | 水位警報#2 | OTHER |  |  |  |  | CDC | 234 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 720 | L187A | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L187A | 雲林大美ㄧ路87RY動作警報 | OTHER |  |  |  |  | CDC | 235 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 720 | L187S | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L187S_U/L | 雲林大美ㄧ路87RY U/L | OTHER |  |  |  |  | CDC | 236 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | 720 | L187CFA | 雲林大美一路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L187CFA | 雲林大美ㄧ路87RY通訊故障警報 | OTHER |  |  |  |  | CDC | 237 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 620 | L487A | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L487A | 雲林大美二路87RY動作警報 | OTHER |  |  |  |  | CDC | 238 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 620 | L487S | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L487S_U/L | 雲林大美二路87RY U/L | OTHER |  |  |  |  | CDC | 239 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 620 | L487CFA | 雲林大美二路 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L487CFA | 雲林大美二路87RY通訊故障警報 | OTHER |  |  |  |  | CDC | 240 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | ComPoint |  |  | IRFA | 69IEDAL | B2,B3,Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 1-32-15 |  |  | 69KVIED | 69IEDAL | 69KV保護電驛故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.69IEDAL | 69KV IED故障警報 | OTHER |  |  |  |  | CDC | 241 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 美一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美一線KVAR | 11KV美一線 KVAR | FEEDER |  |  |  |  | CDC | 242 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 美一線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美一線A1 | 11KV美一線 R相AMP | FEEDER |  |  |  |  | CDC | 243 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 美一線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美一線A2 | 11KV美一線 S相AMP | FEEDER |  |  |  |  | CDC | 244 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 美一線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美一線A3 | 11KV美一線 T相AMP | FEEDER |  |  |  |  | CDC | 245 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 美一線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美一線A0 | 11KV美一線 N相AMP | FEEDER |  |  |  |  | CDC | 246 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 乏 | VAR | 美七線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美七線KVAR | 11KV美七線 KVAR | FEEDER |  |  |  |  | CDC | 247 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 R相電流 | A1 | 美七線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美七線A1 | 11KV美七線 R相AMP | FEEDER |  |  |  |  | CDC | 248 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 S相電流 | A2 | 美七線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美七線A2 | 11KV美七線 S相AMP | FEEDER |  |  |  |  | CDC | 249 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 T相電流 | A3 | 美七線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美七線A3 | 11KV美七線 T相AMP | FEEDER |  |  |  |  | CDC | 250 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F9 N相電流 | AMP | 美七線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美七線A0 | 11KV美七線 N相AMP | FEEDER |  |  |  |  | CDC | 251 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 美九線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美九線KVAR | 11KV美九線 KVAR | FEEDER |  |  |  |  | CDC | 252 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 美九線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美九線A1 | 11KV美九線 R相AMP | FEEDER |  |  |  |  | CDC | 253 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 美九線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美九線A2 | 11KV美九線 S相AMP | FEEDER |  |  |  |  | CDC | 254 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 美九線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美九線A3 | 11KV美九線 T相AMP | FEEDER |  |  |  |  | CDC | 255 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 美九線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美九線A0 | 11KV美九線 N相AMP | FEEDER |  |  |  |  | CDC | 256 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 美二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美二線KVAR | 11KV美二線 KVAR | FEEDER |  |  |  |  | CDC | 257 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 美二線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美二線A1 | 11KV美二線 R相AMP | FEEDER |  |  |  |  | CDC | 258 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 美二線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美二線A2 | 11KV美二線 S相AMP | FEEDER |  |  |  |  | CDC | 259 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 美二線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美二線A3 | 11KV美二線 T相AMP | FEEDER |  |  |  |  | CDC | 260 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 美二線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美二線A0 | 11KV美二線 N相AMP | FEEDER |  |  |  |  | CDC | 261 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F10 乏 | VAR | 美八線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美八線KVAR | 11KV美八線 KVAR | FEEDER |  |  |  |  | CDC | 262 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 R相電流 | A1 | 美八線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美八線A1 | 11KV美八線 R相AMP | FEEDER |  |  |  |  | CDC | 263 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 S相電流 | A2 | 美八線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美八線A2 | 11KV美八線 S相AMP | FEEDER |  |  |  |  | CDC | 264 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 T相電流 | A3 | 美八線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美八線A3 | 11KV美八線 T相AMP | FEEDER |  |  |  |  | CDC | 265 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F10 N相電流 | AMP | 美八線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美八線A0 | 11KV美八線 N相AMP | FEEDER |  |  |  |  | CDC | 266 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 美十線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美十線KVAR | 11KV美十線 KVAR | FEEDER |  |  |  |  | CDC | 267 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 美十線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美十線A1 | 11KV美十線 R相AMP | FEEDER |  |  |  |  | CDC | 268 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 美十線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美十線A2 | 11KV美十線 S相AMP | FEEDER |  |  |  |  | CDC | 269 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 美十線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美十線A3 | 11KV美十線 T相AMP | FEEDER |  |  |  |  | CDC | 270 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 美十線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美十線A0 | 11KV美十線 N相AMP | FEEDER |  |  |  |  | CDC | 271 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 美三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美三線KVAR | 11KV美三線 KVAR | FEEDER |  |  |  |  | CDC | 272 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 美三線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美三線A1 | 11KV美三線 R相AMP | FEEDER |  |  |  |  | CDC | 273 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 美三線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美三線A2 | 11KV美三線 S相AMP | FEEDER |  |  |  |  | CDC | 274 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 美三線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美三線A3 | 11KV美三線 T相AMP | FEEDER |  |  |  |  | CDC | 275 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 美三線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美三線A0 | 11KV美三線 N相AMP | FEEDER |  |  |  |  | CDC | 276 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 乏 | VAR | 美五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美五線KVAR | 11KV美五線 KVAR | FEEDER |  |  |  |  | CDC | 277 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 R相電流 | A1 | 美五線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美五線A1 | 11KV美五線 R相AMP | FEEDER |  |  |  |  | CDC | 278 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 S相電流 | A2 | 美五線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美五線A2 | 11KV美五線 S相AMP | FEEDER |  |  |  |  | CDC | 279 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F7 T相電流 | A3 | 美五線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美五線A3 | 11KV美五線 T相AMP | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F7 N相電流 | AMP | 美五線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美五線A0 | 11KV美五線 N相AMP | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 乏 | VAR | 美六線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美六線KVAR | 11KV美六線 KVAR | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 R相電流 | A1 | 美六線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美六線A1 | 11KV美六線 R相AMP | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 S相電流 | A2 | 美六線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美六線A2 | 11KV美六線 S相AMP | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 T相電流 | A3 | 美六線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美六線A3 | 11KV美六線 T相AMP | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F8 N相電流 | AMP | 美六線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美六線A0 | 11KV美六線 N相AMP | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 乏 | VAR | 美四線 | KVAR_-9000_9000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美四線KVAR | 11KV美四線 KVAR | FEEDER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F6 R相電流 | A1 | 美四線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美四線A1 | 11KV美四線 R相AMP | FEEDER |  |  |  |  | CDC | 288 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F6 S相電流 | A2 | 美四線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美四線A2 | 11KV美四線 S相AMP | FEEDER |  |  |  |  | CDC | 289 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F6 T相電流 | A3 | 美四線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美四線A3 | 11KV美四線 T相AMP | FEEDER |  |  |  |  | CDC | 290 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | F6 N相電流 | AMP | 美四線 | A_-500_500(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.美四線A0 | 11KV美四線 N相AMP | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S09_D1 | [8 empty] | 大美SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1MTR | #163Q | 一號主變ULTC保護 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#163Q | #1主變ULTC保護警報 | OTHER | [5 empty] | 293 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1MTR | #196B1 | 一號主變撲氣電驛第一段 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#196B1 | #1主變撲氣電驛第ㄧ段警報 | OTHER | [5 empty] | 294 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1MTR | #196B2 | 一號主變撲氣電驛第二段 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#196B2 | #1主變撲氣電驛第二段警報 | OTHER | [5 empty] | 295 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1MTR | #196D | 一號主變放壓裝置 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#196D | #1主變放壓裝置警報 | OTHER | [5 empty] | 296 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1MTR | #196P | 一號主變衝擊油壓 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#196P | #1主變衝擊油壓警報 | OTHER | [5 empty] | 297 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2MTR | #263Q | 二號主變ULTC保護 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#263Q | #2主變ULTC保護警報 | OTHER | [5 empty] | 298 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2MTR | #296B1 | 二號主變撲氣電驛第一段 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#296B1 | #2主變撲氣電驛第ㄧ段警報 | OTHER | [5 empty] | 299 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2MTR | #296B2 | 二號主變撲氣電驛第二段 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#296B2 | #2主變撲氣電驛第二段警報 | OTHER | [5 empty] | 300 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2MTR | #296D | 二號主變放壓裝置 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#296D | #2主變放壓裝置警報 | OTHER | [5 empty] | 301 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2MTR | #296P | 二號主變衝擊油壓 |  |  | B1/S09_D1 | [8 empty] | 大美SS.#296P | #2主變衝擊油壓警報 | OTHER | [5 empty] | 302 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 640 | L387A | 大美濁水線87電驛動作 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L387A | 640大美濁水線差動電驛動作警報 | OTHER | [5 empty] | 303 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | 640 | L387CFA | 大美濁水線87RY通訊故障 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L387CFA | 640大美濁水線87RY通訊故障警報 | OTHER | [5 empty] | 304 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 640 | L387S | 大美濁水線87RY U/L |  |  | B2/S09_A1 | [8 empty] | 大美SS.L387S | 640大美濁水線差動電驛設定 | OTHER | [5 empty] | 305 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | 640 | L3RYFA | 大美濁水線電驛故障 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L3RYFA | 640大美濁水線電驛故障警報 | OTHER | [5 empty] | 306 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 610 | L287A | 大美建大線87電驛動作 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L287A | 610大美建大線差動電驛動作警報 | OTHER | [5 empty] | 307 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | 610 | L287CFA | 大美建大線87RY通訊故障 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L287CFA | 610大美建大線87RY通訊故障警報 | OTHER | [5 empty] | 308 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 610 | L287S | 大美建大線87RY U/L |  |  | B2/S09_A1 | [8 empty] | 大美SS.L287S | 610大美建大線差動電驛設定 | OTHER | [5 empty] | 309 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 610 | L2RYFA | 大美建大線電驛故障 |  |  | B2/S09_A1 | [8 empty] | 大美SS.L2RYFA | 610大美建大線電驛故障警報 | OTHER | [5 empty] | 310 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | ComPoint |  |  | IRFA | #1保護電驛IED故障警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | IED | #1-IEDAL | #1-IED保護電驛故障 |  |  | B3/S09_D1 | [8 empty] | 大美SS.#1IEDAL | #1保護電驛IED故障警報 | OTHER | [5 empty] | 311 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | ComPoint | 所內設施 |  | IRFA | #2保護電驛IED故障警報 | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0333 |  |  | 1-34-13 |  |  | SPARE |  |  |  |  | B3/S09_D1 | [8 empty] | 大美SS.#2IEDAL | #2保護電驛IED故障警報 | OTHER | [5 empty] | 312 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1MT | GDA | 一號主變二次側 51N RY |  |  | B2/S09_D1 | [8 empty] | 大美SS.1M_51NA | #1MTR二次側(1M) 51NRY | OTHER | [5 empty] | 313 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 2MTA | GDA | 二號主變二次(A)51N RY |  |  | B2/S09_D1 | [8 empty] | 大美SS.2M_51NA | #2MTR二次側(2M) 51NRY | OTHER | [5 empty] | 314 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/1SSTR |  |  | 0160 |  | 0067 | 1-14-00 |  | 1-43 | #1 SSTR CB | CB ON/OFF | #1 所內用電 |  | baab | B2/S09_D1 | [8 empty] | 大美SS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 315 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | #1 SSTR PH | PHA | #1 所內用電 |  |  | B2/S09_D1 | [8 empty] | 大美SS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 316 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | #1 SSTR GD | GDA | #1 所內用電 |  |  | B2/S09_D1 | [8 empty] | 大美SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 317 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 KWH | KWH | 美一線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 318 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 KWH | KWH | 美二線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 319 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 KWH | KWH | 美三線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 320 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 KWH | KWH | 美九線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 321 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 KWH | KWH | 美十線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 322 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 KWH | KWH | 美四線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 323 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 KWH | KWH | 美五線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 324 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 KWH | KWH | 美六線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 325 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 KWH | KWH | 美七線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 326 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 KWH | KWH | 美八線 |  |  | B2/S09_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 327 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | KVAR |  | DEL | MvMoment | KVAR |  | Y |  | AI | [17 empty] | B2/S09_D1 | [16 empty] | 328 |  |  |  |  | AI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | I_R |  | DEL | MvMoment | R相AMP |  | Y |  | AI | [17 empty] | B2/S09_D1 | [16 empty] | 329 |  |  |  |  | AI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | I_S |  | DEL | MvMoment | S相AMP |  | Y |  | AI | [17 empty] | B2/S09_D1 | [16 empty] | 330 |  |  |  |  | AI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | I_T |  | DEL | MvMoment | T相AMP |  | Y |  | AI | [17 empty] | B2/S09_D1 | [16 empty] | 331 |  |  |  |  | AI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | V_R |  |  | MvMoment | R相電壓 |  | Y |  | AI | [15 empty] | kV_-9_9(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_KV1 | 11KV建大莿桐(XK29) VR | OTHER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | V_S |  |  | MvMoment | S相電壓 |  | Y |  | AI | [15 empty] | kV_-9_9(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_KV2 | 11KV建大莿桐(XK29) VS | OTHER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | V_T |  |  | MvMoment | T相電壓 |  | Y |  | AI | [15 empty] | kV_-9_9(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_KV3 | 11KV建大莿桐(XK29) VT | OTHER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [15 empty] | KW_-6000_6000(-2000_2000) |  | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_KW | 11KV建大莿桐(XK29) KW | OTHER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_KW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 3.6 | 0.01 | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | 59V0A | [25 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐59V0 | 11KV建大莿桐(XK29)59V0 | OTHER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | 81AS1 |  |  | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_81A | 11KV建大莿桐(XK29)81A | OTHER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | CB |  | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B2/S09_D1 | [16 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | CFA | [25 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_CFA | 11KV建大莿桐(XK29)通訊警報 | OTHER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | DS1 |  | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_DS | 11KV建大莿桐(XK29) DS | OTHER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | GDA |  | DEL | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [17 empty] | B2/S09_D1 | [16 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | PHA |  | DEL | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [17 empty] | B2/S09_D1 | [16 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | PTDS | [25 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_PTDS | 11KV建大莿桐(XK29) PTDS | OTHER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 11 | 11kV | XK29 | 建大莿桐(XK29) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.建大莿桐_RYA | 11KV建大莿桐(XK29)27/59 | OTHER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.TIE1ES | TIE1ES (非取樣點) | TIE | [5 empty] | 345 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391 (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 347 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S09_D1 | [8 empty] | 大美SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 348 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S09 | 大美SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S09_D1 | [12 empty] | 大美SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S09/69/1BUS/V
S09 | 大美SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S09_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S09/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S09 | 大美SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S09_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: S09/11/M1/MW; OPRD2: S09/11/M2/MW; OPRD3: S09/69/610/MW; OPRD4: S09/69/620/MW; OPRD5: S09/69/640/MW; OPRD6: S09/69/720/MW
S09 | 大美SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S09_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S09/0/CalcPoint/OPRN2_MW
S09 | 大美SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S09_D1 | [17 empty] | none
S09 | 大美SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S09_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S09/0/CalcPoint/OPRN1; OPRD2: S09/0/CalcPoint/OPRN2; OPRD3: S09/0/CalcPoint/PRFL_UL
S09 | 大美SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S09_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S09/11/M1/MW; OPRD2: S09/11/M1/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S09_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S09/11/M2/MW; OPRD2: S09/11/M2/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS | 69 | 69kV | 610 | 大美～建大、福懋、雲資、合眾線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S09_A1 | [12 empty] | 大美SS.610_AMP | 建大線 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: S09/69/610/MW; OPRD2: S09/69/610/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS | 69 | 69kV | 620 | 雲林～大美二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S09_A1 | [12 empty] | 大美SS.620_AMP | 雲林二路 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S09/69/620/MW; OPRD2: S09/69/620/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS | 69 | 69kV | 640 | 濁水～大美線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S09_A1 | [12 empty] | 大美SS.640_AMP | 濁水線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S09/69/640/MW; OPRD2: S09/69/640/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS | 69 | 69kV | 720 | 雲林～大美一路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S09_A1 | [12 empty] | 大美SS.720_AMP | 雲林ㄧ路 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S09/69/720/MW; OPRD2: S09/69/720/MVAR; OPRD3: S09/0/CalcPoint/Vbs1
S09 | 大美SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S09_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S09/11/1BUS/V
S09 | 大美SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S09_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S09/11/2BUS/V
S09 | 大美SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S09_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大美SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S09/11/M1/MW; OPRD2: S09/11/M1/MVAR
S09 | 大美SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S09_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大美SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S09/11/M2/MW; OPRD2: S09/11/M2/MVAR
S09 | 大美SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S09_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S09//1MTR/MVA; OPRD2: 0
S09 | 大美SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S09_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S09//2MTR/MVA; OPRD2: 0
S09 | 大美SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S09_D1 | [12 empty] | 大美SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S09/11/M1/MW; OPRD2: S09/11/M1/MVAR
S09 | 大美SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S09_D1 | [12 empty] | 大美SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S09/11/M2/MW; OPRD2: S09/11/M2/MVAR
S09 | 大美SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S09_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S09//1MTR/SupLocal; OPRD2: S09//1MTR/Tap Chan; OPRD3: NULL
S09 | 大美SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S09_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S09//2MTR/SupLocal; OPRD2: S09//2MTR/Tap Chan; OPRD3: NULL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/1BUS/V; OPRD2: S09/11/XK21/I_R; OPRD3: S09/11/XK21/I_S; OPRD4: S09/11/XK21/I_T
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/1BUS/V; OPRD2: S09/11/XK22/I_R; OPRD3: S09/11/XK22/I_S; OPRD4: S09/11/XK22/I_T
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/1BUS/V; OPRD2: S09/11/XK23/I_R; OPRD3: S09/11/XK23/I_S; OPRD4: S09/11/XK23/I_T
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/2BUS/V; OPRD2: S09/11/XK24/I_R; OPRD3: S09/11/XK24/I_S; OPRD4: S09/11/XK24/I_T
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/2BUS/V; OPRD2: S09/11/XK25/I_R; OPRD3: S09/11/XK25/I_S; OPRD4: S09/11/XK25/I_T
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/2BUS/V; OPRD2: S09/11/XK26/I_R; OPRD3: S09/11/XK26/I_S; OPRD4: S09/11/XK26/I_T
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/2BUS/V; OPRD2: S09/11/XK27/I_R; OPRD3: S09/11/XK27/I_S; OPRD4: S09/11/XK27/I_T
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/2BUS/V; OPRD2: S09/11/XK28/I_R; OPRD3: S09/11/XK28/I_S; OPRD4: S09/11/XK28/I_T
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/1BUS/V; OPRD2: S09/11/XK29/I_R; OPRD3: S09/11/XK29/I_S; OPRD4: S09/11/XK29/I_T
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S09/11/1BUS/V; OPRD2: S09/11/XK30/I_R; OPRD3: S09/11/XK30/I_S; OPRD4: S09/11/XK30/I_T
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK21/kVA; OPRD2: S09/11/XK21/KVAR
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK22/kVA; OPRD2: S09/11/XK22/KVAR
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK23/kVA; OPRD2: S09/11/XK23/KVAR
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK24/kVA; OPRD2: S09/11/XK24/KVAR
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK25/kVA; OPRD2: S09/11/XK25/KVAR
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK26/kVA; OPRD2: S09/11/XK26/KVAR
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK27/kVA; OPRD2: S09/11/XK27/KVAR
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK28/kVA; OPRD2: S09/11/XK28/KVAR
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK29/kVA; OPRD2: S09/11/XK29/KVAR
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S09/11/XK30/kVA; OPRD2: S09/11/XK30/KVAR
S09 | 大美SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S09_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S09/11/M1/MW; OPRD2: S09/11/M2/MW
S09 | 大美SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S09_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S09/11/M1/MVAR; OPRD2: S09/11/M2/MVAR
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S09_D1 | [12 empty] | 大美SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S09/11/210/CB; OPRD2: 6.9; OPRD3: 0
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S09_D1 | [12 empty] | 大美SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S09/11/220/CB; OPRD2: 6.9; OPRD3: 0
S09 | 大美SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S09_D1 | [12 empty] | 大美SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_8 |  | com_alarm_16 | OPRD1: S09//1MTR/96B1; OPRD2: S09//1MTR/TRA; OPRD3: S09//1MTR/63Q; OPRD4: S09//1MTR/96PA; OPRD5: S09//1MTR/87A; OPRD6: S09//1MTR/51ZA; OPRD7: S09//1MTR/96B2; OPRD8: S09//1MTR/96D; OPRD9: S09//2MTR/96B2; OPRD10: S09//2MTR/96D; OPRD11: S09//2MTR/63Q; OPRD12: S09//2MTR/96B1; OPRD13: S09//2MTR/87A; OPRD14: S09//2MTR/51ZA; OPRD15: S09//2MTR/96PA; OPRD16: S09//2MTR/TRA
S09 | 大美SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S09_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S09//1MTR/TRF; OPRD2: S09//2MTR/TRF
S09 | 大美SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S09_A1 | [17 empty] | lamp2CC | OPRD1: S09/0/RTU/RTU_R_L
S09 | 大美SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S09_A1 | [17 empty] | lamp2CC | OPRD1: S09/0/StaDev/PSA
S09 | 大美SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S09_A1 | [17 empty] | lamp2CC | OPRD1: S09/0/StaDev/PSF
S09 | 大美SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S09_A1 | [17 empty] | lamp2CC | OPRD1: S09/0/StaDev/DCA
S09 | 大美SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S09_A1 | [17 empty] | lamp2CC | OPRD1: S09/0/StaDev/DCE
S09 | 大美SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S09_D1 | [17 empty] | lamp2CC | OPRD1: S09/69/ComPoint/CBA
S09 | 大美SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S09_D1 | [17 empty] | lamp2CC | OPRD1: S09/69/ComPoint/CBF
S09 | 大美SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S09_D1 | [17 empty] | lamp2CC | OPRD1: S09/69/ComPoint/ABS_89A
S09 | 大美SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69IEDAL |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S09_D1 | [17 empty] | lamp2CC | OPRD1: S09/69/ComPoint/IRFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S09 | 大美SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 大美SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S09/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 大美SS.610_AMP | 建大線 AMP | LINE69 | S09/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 大美SS.620_AMP | 雲林二路 AMP | LINE69 | S09/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 大美SS.640_AMP | 濁水線 AMP | LINE69 | S09/69/640/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | I | [25 empty] | ADCS_N | [8 empty] | 大美SS.720_AMP | 雲林ㄧ路 AMP | LINE69 | S09/69/720/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S09 | 大美SS | 0 |  |  |  |  | 美一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美一線KVA | 11KV美一線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美一線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美一線KW | 11KV美一線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美七線KVA | 11KV美七線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美七線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美七線KW | 11KV美七線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美九線KVA | 11KV美九線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美九線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美九線KW | 11KV美九線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美二線KVA | 11KV美二線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美二線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美二線KW | 11KV美二線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美八線KVA | 11KV美八線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美八線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美八線KW | 11KV美八線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美十線KVA | 11KV美十線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美十線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美十線KW | 11KV美十線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美三線KVA | 11KV美三線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美三線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美三線KW | 11KV美三線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美五線KVA | 11KV美五線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美五線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美五線KW | 11KV美五線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美六線KVA | 11KV美六線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美六線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美六線KW | 11KV美六線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美四線KVA | 11KV美四線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  |  |  |  | 美四線KW | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.美四線KW | 11KV美四線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S09//1MTR/MVA |  | MVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_PF | #1MTR 功率因素 | DTR | S09//1MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S09//2MTR/MVA |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_PF | #2MTR 功率因素 | DTR | S09//2MTR/PF |  | RPDC_PF_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S09 | 大美SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S09/11/210/MVAR |  | SC_CAL_11 |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S09/11/220/MVAR |  | SC_CAL_11 |  |  | 32 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  | MTR_TOT | MTR |  | MVA | [25 empty] | ADCS_N | [8 empty] | 大美SS.MTR_TOT_MVA | MTR TOT MVA | DTR |  |  | MTR_PQ_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S09 | 大美SS | 69 | 69kV | 610_CB | 建大線(610_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.610_CB_1 | 610(建大線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 34 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 620_CB | 雲林二路(620_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.620_CB_1 | 620(雲林二路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 640_CB | 濁水線(640_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.640_CB_1 | 640(濁水線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 720_CB | 雲林ㄧ路(720_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.720_CB_1 | 720(雲林ㄧ路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 37 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 大美SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 38 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 大美SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 大美SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S09/0/CalcPoint/SUBA |  | STATION_FAULT_8 |  |  | 40 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 41 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | STATION_FAULT_2 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610_AMP | 建大線 | [27 empty] | ADCS_N | [8 empty] | 大美SS.610_AMP_A | 建大線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 43 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 610_AMP | 建大線 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.610_AMP_1 | 建大線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 44 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 620_AMP | 雲林二路 | [27 empty] | ADCS_N | [8 empty] | 大美SS.620_AMP_A | 雲林二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 45 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 620_AMP | 雲林二路 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.620_AMP_1 | 雲林二路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 640_AMP | 濁水線 | [27 empty] | ADCS_N | [8 empty] | 大美SS.640_AMP_A | 濁水線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 640_AMP | 濁水線 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.640_AMP_1 | 濁水線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 720_AMP | 雲林ㄧ路 | [27 empty] | ADCS_N | [8 empty] | 大美SS.720_AMP_A | 雲林ㄧ路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 69 | 69kV | 720_AMP | 雲林ㄧ路 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.720_AMP_1 | 雲林ㄧ路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | 1MTR_MVA | #1MTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_MVA_1 | #1MTR MVA 點燈 (D1) | DTR |  |  | MAP_SET |  |  | 51 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | 2MTR_MVA | #2MTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_MVA_1 | #2MTR MVA 點燈 (D1) | DTR |  |  | MAP_SET |  |  | 53 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 54 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  | L387A | L387A |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L387A_1 | 640大美濁水差動電驛動作警報(D1 | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L387CFA | L387CFA |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L387CFA_1 | 640大美濁水87RY通訊故障警報(D1 | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L3RYFA | L3RYFA |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L3RYFA_1 | 640大美濁水線電驛故障警報(D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 57 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L287A | 610大美建大線差動電驛動作 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L287A_1 | 610大美建大線差動電驛動作 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 58 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L287CFA | 610大美建大線87RY通訊故障 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L287CFA_1 | 610大美建大線87RY通訊故障 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 59 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L2RYFA | 610大美建大線電驛故障警報 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.L2RYFA_1 | 610大美建大線電驛故障警報 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 60 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐 |  | 建大莿桐KVAR | [14 empty] | 0001 | [8 empty] | KVAR_-6000_6000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐KVAR | 11KV建大莿桐 KVAR | FEEDER |  |  |  |  | DNP | 61 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐 |  | 建大莿桐A1 | [14 empty] | 0002 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐A1 | 11KV建大莿桐 R相AMP | FEEDER |  |  |  |  | DNP | 62 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐 |  | 建大莿桐A2 | [14 empty] | 0003 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐A2 | 11KV建大莿桐 S相AMP | FEEDER |  |  |  |  | DNP | 63 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐 |  | 建大莿桐A3 | [14 empty] | 0004 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐A3 | 11KV建大莿桐 T相AMP | FEEDER |  |  |  |  | DNP | 64 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | KV1 | [14 empty] | 0005 | [8 empty] | kV_-9_9(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_KV1 | 11KV建大莿桐(XK29) VR | OTHER | S09/11/XK29/V_R |  |  |  | DNP | 65 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | KV2 | [14 empty] | 0006 | [8 empty] | kV_-9_9(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_KV2 | 11KV建大莿桐(XK29) VS | OTHER | S09/11/XK29/V_S |  |  |  | DNP | 66 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | KV3 | [14 empty] | 0007 | [8 empty] | kV_-9_9(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_KV3 | 11KV建大莿桐(XK29) VT | OTHER | S09/11/XK29/V_T |  |  |  | DNP | 67 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | KW | [14 empty] | 0000 | [8 empty] | KW_-6000_6000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_KW | 11KV建大莿桐(XK29) KW | OTHER | S09/11/XK29/KW |  |  |  | DNP | 68 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
S09 | 大美SS | 0 |  |  |  |  | 建大莿桐59V0 | [14 empty] | 0002 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐59V0 | 11KV建大莿桐(XK29)59V0 | OTHER | S09/11/XK29/59V0A |  |  |  | DNP | 69 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 建大莿桐 | 建大莿桐 |  | 81A | [14 empty] | 0005 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_81A | 11KV建大莿桐(XK29)81A | OTHER | S09/11/XK29/81AS1 |  |  |  | DNP | 70 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | CB | [14 empty] | 0000 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_CB | 11KV建大莿桐(XK29) CB | OTHER |  |  |  |  | DNP | 71 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 建大莿桐 | 建大莿桐 |  | CFA | [14 empty] | 1031 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_CFA | 11KV建大莿桐(XK29)通訊警報 | OTHER | S09/11/XK29/CFA |  |  |  | DNP | 72 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | DS1 | 建大莿桐 | [13 empty] | 1024 | 1025 | [9 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_DS | 11KV建大莿桐(XK29) DS | OTHER | S09/11/XK29/DS1 |  |  |  | DNP | 73 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 0 |  | 建大莿桐 | 建大莿桐 |  | GDA | [14 empty] | 0004 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_GDA | 11KV建大莿桐(XK29)GDA | OTHER |  |  |  |  | DNP | 74 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 建大莿桐 | 建大莿桐 |  | PHA | [14 empty] | 0003 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_PHA | 11KV建大莿桐(XK29)PHA | OTHER |  |  |  |  | DNP | 75 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 建大莿桐 | 建大莿桐(XK29) |  | PTDS | [14 empty] | 1026 | 1027 | [9 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_PTDS | 11KV建大莿桐(XK29) PTDS | OTHER | S09/11/XK29/PTDS |  |  |  | DNP | 76 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 0 |  | 建大莿桐 | 建大莿桐 |  | RYFA | [14 empty] | 0001 | [10 empty] | DDCS1_1 | [8 empty] | 大美SS.建大莿桐_RYA | 11KV建大莿桐(XK29)27/59 | OTHER | S09/11/XK29/UVA |  |  |  | DNP | 77 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S09/0/RTU/ADCH1 |  |  |  | CDC | 78 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S09/0/RTU/ADCH2 |  |  |  | CDC | 79 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S09/0/RTU/ADCH3 |  |  |  | CDC | 80 | GENERICAIPoint | SS110_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S09/0/RTU/ADCL1 |  |  |  | CDC | 81 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S09/0/RTU/ADCL2 |  |  |  | CDC | 82 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S09/0/RTU/ADCL3 |  |  |  | CDC | 83 | GENERICAIPoint | SS110_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S09 | 大美SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S09/69/1BUS/V |  |  |  | CDC | 84 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S09 | 大美SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S09/11/1BUS/V |  |  |  | CDC | 85 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S09/11/2BUS/V |  |  |  | CDC | 86 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.610_MW | 建大線 MW | LINE69 | S09/69/610/MW |  |  |  | CDC | 87 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.610_MVAR | 建大線 MVAR | LINE69 | S09/69/610/MVAR |  |  |  | CDC | 88 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.620_MW | 雲林二路 MW | LINE69 | S09/69/620/MW |  |  |  | CDC | 89 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.620_MVAR | 雲林二路 MVAR | LINE69 | S09/69/620/MVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.640_MW | 濁水線 MW | LINE69 | S09/69/640/MW |  |  |  | CDC | 91 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.640_MVAR | 濁水線 MVAR | LINE69 | S09/69/640/MVAR |  |  |  | CDC | 92 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.720_MW | 雲林ㄧ路 MW | LINE69 | S09/69/720/MW |  |  |  | CDC | 93 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大美SS.720_MVAR | 雲林ㄧ路 MVAR | LINE69 | S09/69/720/MVAR |  |  |  | CDC | 94 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美一線 | 美一線 |  | 美一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美一線KVAR | 11KV美一線 KVAR | FEEDER | S09/11/XK21/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美一線 | 美一線 |  | 美一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美一線A1 | 11KV美一線 R相AMP | FEEDER | S09/11/XK21/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美一線 | 美一線 |  | 美一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美一線A2 | 11KV美一線 S相AMP | FEEDER | S09/11/XK21/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美一線 | 美一線 |  | 美一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美一線A3 | 11KV美一線 T相AMP | FEEDER | S09/11/XK21/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美一線 | 美一線 |  | 美一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美一線A0 | 11KV美一線 N相AMP | FEEDER | S09/11/XK21/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美七線 | 美七線 |  | 美七線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美七線KVAR | 11KV美七線 KVAR | FEEDER | S09/11/XK27/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美七線 | 美七線 |  | 美七線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美七線A1 | 11KV美七線 R相AMP | FEEDER | S09/11/XK27/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美七線 | 美七線 |  | 美七線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美七線A2 | 11KV美七線 S相AMP | FEEDER | S09/11/XK27/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美七線 | 美七線 |  | 美七線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美七線A3 | 11KV美七線 T相AMP | FEEDER | S09/11/XK27/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美七線 | 美七線 |  | 美七線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美七線A0 | 11KV美七線 N相AMP | FEEDER | S09/11/XK27/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美九線 | 美九線 |  | 美九線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美九線KVAR | 11KV美九線 KVAR | FEEDER | S09/11/XK29/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美九線 | 美九線 |  | 美九線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美九線A1 | 11KV美九線 R相AMP | FEEDER | S09/11/XK29/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美九線 | 美九線 |  | 美九線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美九線A2 | 11KV美九線 S相AMP | FEEDER | S09/11/XK29/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美九線 | 美九線 |  | 美九線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美九線A3 | 11KV美九線 T相AMP | FEEDER | S09/11/XK29/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美九線 | 美九線 |  | 美九線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美九線A0 | 11KV美九線 N相AMP | FEEDER | S09/11/XK29/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美二線 | 美二線 |  | 美二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美二線KVAR | 11KV美二線 KVAR | FEEDER | S09/11/XK22/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美二線 | 美二線 |  | 美二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美二線A1 | 11KV美二線 R相AMP | FEEDER | S09/11/XK22/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美二線 | 美二線 |  | 美二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美二線A2 | 11KV美二線 S相AMP | FEEDER | S09/11/XK22/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美二線 | 美二線 |  | 美二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美二線A3 | 11KV美二線 T相AMP | FEEDER | S09/11/XK22/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美二線 | 美二線 |  | 美二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美二線A0 | 11KV美二線 N相AMP | FEEDER | S09/11/XK22/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美八線 | 美八線 |  | 美八線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美八線KVAR | 11KV美八線 KVAR | FEEDER | S09/11/XK28/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美八線 | 美八線 |  | 美八線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美八線A1 | 11KV美八線 R相AMP | FEEDER | S09/11/XK28/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美八線 | 美八線 |  | 美八線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美八線A2 | 11KV美八線 S相AMP | FEEDER | S09/11/XK28/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美八線 | 美八線 |  | 美八線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美八線A3 | 11KV美八線 T相AMP | FEEDER | S09/11/XK28/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美八線 | 美八線 |  | 美八線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美八線A0 | 11KV美八線 N相AMP | FEEDER | S09/11/XK28/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美十線 | 美十線 |  | 美十線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美十線KVAR | 11KV美十線 KVAR | FEEDER | S09/11/XK30/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美十線 | 美十線 |  | 美十線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美十線A1 | 11KV美十線 R相AMP | FEEDER | S09/11/XK30/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美十線 | 美十線 |  | 美十線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美十線A2 | 11KV美十線 S相AMP | FEEDER | S09/11/XK30/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美十線 | 美十線 |  | 美十線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美十線A3 | 11KV美十線 T相AMP | FEEDER | S09/11/XK30/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美十線 | 美十線 |  | 美十線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美十線A0 | 11KV美十線 N相AMP | FEEDER | S09/11/XK30/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美三線 | 美三線 |  | 美三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美三線KVAR | 11KV美三線 KVAR | FEEDER | S09/11/XK23/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美三線 | 美三線 |  | 美三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美三線A1 | 11KV美三線 R相AMP | FEEDER | S09/11/XK23/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美三線 | 美三線 |  | 美三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美三線A2 | 11KV美三線 S相AMP | FEEDER | S09/11/XK23/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美三線 | 美三線 |  | 美三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美三線A3 | 11KV美三線 T相AMP | FEEDER | S09/11/XK23/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美三線 | 美三線 |  | 美三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美三線A0 | 11KV美三線 N相AMP | FEEDER | S09/11/XK23/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美五線 | 美五線 |  | 美五線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美五線KVAR | 11KV美五線 KVAR | FEEDER | S09/11/XK25/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美五線 | 美五線 |  | 美五線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美五線A1 | 11KV美五線 R相AMP | FEEDER | S09/11/XK25/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美五線 | 美五線 |  | 美五線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美五線A2 | 11KV美五線 S相AMP | FEEDER | S09/11/XK25/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美五線 | 美五線 |  | 美五線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美五線A3 | 11KV美五線 T相AMP | FEEDER | S09/11/XK25/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美五線 | 美五線 |  | 美五線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美五線A0 | 11KV美五線 N相AMP | FEEDER | S09/11/XK25/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美六線 | 美六線 |  | 美六線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美六線KVAR | 11KV美六線 KVAR | FEEDER | S09/11/XK26/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美六線 | 美六線 |  | 美六線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美六線A1 | 11KV美六線 R相AMP | FEEDER | S09/11/XK26/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美六線 | 美六線 |  | 美六線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美六線A2 | 11KV美六線 S相AMP | FEEDER | S09/11/XK26/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美六線 | 美六線 |  | 美六線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美六線A3 | 11KV美六線 T相AMP | FEEDER | S09/11/XK26/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美六線 | 美六線 |  | 美六線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美六線A0 | 11KV美六線 N相AMP | FEEDER | S09/11/XK26/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美四線 | 美四線 |  | 美四線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美四線KVAR | 11KV美四線 KVAR | FEEDER | S09/11/XK24/KVAR |  |  |  | CDC | 140 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美四線 | 美四線 |  | 美四線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美四線A1 | 11KV美四線 R相AMP | FEEDER | S09/11/XK24/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美四線 | 美四線 |  | 美四線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美四線A2 | 11KV美四線 S相AMP | FEEDER | S09/11/XK24/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美四線 | 美四線 |  | 美四線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美四線A3 | 11KV美四線 T相AMP | FEEDER | S09/11/XK24/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | 美四線 | 美四線 |  | 美四線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.美四線A0 | 11KV美四線 N相AMP | FEEDER | S09/11/XK24/I_N |  |  |  | CDC | 144 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S09/11/TIE1/I_R |  |  |  | CDC | 145 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S09/11/TIE1/I_S |  |  |  | CDC | 146 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S09/11/TIE1/I_T |  |  |  | CDC | 147 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_MW | #1MTR二次側 MW | DTR | S09/11/M1/MW |  |  |  | CDC | 148 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S09/11/M1/MVAR |  |  |  | CDC | 149 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S09/11/M1/I_R |  |  |  | CDC | 150 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S09/11/M1/I_S |  |  |  | CDC | 151 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S09/11/M1/I_T |  |  |  | CDC | 152 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_OIL | #1MTR 油溫 | DTR | S09//1MTR/OilTemp |  |  |  | CDC | 153 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_COIL | #1MTR 線溫 | DTR | S09//1MTR/CoilTemp |  |  |  | CDC | 154 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S09//1MTR/TapPosMv |  |  |  | CDC | 155 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_MW | #2MTR二次側 MW | DTR | S09/11/M2/MW |  |  |  | CDC | 156 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S09/11/M2/MVAR |  |  |  | CDC | 157 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S09/11/M2/I_R |  |  |  | CDC | 158 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S09/11/M2/I_S |  |  |  | CDC | 159 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S09/11/M2/I_T |  |  |  | CDC | 160 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_OIL | #2MTR 油溫 | DTR | S09//2MTR/OilTemp |  |  |  | CDC | 161 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_COIL | #2MTR 線溫 | DTR | S09//2MTR/CoilTemp |  |  |  | CDC | 162 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS1_1 | [8 empty] | 大美SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S09//2MTR/TapPosMv |  |  |  | CDC | 163 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S09 | 大美SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS1_1 | [8 empty] | 大美SS.直流電源電壓 | 直流電源電壓 | OTHER | S09/0/StaDev/DCV |  |  |  | CDC | 164 | GENERICAIPoint | SS110_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 大美SS.610_PHA | 建大線(610) 相間RY | LINE69 | S09/69/610/PHA |  |  |  | CDC | 165 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 大美SS.610_GDA | 建大線(610) 接地RY | LINE69 | S09/69/610/GDA |  |  |  | CDC | 166 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 大美SS.610_CB | 610(建大線) CB | LINE69 | S09/69/610/CB |  |  |  | CDC | 167 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | 81AS | [17 empty] | 1-00-00 |  | 1-11 | [5 empty] | 69KV_N | [8 empty] | 大美SS.610_81A/S | (610) 81RY A/S | LINE69 | S09/69/610/81AS |  |  |  | CDC | 168 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | ABS1 | 611 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 大美SS.611_ABS | 611(建大線) ABS | LINE69 | S09/69/610/ABS1 |  |  |  | CDC | 169 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | ABS2 | 612 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 大美SS.612_ABS | 612(建大線) ABS | LINE69 | S09/69/610/ABS2 |  |  |  | CDC | 170 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 610 | 備用線(610) |  | E2 | 612E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 大美SS.612E_ES | 612E(建大線) ES | LINE69 | S09/69/610/ES2 |  |  |  | CDC | 171 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 大美SS.620_PHA | 雲林二路(620) 相間RY | LINE69 | S09/69/620/PHA |  |  |  | CDC | 172 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 大美SS.620_GDA | 雲林二路(620) 接地RY | LINE69 | S09/69/620/GDA |  |  |  | CDC | 173 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 大美SS.620_CB | 620(雲林二路) CB | LINE69 | S09/69/620/CB |  |  |  | CDC | 174 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | ABS1 | 621 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 大美SS.621_ABS | 621(雲林二路) ABS | LINE69 | S09/69/620/ABS1 |  |  |  | CDC | 175 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | ABS2 | 622 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 大美SS.622_ABS | 622(雲林二路) ABS | LINE69 | S09/69/620/ABS2 |  |  |  | CDC | 176 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | E2 | 622E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 大美SS.622E_ES | 622E(雲林二路) ES | LINE69 | S09/69/620/ES2 |  |  |  | CDC | 177 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 大美SS.640_PHA | 濁水線(640) 相間RY | LINE69 | S09/69/640/PHA |  |  |  | CDC | 178 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 大美SS.640_GDA | 濁水線(640) 接地RY | LINE69 | S09/69/640/GDA |  |  |  | CDC | 179 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 大美SS.640_CB | 640(濁水線) CB | LINE69 | S09/69/640/CB |  |  |  | CDC | 180 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | ABS1 | 641 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 大美SS.641_ABS | 641(濁水線) ABS | LINE69 | S09/69/640/ABS1 |  |  |  | CDC | 181 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | ABS2 | 642 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 大美SS.642_ABS | 642(濁水線) ABS | LINE69 | S09/69/640/ABS2 |  |  |  | CDC | 182 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 640 | 濁水線(640) |  | E2 | 642E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 大美SS.642E_ES | 642E(濁水線) ES | LINE69 | S09/69/640/ES2 |  |  |  | CDC | 183 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 大美SS.720_PHA | 雲林ㄧ路(720) 相間RY | LINE69 | S09/69/720/PHA |  |  |  | CDC | 184 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 大美SS.720_GDA | 雲林ㄧ路(720) 接地RY | LINE69 | S09/69/720/GDA |  |  |  | CDC | 185 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 大美SS.720_CB | 720(雲林ㄧ路) CB | LINE69 | S09/69/720/CB |  |  |  | CDC | 186 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | ABS1 | 721 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 大美SS.721_ABS | 721(雲林ㄧ路) ABS | LINE69 | S09/69/720/ABS1 |  |  |  | CDC | 187 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | ABS2 | 722 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 大美SS.722_ABS | 722(雲林ㄧ路) ABS | LINE69 | S09/69/720/ABS2 |  |  |  | CDC | 188 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | E2 | 722E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 大美SS.722E_ES | 722E(雲林ㄧ路) ES | LINE69 | S09/69/720/ES2 |  |  |  | CDC | 189 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_PHA | 11KV美一線(XK21) 相間RY | FEEDER | S09/11/XK21/PHA |  |  |  | CDC | 190 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_GDA | 11KV美一線(XK21) 接地RY | FEEDER | S09/11/XK21/GDA |  |  |  | CDC | 191 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_79UL | 11KV美一線(XK21) 79RY U/L | FEEDER | S09/11/XK21/79UL |  |  |  | CDC | 192 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK21 | 美一線(XK21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_ADJ | 11KV美一線(XK21) LCO分流器 U/L | FEEDER | S09/11/XK21/ADJ |  |  |  | CDC | 193 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK21 | XK21(11KV美一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_CB | XK21(11KV美一線) CB | FEEDER | S09/11/XK21/CB |  |  |  | CDC | 194 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_PHA | 11KV美二線(XK22) 相間RY | FEEDER | S09/11/XK22/PHA |  |  |  | CDC | 195 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_GDA | 11KV美二線(XK22) 接地RY | FEEDER | S09/11/XK22/GDA |  |  |  | CDC | 196 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_79UL | 11KV美二線(XK22) 79RY U/L | FEEDER | S09/11/XK22/79UL |  |  |  | CDC | 197 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK22 | 美二線(XK22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_ADJ | 11KV美二線(XK22) LCO分流器 U/L | FEEDER | S09/11/XK22/ADJ |  |  |  | CDC | 198 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK22 | XK22(11KV美二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_CB | XK22(11KV美二線) CB | FEEDER | S09/11/XK22/CB |  |  |  | CDC | 199 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_PHA | 11KV美三線(XK23) 相間RY | FEEDER | S09/11/XK23/PHA |  |  |  | CDC | 200 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_GDA | 11KV美三線(XK23) 接地RY | FEEDER | S09/11/XK23/GDA |  |  |  | CDC | 201 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_79UL | 11KV美三線(XK23) 79RY U/L | FEEDER | S09/11/XK23/79UL |  |  |  | CDC | 202 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK23 | 美三線(XK23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_ADJ | 11KV美三線(XK23) LCO分流器 U/L | FEEDER | S09/11/XK23/ADJ |  |  |  | CDC | 203 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK23 | XK23(11KV美三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_CB | XK23(11KV美三線) CB | FEEDER | S09/11/XK23/CB |  |  |  | CDC | 204 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_PHA | 11KV美四線(XK24) 相間RY | FEEDER | S09/11/XK24/PHA |  |  |  | CDC | 205 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_GDA | 11KV美四線(XK24) 接地RY | FEEDER | S09/11/XK24/GDA |  |  |  | CDC | 206 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_79UL | 11KV美四線(XK24) 79RY U/L | FEEDER | S09/11/XK24/79UL |  |  |  | CDC | 207 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK24 | 美四線(XK24) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_ADJ | 11KV美四線(XK24) LCO分流器 U/L | FEEDER | S09/11/XK24/ADJ |  |  |  | CDC | 208 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK24 | XK24(11KV美四線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_CB | XK24(11KV美四線) CB | FEEDER | S09/11/XK24/CB |  |  |  | CDC | 209 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_PHA | 11KV美五線(XK25) 相間RY | FEEDER | S09/11/XK25/PHA |  |  |  | CDC | 210 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_GDA | 11KV美五線(XK25) 接地RY | FEEDER | S09/11/XK25/GDA |  |  |  | CDC | 211 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_79UL | 11KV美五線(XK25) 79RY U/L | FEEDER | S09/11/XK25/79UL |  |  |  | CDC | 212 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK25 | 美五線(XK25) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_ADJ | 11KV美五線(XK25) LCO分流器 U/L | FEEDER | S09/11/XK25/ADJ |  |  |  | CDC | 213 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK25 | XK25(11KV美五線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_CB | XK25(11KV美五線) CB | FEEDER | S09/11/XK25/CB |  |  |  | CDC | 214 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_PHA | 11KV美六線(XK26) 相間RY | FEEDER | S09/11/XK26/PHA |  |  |  | CDC | 215 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_GDA | 11KV美六線(XK26) 接地RY | FEEDER | S09/11/XK26/GDA |  |  |  | CDC | 216 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_79UL | 11KV美六線(XK26) 79RY U/L | FEEDER | S09/11/XK26/79UL |  |  |  | CDC | 217 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK26 | 美六線(XK26) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_ADJ | 11KV美六線(XK26) LCO分流器 U/L | FEEDER | S09/11/XK26/ADJ |  |  |  | CDC | 218 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK26 | XK26(11KV美六線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_CB | XK26(11KV美六線) CB | FEEDER | S09/11/XK26/CB |  |  |  | CDC | 219 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_PHA | 11KV美七線(XK27) 相間RY | FEEDER | S09/11/XK27/PHA |  |  |  | CDC | 220 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_GDA | 11KV美七線(XK27) 接地RY | FEEDER | S09/11/XK27/GDA |  |  |  | CDC | 221 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_79UL | 11KV美七線(XK27) 79RY U/L | FEEDER | S09/11/XK27/79UL |  |  |  | CDC | 222 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK27 | 美七線(XK27) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_ADJ | 11KV美七線(XK27) LCO分流器 U/L | FEEDER | S09/11/XK27/ADJ |  |  |  | CDC | 223 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK27 | XK27(11KV美七線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_CB | XK27(11KV美七線) CB | FEEDER | S09/11/XK27/CB |  |  |  | CDC | 224 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_PHA | 11KV美八線(XK28) 相間RY | FEEDER | S09/11/XK28/PHA |  |  |  | CDC | 225 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_GDA | 11KV美八線(XK28) 接地RY | FEEDER | S09/11/XK28/GDA |  |  |  | CDC | 226 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_79UL | 11KV美八線(XK28) 79RY U/L | FEEDER | S09/11/XK28/79UL |  |  |  | CDC | 227 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK28 | 美八線(XK28) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_ADJ | 11KV美八線(XK28) LCO分流器 U/L | FEEDER | S09/11/XK28/ADJ |  |  |  | CDC | 228 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK28 | XK28(11KV美八線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_CB | XK28(11KV美八線) CB | FEEDER | S09/11/XK28/CB |  |  |  | CDC | 229 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_PHA | 11KV美九線(XK29) 相間RY | FEEDER | S09/11/XK29/PHA |  |  |  | CDC | 230 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_GDA | 11KV美九線(XK29) 接地RY | FEEDER | S09/11/XK29/GDA |  |  |  | CDC | 231 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_79UL | 11KV美九線(XK29) 79RY U/L | FEEDER | S09/11/XK29/79UL |  |  |  | CDC | 232 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK29 | 美九線(XK29) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_ADJ | 11KV美九線(XK29) LCO分流器 U/L | FEEDER | S09/11/XK29/ADJ |  |  |  | CDC | 233 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK29 | XK29(11KV美九線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_CB | XK29(11KV美九線) CB | FEEDER | S09/11/XK29/CB |  |  |  | CDC | 234 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_PHA | 11KV美十線(XK30) 相間RY | FEEDER | S09/11/XK30/PHA |  |  |  | CDC | 235 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_GDA | 11KV美十線(XK30) 接地RY | FEEDER | S09/11/XK30/GDA |  |  |  | CDC | 236 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_79UL | 11KV美十線(XK30) 79RY U/L | FEEDER | S09/11/XK30/79UL |  |  |  | CDC | 237 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 11 | 11kV | XK30 | 美十線(XK30) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_ADJ | 11KV美十線(XK30) LCO分流器 U/L | FEEDER | S09/11/XK30/ADJ |  |  |  | CDC | 238 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S09 | 大美SS | 11 | 11kV | XK30 | XK30(11KV美十線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_CB | XK30(11KV美十線) CB | FEEDER | S09/11/XK30/CB |  |  |  | CDC | 239 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.TIE1_CB | 11KV TIE1 CB | TIE | S09/11/TIE1/CB |  |  |  | CDC | 240 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.TIE1_51A | 11KV TIE1 51RY | TIE | S09/11/TIE1/51A |  |  |  | CDC | 241 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S09/11/TIE1/51NA |  |  |  | CDC | 242 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.750_CB | 750(#1MTR) CB | DTR | S09/69/750/CB |  |  |  | CDC | 243 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.1M_CB | 1M(#1MTR) CB | DTR | S09/11/M1/CB |  |  |  | CDC | 244 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_51A | #1MTR 51RY | DTR | S09/69/750/51A |  |  |  | CDC | 245 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_51NA | #1MTR 51N RY | DTR | S09/69/750/51NA |  |  |  | CDC | 246 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S09//1MTR/51ZA |  |  |  | CDC | 247 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_87A | #1MTR 87RY | DTR | S09//1MTR/87A |  |  |  | CDC | 248 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S09//1MTR/87UL |  |  |  | CDC | 249 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S09/11/M1/51A |  |  |  | CDC | 250 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_TRA | #1MTR 重故障 | DTR | S09//1MTR/TRA |  |  |  | CDC | 251 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S09//1MTR/TRF |  |  |  | CDC | 252 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S09//1MTR/SupLocal |  |  |  | CDC | 253 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S09//1MTR/Tap Chan |  |  |  | CDC | 254 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.751_ABS | 751(#1MTR) ABS | DTR | S09/69/750/ABS1 |  |  |  | CDC | 255 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_96A | #1MTR 96P RY | DTR | S09//1MTR/96PA |  |  |  | CDC | 256 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S09//1MTR/OLTC_DLY |  |  |  | CDC | 257 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S09//1MTR/AC_Fault |  |  |  | CDC | 258 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.760_CB | 760(#2MTR) CB | DTR | S09/69/760/CB |  |  |  | CDC | 259 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.2MA_CB | 2MA(#2MTR) CB | DTR | S09/11/M2/CB |  |  |  | CDC | 260 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_51A | #2MTR 51RY | DTR | S09/69/760/51A |  |  |  | CDC | 261 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_51NA | #2MTR 51N RY | DTR | S09/69/760/51NA |  |  |  | CDC | 262 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S09//2MTR/51ZA |  |  |  | CDC | 263 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_87A | #2MTR 87RY | DTR | S09//2MTR/87A |  |  |  | CDC | 264 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S09//2MTR/87UL |  |  |  | CDC | 265 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S09/11/M2/51A |  |  |  | CDC | 266 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_TRA | #2MTR 重故障 | DTR | S09//2MTR/TRA |  |  |  | CDC | 267 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S09//2MTR/TRF |  |  |  | CDC | 268 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S09//2MTR/SupLocal |  |  |  | CDC | 269 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S09//2MTR/Tap Chan |  |  |  | CDC | 270 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.761_ABS | 761(#2MTR) ABS | DTR | S09/69/760/ABS1 |  |  |  | CDC | 271 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_96A | #2MTR 96P RY | DTR | S09//2MTR/96PA |  |  |  | CDC | 272 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S09//2MTR/OLTC_DLY |  |  |  | CDC | 273 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S09//2MTR/AC_Fault |  |  |  | CDC | 274 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.210_CB | 210(11KV #1SC) CB | SC | S09/11/210/CB |  |  |  | CDC | 275 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S09/11/210/Tap Chan |  |  |  | CDC | 276 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.210_SCA | 11KV #1SC 51,51N RY | SC | S09/11/210/SCA |  |  |  | CDC | 277 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S09/11/210/UVA |  |  |  | CDC | 278 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.220_CB | 220(11KV #2SC) CB | SC | S09/11/220/CB |  |  |  | CDC | 279 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S09/11/220/Tap Chan |  |  |  | CDC | 280 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.220_SCA | 11KV #2SC 51,51N RY | SC | S09/11/220/SCA |  |  |  | CDC | 281 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S09/11/220/UVA |  |  |  | CDC | 282 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 大美SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S09/69/1BUS/BUS_VUA |  |  |  | CDC | 283 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S09/11/ComPoint/CBA |  |  |  | CDC | 284 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S09/11/ComPoint/CBF |  |  |  | CDC | 285 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S09/69/ComPoint/ABS_89A |  |  |  | CDC | 286 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S09/69/ComPoint/CBA |  |  |  | CDC | 287 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S09/69/ComPoint/CBF |  |  |  | CDC | 288 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.81RY_A/S(1) | 81電驛動作,美二,三,六卸載 | OTHER | S09/0/StaDev/81AS1 |  |  |  | CDC | 289 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S09 | 大美SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S09/0/RTU/RTU_R_L |  |  |  | CDC | 290 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S09 | 大美SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.TEST_CB | TEST CB | OTHER | S09/0/RTU/Test_CB |  |  |  | CDC | 291 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.火災警報(1) | 火警-自行裝設 | OTHER | S09/0/StaDev/Fire1 |  |  |  | CDC | 292 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.火災警報(2) | 煙烙燼氣體自動滅火系統警報 | OTHER | S09/0/StaDev/Fire2 |  |  |  | CDC | 293 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-31-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.火災警報(3) | 水氣霧自動滅火系統警報 | OTHER | S09/0/StaDev/Fire3 |  |  |  | CDC | 294 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.其他重故障 | 變電所內其他重故障 | OTHER | S09/0/StaDev/PSA |  |  |  | CDC | 295 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S09/0/StaDev/PSF |  |  |  | CDC | 296 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-30-08 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.所內電源ACBA | 所內電源開關ACB警報 | OTHER | S09/0/StaDev/ACBA |  |  |  | CDC | 297 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S09/0/StaDev/CHG1 |  |  |  | CDC | 298 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.直流電源DCA | 直流電源NFB開關警報 | OTHER | S09/0/StaDev/DCA |  |  |  | CDC | 299 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S09/0/StaDev/DCE |  |  |  | CDC | 300 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S09/0/StaDev/OilLeak |  |  |  | CDC | 301 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S09/0/StaDev/3A5Other |  |  |  | CDC | 302 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S09/0/StaDev/4A5Other |  |  |  | CDC | 303 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S09/0/StaDev/5A5Other |  |  |  | CDC | 304 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S09/0/StaDev/CHG2 |  |  |  | CDC | 305 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S09/0/StaDev/CommACF |  |  |  | CDC | 306 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S09/0/StaDev/Burglar1 |  |  |  | CDC | 307 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S09/0/StaDev/Burglar2 |  |  |  | CDC | 308 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化防盜(3) | 無人化防盜(3) | OTHER | S09/0/StaDev/Burglar3 |  |  |  | CDC | 309 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S09/0/StaDev/Door1 |  |  |  | CDC | 310 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S09/0/StaDev/Door2 |  |  |  | CDC | 311 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S09/0/StaDev/Door3 |  |  |  | CDC | 312 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S09 | 大美SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.開關場照明(A) | 所內開關場照明 | OTHER | S09/0/StaDev/Lights1 |  |  |  | CDC | 313 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S09 | 大美SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS1_1 | [8 empty] | 大美SS.開關場照明(B) | 路燈照明 | OTHER | S09/0/StaDev/Lights2 |  |  |  | CDC | 314 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S09 | 大美SS | 0 |  |  |  |  | 水位警報#1 | [17 empty] | 1-34-14 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.水位警報#1 | 水位警報#1 | OTHER | S09/0/StaDev/Water1 |  |  |  | CDC | 315 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | 水位警報#2 | [17 empty] | 1-34-15 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.水位警報#2 | 水位警報#2 | OTHER | S09/0/StaDev/Water2 |  |  |  | CDC | 316 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | 全所43RS狀態 | [17 empty] | 1-35-13 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.全所43RS狀態 | 全所43RS狀態 | OTHER | S09/0/StaDev/1A5Other |  |  |  | CDC | 317 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  |  |  |  | 全所閘刀U/L | [17 empty] | 1-35-14 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.全所閘刀U/L | 全所閘刀U/L | OTHER | S09/0/StaDev/2A5Other |  |  |  | CDC | 318 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.安全監控 | 安全監控 | OTHER | S09/0/StaDev/Burglar |  |  |  | CDC | 319 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.門禁 | 門禁-自行裝設 | OTHER | S09/0/StaDev/Door |  |  |  | CDC | 320 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S09 | 大美SS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-32-14 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.火災警報(4) | MCSG空氣取樣警報 | OTHER | S09/0/StaDev/Fire4 |  |  |  | CDC | 321 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 69 | 69kV |  |  |  | 69IEDAL | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 大美SS.69IEDAL | 69KV IED故障警報 | OTHER | S09/69/ComPoint/IRFA |  |  |  | CDC | 322 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L187A | [17 empty] | 1-08-01 | [7 empty] | ADCS_N | [8 empty] | 大美SS.L187A | 雲林大美ㄧ路87RY動作警報 | OTHER | S09/69/720/87A |  |  |  | CDC | 323 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L187CFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 大美SS.L187CFA | 雲林大美ㄧ路87RY通訊故障警報 | OTHER | S09/69/720/87CFA |  |  |  | CDC | 324 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L187S | 雲林大美ㄧ路87RY |  | U/L | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 大美SS.L187S_U/L | 雲林大美ㄧ路87RY U/L | OTHER | S09/69/720/87UL |  |  |  | CDC | 325 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  |  |  |  | L487A | [17 empty] | 1-09-05 | [7 empty] | ADCS_N | [8 empty] | 大美SS.L487A | 雲林大美二路87RY動作警報 | OTHER | S09/69/620/87A |  |  |  | CDC | 326 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L487CFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 大美SS.L487CFA | 雲林大美二路87RY通訊故障警報 | OTHER | S09/69/620/87CFA |  |  |  | CDC | 327 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | L487S | 雲林大美二路87RY |  | U/L | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 大美SS.L487S_U/L | 雲林大美二路87RY U/L | OTHER | S09/69/620/87UL |  |  |  | CDC | 328 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  |  |  |  | #163Q | [17 empty] | 1-18-04 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#163Q | #1主變ULTC保護警報 | OTHER | S09//1MTR/63Q |  |  |  | CDC | 329 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #196B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#196B1 | #1主變撲氣電驛第ㄧ段警報 | OTHER | S09//1MTR/96B1 |  |  |  | CDC | 330 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #196B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#196B2 | #1主變撲氣電驛第二段警報 | OTHER | S09//1MTR/96B2 |  |  |  | CDC | 331 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #196D | [17 empty] | 1-18-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#196D | #1主變放壓裝置警報 | OTHER | S09//1MTR/96D |  |  |  | CDC | 332 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #196P | [17 empty] | 1-18-03 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#196P | #1主變衝擊油壓警報 | OTHER | S09//1MTR/96P |  |  |  | CDC | 333 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #263Q | [17 empty] | 1-19-01 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#263Q | #2主變ULTC保護警報 | OTHER | S09//2MTR/63Q |  |  |  | CDC | 334 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #296B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#296B1 | #2主變撲氣電驛第ㄧ段警報 | OTHER | S09//2MTR/96B1 |  |  |  | CDC | 335 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #296B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#296B2 | #2主變撲氣電驛第二段警報 | OTHER | S09//2MTR/96B2 |  |  |  | CDC | 336 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #296D | [17 empty] | 1-18-07 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#296D | #2主變放壓裝置警報 | OTHER | S09//2MTR/96D |  |  |  | CDC | 337 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #296P | [17 empty] | 1-19-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#296P | #2主變衝擊油壓警報 | OTHER | S09//2MTR/96P |  |  |  | CDC | 338 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L387A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L387A | 640大美濁水線差動電驛動作警報 | OTHER | S09/69/640/87A |  |  |  | CDC | 339 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L387CFA | [17 empty] | 1-32-05 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L387CFA | 640大美濁水線87RY通訊故障警報 | OTHER | S09/69/640/87CFA |  |  |  | CDC | 340 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L387S | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 大美SS.L387S | 640大美濁水線差動電驛設定 | OTHER | S09/69/640/87UL |  |  |  | CDC | 341 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  |  |  |  | L3RYFA | [17 empty] | 1-32-12 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L3RYFA | 640大美濁水線電驛故障警報 | OTHER | S09/69/640/RYFA |  |  |  | CDC | 342 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L287A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L287A | 610大美建大線差動電驛動作警報 | OTHER | S09/69/610/87A |  |  |  | CDC | 343 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L287CFA | [17 empty] | 1-32-03 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L287CFA | 610大美建大線87RY通訊故障警報 | OTHER | S09/69/610/87CFA |  |  |  | CDC | 344 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | L287S | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 大美SS.L287S | 610大美建大線差動電驛設定 | OTHER | S09/69/610/87UL |  |  |  | CDC | 345 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  |  |  |  | L2RYFA | [17 empty] | 1-32-11 | [7 empty] | 69KV_N | [8 empty] | 大美SS.L2RYFA | 610大美建大線電驛故障警報 | OTHER | S09/69/610/RYFA |  |  |  | CDC | 346 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #1IEDAL | [17 empty] | 1-33-13 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#1IEDAL | #1保護電驛IED故障警報 | OTHER | S09/0/ComPoint/IRFA |  |  |  | CDC | 347 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  |  |  |  | #2IEDAL | [17 empty] | 1-34-13 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.#2IEDAL | #2保護電驛IED故障警報 | OTHER | S09/0/ComPoint/1A5Other |  |  |  | CDC | 348 | GENERICDIPoint | SS110_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.1M_51NA | #1MTR二次側(1M) 51NRY | OTHER | S09/11/M1/51NA |  |  |  | CDC | 349 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS1_1 | [8 empty] | 大美SS.2M_51NA | #2MTR二次側(2M) 51NRY | OTHER | S09/11/M2/51NA |  |  |  | CDC | 350 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-14-00 |  | 1-43 | [5 empty] | DDCS1_2 | [8 empty] | 大美SS.390_CB | 390(#1SSTR) CB | OTHER | S09/11/390/CB |  |  |  | CDC | 351 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-14-01 | [7 empty] | DDCS1_2 | [8 empty] | 大美SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S09/11/390/51A |  |  |  | CDC | 352 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-14-02 | [7 empty] | DDCS1_2 | [8 empty] | 大美SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S09/11/390/51NA |  |  |  | CDC | 353 | GENERICDIPoint | SS110_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S09 | 大美SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 354 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS1_1 | [8 empty] | 大美SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 355 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S09 | 大美SS | 0 |  | XK21 | XK21_DS |  | DS1 | XK21_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_DS | XK21_DS (非取樣點) | FEEDER | S09/11/XK21/DS |  |  |  |  | 356 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK21 | XK21_ES |  | LE0 | XK21_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK21_ES | XK21_ES (非取樣點) | FEEDER | S09/11/XK21/ES |  |  |  |  | 357 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK22 | XK22_DS |  | DS1 | XK22_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_DS | XK22_DS (非取樣點) | FEEDER | S09/11/XK22/DS |  |  |  |  | 358 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK22 | XK22_ES |  | LE0 | XK22_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK22_ES | XK22_ES (非取樣點) | FEEDER | S09/11/XK22/ES |  |  |  |  | 359 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK23 | XK23_DS |  | DS1 | XK23_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_DS | XK23_DS (非取樣點) | FEEDER | S09/11/XK23/DS |  |  |  |  | 360 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK23 | XK23_ES |  | LE0 | XK23_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK23_ES | XK23_ES (非取樣點) | FEEDER | S09/11/XK23/ES |  |  |  |  | 361 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK24 | XK24_DS |  | DS1 | XK24_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_DS | XK24_DS (非取樣點) | FEEDER | S09/11/XK24/DS |  |  |  |  | 362 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK24 | XK24_ES |  | LE0 | XK24_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK24_ES | XK24_ES (非取樣點) | FEEDER | S09/11/XK24/ES |  |  |  |  | 363 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK25 | XK25_DS |  | DS1 | XK25_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_DS | XK25_DS (非取樣點) | FEEDER | S09/11/XK25/DS |  |  |  |  | 364 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK25 | XK25_ES |  | LE0 | XK25_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK25_ES | XK25_ES (非取樣點) | FEEDER | S09/11/XK25/ES |  |  |  |  | 365 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK26 | XK26_DS |  | DS1 | XK26_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_DS | XK26_DS (非取樣點) | FEEDER | S09/11/XK26/DS |  |  |  |  | 366 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK26 | XK26_ES |  | LE0 | XK26_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK26_ES | XK26_ES (非取樣點) | FEEDER | S09/11/XK26/ES |  |  |  |  | 367 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK27 | XK27_DS |  | DS1 | XK27_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_DS | XK27_DS (非取樣點) | FEEDER | S09/11/XK27/DS |  |  |  |  | 368 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK27 | XK27_ES |  | LE0 | XK27_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK27_ES | XK27_ES (非取樣點) | FEEDER | S09/11/XK27/ES |  |  |  |  | 369 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK28 | XK28_DS |  | DS1 | XK28_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_DS | XK28_DS (非取樣點) | FEEDER | S09/11/XK28/DS |  |  |  |  | 370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK28 | XK28_ES |  | LE0 | XK28_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK28_ES | XK28_ES (非取樣點) | FEEDER | S09/11/XK28/ES |  |  |  |  | 371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK29 | XK29_DS |  | DS1 | XK29_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_DS | XK29_DS (非取樣點) | FEEDER | S09/11/XK29/DS |  |  |  |  | 372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK29 | XK29_ES |  | LE0 | XK29_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK29_ES | XK29_ES (非取樣點) | FEEDER | S09/11/XK29/ES |  |  |  |  | 373 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | XK30 | XK30_DS |  | DS1 | XK30_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_DS | XK30_DS (非取樣點) | FEEDER | S09/11/XK30/DS |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | XK30 | XK30_ES |  | LE0 | XK30_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.XK30_ES | XK30_ES (非取樣點) | FEEDER | S09/11/XK30/ES |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | TIE1DS1 | TIE1DS1 |  | TIE1DS1 | TIE1DS1 | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.TIE1DS1 | TIE1DS1 (非取樣點) | TIE | S09/11/TIE1/D1 |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.750TE | 750TE (非取樣點) | DTR | S09/69/750/TE0 |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.750BE | 750BE (非取樣點) | DTR | S09/69/750/BE0 |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.1M_DS | 1M_DS (非取樣點) | DTR | S09/11/M1/DS1 |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.760TE | 760TE (非取樣點) | DTR | S09/69/760/TE0 |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.760BE | 760BE (非取樣點) | DTR | S09/69/760/BE0 |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S09/11/M2/DS |  |  |  |  | 382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.210ES | 210ES (非取樣點) | SC | S09/11/210/ES |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | 210DS | 210DS |  | 210DS | 210DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.210DS | 210DS (非取樣點) | SC | S09/11/210/DS |  |  |  |  | 384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 220ES | 220ES |  | 220ES | 220ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.220ES | 220ES (非取樣點) | SC | S09/11/220/ES |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | 220DS | 220DS |  | 220DS | 220DS | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.220DS | 220DS (非取樣點) | SC | S09/11/220/DS |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 大美SS.69B1E | 69B1E (非取樣點) | BUS | S09/69/1BUS/BE1 |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 388 | NotelDIPoint | [38 empty] | START/STOP | STOP
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | PW1UL | 720_PW1UL | [24 empty] | ADCS_N | [8 empty] | 大美SS.720_PW1UL | 雲林ㄧ路(720)PW1_UL(非取樣點) | LINE69 | [5 empty] | 389 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | PW2UL | 720_PW2UL | [24 empty] | ADCS_N | [8 empty] | 大美SS.720_PW2UL | 雲林ㄧ路(720)PW2_UL(非取樣點) | LINE69 | [5 empty] | 390 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S09 | 大美SS | 69 | 69kV | 720 | 雲林ㄧ路(720) |  | HCBUL | 720_HCBUL | [24 empty] | ADCS_N | [8 empty] | 大美SS.720_HCBUL | 雲林ㄧ路(720)HCB_UL(非取樣點) | LINE69 | [5 empty] | 391 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_N | [8 empty] | 大美SS.620_PW1UL | 雲林二路(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 392 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_N | [8 empty] | 大美SS.620_PW2UL | 雲林二路(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 393 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S09 | 大美SS | 69 | 69kV | 620 | 雲林二路(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_N | [8 empty] | 大美SS.620_HCBUL | 雲林二路(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 394 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S09 | 大美SS | 0 |  | TIE1ES | TIE1ES |  | LE0 | TIE1ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.TIE1ES | TIE1ES (非取樣點) | TIE | S09/11/TIE1/ES |  |  |  |  | 395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | DDCS1_2 | [8 empty] | 大美SS.391 | 391 (非取樣點) | OTHER | S09/11/390/D1 |  |  |  |  | 396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S09 | 大美SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | DDCS1_2 | [8 empty] | 大美SS.391E | 391E (非取樣點) | OTHER | S09/11/390/E1 |  |  |  |  | 397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S09 | 大美SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS1_1 | [8 empty] | 大美SS.1M_ES | 1M_ES (非取樣點) | DTR | S09/11/M1/ES |  |  |  |  | 398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo