## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 一號 BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S21_A1 | [8 empty] | 大寮SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S21 | 大寮SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0014 |  |  | 1-8E |  |  | SPARE |  |  | kV_-90_90(-2000_2000) | not found | B2/S21_A1 | [8 empty] | 大寮SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S21 | 大寮SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | ＃1 MTR | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | aaa | B2/S21_D1 | [8 empty] | 大寮SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | ＃2 MTR | KV | 二號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aba | B2/S21_D1 | [8 empty] | 大寮SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | SPARE |  |  | kV_-9_9(-2000_2000) | aca | B2/S21_D1 | [8 empty] | 大寮SS.11KV#2(臨)BKV | 11KV #2(臨)BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaab | B2/S21_A1 | [8 empty] | 大寮SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0256 |  |  | 1-31-13 |  |  | 69KV＃1 BUS | 6VUA | 69KV BUS衡相監視警報 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 640 | MW | 新營大寮二路有效電力 | MW_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.640_MW | 新營二路 MW | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 640 | MVAR | 新營大寮二路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.640_MVAR | 新營二路 MVAR | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 69KV 640 | MWH (+) | 640新營大寮二路線瓦時(正)計量值 |  |  | B2/S21_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 11 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 630 | MW | 大寮新塭線有效電力 | MW_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.630_MW | 新塭線 MW | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 630 | MVAR | 大寮新塭線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.630_MVAR | 新塭線 MVAR | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 69KV 630 | MWH (+) | 630大寮新塭線瓦時(正)計量值 |  |  | B2/S21_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 14 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 710 | MW | 新營大寮一路有效電力 | MW_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.710_MW | 新營一路 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 710 | MVAR | 新營大寮一路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.710_MVAR | 新營一路 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 69KV 710 | MWH (+) | 710新營大寮一路線瓦時(正)計量值 |  |  | B2/S21_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 640 | PHA | 新營大寮二路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_PHA | 新營二路(640) 相間RY | LINE69 |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 640 | GDA | 新營大寮二路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_GDA | 新營二路(640) 接地RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 630 | PHA | 大寮新塭線 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_PHA | 新塭線(630) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 630 | GDA | 大寮新塭線 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_GDA | 新塭線(630) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-02 |  |  | 710 | PHA | 新營大寮一路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_PHA | 新營一路(710) 相間RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-03 |  |  | 710 | GDA | 新營大寮一路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_GDA | 新營一路(710) 接地RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0A-05 |  |  | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630(臨)_PHA | 新塭(臨)線(630) 相間RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0A-06 |  |  | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630(臨)_GDA | 新塭(臨)線(630) 接地RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1BUS | L/P01S212/T2 |  |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 640 | CB ON/OFF | 新營大寮二路 |  | aaba | B2/S21_A1 | [8 empty] | 大寮SS.640_CB | 640(新營二路) CB | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1BUS | L/S21S32/T1 |  |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 630 | CB ON/OFF | 大寮新塭線 |  | aada | B2/S21_A1 | [8 empty] | 大寮SS.630_CB | 630(新塭線) CB | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1BUS | L/P01S211/T2 |  |  | 0075 |  | 0004 | 1-09-00 |  | 1-03 | 710 | CB ON/OFF | 新營大寮一路 |  | aafa | B2/S21_A1 | [8 empty] | 大寮SS.710_CB | 710(新營一路) CB | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0087 |  | 0007 | 1-0A-04 |  | 1-06 | SPARE |  |  |  | not found | B2/S21_A1 | [8 empty] | 大寮SS.630(臨)_CB | 630(新塭(臨)線) CB | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0363 | 364 | 0019 | 1-38-08 | 1-38-09 | 1-12 | 641 | ABS ON | 新營大寮二路BUS側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.641_DS | 641(新營二路) DS | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0365 | 366 | 0020 | 1-38-10 | 1-38-11 | 1-13 | 642 | ABS ON | 新營大寮二路線路側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.642_DS | 642(新營二路) DS | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | DS1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0369 | 370 | 0022 | 1-38-14 | 1-38-15 | 1-15 | 631 | ABS ON | 大寮新塭線BUS側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.631_DS | 631(新塭線) DS | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | DS2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0371 | 372 | 0023 | 1-39-00 | 1-39-01 | 1-16 | 632 | ABS ON | 大寮新塭線線路側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.632_DS | 632(新塭線) DS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | DS1 | 711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0375 | 376 | 0025 | 1-39-04 | 1-39-05 | 1-18 | 711 | ABS ON | 新營大寮一路BUS側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.711_DS | 711(新營一路) DS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | DS2 | 712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0377 | 378 | 0026 | 1-39-06 | 1-39-07 | 1-19 | 712 | ABS ON | 新營大寮一路線路側 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.712_DS | 712(新營一路) DS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | ABS1 | 361 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0393 | 394 | 0034 | 1-3A-06 | 1-3A-07 | 1-21 | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.631(臨)_ABS | 631(新塭(臨)線) ABS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | ABS2 | 362 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0395 | 396 | 0035 | 1-3A-08 | 1-3A-09 | 1-22 | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.632(臨)_ABS | 632(新塭(臨)線) ABS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | ES2 | 642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0367 | 368 | 0021 | 1-38-12 | 1-38-13 | 1-14 | 642E | ABS ON | 新營大寮二路接地組 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.642E_ES | 642E(新營二路) ES | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 39 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 40 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0373 | 374 | 0024 | 1-39-02 | 1-39-03 | 1-17 | 632E | ABS ON | 大寮新塭線接地組 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.632E_ES | 632E(新塭線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | ES2 | 712E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0379 | 380 | 0027 | 1-39-08 | 1-39-09 | 1-1A | 712E | ABS ON | 新營大寮一路接地組 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.712E_ES | 712E(新營一路) ES | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 45 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 46 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | ES2 | 362E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0397 | 398 | 0036 | 1-3A-10 | 1-3A-11 | 1-23 | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.632E(臨)_ES | 632E(新塭(臨)線) ES | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | LE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.632(臨)LE | 630LE (非取樣點) | LINE69 | [5 empty] | 48 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 360 | 新塭(臨)線(360) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_A1 | [8 empty] | 大寮SS.632(臨)BE | 632BE (非取樣點) | LINE69 | [5 empty] | 49 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JE21 | PHA | 大溝線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE21_PHA | 11KV大溝線(JE21) 相間RY | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JE21 | GDA | 大溝線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE21_GDA | 11KV大溝線(JE21) 接地RY | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0282 |  | 0061 | 1-33-07 |  | 1-3C | JE21 | 79S U/L | 大溝線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE21_79UL | 11KV大溝線(JE21) 79RY U/L | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0323 |  | 0113 | 1-36-00 |  | 1-70 | JE21 | ADJ(U/L) | 大溝線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE21_ADJ | 11KV大溝線(JE21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-03 |  |  | JE22 | PHA | 大塭線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE22_PHA | 11KV大塭線(JE22) 相間RY | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JE22 | GDA | 大塭線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE22_GDA | 11KV大塭線(JE22) 接地RY | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0283 |  | 0062 | 1-33-08 |  | 1-3D | JE22 | 79S U/L | 大塭線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE22_79UL | 11KV大塭線(JE22) 79RY U/L | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0324 |  | 0114 | 1-36-01 |  | 1-71 | JE22 | ADJ(U/L) | 大塭線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE22_ADJ | 11KV大塭線(JE22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JE23 | PHA | 大布線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE23_PHA | 11KV大布線(JE23) 相間RY | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0D-06 |  |  | JE23 | GDA | 大布線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE23_GDA | 11KV大布線(JE23) 接地RY | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0284 |  | 0063 | 1-33-09 |  | 1-3E | JE23 | 79S U/L | 大布線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE23_79UL | 11KV大布線(JE23) 79RY U/L | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0325 |  | 0115 | 1-36-02 |  | 1-72 | JE23 | ADJ(U/L) | 大布線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE23_ADJ | 11KV大布線(JE23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | JE24 | PHA | 大義線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE24_PHA | 11KV大義線(JE24) 相間RY | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | JE24 | GDA | 大義線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE24_GDA | 11KV大義線(JE24) 接地RY | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0285 |  | 0064 | 1-33-10 |  | 1-3F | JE24 | 79S U/L | 大義線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE24_79UL | 11KV大義線(JE24) 79RY U/L | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0326 |  | 0116 | 1-36-03 |  | 1-73 | JE24 | ADJ(U/L) | 大義線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE24_ADJ | 11KV大義線(JE24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-01 |  |  | JE25 | PHA | 大新線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE25_PHA | 11KV大新線(JE25) 相間RY | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | JE25 | GDA | 大新線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE25_GDA | 11KV大新線(JE25) 接地RY | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0286 |  | 0065 | 1-33-11 |  | 1-40 | JE25 | 79S U/L | 大新線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE25_79UL | 11KV大新線(JE25) 79RY U/L | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0327 |  | 0117 | 1-36-04 |  | 1-74 | JE25 | ADJ(U/L) | 大新線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE25_ADJ | 11KV大新線(JE25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JE26 | PHA | 大江線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE26_PHA | 11KV大江線(JE26) 相間RY | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | JE26 | GDA | 大江線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE26_GDA | 11KV大江線(JE26) 接地RY | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0298 |  | 0082 | 1-34-07 |  | 1-51 | JE26 | 79S U/L | 大江線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE26_79UL | 11KV大江線(JE26) 79RY U/L | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0328 |  | 0118 | 1-36-05 |  | 1-75 | JE26 | ADJ(U/L) | 大江線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE26_ADJ | 11KV大江線(JE26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | JE27 | PHA | 大華線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE27_PHA | 11KV大華線(JE27) 相間RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JE27 | GDA | 大華線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE27_GDA | 11KV大華線(JE27) 接地RY | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0299 |  | 0083 | 1-34-08 |  | 1-52 | JE27 | 79S U/L | 大華線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE27_79UL | 11KV大華線(JE27) 79RY U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0329 |  | 0119 | 1-36-06 |  | 1-76 | JE27 | ADJ(U/L) | 大華線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE27_ADJ | 11KV大華線(JE27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | JE28 | PHA | 大順線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE28_PHA | 11KV大順線(JE28) 相間RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | JE28 | GDA | 大順線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE28_GDA | 11KV大順線(JE28) 接地RY | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0300 |  | 0084 | 1-34-09 |  | 1-53 | JE28 | 79S U/L | 大順線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE28_79UL | 11KV大順線(JE28) 79RY U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0330 |  | 0120 | 1-36-07 |  | 1-77 | JE28 | ADJ(U/L) | 大順線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE28_ADJ | 11KV大順線(JE28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JE29 | PHA | 大龍線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE29_PHA | 11KV大龍線(JE29) 相間RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | JE29 | GDA | 大龍線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE29_GDA | 11KV大龍線(JE29) 接地RY | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0301 |  | 0085 | 1-34-10 |  | 1-54 | JE29 | 79S U/L | 大龍線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE29_79UL | 11KV大龍線(JE29) 79RY U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0331 |  | 0121 | 1-36-08 |  | 1-78 | JE29 | ADJ(U/L) | 大龍線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE29_ADJ | 11KV大龍線(JE29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | JE30 | PHA | 大海線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE30_PHA | 11KV大海線(JE30) 相間RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JE30 | GDA | 大海線 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE30_GDA | 11KV大海線(JE30) 接地RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0302 |  | 0086 | 1-34-11 |  | 1-55 | JE30 | 79S U/L | 大海線復閉電驛(使用 /閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE30_79UL | 11KV大海線(JE30) 79RY U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0332 |  | 0122 | 1-36-09 |  | 1-79 | JE30 | ADJ(U/L) | 大海線分流器(使用 / 閉鎖)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.JE30_ADJ | 11KV大海線(JE30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JE21/T1 |  |  | 0099 |  | 0053 | 1-0C-00 |  | 1-34 | JE21 | CB ON/OFF | 大溝線 11KV |  | aabb | B2/S21_D1 | [8 empty] | 大寮SS.JE21_CB | JE21(11KV大溝線) CB | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | D1 | 211_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.211_DS | 211_DS (非取樣點) | FEEDER | [5 empty] | 91 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | D2 | 2122_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.2122_DS | 2122_DS (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE21_ES | JE21_ES (非取樣點) | FEEDER | [5 empty] | 93 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JE22/T1 |  |  | 0100 |  | 0054 | 1-0C-01 |  | 1-35 | JE22 | CB ON/OFF | 大塭線 11KV |  | aacb | B2/S21_D1 | [8 empty] | 大寮SS.JE22_CB | JE22(11KV大塭線) CB | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | D1 | 221_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.221_DS | 221_DS (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE22_ES | JE22_ES (非取樣點) | FEEDER | [5 empty] | 96 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JE23/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | JE23 | CB ON/OFF | 大布線 11KV |  | aaeb | B2/S21_D1 | [8 empty] | 大寮SS.JE23_CB | JE23(11KV大布線) CB | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | D1 | 231_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.231_DS | 231_DS (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | D2 | 2322_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.2322_DS | 2322_DS (非取樣點) | FEEDER | [5 empty] | 99 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE23_ES | JE23_ES (非取樣點) | FEEDER | [5 empty] | 100 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JE24/T1 |  |  | 0102 |  | 0056 | 1-0C-03 |  | 1-37 | JE24 | CB ON/OFF | 大義線 11KV |  | aafb | B2/S21_D1 | [8 empty] | 大寮SS.JE24_CB | JE24(11KV大義線) CB | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | D1 | 241_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.241_DS | 241_DS (非取樣點) | FEEDER | [5 empty] | 102 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | D2 | 242_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.242_DS | 242_DS (非取樣點) | FEEDER | [5 empty] | 103 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE24_ES | JE24_ES (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JE25/T1 |  |  | 0103 |  | 0057 | 1-0C-04 |  | 1-38 | JE25 | CB ON/OFF | 大新線 11KV |  | aagb | B2/S21_D1 | [8 empty] | 大寮SS.JE25_CB | JE25(11KV大新線) CB | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | D1 | 251_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.251_DS | 251_DS (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | D2 | 252_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.252_DS | 252_DS (非取樣點) | FEEDER | [5 empty] | 107 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE25_ES | JE25_ES (非取樣點) | FEEDER | [5 empty] | 108 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JE26/T1 |  |  | 0121 |  | 0074 | 1-0E-06 |  | 1-49 | JE26 | CB ON/OFF | 大江線 11KV |  | abab | B2/S21_D1 | [8 empty] | 大寮SS.JE26_CB | JE26(11KV大江線) CB | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | D1 | 261_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.261_DS | 261_DS (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | D2 | 262_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.262_DS | 262_DS (非取樣點) | FEEDER | [5 empty] | 111 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE26_ES | JE26_ES (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JE27/T1 |  |  | 0122 |  | 0075 | 1-0E-07 |  | 1-4A | JE27 | CB ON/OFF | 大華線 11KV |  | abcb | B2/S21_D1 | [8 empty] | 大寮SS.JE27_CB | JE27(11KV大華線) CB | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | D1 | 271_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.271_DS | 271_DS (非取樣點) | FEEDER | [5 empty] | 114 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | D2 | 272_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.272_DS | 272_DS (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE27_ES | JE27_ES (非取樣點) | FEEDER | [5 empty] | 116 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JE28/T1 |  |  | 0123 |  | 0076 | 1-0F-00 |  | 1-4B | JE28 | CB ON/OFF | 大順線 11KV |  | abdb | B2/S21_D1 | [8 empty] | 大寮SS.JE28_CB | JE28(11KV大順線) CB | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | D1 | 281_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.281_DS | 281_DS (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | D2 | 282_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.282_DS | 282_DS (非取樣點) | FEEDER | [5 empty] | 119 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE28_ES | JE28_ES (非取樣點) | FEEDER | [5 empty] | 120 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JE29/T1 |  |  | 0124 |  | 0077 | 1-0F-01 |  | 1-4C | JE29 | CB ON/OFF | 大龍線 11KV |  | abeb | B2/S21_D1 | [8 empty] | 大寮SS.JE29_CB | JE29(11KV大龍線) CB | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | D1 | 291_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.291_DS | 291_DS (非取樣點) | FEEDER | [5 empty] | 122 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | D2 | 292_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.292_DS | 292_DS (非取樣點) | FEEDER | [5 empty] | 123 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE29_ES | JE29_ES (非取樣點) | FEEDER | [5 empty] | 124 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JE30/T1 |  |  | 0125 |  | 0078 | 1-0F-02 |  | 1-4D | JE30 | CB ON/OFF | 大海線 11KV |  | abfb | B2/S21_D1 | [8 empty] | 大寮SS.JE30_CB | JE30(11KV大海線) CB | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | D1 | 301_DS(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.301_DS | 301_DS (非取樣點) | FEEDER | [5 empty] | 126 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | D2 | 302_DS(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.302_DS | 302_DS (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.JE30_ES | JE30_ES (非取樣點) | FEEDER | [5 empty] | 128 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | ＃1 TIE | A1 | 一號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 129 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | ＃1 TIE | A2 | 一號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 130 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | ＃1 TIE | A3 | 一號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 131 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2BUS |  |  | 0104 |  | 0051 | 1-0C-05 |  | 1-32 | ＃1 TIE | CB ON/OFF | 一號聯絡斷路器 |  | zzzz | B2/S21_D1 | [8 empty] | 大寮SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 132 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | ＃1 TIE | PHA | 一號聯絡斷路器 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 133 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-04 |  |  | ＃1 TIE | GDA | 一號聯絡斷路器 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 134 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 135 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | TIE1(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | Point Empty | [7 empty] | 136 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | ＃1 MCB | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 137 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | ＃1 MCB | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 138 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | ＃1 MCB | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 139 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | ＃1 MCB | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 140 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | ＃1 MCB | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 141 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2 MCB | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 142 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | ＃2 MCB | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 143 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | ＃2 MCB | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 144 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | ＃2 MCB | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 145 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | ＃2 MCB | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 146 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | SPARE |  |  | MW_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_MW | #2(臨)MTR二次側 MW | DTR |  |  |  |  | CDC | 147 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | SPARE |  |  | MVAR_-36_36(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_MVAR | #2(臨)MTR二次側 MVAR | DTR |  |  |  |  | CDC | 148 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_A1 | #2(臨)MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 149 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_A2 | #2M(臨)MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 150 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_A3 | #2(臨)MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 151 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | ＃1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 152 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 153 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0058 | 1-9B |  | 1-39 | ＃1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 154 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | ＃1 MTR | MWH (+) | 一號主變瓦時(正)計量值 |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 155 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | ＃1 MTR | MVARH (+) | 一號主變乏時(正)計量值 |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 156 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | ＃2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 157 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | ＃2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 158 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0079 | 1-BF |  | 1-4E | ＃2 MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 159 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | ＃2 MTR | MWH (+) | 二號主變瓦時(正)計量值 |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 160 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | ＃2 MTR | MVARH (+) | 二號主變乏時(正)計量值 |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 161 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | SPARE |  |  | OIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_OIL | #2(臨)MTR 油溫 | DTR |  |  |  |  | CDC | 162 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | SPARE |  |  | COIL_-120_120(-2000_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_COIL | #2(臨)MTR 線溫 | DTR |  |  |  |  | CDC | 163 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-61 | SPARE |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_TAP | #2(臨)MTR OLTC TAP | DTR |  |  |  |  | CDC | 164 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 165 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 166 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/1BUS | T/1MTR |  |  | 0004 |  | 0049 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aacb | B3/S21_D1 | [8 empty] | 大寮SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 167 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 168 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 169 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/1BUS | T/2MTR |  |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aaeb | B3/S21_D1 | [8 empty] | 大寮SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 170 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 171 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 172 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0025 |  | 0089 | 1-02-06 |  | 1-58 | SPARE |  |  |  | not found | B3/S21_D1 | [8 empty] | 大寮SS.760(臨)_CB | 760(臨)(#2MTR) CB | DTR |  |  |  |  | CDC | 173 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.760(臨)TE | 760(臨)TE (非取樣點) | DTR | [5 empty] | 174 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S21_D1 | [8 empty] | 大寮SS.760(臨)BE | 760(臨)BE (非取樣點) | DTR | [5 empty] | 175 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | T/1MTR |  |  | 0005 |  | 0050 | 1-00-02 |  | 1-31 | ＃1 MCB | CB ON/OFF | 一號主變二次側 |  | aada | B2/S21_D1 | [8 empty] | 大寮SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 176 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | T/2MTR |  |  | 0014 |  | 0070 | 1-01-03 |  | 1-45 | ＃2 MCB | CB ON/OFF | 二號主變二次側 |  | abba | B2/S21_D1 | [8 empty] | 大寮SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 177 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750 | 51A | 一號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 178 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | 750 | 51NA | 一號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 179 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | ＃1 MTR | 51ZA | 一號主變 51Z RY |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 180 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | ＃1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 181 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 1-33-03 |  |  | ＃1 MTR | 187S U/L | 一號主變差動電驛(使用/閉鎖)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 182 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  | 0066 | 1-0C-06 |  | 1-41 | ＃1 MCB | 81RY RESET | 一號低頻電驛(跳脫＃1 MCB) |  |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 183 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | 760 | 51A | 二號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 184 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | 760 | 51NA | 二號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | ＃2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 186 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | ＃2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 187 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-34-03 |  |  | ＃2 MTR | 287S U/L | 二號主變差動電驛(使用 /閉鎖)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 188 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_51A | #2(臨)MTR 51RY | DTR |  |  |  |  | CDC | 189 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_51NA | #2(臨)MTR 51N RY | DTR |  |  |  |  | CDC | 190 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_51ZA | #2(臨)MTR 51Z RY | DTR |  |  |  |  | CDC | 191 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-04 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_87A | #2(臨)MTR 87RY | DTR |  |  |  |  | CDC | 192 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  |  | 1-35-03 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_87UL | #2(臨)MTR 87RY U/L | DTR |  |  |  |  | CDC | 193 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-00-07 |  |  | ＃1 MCB | 51A | 一號主變二次側 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 194 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 1-33-00 |  |  | ＃1 MTR | 1TRA | 一號主變重故障警報 |  | a | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 195 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-33-01 |  |  | ＃1 MTR | 1TRF | 一號主變輕故障警報 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 196 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-33-04 |  |  | ＃1 MTR | S/L | 一號主變OLTC(中心/現場)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 197 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0280 |  | 0059 | 1-33-05 |  | 1-3A | ＃1 MTR | A/M | 一號主變OLTC(自動 /手動)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 198 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S21 | 大寮SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-01 |  |  | ＃2 MCB | 51A | 二號主變二次側 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 199 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 1-34-00 |  |  | ＃2 MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 200 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0292 |  |  | 1-34-01 |  |  | ＃2 MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 201 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-34-04 |  |  | ＃2 MTR | S/L | 二號主變OLTC(中心 /現場)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 202 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0080 | 1-34-05 |  | 1-4F | ＃2 MTR | A/M | 二號主變OLTC(自動 /手動)指示 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 203 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-35-00 |  |  | SPARE |  |  |  | a | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_TRA | #2(臨)MTR 重故障 | DTR |  |  |  |  | CDC | 204 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0308 |  |  | 1-35-01 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_TRF | #2(臨)MTR 輕故障 | DTR |  |  |  |  | CDC | 205 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 1-35-04 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_S/L | #2(臨)MTR OLTC S/L | DTR |  |  |  |  | CDC | 206 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0099 | 1-35-05 |  | 1-62 | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_A/M | #2(臨)MTR OLTC A/M | DTR |  |  |  |  | CDC | 207 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0355 | 356 | 0043 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | ＃1MTR 一號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 208 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0357 | 358 | 0044 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | ＃2MTR 二號主變一次側 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 209 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0359 | 360 | 0045 | 1-38-04 | 1-38-05 | 1-2C | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.761(臨)_ABS | 761(臨)(#2MTR) ABS | DTR |  |  |  |  | CDC | 210 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 211 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 212 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | ＃1 MTR | 96PA | 一號主變 96P RY |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 213 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 1-33-02 |  |  | ＃1 MTR | 148T | 一號主變OLTC遲滯警報 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 214 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-33-12 |  |  | ＃1 MTR | 127C | 一號主變AC電源欠壓 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 215 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 216 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 217 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | ＃2 MTR | 96PA | 二號主變 96P RY |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 218 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-34-02 |  |  | ＃2 MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 219 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 1-34-12 |  |  | ＃2 MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 220 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | M3 | #3MTR(M3) |  | D1 | 3M(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 221 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 222 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-03 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)MTR_96A | #2(臨)MTR 96P RY | DTR |  |  |  |  | CDC | 223 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0309 |  |  | 1-35-02 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)M_O遲滯 | #2(臨)MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 224 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-35-12 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2(臨)M_AC_F | #2(臨)MTR AC電源失效 | DTR |  |  |  |  | CDC | 225 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/1BUS | C/1SC |  |  | 0098 |  | 0052 | 1-0B-07 |  | 1-33 | ＃1 SC | CB ON/OFF | 一號 SC 11KV |  | aaab | B2/S21_D1 | [8 empty] | 大寮SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 226 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0281 |  | 0060 | 1-33-06 |  | 1-3B | ＃1 SC | A/M | 一號SC乏控器(自動 /手動)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 227 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 228 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/2BUS | C/2SC |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | ＃2 SC | CB ON/OFF | 二號 SC 11KV |  | abgb | B2/S21_D1 | [8 empty] | 大寮SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 229 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0297 |  | 0081 | 1-34-06 |  | 1-50 | ＃2 SC | A/M | 二號SC乏控器(自動 /手動)指示 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 230 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 231 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | ＃1 SC | SCA | 一號 SC 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 232 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-00 |  |  | ＃1 SC | UVA | 一號 SC 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 233 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | ＃2 SC | SCA | 二號 SC 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 234 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | ＃2 SC | UVA | 二號 SC 11KV |  |  | B2/S21_D1 | [8 empty] | 大寮SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 235 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 236 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 237 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 238 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S21_D1 | [8 empty] | 大寮SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 239 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪A I 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S21_D1 | [8 empty] | 大寮SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 240 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪A I 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S21_D1 | [8 empty] | 大寮SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 241 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S21_D1 | [8 empty] | 大寮SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 242 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S21_D1 | [8 empty] | 大寮SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 243 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0227 |  | 0001 | 1-30-00 |  | 1-00 | TEST CB | TSS | ON/OFF |  |  | ELEM/ALL | [8 empty] | 大寮SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 244 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0228 |  |  | 1-30-01 |  |  | RTU | L/R-S | LOCAL/REMOTE(STATUS) |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-30-02 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0230 |  |  | 1-30-03 |  |  | 通訊充電機 | CHG2 | 通訊充電機故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0231 |  |  | 1-30-04 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0233 |  | 0046 | 1-30-06 |  | 1-2D | 所內開關場 | FLA | 開關場照明 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0234 |  | 0047 | 1-30-07 |  | 1-2E | 所內配電盤 | FLB | 市區路燈照明 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-30-08 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0236 |  |  | 1-30-09 |  |  | 充油電纜 | OPA | 油壓電力電纜警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0237 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火災警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.火災警報(1) | [大寮]火警 | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Water1 | 所內水位輕警報 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0239 |  |  | 1-30-12 |  |  | 變電所內 | PSF | 所內水位輕警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.水位警報(1) | 所內水位輕警報 | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Water2 | 所內水位重警報 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0240 |  |  | 1-30-13 |  |  | 變電所內 | PSA | 所內水位重警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.水位警報(2) | 所內水位重警報 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0241 |  |  | 1-30-14 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0242 |  |  | 1-30-15 |  |  | 洩油池幫 | OWF | 洩油池幫警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0248 |  |  | 1-31-05 |  |  | 門禁警報(1) |  | 無人化門禁警報(1) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0249 |  |  | 1-31-06 |  |  | 門禁警報(2) |  | 無人化門禁警報(2) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0250 |  |  | 1-31-07 |  |  | 門禁警報(3) |  | 無人化門禁警報(3) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0252 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 | 6CBF | 69KV CB 輕警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 1-31-10 |  |  | 69KV CB 重故障 | 6CBA | 69KV CB 重警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0254 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 | 1CBF | 11KV CB NFB跳脫警報 |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-31-12 |  |  | 11KV CB 重故障 | 1CBA | 11KV CB NFB跳脫警報 |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 264 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-31-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 265 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-37-00 |  |  | 光纖通訊系統 | ACFA | 通訊設備AC故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 266 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0340 |  |  | 1-37-01 |  |  | 光纖通訊系統 | OLTEA | 通訊設備光纖主故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 267 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0341 |  |  | 1-37-02 |  |  | 光纖通訊系統 | OLTEF | 通訊設備光纖次故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 268 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 通訊PCM警報 |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0342 |  |  | 1-37-03 |  |  | 光纖通訊系統 | PCMA | 博碼調變器故障 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 269 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | ＃1 MCB | 51NA | 一號主變二次側 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.#1MAIN51NA | #1MAIN51NA | OTHER |  |  |  |  | CDC | 270 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | ＃2 MCB | 51NA | 二號主變二次側 |  |  | B2/S21_D1 | [8 empty] | 大寮SS.#2MAIN51NA | #2MAIN51NA | OTHER |  |  |  |  | CDC | 271 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0232 |  |  | 1-30-05 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 272 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0238 |  |  | 1-30-11 |  |  | 安全監控 | SUPA | 所內安全監控 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 273 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Fire2 | MCSG火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0243 |  |  | 1-31-00 |  |  | MCSG火警 |  | 無人化防火警報(1) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.MCSG火警 | MCSG火警 | OTHER |  |  |  |  | CDC | 274 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | MCSG_89A | MCSG系統故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0244 |  |  | 1-31-01 |  |  | MCSG系統故障 |  | 無人化防火警報(2) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.MCSG系統故障 | MCSG系統故障 | OTHER |  |  |  |  | CDC | 275 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | StaDev | 所內設施 |  | SCA | 69KVSC警報 | B2,B3,Element | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-31-08 |  |  | 69KV SC |  | 69KV SC 警報 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 276 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA | 69KVBUS#2VUA | B2,B3,Element | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-31-14 |  |  | 69KV＃2 BUS | 6VUA | 69KV BUS衡相監視警報 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER |  |  |  |  | CDC | 277 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Fire | 主變火警 | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0245 |  |  | 1-31-02 |  |  | 主變火警 |  | 無人化防盜警報(1) |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 278 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0246 |  |  | 1-31-03 |  |  | 細水霧故障 |  | 無人化防盜警報(2) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 279 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0247 |  |  | 1-31-04 |  |  | 細水霧噴灑 |  | 無人化防盜警報(3) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 280 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 維護運轉警報 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0354 |  |  | 1-37-15 |  |  | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 281 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 數據機重置 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0322 |  | 0088 | 1-35-15 |  | 1-57 | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.數據機重置 | 數據機重置 | OTHER |  |  |  |  | CDC | 282 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/RESET | RESET
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | DD_Light | 路燈電源監視 | Element | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 0344 |  |  | 1-37-05 |  |  | SPARE |  |  |  |  | B3/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 283 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1 MTR | 196B1 |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 284 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | #1 MTR | 196B2 |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 285 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1 MTR | 196D |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 286 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1 MTR | 196P |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 287 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1 MTR | 163Q |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 288 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2 MTR | 296B1 |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 289 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | #2 MTR | 296B2 |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 290 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2 MTR | 296D |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 291 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2 MTR | 296P |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 292 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2 MTR | 263Q |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 293 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | JE23 | VAR | 大布線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線KVAR | 11KV大布線 KVAR | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | JE23 | A1 | 大布線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線A1 | 11KV大布線 R相AMP | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | JE23 | A2 | 大布線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線A2 | 11KV大布線 S相AMP | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | JE23 | A3 | 大布線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線A3 | 11KV大布線 T相AMP | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | JE23 | NA | 大布線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線A0 | 11KV大布線 N相AMP | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | JE26 | VAR | 大江線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線KVAR | 11KV大江線 KVAR | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JE26 | A1 | 大江線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線A1 | 11KV大江線 R相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JE26 | A2 | 大江線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線A2 | 11KV大江線 S相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JE26 | A3 | 大江線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線A3 | 11KV大江線 T相AMP | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | JE26 | NA | 大江線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線A0 | 11KV大江線 N相AMP | FEEDER |  |  |  |  | CDC | 303 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JE30 | VAR | 大海線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線KVAR | 11KV大海線 KVAR | FEEDER |  |  |  |  | CDC | 304 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JE30 | A1 | 大海線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線A1 | 11KV大海線 R相AMP | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JE30 | A2 | 大海線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線A2 | 11KV大海線 S相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JE30 | A3 | 大海線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線A3 | 11KV大海線 T相AMP | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JE30 | NA | 大海線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線A0 | 11KV大海線 N相AMP | FEEDER |  |  |  |  | CDC | 308 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JE27 | VAR | 大華線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線KVAR | 11KV大華線 KVAR | FEEDER |  |  |  |  | CDC | 309 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JE27 | A1 | 大華線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線A1 | 11KV大華線 R相AMP | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JE27 | A2 | 大華線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線A2 | 11KV大華線 S相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JE27 | A3 | 大華線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線A3 | 11KV大華線 T相AMP | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JE27 | NA | 大華線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線A0 | 11KV大華線 N相AMP | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JE28 | VAR | 大順線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線KVAR | 11KV大順線 KVAR | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JE28 | A1 | 大順線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線A1 | 11KV大順線 R相AMP | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JE28 | A2 | 大順線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線A2 | 11KV大順線 S相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JE28 | A3 | 大順線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線A3 | 11KV大順線 T相AMP | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | JE28 | NA | 大順線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線A0 | 11KV大順線 N相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | JE22 | VAR | 大塭線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線KVAR | 11KV大塭線 KVAR | FEEDER |  |  |  |  | CDC | 319 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | JE22 | A1 | 大塭線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線A1 | 11KV大塭線 R相AMP | FEEDER |  |  |  |  | CDC | 320 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | JE22 | A2 | 大塭線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線A2 | 11KV大塭線 S相AMP | FEEDER |  |  |  |  | CDC | 321 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | JE22 | A3 | 大塭線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線A3 | 11KV大塭線 T相AMP | FEEDER |  |  |  |  | CDC | 322 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | JE22 | NA | 大塭線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線A0 | 11KV大塭線 N相AMP | FEEDER |  |  |  |  | CDC | 323 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | JE25 | VAR | 大新線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線KVAR | 11KV大新線 KVAR | FEEDER |  |  |  |  | CDC | 324 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | JE25 | A1 | 大新線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線A1 | 11KV大新線 R相AMP | FEEDER |  |  |  |  | CDC | 325 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | JE25 | A2 | 大新線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線A2 | 11KV大新線 S相AMP | FEEDER |  |  |  |  | CDC | 326 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JE25 | A3 | 大新線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線A3 | 11KV大新線 T相AMP | FEEDER |  |  |  |  | CDC | 327 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | JE25 | NA | 大新線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線A0 | 11KV大新線 N相AMP | FEEDER |  |  |  |  | CDC | 328 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | JE21 | VAR | 大溝線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線KVAR | 11KV大溝線 KVAR | FEEDER |  |  |  |  | CDC | 329 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | JE21 | A1 | 大溝線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線A1 | 11KV大溝線 R相AMP | FEEDER |  |  |  |  | CDC | 330 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | JE21 | A2 | 大溝線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線A2 | 11KV大溝線 S相AMP | FEEDER |  |  |  |  | CDC | 331 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | JE21 | A3 | 大溝線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線A3 | 11KV大溝線 T相AMP | FEEDER |  |  |  |  | CDC | 332 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | JE21 | NA | 大溝線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線A0 | 11KV大溝線 N相AMP | FEEDER |  |  |  |  | CDC | 333 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | JE24 | VAR | 大義線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線KVAR | 11KV大義線 KVAR | FEEDER |  |  |  |  | CDC | 334 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | JE24 | A1 | 大義線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線A1 | 11KV大義線 R相AMP | FEEDER |  |  |  |  | CDC | 335 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | JE24 | A2 | 大義線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線A2 | 11KV大義線 S相AMP | FEEDER |  |  |  |  | CDC | 336 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | JE24 | A3 | 大義線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線A3 | 11KV大義線 T相AMP | FEEDER |  |  |  |  | CDC | 337 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | JE24 | NA | 大義線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線A0 | 11KV大義線 N相AMP | FEEDER |  |  |  |  | CDC | 338 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JE29 | VAR | 大龍線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線KVAR | 11KV大龍線 KVAR | FEEDER |  |  |  |  | CDC | 339 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JE29 | A1 | 大龍線R相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線A1 | 11KV大龍線 R相AMP | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JE29 | A2 | 大龍線S相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線A2 | 11KV大龍線 S相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JE29 | A3 | 大龍線T相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線A3 | 11KV大龍線 T相AMP | FEEDER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JE29 | NA | 大龍線零相電流 | A_-500_500(-2000_2000) |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線A0 | 11KV大龍線 N相AMP | FEEDER |  |  |  |  | CDC | 343 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 充電機 | DC-V | 配電盤 "MAIN"NFB電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S21_D1 | [8 empty] | 大寮SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 344 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 63Q | #2(臨)MTR ULTC電驛動作 | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-19-06 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2臨MTR63Q | #2(臨)MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 345 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 96B1 | #2(臨)MTR撲氣電驛警報 | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-02 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2臨MTR96B1 | #2(臨)MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 346 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 96B2 | #2(臨)MTR撲氣電驛動作 | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-03 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2臨MTR96B2 | #2(臨)MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 347 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 96D | #2(臨)MTR放壓電驛動作 | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-04 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2臨MTR96D | #2(臨)MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 348 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 96P | #2(臨)MTR突壓電驛動作 | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-19-05 |  |  | SPARE |  |  |  |  | B1/S21_D1 | [8 empty] | 大寮SS.#2臨MTR96P | #2(臨)MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 349 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | 69KV BUS | 87BA | 69KV BUS RY 87BA |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | [5 empty] | 350 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0265 |  | 0013 | 1-32-06 |  | 1-0C | 69KV BUS | 87BS | 69KV BUS RY |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER | [5 empty] | 351 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Lights3 | 路燈操作線電源監視 | INSERT | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0346 |  |  | 1-37-07 |  |  | Locate Empty |  | 路燈操作線電源監視 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 352 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | 9A5Other | 通訊室溫度異常 | INSERT | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0345 |  |  | 1-37-06 |  |  | Locate Empty |  | 通訊溫度異常 |  |  | B3/S21_D1 | [8 empty] | 大寮SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | [5 empty] | 353 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 640 | 85A | 新營大寮二路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_87A | 新營二路(640) 87RY | LINE69 | [5 empty] | 354 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-32-01 |  |  | 640 | 640 CFA | 新營大寮二路副線 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_CFA | 新營二路(640) 通訊故障 | LINE69 | [5 empty] | 355 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0259 |  | 0010 | 1-32-00 |  | 1-09 | 640 | 85RY U/L | 新營大寮二路 69KV |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_87UL | 新營二路(640) 87RY U/L | LINE69 | [5 empty] | 356 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0349 |  |  | 1-37-10 |  |  | 640 |  | 640 RYFA |  |  | B2/S21_A1 | [8 empty] | 大寮SS.640_RYFA | 640 IED警報 | OTHER | [5 empty] | 357 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-01 |  |  | 710 | 85A | 新營大寮一路 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_87A | 新營一路(710) 87RY | LINE69 | [5 empty] | 358 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-32-05 |  |  | 710 | 710 CFA | 新營大寮一路副線 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_CFA | 新營一路(710) 通訊故障 | LINE69 | [5 empty] | 359 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0263 |  | 0012 | 1-32-04 |  | 1-0B | 710 | 85RY U/L | 新營大寮一路 69KV |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_87UL | 新營一路(710) 87RY U/L | LINE69 | [5 empty] | 360 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 1-37-11 |  |  | 710 |  | 710 RYFA |  |  | B2/S21_A1 | [8 empty] | 大寮SS.710_RYFA | 710 IED警報 | OTHER | [5 empty] | 361 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Water3 | 開關場水位警報 | INSERT | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0353 |  |  | 1-37-14 |  |  | 開關場水位警報 |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 362 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 1-3F-15 |  |  | Locate Empty |  | 11KV IED重警報 (3F-15) |  |  | B3/S21_D1 | [8 empty] | 大寮SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 363 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | Water4 | 開關場水位二段 | INSERT | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0352 |  |  | 1-37-13 |  |  | 開關場水位二段 |  |  |  |  | B3/S21_D1 | [8 empty] | 大寮SS.開關場水位二段 | 開關場水位二段警報 | OTHER | [5 empty] | 364 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0421 |  |  | 1-3E-02 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大布線79LOA | 大布線79LOA | OTHER | [5 empty] | 365 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0424 |  |  | 1-3E-05 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大江線79LOA | 大江線79LOA | OTHER | [5 empty] | 366 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0428 |  |  | 1-3E-09 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大海線79LOA | 大海線79LOA | OTHER | [5 empty] | 367 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0426 |  |  | 1-3E-07 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大順線79LOA | 大順線79LOA | OTHER | [5 empty] | 368 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0420 |  |  | 1-3E-01 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大塭線79LOA | 大塭線79LOA | OTHER | [5 empty] | 369 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0423 |  |  | 1-3E-04 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大新線79LOA | 大新線79LOA | OTHER | [5 empty] | 370 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0419 |  |  | 1-3E-00 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大溝線79LOA | 大溝線79LOA | OTHER | [5 empty] | 371 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0422 |  |  | 1-3E-03 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大義線79LOA | 大義線79LOA | OTHER | [5 empty] | 372 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0427 |  |  | 1-3E-08 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大龍線79LOA | 大龍線79LOA | OTHER | [5 empty] | 373 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0425 |  |  | 1-3E-06 |  |  | Locate Empty |  |  |  |  | B2/S21_D1 | [8 empty] | 大寮SS.大華線79LOA | 大華線79LOA | OTHER | [5 empty] | 374 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | SPARE | 87A | 大寮新塭線 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_87A | 新塭線(630) 87RY | LINE161 | [5 empty] | 375 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0261 |  | 0011 | 1-32-02 |  | 1-0A | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_87UL | 新塭線(630) 87RY U/L | LINE161 | [5 empty] | 376 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0262 |  |  | 1-32-03 |  |  | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_CFA | 630 CFA | OTHER | [5 empty] | 377 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0417 |  |  | 1-3B-14 |  |  | SPARE |  |  |  |  | B2/S21_A1 | [8 empty] | 大寮SS.630_RYFA | 630 RYFA | OTHER | [5 empty] | 378 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | 27A |  | INSERT | Status | 27RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-32-15 |  |  | 69KV BUS | 27BA | 69KV BUS欠壓電驛警報 |  |  | B2/S21_A1 | [8 empty] | 大寮SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | [5 empty] | 379 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | ComPoint |  |  | BFA | 69KV BUS RY 87BF | INSERT | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 1-32-13 |  |  | 69KV BUS | 87BF | 69KV BUS RY 87BF |  |  | B3/S21_D1 | [8 empty] | 大寮SS.BUSRY_BF | BUSRY BF | OTHER | [5 empty] | 380 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | ComPoint |  |  | 87CTFA | 69KV BUS RY CTFA | INSERT | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-32-14 |  |  | 69KV BUS | CTFA | 69KV BUS RY CTFA |  |  | B3/S21_D1 | [8 empty] | 大寮SS.BUSRY_CTFA | BUSRY CTFA | OTHER | [5 empty] | 381 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | StaDev | 所內設施 |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0449 |  |  | 1-3F-14 |  |  | Locate Empty | Ladder 14,1 | PMA (Power Meter) |  |  | ELEM/S21_D1 | [8 empty] | 大寮SS.PMA | POWER METER警報 | OTHER | [5 empty] | 382 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JE21 | KWH(+) | 大溝線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 383 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JE22 | KWH(+) | 大塭線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 384 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JE23 | KWH(+) | 大布線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 385 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JE24 | KWH(+) | 大義線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 386 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JE25 | KWH(+) | 大新線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 387 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | JE26 | KWH(+) | 大江線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 388 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | JE27 | KWH(+) | 大華線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 389 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | JE28 | KWH(+) | 大順線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 390 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | JE29 | KWH(+) | 大龍線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 391 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | JE30 | KWH(+) | 大海線瓦時(正)計量值 |  |  | B2/S21_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 392 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S21 | 大寮SS | 69 | 69kV | 630臨 | 新塭臨線(630) |  | MW |  | DEL | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | SPARE |  |  | MW_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.(臨)630_MW | 新塭(臨)線 MW | LINE69 | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 630臨 | 新塭臨線(630) |  | MVAR |  | DEL | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | SPARE |  |  | MVAR_-144_144(-2000_2000) |  | B2/S21_A1 | [8 empty] | 大寮SS.(臨)630_MVAR | 新塭(臨)線 MVAR | LINE69 | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S21 | 大寮SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S21_D1 | [12 empty] | 大寮SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S21/69/1BUS/V; OPRD2: S21/69/2BUS/V
S21 | 大寮SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S21_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S21/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S21 | 大寮SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S21_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_7 | OPRD1: S21/11/M1/MW; OPRD2: S21/11/M2/MW; OPRD3: S21/11/M3/MW; OPRD4: S21/69/630/MW; OPRD5: S21/69/630臨/MW; OPRD6: S21/69/640/MW; OPRD7: S21/69/710/MW
S21 | 大寮SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S21_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S21/0/CalcPoint/OPRN2_MW
S21 | 大寮SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S21_D1 | [17 empty] | none
S21 | 大寮SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S21_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S21/0/CalcPoint/OPRN1; OPRD2: S21/0/CalcPoint/OPRN2; OPRD3: S21/0/CalcPoint/PRFL_UL
S21 | 大寮SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S21_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S21/11/M1/MW; OPRD2: S21/11/M1/MVAR; OPRD3: S21/0/CalcPoint/Vbs2
S21 | 大寮SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S21_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S21/11/M2/MW; OPRD2: S21/11/M2/MVAR; OPRD3: S21/0/CalcPoint/Vbs2
S21 | 大寮SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S21_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S21/11/M3/MW; OPRD2: S21/11/M3/MVAR; OPRD3: NULL
S21 | 大寮SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S21_A1 | [12 empty] | 大寮SS.630_AMP | 新塭線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: S21/69/630/MW; OPRD2: S21/69/630/MVAR; OPRD3: S21/0/CalcPoint/Vbs2
S21 | 大寮SS | 69 | 69kV | 630臨 | 新塭臨線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S21_A1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S21/69/630臨/MW; OPRD2: S21/69/630臨/MVAR; OPRD3: NULL
S21 | 大寮SS | 69 | 69kV | 640 | 新營～大寮二路(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S21_A1 | [12 empty] | 大寮SS.640_AMP | 新營二路 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: S21/69/640/MW; OPRD2: S21/69/640/MVAR; OPRD3: S21/0/CalcPoint/Vbs2
S21 | 大寮SS | 69 | 69kV | 710 | 新營～大寮一路(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S21_A1 | [12 empty] | 大寮SS.710_AMP | 新營一路 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S21/69/710/MW; OPRD2: S21/69/710/MVAR; OPRD3: S21/0/CalcPoint/Vbs2
S21 | 大寮SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S21_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S21/11/1BUS/V
S21 | 大寮SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S21_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S21/11/2BUS/V
S21 | 大寮SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S21_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S21/11/3BUS/V
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S21_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大寮SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S21/11/M1/MW; OPRD2: S21/11/M1/MVAR
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S21_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大寮SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S21/11/M2/MW; OPRD2: S21/11/M2/MVAR
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S21_D1 | [15 empty] | MVA_CAL |  | va_million | OPRD1: S21/11/M3/MW; OPRD2: S21/11/M3/MVAR
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S21_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S21//1MTR/MVA; OPRD2: 0
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S21_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S21//2MTR/MVA; OPRD2: 0
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S21_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S21//3MTR/MVA; OPRD2: 0
S21 | 大寮SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S21_D1 | [12 empty] | 大寮SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S21/11/M1/MW; OPRD2: S21/11/M1/MVAR
S21 | 大寮SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S21_D1 | [12 empty] | 大寮SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S21/11/M2/MW; OPRD2: S21/11/M2/MVAR
S21 | 大寮SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S21_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S21/11/M3/MW; OPRD2: S21/11/M3/MVAR
S21 | 大寮SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S21_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S21//1MTR/SupLocal; OPRD2: S21//1MTR/Tap Chan; OPRD3: NULL
S21 | 大寮SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S21_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S21//2MTR/SupLocal; OPRD2: S21//2MTR/Tap Chan; OPRD3: NULL
S21 | 大寮SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S21_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S21//3MTR/SupLocal; OPRD2: S21//3MTR/Tap Chan; OPRD3: NULL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/1BUS/V; OPRD2: S21/11/JE21/I_R; OPRD3: S21/11/JE21/I_S; OPRD4: S21/11/JE21/I_T
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/1BUS/V; OPRD2: S21/11/JE22/I_R; OPRD3: S21/11/JE22/I_S; OPRD4: S21/11/JE22/I_T
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/1BUS/V; OPRD2: S21/11/JE23/I_R; OPRD3: S21/11/JE23/I_S; OPRD4: S21/11/JE23/I_T
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/1BUS/V; OPRD2: S21/11/JE24/I_R; OPRD3: S21/11/JE24/I_S; OPRD4: S21/11/JE24/I_T
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/1BUS/V; OPRD2: S21/11/JE25/I_R; OPRD3: S21/11/JE25/I_S; OPRD4: S21/11/JE25/I_T
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/2BUS/V; OPRD2: S21/11/JE26/I_R; OPRD3: S21/11/JE26/I_S; OPRD4: S21/11/JE26/I_T
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/2BUS/V; OPRD2: S21/11/JE27/I_R; OPRD3: S21/11/JE27/I_S; OPRD4: S21/11/JE27/I_T
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/2BUS/V; OPRD2: S21/11/JE28/I_R; OPRD3: S21/11/JE28/I_S; OPRD4: S21/11/JE28/I_T
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/2BUS/V; OPRD2: S21/11/JE29/I_R; OPRD3: S21/11/JE29/I_S; OPRD4: S21/11/JE29/I_T
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S21/11/2BUS/V; OPRD2: S21/11/JE30/I_R; OPRD3: S21/11/JE30/I_S; OPRD4: S21/11/JE30/I_T
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE21/kVA; OPRD2: S21/11/JE21/KVAR
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE22/kVA; OPRD2: S21/11/JE22/KVAR
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE23/kVA; OPRD2: S21/11/JE23/KVAR
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE24/kVA; OPRD2: S21/11/JE24/KVAR
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE25/kVA; OPRD2: S21/11/JE25/KVAR
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE26/kVA; OPRD2: S21/11/JE26/KVAR
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE27/kVA; OPRD2: S21/11/JE27/KVAR
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE28/kVA; OPRD2: S21/11/JE28/KVAR
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE29/kVA; OPRD2: S21/11/JE29/KVAR
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S21/11/JE30/kVA; OPRD2: S21/11/JE30/KVAR
S21 | 大寮SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S21_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S21/11/M1/MW; OPRD2: S21/11/M2/MW; OPRD3: S21/11/M3/MW
S21 | 大寮SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S21_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S21/11/M1/MVAR; OPRD2: S21/11/M2/MVAR; OPRD3: S21/11/M3/MVAR
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S21_D1 | [12 empty] | 大寮SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S21/11/210/CB; OPRD2: 6.9; OPRD3: 0
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S21_D1 | [12 empty] | 大寮SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S21/11/220/CB; OPRD2: 6.9; OPRD3: 0
S21 | 大寮SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S21_D1 | [12 empty] | 大寮SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_8 |  | com_alarm_25 | OPRD1: S21//1MTR/96B1; OPRD2: S21//1MTR/96PA; OPRD3: S21//1MTR/TRA; OPRD4: S21//1MTR/63Q; OPRD5: S21//1MTR/96D; OPRD6: S21//1MTR/96B2; OPRD7: S21//1MTR/87A; OPRD8: S21//1MTR/51ZA; OPRD9: S21//2MTR/96B1; OPRD10: S21//2MTR/TRA; OPRD11: S21//2MTR/96B2; OPRD12: S21//2MTR/63Q; OPRD13: S21//2MTR/96D; OPRD14: S21//2MTR/51ZA; OPRD15: S21//2MTR/96PA; OPRD16: S21//2MTR/87A; OPRD17: S21//3MTR/51ZA; OPRD18: S21//3MTR/TRA; OPRD19: S21//3MTR/87A; OPRD20: S21//3MTR/96PA; OPRD21: S21/0/2MTR/96B2; OPRD22: S21/0/2MTR/96D; OPRD23: S21/0/2MTR/63Q; OPRD24: S21/0/2MTR/96B1; OPRD25: S21/69/1BUS/87A
S21 | 大寮SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S21_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S21//1MTR/TRF; OPRD2: S21//2MTR/TRF; OPRD3: S21//3MTR/TRF
S21 | 大寮SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S21_A1 | [17 empty] | lamp2CC | OPRD1: S21/0/RTU/RTU_R_L
S21 | 大寮SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S21_A1 | [17 empty] | lamp2CC | OPRD1: S21/0/StaDev/DCE
S21 | 大寮SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S21_A1 | [17 empty] | lamp2CC | OPRD1: S21/0/StaDev/DCA
S21 | 大寮SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S21_D1 | [17 empty] | lamp2CC | OPRD1: S21/69/ComPoint/CBF
S21 | 大寮SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S21_D1 | [17 empty] | lamp2CC | OPRD1: S21/69/ComPoint/CBA
S21 | 大寮SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S21_D1 | [17 empty] | lamp2CC | OPRD1: S21/69/ComPoint/ABS_89A
S21 | 大寮SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 主變火警 |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S21_A1 | [17 empty] | lamp2CC | OPRD1: S21/0/StaDev/Fire
S21 | 大寮SS | 69 | 69kV | ComPoint_D1 |  |  | BFA | 69KV BUS RY 87BF |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | B3/S21_D1 | [17 empty] | lamp2CC | OPRD1: S21/69/ComPoint/BFA
S21 | 大寮SS | 69 | 69kV | ComPoint_D1 |  |  | 87CTFA | 69KV BUS RY CTFA |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S21_D1 | [17 empty] | lamp2CC | OPRD1: S21/69/ComPoint/87CTFA
S21 | 大寮SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S21_A1 | [17 empty] | lamp2CC | OPRD1: S21/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S21 | 大寮SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 大寮SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S21/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 大寮SS.630_AMP | 新塭線 AMP | LINE69 | S21/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 大寮SS.640_AMP | 新營二路 AMP | LINE69 | S21/69/640/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | I | [25 empty] | ADCS_N | [8 empty] | 大寮SS.710_AMP | 新營一路 AMP | LINE69 | S21/69/710/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S21 | 大寮SS | 0 |  |  |  |  | 大布線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大布線KVA | 11KV大布線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大布線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大布線KW | 11KV大布線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大江線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大江線KVA | 11KV大江線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大江線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大江線KW | 11KV大江線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大海線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大海線KVA | 11KV大海線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大海線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大海線KW | 11KV大海線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大華線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大華線KVA | 11KV大華線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大華線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大華線KW | 11KV大華線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大順線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大順線KVA | 11KV大順線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大順線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大順線KW | 11KV大順線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大塭線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大塭線KVA | 11KV大塭線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大塭線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大塭線KW | 11KV大塭線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大新線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大新線KVA | 11KV大新線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大新線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大新線KW | 11KV大新線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大溝線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大溝線KVA | 11KV大溝線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大溝線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大溝線KW | 11KV大溝線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大義線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大義線KVA | 11KV大義線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大義線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大義線KW | 11KV大義線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大龍線KVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大龍線KVA | 11KV大龍線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  |  |  |  | 大龍線KW | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.大龍線KW | 11KV大龍線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S21//1MTR/MVA |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_PF | #1MTR 功率因素 | DTR | S21//1MTR/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S21//2MTR/MVA |  | MVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_PF | #2MTR 功率因素 | DTR | S21//2MTR/PF |  | RPDC_PF_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S21 | 大寮SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S21/11/210/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S21/11/220/MVAR |  | SC_CAL_11 |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 69 | 69kV | (臨)630 | 新塭(臨)線 |  | I | [25 empty] | ADCS_N | [8 empty] | 大寮SS.(臨)630_AMP | 新塭(臨)線 AMP | LINE69 |  |  | AMP_CAL |  |  | 32 | CalcAIPoint | [21 empty] | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_MVA | #2(臨)MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_PF | #2(臨)MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S21 | 大寮SS | 69 | 69kV | 630_CB | 新塭線(630_CB) | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.630_CB_2 | 630(新塭線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 640_CB | 新營二路(640_CB) | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.640_CB_2 | 640(新營二路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 710_CB | 新營一路(710_CB) | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.710_CB_2 | 710(新營一路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 37 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 38 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 40 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 大寮SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 41 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S21 | 大寮SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | BUS2VUA | BUS#2VUA | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69KVBUS#2VUA_A | 69KVBUS#2VUA (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 43 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 44 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 大寮SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S21/0/CalcPoint/SUBA |  | STATION_FAULT_8 |  |  | 45 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 46 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 47 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630_AMP | 新塭線 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.630_AMP_A | 新塭線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 630_AMP | 新塭線 | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.630_AMP_2 | 新塭線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 640_AMP | 新營二路 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.640_AMP_A | 新營二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 640_AMP | 新營二路 | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.640_AMP_2 | 新營二路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 51 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 710_AMP | 新營一路 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.710_AMP_A | 新營一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 710_AMP | 新營一路 | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.710_AMP_2 | 新營一路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 53 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 54 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 55 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 56 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 57 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | 630(臨)_CB | 新塭(630(臨)_CB) | [27 empty] | DDCS2_1 | [8 empty] | 大寮SS.630(臨)_CB_2 | 630(新塭(臨)線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 58 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_PERM | #2(臨)MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 69 | 69kV | (臨)630_AMP | 新塭(臨)線 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.(臨)630_AMP_A | 新塭(臨)線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S21 | 大寮SS | 0 |  | 640_RYFA | 640 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.640_RYFA_A | 640 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 61 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 710_RYFA | 710 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.710_RYFA_A | 710 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 62 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 630_CFA | 630 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.630_CFA_A | 630 CFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 63 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 大寮SS.630_RYFA_A | 630 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 64 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 691BUS_27BA | 69#1BUS | [27 empty] | ADCS_N | [8 empty] | 大寮SS.69#1BUS_27BA_A | 69#1BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 65 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | BUSRY_BF | BUSRY | [27 empty] | ADCS_N | [8 empty] | 大寮SS.BUSRY_BF_A | BUSRY BF (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 66 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | BUSRY_CTFA | BUSRY | [27 empty] | ADCS_N | [8 empty] | 大寮SS.BUSRY_CTFA_A | BUSRY CTFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 67 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S21/0/RTU/ADCH1 |  |  |  | CDC | 68 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S21/0/RTU/ADCH2 |  |  |  | CDC | 69 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S21/0/RTU/ADCL1 |  |  |  | CDC | 70 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S21/0/RTU/ADCL2 |  |  |  | CDC | 71 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S21/69/1BUS/V |  |  |  | CDC | 72 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S21 | 大寮SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S21/11/1BUS/V |  |  |  | CDC | 73 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S21/11/2BUS/V |  |  |  | CDC | 74 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.630_MW | 新塭線 MW | LINE69 | S21/69/630/MW |  |  |  | CDC | 75 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.630_MVAR | 新塭線 MVAR | LINE69 | S21/69/630/MVAR |  |  |  | CDC | 76 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.640_MW | 新營二路 MW | LINE69 | S21/69/640/MW |  |  |  | CDC | 77 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.640_MVAR | 新營二路 MVAR | LINE69 | S21/69/640/MVAR |  |  |  | CDC | 78 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.710_MW | 新營一路 MW | LINE69 | S21/69/710/MW |  |  |  | CDC | 79 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.710_MVAR | 新營一路 MVAR | LINE69 | S21/69/710/MVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大布線 | 大布線 |  | 大布線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大布線KVAR | 11KV大布線 KVAR | FEEDER | S21/11/JE23/KVAR |  |  |  | CDC | 81 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大布線 | 大布線 |  | 大布線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大布線A1 | 11KV大布線 R相AMP | FEEDER | S21/11/JE23/I_R |  |  |  | CDC | 82 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大布線 | 大布線 |  | 大布線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大布線A2 | 11KV大布線 S相AMP | FEEDER | S21/11/JE23/I_S |  |  |  | CDC | 83 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大布線 | 大布線 |  | 大布線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大布線A3 | 11KV大布線 T相AMP | FEEDER | S21/11/JE23/I_T |  |  |  | CDC | 84 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大布線 | 大布線 |  | 大布線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大布線A0 | 11KV大布線 N相AMP | FEEDER | S21/11/JE23/I_N |  |  |  | CDC | 85 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大江線 | 大江線 |  | 大江線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大江線KVAR | 11KV大江線 KVAR | FEEDER | S21/11/JE26/KVAR |  |  |  | CDC | 86 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大江線 | 大江線 |  | 大江線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大江線A1 | 11KV大江線 R相AMP | FEEDER | S21/11/JE26/I_R |  |  |  | CDC | 87 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大江線 | 大江線 |  | 大江線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大江線A2 | 11KV大江線 S相AMP | FEEDER | S21/11/JE26/I_S |  |  |  | CDC | 88 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大江線 | 大江線 |  | 大江線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大江線A3 | 11KV大江線 T相AMP | FEEDER | S21/11/JE26/I_T |  |  |  | CDC | 89 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大江線 | 大江線 |  | 大江線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大江線A0 | 11KV大江線 N相AMP | FEEDER | S21/11/JE26/I_N |  |  |  | CDC | 90 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大海線 | 大海線 |  | 大海線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大海線KVAR | 11KV大海線 KVAR | FEEDER | S21/11/JE30/KVAR |  |  |  | CDC | 91 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大海線 | 大海線 |  | 大海線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大海線A1 | 11KV大海線 R相AMP | FEEDER | S21/11/JE30/I_R |  |  |  | CDC | 92 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大海線 | 大海線 |  | 大海線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大海線A2 | 11KV大海線 S相AMP | FEEDER | S21/11/JE30/I_S |  |  |  | CDC | 93 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大海線 | 大海線 |  | 大海線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大海線A3 | 11KV大海線 T相AMP | FEEDER | S21/11/JE30/I_T |  |  |  | CDC | 94 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大海線 | 大海線 |  | 大海線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大海線A0 | 11KV大海線 N相AMP | FEEDER | S21/11/JE30/I_N |  |  |  | CDC | 95 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大華線 | 大華線 |  | 大華線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大華線KVAR | 11KV大華線 KVAR | FEEDER | S21/11/JE27/KVAR |  |  |  | CDC | 96 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大華線 | 大華線 |  | 大華線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大華線A1 | 11KV大華線 R相AMP | FEEDER | S21/11/JE27/I_R |  |  |  | CDC | 97 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大華線 | 大華線 |  | 大華線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大華線A2 | 11KV大華線 S相AMP | FEEDER | S21/11/JE27/I_S |  |  |  | CDC | 98 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大華線 | 大華線 |  | 大華線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大華線A3 | 11KV大華線 T相AMP | FEEDER | S21/11/JE27/I_T |  |  |  | CDC | 99 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大華線 | 大華線 |  | 大華線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大華線A0 | 11KV大華線 N相AMP | FEEDER | S21/11/JE27/I_N |  |  |  | CDC | 100 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大順線 | 大順線 |  | 大順線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大順線KVAR | 11KV大順線 KVAR | FEEDER | S21/11/JE28/KVAR |  |  |  | CDC | 101 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大順線 | 大順線 |  | 大順線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大順線A1 | 11KV大順線 R相AMP | FEEDER | S21/11/JE28/I_R |  |  |  | CDC | 102 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大順線 | 大順線 |  | 大順線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大順線A2 | 11KV大順線 S相AMP | FEEDER | S21/11/JE28/I_S |  |  |  | CDC | 103 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大順線 | 大順線 |  | 大順線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大順線A3 | 11KV大順線 T相AMP | FEEDER | S21/11/JE28/I_T |  |  |  | CDC | 104 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大順線 | 大順線 |  | 大順線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大順線A0 | 11KV大順線 N相AMP | FEEDER | S21/11/JE28/I_N |  |  |  | CDC | 105 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大塭線 | 大塭線 |  | 大塭線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大塭線KVAR | 11KV大塭線 KVAR | FEEDER | S21/11/JE22/KVAR |  |  |  | CDC | 106 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大塭線 | 大塭線 |  | 大塭線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大塭線A1 | 11KV大塭線 R相AMP | FEEDER | S21/11/JE22/I_R |  |  |  | CDC | 107 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大塭線 | 大塭線 |  | 大塭線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大塭線A2 | 11KV大塭線 S相AMP | FEEDER | S21/11/JE22/I_S |  |  |  | CDC | 108 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大塭線 | 大塭線 |  | 大塭線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大塭線A3 | 11KV大塭線 T相AMP | FEEDER | S21/11/JE22/I_T |  |  |  | CDC | 109 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大塭線 | 大塭線 |  | 大塭線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大塭線A0 | 11KV大塭線 N相AMP | FEEDER | S21/11/JE22/I_N |  |  |  | CDC | 110 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大新線KVAR | 11KV大新線 KVAR | FEEDER | S21/11/JE25/KVAR |  |  |  | CDC | 111 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大新線A1 | 11KV大新線 R相AMP | FEEDER | S21/11/JE25/I_R |  |  |  | CDC | 112 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大新線A2 | 11KV大新線 S相AMP | FEEDER | S21/11/JE25/I_S |  |  |  | CDC | 113 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大新線A3 | 11KV大新線 T相AMP | FEEDER | S21/11/JE25/I_T |  |  |  | CDC | 114 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大新線A0 | 11KV大新線 N相AMP | FEEDER | S21/11/JE25/I_N |  |  |  | CDC | 115 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大溝線 | 大溝線 |  | 大溝線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大溝線KVAR | 11KV大溝線 KVAR | FEEDER | S21/11/JE21/KVAR |  |  |  | CDC | 116 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大溝線 | 大溝線 |  | 大溝線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大溝線A1 | 11KV大溝線 R相AMP | FEEDER | S21/11/JE21/I_R |  |  |  | CDC | 117 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大溝線 | 大溝線 |  | 大溝線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大溝線A2 | 11KV大溝線 S相AMP | FEEDER | S21/11/JE21/I_S |  |  |  | CDC | 118 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大溝線 | 大溝線 |  | 大溝線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大溝線A3 | 11KV大溝線 T相AMP | FEEDER | S21/11/JE21/I_T |  |  |  | CDC | 119 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大溝線 | 大溝線 |  | 大溝線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大溝線A0 | 11KV大溝線 N相AMP | FEEDER | S21/11/JE21/I_N |  |  |  | CDC | 120 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大義線 | 大義線 |  | 大義線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大義線KVAR | 11KV大義線 KVAR | FEEDER | S21/11/JE24/KVAR |  |  |  | CDC | 121 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大義線 | 大義線 |  | 大義線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大義線A1 | 11KV大義線 R相AMP | FEEDER | S21/11/JE24/I_R |  |  |  | CDC | 122 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大義線 | 大義線 |  | 大義線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大義線A2 | 11KV大義線 S相AMP | FEEDER | S21/11/JE24/I_S |  |  |  | CDC | 123 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大義線 | 大義線 |  | 大義線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大義線A3 | 11KV大義線 T相AMP | FEEDER | S21/11/JE24/I_T |  |  |  | CDC | 124 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大義線 | 大義線 |  | 大義線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大義線A0 | 11KV大義線 N相AMP | FEEDER | S21/11/JE24/I_N |  |  |  | CDC | 125 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大龍線 | 大龍線 |  | 大龍線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大龍線KVAR | 11KV大龍線 KVAR | FEEDER | S21/11/JE29/KVAR |  |  |  | CDC | 126 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大龍線 | 大龍線 |  | 大龍線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大龍線A1 | 11KV大龍線 R相AMP | FEEDER | S21/11/JE29/I_R |  |  |  | CDC | 127 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大龍線 | 大龍線 |  | 大龍線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大龍線A2 | 11KV大龍線 S相AMP | FEEDER | S21/11/JE29/I_S |  |  |  | CDC | 128 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大龍線 | 大龍線 |  | 大龍線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大龍線A3 | 11KV大龍線 T相AMP | FEEDER | S21/11/JE29/I_T |  |  |  | CDC | 129 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | 大龍線 | 大龍線 |  | 大龍線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.大龍線A0 | 11KV大龍線 N相AMP | FEEDER | S21/11/JE29/I_N |  |  |  | CDC | 130 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S21/11/TIE1/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S21/11/TIE1/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S21/11/TIE1/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_MW | #1MTR二次側 MW | DTR | S21/11/M1/MW |  |  |  | CDC | 134 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S21/11/M1/MVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S21/11/M1/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S21/11/M1/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S21/11/M1/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_OIL | #1MTR 油溫 | DTR | S21//1MTR/OilTemp |  |  |  | CDC | 139 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_COIL | #1MTR 線溫 | DTR | S21//1MTR/CoilTemp |  |  |  | CDC | 140 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S21//1MTR/TapPosMv |  |  |  | CDC | 141 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_MW | #2MTR二次側 MW | DTR | S21/11/M2/MW |  |  |  | CDC | 142 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S21/11/M2/MVAR |  |  |  | CDC | 143 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S21/11/M2/I_R |  |  |  | CDC | 144 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S21/11/M2/I_S |  |  |  | CDC | 145 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S21/11/M2/I_T |  |  |  | CDC | 146 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_OIL | #2MTR 油溫 | DTR | S21//2MTR/OilTemp |  |  |  | CDC | 147 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_COIL | #2MTR 線溫 | DTR | S21//2MTR/CoilTemp |  |  |  | CDC | 148 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S21//2MTR/TapPosMv |  |  |  | CDC | 149 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.直流電源電壓 | 直流電源電壓 | OTHER | S21/0/StaDev/DCV |  |  |  | CDC | 150 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S21 | 大寮SS | 0 |  | 臨 | 臨 |  | 11KV#2(臨)BKV | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.11KV#2(臨)BKV | 11KV #2(臨)BUS KV | BUS | S21/11/3BUS/V |  |  |  | CDC | 151 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S21 | 大寮SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-8E | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S21/69/2BUS/V |  |  |  | CDC | 152 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S21 | 大寮SS | 69 | 69kV | (臨)630 | 新塭(臨)線 |  | MW | [17 empty] | 1-8F | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.(臨)630_MW | 新塭(臨)線 MW | LINE69 | S21/69/630臨/MW |  |  |  | CDC | 153 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 69 | 69kV | (臨)630 | 新塭(臨)線 |  | MVAR | [17 empty] | 1-90 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 大寮SS.(臨)630_MVAR | 新塭(臨)線 MVAR | LINE69 | S21/69/630臨/MVAR |  |  |  | CDC | 154 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_MW | #2(臨)MTR二次側 MW | DTR | S21/11/M3/MW |  |  |  | CDC | 155 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_MVAR | #2(臨)MTR二次側 MVAR | DTR | S21/11/M3/MVAR |  |  |  | CDC | 156 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_A1 | #2(臨)MTR二次側 R相AMP | DTR | S21/11/M3/I_R |  |  |  | CDC | 157 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_A2 | #2M(臨)MTR二次側 S相AMP | DTR | S21/11/M3/I_S |  |  |  | CDC | 158 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_A3 | #2(臨)MTR二次側 T相AMP | DTR | S21/11/M3/I_T |  |  |  | CDC | 159 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_OIL | #2(臨)MTR 油溫 | DTR | S21//3MTR/OilTemp |  |  |  | CDC | 160 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_COIL | #2(臨)MTR 線溫 | DTR | S21//3MTR/CoilTemp |  |  |  | CDC | 161 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_TAP | #2(臨)MTR OLTC TAP | DTR | S21//3MTR/TapPosMv |  |  |  | CDC | 162 | GENERICAIPoint | SS200_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.630_PHA | 新塭線(630) 相間RY | LINE69 | S21/69/630/PHA |  |  |  | CDC | 163 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.630_GDA | 新塭線(630) 接地RY | LINE69 | S21/69/630/GDA |  |  |  | CDC | 164 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 大寮SS.630_CB | 630(新塭線) CB | LINE69 | S21/69/630/CB |  |  |  | CDC | 165 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | E2 | 632E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.632E_ES | 632E(新塭線) ES | LINE69 | S21/69/630/ES2 |  |  |  | CDC | 166 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.640_PHA | 新營二路(640) 相間RY | LINE69 | S21/69/640/PHA |  |  |  | CDC | 167 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.640_GDA | 新營二路(640) 接地RY | LINE69 | S21/69/640/GDA |  |  |  | CDC | 168 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 大寮SS.640_CB | 640(新營二路) CB | LINE69 | S21/69/640/CB |  |  |  | CDC | 169 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | E2 | 642E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.642E_ES | 642E(新營二路) ES | LINE69 | S21/69/640/ES2 |  |  |  | CDC | 170 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.710_PHA | 新營一路(710) 相間RY | LINE69 | S21/69/710/PHA |  |  |  | CDC | 171 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.710_GDA | 新營一路(710) 接地RY | LINE69 | S21/69/710/GDA |  |  |  | CDC | 172 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 大寮SS.710_CB | 710(新營一路) CB | LINE69 | S21/69/710/CB |  |  |  | CDC | 173 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | E2 | 712E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 大寮SS.712E_ES | 712E(新營一路) ES | LINE69 | S21/69/710/ES2 |  |  |  | CDC | 174 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_PHA | 11KV大溝線(JE21) 相間RY | FEEDER | S21/11/JE21/PHA |  |  |  | CDC | 175 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_GDA | 11KV大溝線(JE21) 接地RY | FEEDER | S21/11/JE21/GDA |  |  |  | CDC | 176 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_79UL | 11KV大溝線(JE21) 79RY U/L | FEEDER | S21/11/JE21/79UL |  |  |  | CDC | 177 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE21 | 大溝線(JE21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_ADJ | 11KV大溝線(JE21) LCO分流器 U/L | FEEDER | S21/11/JE21/ADJ |  |  |  | CDC | 178 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE21 | JE21(11KV大溝線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_CB | JE21(11KV大溝線) CB | FEEDER | S21/11/JE21/CB |  |  |  | CDC | 179 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_PHA | 11KV大塭線(JE22) 相間RY | FEEDER | S21/11/JE22/PHA |  |  |  | CDC | 180 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_GDA | 11KV大塭線(JE22) 接地RY | FEEDER | S21/11/JE22/GDA |  |  |  | CDC | 181 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_79UL | 11KV大塭線(JE22) 79RY U/L | FEEDER | S21/11/JE22/79UL |  |  |  | CDC | 182 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE22 | 大塭線(JE22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_ADJ | 11KV大塭線(JE22) LCO分流器 U/L | FEEDER | S21/11/JE22/ADJ |  |  |  | CDC | 183 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE22 | JE22(11KV大塭線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_CB | JE22(11KV大塭線) CB | FEEDER | S21/11/JE22/CB |  |  |  | CDC | 184 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_PHA | 11KV大布線(JE23) 相間RY | FEEDER | S21/11/JE23/PHA |  |  |  | CDC | 185 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_GDA | 11KV大布線(JE23) 接地RY | FEEDER | S21/11/JE23/GDA |  |  |  | CDC | 186 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_79UL | 11KV大布線(JE23) 79RY U/L | FEEDER | S21/11/JE23/79UL |  |  |  | CDC | 187 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE23 | 大布線(JE23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_ADJ | 11KV大布線(JE23) LCO分流器 U/L | FEEDER | S21/11/JE23/ADJ |  |  |  | CDC | 188 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE23 | JE23(11KV大布線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_CB | JE23(11KV大布線) CB | FEEDER | S21/11/JE23/CB |  |  |  | CDC | 189 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_PHA | 11KV大義線(JE24) 相間RY | FEEDER | S21/11/JE24/PHA |  |  |  | CDC | 190 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_GDA | 11KV大義線(JE24) 接地RY | FEEDER | S21/11/JE24/GDA |  |  |  | CDC | 191 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_79UL | 11KV大義線(JE24) 79RY U/L | FEEDER | S21/11/JE24/79UL |  |  |  | CDC | 192 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE24 | 大義線(JE24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_ADJ | 11KV大義線(JE24) LCO分流器 U/L | FEEDER | S21/11/JE24/ADJ |  |  |  | CDC | 193 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE24 | JE24(11KV大義線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_CB | JE24(11KV大義線) CB | FEEDER | S21/11/JE24/CB |  |  |  | CDC | 194 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_PHA | 11KV大新線(JE25) 相間RY | FEEDER | S21/11/JE25/PHA |  |  |  | CDC | 195 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_GDA | 11KV大新線(JE25) 接地RY | FEEDER | S21/11/JE25/GDA |  |  |  | CDC | 196 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_79UL | 11KV大新線(JE25) 79RY U/L | FEEDER | S21/11/JE25/79UL |  |  |  | CDC | 197 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE25 | 大新線(JE25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_ADJ | 11KV大新線(JE25) LCO分流器 U/L | FEEDER | S21/11/JE25/ADJ |  |  |  | CDC | 198 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE25 | JE25(11KV大新線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_CB | JE25(11KV大新線) CB | FEEDER | S21/11/JE25/CB |  |  |  | CDC | 199 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_PHA | 11KV大江線(JE26) 相間RY | FEEDER | S21/11/JE26/PHA |  |  |  | CDC | 200 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_GDA | 11KV大江線(JE26) 接地RY | FEEDER | S21/11/JE26/GDA |  |  |  | CDC | 201 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_79UL | 11KV大江線(JE26) 79RY U/L | FEEDER | S21/11/JE26/79UL |  |  |  | CDC | 202 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE26 | 大江線(JE26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_ADJ | 11KV大江線(JE26) LCO分流器 U/L | FEEDER | S21/11/JE26/ADJ |  |  |  | CDC | 203 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE26 | JE26(11KV大江線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_CB | JE26(11KV大江線) CB | FEEDER | S21/11/JE26/CB |  |  |  | CDC | 204 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_PHA | 11KV大華線(JE27) 相間RY | FEEDER | S21/11/JE27/PHA |  |  |  | CDC | 205 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_GDA | 11KV大華線(JE27) 接地RY | FEEDER | S21/11/JE27/GDA |  |  |  | CDC | 206 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_79UL | 11KV大華線(JE27) 79RY U/L | FEEDER | S21/11/JE27/79UL |  |  |  | CDC | 207 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE27 | 大華線(JE27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_ADJ | 11KV大華線(JE27) LCO分流器 U/L | FEEDER | S21/11/JE27/ADJ |  |  |  | CDC | 208 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE27 | JE27(11KV大華線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_CB | JE27(11KV大華線) CB | FEEDER | S21/11/JE27/CB |  |  |  | CDC | 209 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_PHA | 11KV大順線(JE28) 相間RY | FEEDER | S21/11/JE28/PHA |  |  |  | CDC | 210 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_GDA | 11KV大順線(JE28) 接地RY | FEEDER | S21/11/JE28/GDA |  |  |  | CDC | 211 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_79UL | 11KV大順線(JE28) 79RY U/L | FEEDER | S21/11/JE28/79UL |  |  |  | CDC | 212 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE28 | 大順線(JE28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_ADJ | 11KV大順線(JE28) LCO分流器 U/L | FEEDER | S21/11/JE28/ADJ |  |  |  | CDC | 213 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE28 | JE28(11KV大順線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_CB | JE28(11KV大順線) CB | FEEDER | S21/11/JE28/CB |  |  |  | CDC | 214 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_PHA | 11KV大龍線(JE29) 相間RY | FEEDER | S21/11/JE29/PHA |  |  |  | CDC | 215 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_GDA | 11KV大龍線(JE29) 接地RY | FEEDER | S21/11/JE29/GDA |  |  |  | CDC | 216 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_79UL | 11KV大龍線(JE29) 79RY U/L | FEEDER | S21/11/JE29/79UL |  |  |  | CDC | 217 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE29 | 大龍線(JE29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_ADJ | 11KV大龍線(JE29) LCO分流器 U/L | FEEDER | S21/11/JE29/ADJ |  |  |  | CDC | 218 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE29 | JE29(11KV大龍線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_CB | JE29(11KV大龍線) CB | FEEDER | S21/11/JE29/CB |  |  |  | CDC | 219 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_PHA | 11KV大海線(JE30) 相間RY | FEEDER | S21/11/JE30/PHA |  |  |  | CDC | 220 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_GDA | 11KV大海線(JE30) 接地RY | FEEDER | S21/11/JE30/GDA |  |  |  | CDC | 221 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_79UL | 11KV大海線(JE30) 79RY U/L | FEEDER | S21/11/JE30/79UL |  |  |  | CDC | 222 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 11 | 11kV | JE30 | 大海線(JE30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_ADJ | 11KV大海線(JE30) LCO分流器 U/L | FEEDER | S21/11/JE30/ADJ |  |  |  | CDC | 223 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S21 | 大寮SS | 11 | 11kV | JE30 | JE30(11KV大海線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_CB | JE30(11KV大海線) CB | FEEDER | S21/11/JE30/CB |  |  |  | CDC | 224 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.TIE1_CB | 11KV TIE1 CB | TIE | S21/11/TIE1/CB |  |  |  | CDC | 225 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.TIE1_51A | 11KV TIE1 51RY | TIE | S21/11/TIE1/51A |  |  |  | CDC | 226 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S21/11/TIE1/51NA |  |  |  | CDC | 227 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.750_CB | 750(#1MTR) CB | DTR | S21/69/750/CB |  |  |  | CDC | 228 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.1M_CB | 1M(#1MTR) CB | DTR | S21/11/M1/CB |  |  |  | CDC | 229 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_51A | #1MTR 51RY | DTR | S21/69/750/51A |  |  |  | CDC | 230 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_51NA | #1MTR 51N RY | DTR | S21/69/750/51NA |  |  |  | CDC | 231 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S21//1MTR/51ZA |  |  |  | CDC | 232 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_87A | #1MTR 87RY | DTR | S21//1MTR/87A |  |  |  | CDC | 233 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S21//1MTR/87UL |  |  |  | CDC | 234 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S21/11/M1/51A |  |  |  | CDC | 235 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_TRA | #1MTR 重故障 | DTR | S21//1MTR/TRA |  |  |  | CDC | 236 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S21//1MTR/TRF |  |  |  | CDC | 237 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S21//1MTR/SupLocal |  |  |  | CDC | 238 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S21//1MTR/Tap Chan |  |  |  | CDC | 239 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_96A | #1MTR 96P RY | DTR | S21//1MTR/96PA |  |  |  | CDC | 240 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S21//1MTR/OLTC_DLY |  |  |  | CDC | 241 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S21//1MTR/AC_Fault |  |  |  | CDC | 242 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.760_CB | 760(#2MTR) CB | DTR | S21/69/760/CB |  |  |  | CDC | 243 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.2M_CB | 2M(#2MTR) CB | DTR | S21/11/M2/CB |  |  |  | CDC | 244 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_51A | #2MTR 51RY | DTR | S21/69/760/51A |  |  |  | CDC | 245 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_51NA | #2MTR 51N RY | DTR | S21/69/760/51NA |  |  |  | CDC | 246 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S21//2MTR/51ZA |  |  |  | CDC | 247 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_87A | #2MTR 87RY | DTR | S21//2MTR/87A |  |  |  | CDC | 248 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S21//2MTR/87UL |  |  |  | CDC | 249 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S21/11/M2/51A |  |  |  | CDC | 250 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_TRA | #2MTR 重故障 | DTR | S21//2MTR/TRA |  |  |  | CDC | 251 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S21//2MTR/TRF |  |  |  | CDC | 252 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S21//2MTR/SupLocal |  |  |  | CDC | 253 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S21//2MTR/Tap Chan |  |  |  | CDC | 254 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_96A | #2MTR 96P RY | DTR | S21//2MTR/96PA |  |  |  | CDC | 255 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S21//2MTR/OLTC_DLY |  |  |  | CDC | 256 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S21//2MTR/AC_Fault |  |  |  | CDC | 257 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_CB | 210(11KV #1SC) CB | SC | S21/11/210/CB |  |  |  | CDC | 258 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S21/11/210/Tap Chan |  |  |  | CDC | 259 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_SCA | 11KV #1SC 51,51N RY | SC | S21/11/210/SCA |  |  |  | CDC | 260 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S21/11/210/UVA |  |  |  | CDC | 261 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_CB | 220(11KV #2SC) CB | SC | S21/11/220/CB |  |  |  | CDC | 262 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S21/11/220/Tap Chan |  |  |  | CDC | 263 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_SCA | 11KV #2SC 51,51N RY | SC | S21/11/220/SCA |  |  |  | CDC | 264 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S21/11/220/UVA |  |  |  | CDC | 265 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 大寮SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S21/69/1BUS/BUS_VUA |  |  |  | CDC | 266 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S21/11/ComPoint/CBA |  |  |  | CDC | 267 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S21/11/ComPoint/CBF |  |  |  | CDC | 268 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S21/69/ComPoint/ABS_89A |  |  |  | CDC | 269 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S21/69/ComPoint/CBA |  |  |  | CDC | 270 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S21/69/ComPoint/CBF |  |  |  | CDC | 271 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S21/0/RTU/RTU_R_L |  |  |  | CDC | 272 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S21 | 大寮SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.TEST_CB | TEST CB | OTHER | S21/0/RTU/Test_CB |  |  |  | CDC | 273 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.火災警報(1) | [大寮]火警 | OTHER | S21/0/StaDev/Fire1 |  |  |  | CDC | 274 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S21/0/StaDev/OPA |  |  |  | CDC | 275 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S21/0/StaDev/STUV |  |  |  | CDC | 276 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S21/0/StaDev/CHG1 |  |  |  | CDC | 277 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.直流電源DCA | 直流電源故障警報 | OTHER | S21/0/StaDev/DCA |  |  |  | CDC | 278 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S21/0/StaDev/DCE |  |  |  | CDC | 279 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S21/0/StaDev/OilLeak |  |  |  | CDC | 280 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S21/0/StaDev/6A5Other |  |  |  | CDC | 281 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S21/0/StaDev/7A5Other |  |  |  | CDC | 282 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S21/0/StaDev/8A5Other |  |  |  | CDC | 283 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S21/0/StaDev/CHG2 |  |  |  | CDC | 284 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S21/0/StaDev/CommACF |  |  |  | CDC | 285 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S21/0/StaDev/Door1 |  |  |  | CDC | 286 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S21/0/StaDev/Door2 |  |  |  | CDC | 287 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S21/0/StaDev/Door3 |  |  |  | CDC | 288 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S21 | 大寮SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.開關場照明(A) | 所內開關場照明 | OTHER | S21/0/StaDev/Lights1 |  |  |  | CDC | 289 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S21 | 大寮SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.開關場照明(B) | 路燈照明 | OTHER | S21/0/StaDev/Lights2 |  |  |  | CDC | 290 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S21 | 大寮SS | 0 |  |  |  |  | #1MAIN51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MAIN51NA | #1MAIN51NA | OTHER | S21/11/M1/51NA |  |  |  | CDC | 291 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2MAIN51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MAIN51NA | #2MAIN51NA | OTHER | S21/11/M2/51NA |  |  |  | CDC | 292 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 69KVBUS#2VUA | [17 empty] | 1-31-14 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER | S21/69/2BUS/BUS_VUA |  |  |  | CDC | 293 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.69KVSC警報 | 69KVSC警報 | OTHER | S21/69/810/SCA |  |  |  | CDC | 294 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | MCSG火警 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.MCSG火警 | MCSG火警 | OTHER | S21/0/StaDev/Fire2 |  |  |  | CDC | 295 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | MCSG系統故障 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.MCSG系統故障 | MCSG系統故障 | OTHER | S21/0/StaDev/1A5Other |  |  |  | CDC | 296 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.主變火警 | 主變火警 | OTHER | S21/0/StaDev/Fire |  |  |  | CDC | 297 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.安全監控 | 安全監控 | OTHER | S21/0/StaDev/Burglar |  |  |  | CDC | 298 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.門禁 | 大門側門 | OTHER | S21/0/StaDev/Door |  |  |  | CDC | 299 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.細水霧故障 | 細水霧故障 | OTHER | S21/0/StaDev/2A5Other |  |  |  | CDC | 300 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S21/0/StaDev/3A5Other |  |  |  | CDC | 301 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.維護運轉警報 | 維護運轉警報 | OTHER | S21/0/StaDev/4A5Other |  |  |  | CDC | 302 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S21//1MTR/63Q |  |  |  | CDC | 303 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S21//1MTR/96B1 |  |  |  | CDC | 304 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S21//1MTR/96B2 |  |  |  | CDC | 305 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S21//1MTR/96D |  |  |  | CDC | 306 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S21//1MTR/96P |  |  |  | CDC | 307 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S21//2MTR/63Q |  |  |  | CDC | 308 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S21//2MTR/96B1 |  |  |  | CDC | 309 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S21//2MTR/96B2 |  |  |  | CDC | 310 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S21//2MTR/96D |  |  |  | CDC | 311 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S21//2MTR/96P |  |  |  | CDC | 312 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S21/11/M1/81AS |  |  |  | CDC | 313 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S21 | 大寮SS | 0 |  | 臨 | 臨 |  | #2臨MTR63Q | [17 empty] | 1-19-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2臨MTR63Q | #2(臨)MTR ULTC電驛動作 | OTHER | S21/0/2MTR/63Q |  |  |  | CDC | 314 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2臨MTR96B1 | [17 empty] | 1-19-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2臨MTR96B1 | #2(臨)MTR撲氣電驛警報 | OTHER | S21/0/2MTR/96B1 |  |  |  | CDC | 315 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2臨MTR96B2 | [17 empty] | 1-19-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2臨MTR96B2 | #2(臨)MTR撲氣電驛動作 | OTHER | S21/0/2MTR/96B2 |  |  |  | CDC | 316 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2臨MTR96D | [17 empty] | 1-19-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2臨MTR96D | #2(臨)MTR放壓電驛動作 | OTHER | S21/0/2MTR/96D |  |  |  | CDC | 317 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | #2臨MTR96P | [17 empty] | 1-19-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2臨MTR96P | #2(臨)MTR突壓電驛動作 | OTHER | S21/0/2MTR/96P |  |  |  | CDC | 318 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 760(臨) | 臨 |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.760(臨)_CB | 760(臨)(#2MTR) CB | DTR | S21/69/770/CB |  |  |  | CDC | 319 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_51A | #2(臨)MTR 51RY | DTR | S21/69/770/51A |  |  |  | CDC | 320 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_51NA | #2(臨)MTR 51N RY | DTR | S21/69/770/51NA |  |  |  | CDC | 321 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_51ZA | #2(臨)MTR 51Z RY | DTR | S21//3MTR/51ZA |  |  |  | CDC | 322 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_87A | #2(臨)MTR 87RY | DTR | S21//3MTR/87A |  |  |  | CDC | 323 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_87UL | #2(臨)MTR 87RY U/L | DTR | S21//3MTR/87UL |  |  |  | CDC | 324 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_TRA | #2(臨)MTR 重故障 | DTR | S21//3MTR/TRA |  |  |  | CDC | 325 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_TRF | #2(臨)MTR 輕故障 | DTR | S21//3MTR/TRF |  |  |  | CDC | 326 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_S/L | #2(臨)MTR OLTC S/L | DTR | S21//3MTR/SupLocal |  |  |  | CDC | 327 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_A/M | #2(臨)MTR OLTC A/M | DTR | S21//3MTR/Tap Chan |  |  |  | CDC | 328 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761(臨) | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.761(臨)_ABS | 761(臨)(#2MTR) ABS | DTR | S21/69/770/ABS1 |  |  |  | CDC | 329 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 0 |  | 2(臨)MTR | 臨 |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)MTR_96A | #2(臨)MTR 96P RY | DTR | S21//3MTR/96PA |  |  |  | CDC | 330 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)M | 臨 |  | O遲滯 | [17 empty] | 1-35-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)M_O遲滯 | #2(臨)MTR OLTC遲滯 | DTR | S21//3MTR/OLTC_DLY |  |  |  | CDC | 331 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 2(臨)M_AC | 臨 |  | F | [17 empty] | 1-35-12 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.#2(臨)M_AC_F | #2(臨)MTR AC電源失效 | DTR | S21//3MTR/AC_Fault |  |  |  | CDC | 332 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630(臨) | 新塭(臨)線(630) |  | PHA | [17 empty] | 1-0A-05 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.630(臨)_PHA | 新塭(臨)線(630) 相間RY | LINE69 | S21/69/360/PHA |  |  |  | CDC | 333 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630(臨) | 新塭(臨)線(630) |  | GDA | [17 empty] | 1-0A-06 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.630(臨)_GDA | 新塭(臨)線(630) 接地RY | LINE69 | S21/69/360/GDA |  |  |  | CDC | 334 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 630(臨) | 新塭 |  | CB | [17 empty] | 1-0A-04 |  | 1-06 | [5 empty] | 69KV_N | [8 empty] | 大寮SS.630(臨)_CB | 630(新塭(臨)線) CB | LINE69 | S21/69/360/CB |  |  |  | CDC | 335 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | ABS1 | 631(臨) | [16 empty] | 1-3A-06 | 1-3A-07 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.631(臨)_ABS | 631(新塭(臨)線) ABS | LINE69 | S21/69/360/ABS1 |  |  |  | CDC | 336 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | ABS2 | 632(臨) | [16 empty] | 1-3A-08 | 1-3A-09 | 1-22 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.632(臨)_ABS | 632(新塭(臨)線) ABS | LINE69 | S21/69/360/ABS2 |  |  |  | CDC | 337 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | E(臨)2 | 632E(臨) | [16 empty] | 1-3A-10 | 1-3A-11 | 1-23 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.632E(臨)_ES | 632E(新塭(臨)線) ES | LINE69 | S21/69/360/ES2 |  |  |  | CDC | 338 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | DS1 | 631 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.631_DS | 631(新塭線) DS | LINE69 | S21/69/630/DS1 |  |  |  | CDC | 339 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | DS2 | 632 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.632_DS | 632(新塭線) DS | LINE69 | S21/69/630/DS2 |  |  |  | CDC | 340 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | DS1 | 641 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.641_DS | 641(新營二路) DS | LINE69 | S21/69/640/DS1 |  |  |  | CDC | 341 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | DS2 | 642 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.642_DS | 642(新營二路) DS | LINE69 | S21/69/640/DS2 |  |  |  | CDC | 342 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | DS1 | 711 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.711_DS | 711(新營一路) DS | LINE69 | S21/69/710/DS1 |  |  |  | CDC | 343 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | DS2 | 712 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.712_DS | 712(新營一路) DS | LINE69 | S21/69/710/DS2 |  |  |  | CDC | 344 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.751_DS | 751(#1MTR) DS | DTR | S21/69/750/DS1 |  |  |  | CDC | 345 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.761_DS | 761(#2MTR) DS | DTR | S21/69/760/DS1 |  |  |  | CDC | 346 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S21 | 大寮SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S21/69/1BUS/87A |  |  |  | CDC | 347 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 大寮SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER | S21/69/1BUS/87UL |  |  |  | CDC | 348 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  |  |  |  | 數據機重置 | [17 empty] | 1-35-15 |  | 1-57 | [5 empty] | DDCS2_1 | [8 empty] | 大寮SS.數據機重置 | 數據機重置 | OTHER | S21/0/StaDev/5A5Other |  |  |  | CDC | 349 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/RESET | RESET
S21 | 大寮SS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-30-13 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.水位警報(2) | 所內水位重警報 | OTHER | S21/0/StaDev/Water2 |  |  |  | CDC | 350 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-30-12 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.水位警報(1) | 所內水位輕警報 | OTHER | S21/0/StaDev/Water1 |  |  |  | CDC | 351 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S21/0/StaDev/Lights3 |  |  |  | CDC | 352 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-37-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S21/0/StaDev/9A5Other |  |  |  | CDC | 353 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.640_87A | 新營二路(640) 87RY | LINE69 | S21/69/640/87A |  |  |  | CDC | 354 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | CFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 大寮SS.640_CFA | 新營二路(640) 通訊故障 | LINE69 | S21/69/640/87CFA |  |  |  | CDC | 355 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 大寮SS.640_87UL | 新營二路(640) 87RY U/L | LINE69 | S21/69/640/87UL |  |  |  | CDC | 356 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 640 | 新營二路(640) |  | RYFA | [17 empty] | 1-37-10 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.640_RYFA | 640 IED警報 | OTHER | S21/69/640/RYFA |  |  |  | CDC | 357 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 大寮SS.710_87A | 新營一路(710) 87RY | LINE69 | S21/69/710/87A |  |  |  | CDC | 358 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | CFA | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 大寮SS.710_CFA | 新營一路(710) 通訊故障 | LINE69 | S21/69/710/87CFA |  |  |  | CDC | 359 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 大寮SS.710_87UL | 新營一路(710) 87RY U/L | LINE69 | S21/69/710/87UL |  |  |  | CDC | 360 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 710 | 新營一路(710) |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.710_RYFA | 710 IED警報 | OTHER | S21/69/710/RYFA |  |  |  | CDC | 361 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-14 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.開關場水位警報 | 開關場水位警報 | OTHER | S21/0/StaDev/Water3 |  |  |  | CDC | 362 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S21/11/ComPoint/IRFA |  |  |  | CDC | 363 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S21/0/StaDev/Water4 |  |  |  | CDC | 364 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大布線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大布線79LOA | 大布線79LOA | OTHER | S21/11/JE23/LOA |  |  |  | CDC | 365 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大江線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大江線79LOA | 大江線79LOA | OTHER | S21/11/JE26/LOA |  |  |  | CDC | 366 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大海線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大海線79LOA | 大海線79LOA | OTHER | S21/11/JE30/LOA |  |  |  | CDC | 367 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大順線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大順線79LOA | 大順線79LOA | OTHER | S21/11/JE28/LOA |  |  |  | CDC | 368 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大塭線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大塭線79LOA | 大塭線79LOA | OTHER | S21/11/JE22/LOA |  |  |  | CDC | 369 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大新線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大新線79LOA | 大新線79LOA | OTHER | S21/11/JE25/LOA |  |  |  | CDC | 370 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大溝線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大溝線79LOA | 大溝線79LOA | OTHER | S21/11/JE21/LOA |  |  |  | CDC | 371 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大義線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大義線79LOA | 大義線79LOA | OTHER | S21/11/JE24/LOA |  |  |  | CDC | 372 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大龍線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大龍線79LOA | 大龍線79LOA | OTHER | S21/11/JE29/LOA |  |  |  | CDC | 373 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  |  |  |  | 大華線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.大華線79LOA | 大華線79LOA | OTHER | S21/11/JE27/LOA |  |  |  | CDC | 374 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 161 | 161kV | 630 | 新塭線(630) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 大寮SS.630_87A | 新塭線(630) 87RY | LINE161 | S21/69/630/87A |  |  |  | CDC | 375 | GENERICDIPoint | SS200_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S21 | 大寮SS | 161 | 161kV | 630 | 新塭線(630) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 大寮SS.630_87UL | 新塭線(630) 87RY U/L | LINE161 | S21/69/630/87UL |  |  |  | CDC | 376 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S21 | 大寮SS | 0 |  | 630 | 新塭線(630) |  | CFA | [17 empty] | 1-32-03 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.630_CFA | 630 CFA | OTHER | S21/69/630/87CFA |  |  |  | CDC | 377 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 630 | 新塭線(630) |  | RYFA | [17 empty] | 1-3B-14 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.630_RYFA | 630 RYFA | OTHER | S21/69/630/RYFA |  |  |  | CDC | 378 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | 691BUS | 69#1BUS |  | 27BA | [17 empty] | 1-32-15 | [7 empty] | DDCS2_2 | [8 empty] | 大寮SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | S21/69/1BUS/27A |  |  |  | CDC | 379 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | BUSRY | BUSRY |  | BF | [17 empty] | 1-32-13 | [7 empty] | DDCS2_2 | [8 empty] | 大寮SS.BUSRY_BF | BUSRY BF | OTHER | S21/69/ComPoint/BFA |  |  |  | CDC | 380 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | BUSRY | BUSRY |  | 87CTFA | [17 empty] | 1-32-14 | [7 empty] | DDCS2_2 | [8 empty] | 大寮SS.BUSRY_CTFA | BUSRY CTFA | OTHER | S21/69/ComPoint/87CTFA |  |  |  | CDC | 381 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_1 | [8 empty] | 大寮SS.PMA | POWER METER警報 | OTHER | S21/0/StaDev/PMA |  |  |  | CDC | 382 | GENERICDIPoint | SS200_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S21 | 大寮SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 383 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 384 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.630LE | 630LE (非取樣點) | LINE69 | S21/69/630/LE0 |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.630BE | 630BE (非取樣點) | LINE69 | S21/69/630/BE0 |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.640LE | 640LE (非取樣點) | LINE69 | S21/69/640/LE0 |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 640 | 新營二路(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.640BE | 640BE (非取樣點) | LINE69 | S21/69/640/BE0 |  |  |  |  | 388 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | LE0 | 710LE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.710LE | 710LE (非取樣點) | LINE69 | S21/69/710/LE0 |  |  |  |  | 389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 710 | 新營一路(710) |  | BE0 | 710BE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.710BE | 710BE (非取樣點) | LINE69 | S21/69/710/BE0 |  |  |  |  | 390 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 210 | #1SC(210) |  | DS1 | 211 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.211_DS | 211_DS (非取樣點) | FEEDER | S21/11/JE21/D1 |  |  |  |  | 391 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 210 | #1SC(210) |  | DS2 | 212 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.212_DS | 212_DS (非取樣點) | FEEDER | [5 empty] | 392 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2120 | 2122_DS(2120) |  | DS2 | 2122 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2122_DS | 2122_DS (非取樣點) | FEEDER | S21/11/JE21/D2 |  |  |  |  | 393 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE21 | JE21_ES |  | LE0 | JE21_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE21_ES | JE21_ES (非取樣點) | FEEDER | S21/11/JE21/ES |  |  |  |  | 394 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 220 | #2SC(220) |  | DS1 | 221 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.221_DS | 221_DS (非取樣點) | FEEDER | S21/11/JE22/D1 |  |  |  |  | 395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 220 | #2SC(220) |  | DS2 | 222 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.222_DS | 222_DS (非取樣點) | FEEDER | [5 empty] | 396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2220 | 2221_DS(2220) |  | DS1 | 2221 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2221_DS | 2221_DS (非取樣點) | FEEDER | [5 empty] | 397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE22 | JE22_ES |  | LE0 | JE22_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE22_ES | JE22_ES (非取樣點) | FEEDER | S21/11/JE22/ES |  |  |  |  | 398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 230 | 231_DS(230) |  | DS1 | 231 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.231_DS | 231_DS (非取樣點) | FEEDER | S21/11/JE23/D1 |  |  |  |  | 399 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 230 | 232_DS(230) |  | DS2 | 232 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.232_DS | 232_DS (非取樣點) | FEEDER | [5 empty] | 400 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2320 | 2322_DS(2320) |  | DS2 | 2322 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2322_DS | 2322_DS (非取樣點) | FEEDER | S21/11/JE23/D2 |  |  |  |  | 401 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE23 | JE23_ES |  | LE0 | JE23_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE23_ES | JE23_ES (非取樣點) | FEEDER | S21/11/JE23/ES |  |  |  |  | 402 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 240 | 241_DS(240) |  | DS1 | 241 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.241_DS | 241_DS (非取樣點) | FEEDER | S21/11/JE24/D1 |  |  |  |  | 403 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 240 | 242_DS(240) |  | DS2 | 242 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.242_DS | 242_DS (非取樣點) | FEEDER | S21/11/JE24/D2 |  |  |  |  | 404 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2420 | 2425_DS(2420) |  | DS5 | 2425 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2425_DS | 2425_DS (非取樣點) | FEEDER | [5 empty] | 405 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE24 | JE24_ES |  | LE0 | JE24_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE24_ES | JE24_ES (非取樣點) | FEEDER | S21/11/JE24/ES |  |  |  |  | 406 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 250 | 251_DS(250) |  | DS1 | 251 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.251_DS | 251_DS (非取樣點) | FEEDER | S21/11/JE25/D1 |  |  |  |  | 407 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 250 | 252_DS(250) |  | DS2 | 252 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.252_DS | 252_DS (非取樣點) | FEEDER | S21/11/JE25/D2 |  |  |  |  | 408 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2520 | 2524_DS(2520) |  | DS4 | 2524 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2524_DS | 2524_DS (非取樣點) | FEEDER | [5 empty] | 409 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE25 | JE25_ES |  | LE0 | JE25_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE25_ES | JE25_ES (非取樣點) | FEEDER | S21/11/JE25/ES |  |  |  |  | 410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 260 | 261_DS(260) |  | DS1 | 261 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.261_DS | 261_DS (非取樣點) | FEEDER | S21/11/JE26/D1 |  |  |  |  | 411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 260 | 262_DS(260) |  | DS2 | 262 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.262_DS | 262_DS (非取樣點) | FEEDER | S21/11/JE26/D2 |  |  |  |  | 412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2620 | 2625_DS(2620) |  | DS5 | 2625 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2625_DS | 2625_DS (非取樣點) | FEEDER | [5 empty] | 413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE26 | JE26_ES |  | LE0 | JE26_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE26_ES | JE26_ES (非取樣點) | FEEDER | S21/11/JE26/ES |  |  |  |  | 414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 270 | 271_DS(270) |  | DS1 | 271 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.271_DS | 271_DS (非取樣點) | FEEDER | S21/11/JE27/D1 |  |  |  |  | 415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 270 | 272_DS(270) |  | DS2 | 272 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.272_DS | 272_DS (非取樣點) | FEEDER | S21/11/JE27/D2 |  |  |  |  | 416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2720 | 2728_DS(2720) |  | DS8 | 2728 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2728_DS | 2728_DS (非取樣點) | FEEDER | [5 empty] | 417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE27 | JE27_ES |  | LE0 | JE27_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE27_ES | JE27_ES (非取樣點) | FEEDER | S21/11/JE27/ES |  |  |  |  | 418 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 280 | 281_DS(280) |  | DS1 | 281 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.281_DS | 281_DS (非取樣點) | FEEDER | S21/11/JE28/D1 |  |  |  |  | 419 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 280 | 282_DS(280) |  | DS2 | 282 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.282_DS | 282_DS (非取樣點) | FEEDER | S21/11/JE28/D2 |  |  |  |  | 420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2820 | 2829_DS(2820) |  | DS9 | 2829 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2829_DS | 2829_DS (非取樣點) | FEEDER | [5 empty] | 421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE28 | JE28_ES |  | LE0 | JE28_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE28_ES | JE28_ES (非取樣點) | FEEDER | S21/11/JE28/ES |  |  |  |  | 422 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 290 | 291_DS(290) |  | DS1 | 291 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.291_DS | 291_DS (非取樣點) | FEEDER | S21/11/JE29/D1 |  |  |  |  | 423 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 290 | 292_DS(290) |  | DS2 | 292 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.292_DS | 292_DS (非取樣點) | FEEDER | S21/11/JE29/D2 |  |  |  |  | 424 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2920 | 2928_DS(2920) |  | DS8 | 2928 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2928_DS | 2928_DS (非取樣點) | FEEDER | [5 empty] | 425 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE29 | JE29_ES |  | LE0 | JE29_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE29_ES | JE29_ES (非取樣點) | FEEDER | S21/11/JE29/ES |  |  |  |  | 426 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 300 | 301_DS(300) |  | DS1 | 301 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.301_DS | 301_DS (非取樣點) | FEEDER | S21/11/JE30/D1 |  |  |  |  | 427 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 300 | 302_DS(300) |  | DS2 | 302 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.302_DS | 302_DS (非取樣點) | FEEDER | S21/11/JE30/D2 |  |  |  |  | 428 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 345 | 345kV | 3020 | 3029_DS(3020) |  | DS9 | 3029 | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.3029_DS | 3029_DS (非取樣點) | FEEDER | [5 empty] | 429 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | JE30 | JE30_ES |  | LE0 | JE30_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.JE30_ES | JE30_ES (非取樣點) | FEEDER | S21/11/JE30/ES |  |  |  |  | 430 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S21/11/TIE1/D1 |  |  |  |  | 431 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.750TE | 750TE (非取樣點) | DTR | S21/69/750/TE0 |  |  |  |  | 432 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.750BE | 750BE (非取樣點) | DTR | S21/69/750/BE0 |  |  |  |  | 433 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.1M_DS | 1M_DS (非取樣點) | DTR | S21/11/M1/D1 |  |  |  |  | 434 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.1M_ES | 1M_ES (非取樣點) | DTR | S21/11/M1/ES |  |  |  |  | 435 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.760TE | 760TE (非取樣點) | DTR | S21/69/760/TE0 |  |  |  |  | 436 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.760BE | 760BE (非取樣點) | DTR | S21/69/760/BE0 |  |  |  |  | 437 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2M_DS | 2M_DS (非取樣點) | DTR | S21/11/M2/D1 |  |  |  |  | 438 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.2M_ES | 2M_ES (非取樣點) | DTR | S21/11/M2/ES |  |  |  |  | 439 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.3M_DS | 3M_DS (非取樣點) | DTR | S21/11/M3/D1 |  |  |  |  | 440 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.3M_ES | 3M_ES (非取樣點) | DTR | S21/11/M3/ES |  |  |  |  | 441 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.210_ES | 210_ES (非取樣點) | SC | S21/11/210/ES |  |  |  |  | 442 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.211DS | 211DS (非取樣點) | SC | S21/11/210/D1 |  |  |  |  | 443 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.212DS | 212DS (非取樣點) | SC | S21/11/210/D2 |  |  |  |  | 444 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.220_ES | 220_ES (非取樣點) | SC | S21/11/220/ES |  |  |  |  | 445 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.221DS | 221DS (非取樣點) | SC | S21/11/220/D1 |  |  |  |  | 446 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.222DS | 222DS (非取樣點) | SC | S21/11/220/D2 |  |  |  |  | 447 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S21 | 大寮SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 大寮SS.69B1E | 69B1E (非取樣點) | BUS | S21/69/1BUS/BE1 |  |  |  |  | 448 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 449 | NotelDIPoint | [38 empty] | START/STOP | STOP
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | (臨)TE0 | 760(臨)TE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.760(臨)TE | 760(臨)TE (非取樣點) | DTR | S21/69/770/TE0 |  |  |  |  | 450 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 760 | #2MTR(760) |  | (臨)BE0 | 760(臨)BE | [24 empty] | DDCS2_1 | [8 empty] | 大寮SS.760(臨)BE | 760(臨)BE (非取樣點) | DTR | S21/69/770/BE0 |  |  |  |  | 451 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | (臨)LE2 | 632(臨)LE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.632(臨)LE | 630LE (非取樣點) | LINE69 | S21/69/360/LE0 |  |  |  |  | 452 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S21 | 大寮SS | 69 | 69kV | 630 | 新塭線(630) |  | (臨)BE2 | 632(臨)BE | [24 empty] | ADCS_N | [8 empty] | 大寮SS.632(臨)BE | 632BE (非取樣點) | LINE69 | S21/69/360/BE0 |  |  |  |  | 453 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo