## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S23 | 博愛SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 一號 BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S23_A1 | [8 empty] | 博愛SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S23 | 博愛SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0095 |  |  | 1-DF |  |  | 69KV＃2BUS | A2 | 69KV#2BUS 電流 | kV_-90_90(-2000_2000) | aab | B2/S23_A1 | [8 empty] | 博愛SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S23 | 博愛SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | ＃1 MCB | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | aaa | B2/S23_D1 | [8 empty] | 博愛SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | ＃2 MCB | KV | 二號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aba | B2/S23_D1 | [8 empty] | 博愛SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | SPARE |  |  | kV_-9_9(-2000_2000) | not found | B2/S23_D1 | [8 empty] | 博愛SS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0130 |  |  | 2-82 |  |  | SPARE |  |  | kV_-9_9(-2000_2000) | not found | B2/S23_D1 | [8 empty] | 博愛SS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0165 |  |  | 2-A5 |  |  | ＃4 MCB | KV | 四號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aca | B2/S23_D1 | [8 empty] | 博愛SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS |  |  |  |  | CDC | 8 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaaz | B2/S23_A1 | [8 empty] | 博愛SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 9 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0256 |  |  | 1-31-13 |  |  | 69KV #1 BUS | 6VUA1 | 69KV BUS衡相監視警報 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 10 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-02 |  |  | 69KV #1BUS | 87B1A |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/2Bus | [13 empty] | aaaz | B2/S23_A1 | [8 empty] | 博愛SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 12 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-31-14 |  |  | 69KV #2 BUS | 6VUA2 | 69KV BUS衡相監視警報 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-03 |  |  | 69KV #2BUS | 87B2A |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 640 | MW | L2博愛溶劑線有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.640_MW | 溶劑線 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 640 | MVAR | L2博愛溶劑線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.640_MVAR | 溶劑線 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 640 MWH(+) | MWH(+) | 博愛溶劑線 |  |  | B2/S23_A1 | [15 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 610 | MW | L4博愛水上線有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.610_MW | 水上線 MW | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 610 | MVAR | L4博愛水上線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.610_MVAR | 水上線 MVAR | LINE69 |  |  |  |  | CDC | 19 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 610 MWH(+) | MWH(+) | 博愛水上線 |  |  | B2/S23_A1 | [15 empty] | CDC | 20 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 620 | MW | L3後湖博愛線有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.620_MW | 後湖線 MW | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 620 | MVAR | L3後湖博愛線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.620_MVAR | 後湖線 MVAR | LINE69 |  |  |  |  | CDC | 22 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 620 MWH(+) | MWH(+) | 後湖博愛線 |  |  | B2/S23_A1 | [15 empty] | CDC | 23 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 660 | MW | L5博愛鐵嘉白線有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.660_MW | 博鐵白線 MW | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 660 | MVAR | L5博愛鐵嘉白線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.660_MVAR | 博鐵白線 MVAR | LINE69 |  |  |  |  | CDC | 25 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 660 MWH(+) | MWH(+) | 博愛鐵嘉白線 |  |  | B2/S23_A1 | [15 empty] | CDC | 26 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 650 | MW | L1博愛鐵嘉紅線有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.650_MW | 博鐵紅線 MW | LINE69 |  |  |  |  | CDC | 27 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 650 | MVAR | L1 博愛鐵嘉紅線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.650_MVAR | 博鐵紅線 MVAR | LINE69 |  |  |  |  | CDC | 28 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | 650 MWH(+) | MWH(+) | 博愛鐵嘉紅線 |  |  | B2/S23_A1 | [15 empty] | CDC | 29 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 670 | MW | L6 嘉義博愛有效電力 | MW_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.670_MW | 嘉博線 MW | LINE69 |  |  |  |  | CDC | 30 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 670 | MVAR | L6嘉義博愛線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.670_MVAR | 嘉博線 MVAR | LINE69 |  |  |  |  | CDC | 31 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0034 |  |  | 2-42 |  |  | 670 MWH(+) | MWH(+) | 嘉義博愛線 |  |  | B2/S23_A1 | [15 empty] | CDC | 32 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 640 | PHA | 博愛溶劑線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.640_PHA | 溶劑線(640) 相間RY | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 640 | GDA | 博愛溶劑線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.640_GDA | 溶劑線(640) 接地RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 640 | 85A | 博愛溶劑線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.640_85A | 溶劑線(640) 85RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 1-32-01 |  |  | 640 | 274A U/L | 博愛溶劑線 副線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.640_74A | 溶劑線(640) 74RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 610 | PHA | 博愛水上線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610_PHA | 水上線(610) 相間RY | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 610 | GDA | 博愛水上線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610_GDA | 水上線(610) 接地RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | 610 | 87A | 博愛水上線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610_87A | 水上線(610) 87RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 1-32-03 |  |  | SPARE | 474A U/L | 副線(SEQ NO 1-35-04已有定義)(無接線) |  |  | B2/S23_A1 | [15 empty] | CDC | 40 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-02 |  |  | 620 | PHA | 後湖博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620_PHA | 後博線(620) 相間RY | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-03 |  |  | 620 | GDA | 後湖博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620_GDA | 後博線(620) 接地RY | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-01 |  |  | 620 | 87A | 後湖博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620_87A | 後博線(620) 87RY | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 1-32-05 |  |  | 620 | 374A U/L | 後湖博愛線 副線(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620_74A | 後博線(620) 74RY | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-09-06 |  |  | 660 | PHA | 博愛鐵嘉白線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660_PHA | 博鐵白線(660) 相間RY | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-09-07 |  |  | 660 | GDA | 博愛鐵嘉白線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660_GDA | 博鐵白線(660) 接地RY | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-09-05 |  |  | 660 | 87A | 博愛鐵嘉白線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660_87A | 博鐵白線(660) 87RY | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 1-32-07 |  |  | 660 | 574A U/L | 博愛鐵嘉白線 副線(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660_74A | 博鐵白線(660) 74RY | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-02 |  |  | 650 | PHA | 博愛鐵嘉紅線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650_PHA | 博鐵紅線(650) 相間RY | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-03 |  |  | 650 | GDA | 博愛鐵嘉紅線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650_GDA | 博鐵紅線(650) 接地RY | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-01 |  |  | 650 | 87A | 博愛鐵嘉紅線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650_87A | 博鐵紅線(650) 87RY | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 1-32-09 |  |  | 650 | 174A U/L | 博愛鐵嘉紅線 副線(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650_74A | 博鐵紅線(650) 74RY | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0A-06 |  |  | 670 | PHA | 嘉義博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670_PHA | 嘉博線(670) 相間RY | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0A-07 |  |  | 670 | GDA | 嘉義博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670_GDA | 嘉博線(670) 接地RY | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0A-05 |  |  | 670 | 87A | 嘉義博愛線 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670_87A | 嘉博線(670) 87RY | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 1-32-11 |  |  | 670 | 674A U/L | 嘉義博愛線 副線(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670_74A | 嘉博線(670) 74RY | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 680 | 水上線(680) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-04-07 |  |  | SPARE | 85A | 680 |  |  | B2/S23_A1 | [15 empty] | CDC | 57 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0259 |  | 0010 | 1-32-00 |  | 1-09 | 640 | 285S U/L | 博愛溶劑線 69KV |  |  | B2/S23_A1 | [8 empty] | 博愛SS.640_85UL | 溶劑線(640) 85RY U/L | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0261 |  | 0011 | 1-32-02 |  | 1-0A | 610 | 487S U/L | 博愛水上線 69KV |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610_87UL | 水上線(610) 87RY U/L | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0263 |  | 0012 | 1-32-04 |  | 1-0B | 620 | 387S U/L | 後湖博愛線 69KV |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620_87UL | 後博線(620) 87RY U/L | LINE69 |  |  |  |  | CDC | 60 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0265 |  | 0013 | 1-32-06 |  | 1-0C | 660 | 585S U/L | 博愛鐵嘉白線 69KV(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660_87UL | 博鐵白線(660) 87RY U/L | LINE69 |  |  |  |  | CDC | 61 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0267 |  | 0014 | 1-32-08 |  | 1-0D | 650 | 185S U/L | 博愛鐵嘉紅線 69KV(無接線) |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650_87UL | 博鐵紅線(650) 87RY U/L | LINE69 |  |  |  |  | CDC | 62 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0269 |  | 0015 | 1-32-10 |  | 1-0E | 670 | 687S U/L | 嘉義博愛線 69KV |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670_87UL | 嘉博線(670) 87RY U/L | LINE69 |  |  |  |  | CDC | 63 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 680 | 水上線(680) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0271 |  | 0016 | 1-32-12 |  | 1-0F | 680 | 685S U/L | LINE 6 69KV(無接線) |  |  | B2/S23_A1 | [15 empty] | CDC | 64 | DI_LINE69(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/S23C66/T1 |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 640 | 640AS | 博愛溶劑線 |  | aada | B2/S23_A1 | [8 empty] | 博愛SS.640_CB | 640(溶劑線) CB | LINE69 |  |  |  |  | CDC | 65 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/S23S28/T1 |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 610 | 610AS | 博愛水上線 |  | aaga | B2/S23_A1 | [8 empty] | 博愛SS.610_CB | 610(水上線) CB | LINE69 |  |  |  |  | CDC | 66 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/S26S23/T2 |  | 0075 |  | 0004 | 1-09-00 |  | 1-03 | 620 | 620AS | 後湖博愛線 |  | aaea | B2/S23_A1 | [8 empty] | 博愛SS.620_CB | 620(後博線) CB | LINE69 |  |  |  |  | CDC | 67 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/S23C79W/T1 |  | 0079 |  | 0005 | 1-09-04 |  | 1-04 | 660 | 660AS | 博愛鐵嘉白線 |  | aaia | B2/S23_A1 | [8 empty] | 博愛SS.660_CB | 660(博鐵白線) CB | LINE69 |  |  |  |  | CDC | 68 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/S23C79R/T1 |  | 0083 |  | 0006 | 1-0A-00 |  | 1-05 | 650 | 650AS | 博愛鐵嘉紅線 |  | aaba | B2/S23_A1 | [8 empty] | 博愛SS.650_CB | 650(博鐵紅線) CB | LINE69 |  |  |  |  | CDC | 69 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1BUS | B/2BUS | L/P05S23/T2 |  | 0087 |  | 0007 | 1-0A-04 |  | 1-06 | 670 | 670AS | 嘉義博愛線 |  | aaja | B2/S23_A1 | [8 empty] | 博愛SS.670_CB | 670(嘉博線) CB | LINE69 |  |  |  |  | CDC | 70 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0363 | 364 | 0019 | 1-38-08 | 1-38-09 | 1-12 | LINE-2 1AS | 641AS | 博愛溶劑線 641 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.641_DS | 641(溶劑線) DS | LINE69 |  |  |  |  | CDC | 71 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0365 | 366 | 0020 | 1-38-10 | 1-38-11 | 1-13 | LINE-2 2AS | 642AS | 博愛溶劑線 642 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.642_DS | 642(溶劑線) DS | LINE69 |  |  |  |  | CDC | 72 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | DS1 | 611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0371 | 372 | 0023 | 1-39-00 | 1-39-01 | 1-16 | LINE-3 1AS | 611AS | 博愛水上線 611 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.611_DS | 611(水上線) DS | LINE69 |  |  |  |  | CDC | 73 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | DS2 | 612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0373 | 374 | 0024 | 1-39-02 | 1-39-03 | 1-17 | LINE-3 2AS | 612AS | 博愛水上線 612 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.612_DS | 612(水上線) DS | LINE69 |  |  |  |  | CDC | 74 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | DS1 | 621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0379 | 380 | 0027 | 1-39-08 | 1-39-09 | 1-1A | LINE-4 1AS | 621AS | 後湖博愛線 621 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.621_DS | 621(後博線) DS | LINE69 |  |  |  |  | CDC | 75 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | DS2 | 622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0381 | 382 | 0028 | 1-39-10 | 1-39-11 | 1-1B | LINE-4 2AS | 622AS | 後湖博愛線 622 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.622_DS | 622(後博線) DS | LINE69 |  |  |  |  | CDC | 76 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | DS1 | 661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0387 | 388 | 0031 | 1-3A-00 | 1-3A-01 | 1-1E | LINE-5 1AS | 661AS | 博愛鐵嘉白線 661 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.661_DS | 661(博鐵白線) DS | LINE69 |  |  |  |  | CDC | 77 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | DS2 | 662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0389 | 390 | 0032 | 1-3A-02 | 1-3A-03 | 1-1F | LINE-5 2AS | 662AS | 博愛鐵嘉白線 662 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.662_DS | 662(博鐵白線) DS | LINE69 |  |  |  |  | CDC | 78 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | DS1 | 651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0395 | 396 | 0035 | 1-3A-08 | 1-3A-09 | 1-22 | LINE-6 1AS | 651AS | 博愛鐵嘉紅線 651 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.651_DS | 651(博鐵紅線) DS | LINE69 |  |  |  |  | CDC | 79 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | DS2 | 652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0397 | 398 | 0036 | 1-3A-10 | 1-3A-11 | 1-23 | LINE-6 2AS | 652AS | 博愛鐵嘉紅線 652 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.652_DS | 652(博鐵紅線) DS | LINE69 |  |  |  |  | CDC | 80 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | DS1 | 671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0403 | 404 | 0039 | 1-3B-00 | 1-3B-01 | 1-26 | #1TR 1AS | 671AS | 嘉義博愛線 671 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.671_DS | 671(嘉博線) DS | LINE69 |  |  |  |  | CDC | 81 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | DS2 | 672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0405 | 406 | 0040 | 1-3B-02 | 1-3B-03 | 1-27 | #1TR 2AS | 672AS | 嘉義博愛線 672 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.672_DS | 672(嘉博線) DS | LINE69 |  |  |  |  | CDC | 82 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0367 | 368 | 0021 | 1-38-12 | 1-38-13 | 1-14 | LINE-2 3AS | 643AS | 博愛溶劑線 643 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.643_DS | 643(溶劑線) DS | LINE69 |  |  |  |  | CDC | 83 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | ES3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0369 | 370 | 0022 | 1-38-14 | 1-38-15 | 1-15 | LINE-2 3EAS | 643EAS | 博愛溶劑線 643E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.643E_ES | 643E(溶劑線) ES | LINE69 |  |  |  |  | CDC | 84 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 85 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 86 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | DS3 | 613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0375 | 376 | 0025 | 1-39-04 | 1-39-05 | 1-18 | LINE-3 3AS | 613AS | 博愛水上線 613 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.613_DS | 613(水上線) DS | LINE69 |  |  |  |  | CDC | 87 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | ES3 | 613E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0377 | 378 | 0026 | 1-39-06 | 1-39-07 | 1-19 | LINE-3 3EAS | 613EAS | 博愛水上線 613E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.613E_ES | 613E(水上線) ES | LINE69 |  |  |  |  | CDC | 88 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 89 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 90 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | DS3 | 623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0383 | 384 | 0029 | 1-39-12 | 1-39-13 | 1-1C | LINE-4 3AS | 623AS | 後湖博愛線 623 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.623_DS | 623(後博線) DS | LINE69 |  |  |  |  | CDC | 91 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | ES3 | 623E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0385 | 386 | 0030 | 1-39-14 | 1-39-15 | 1-1D | LINE-4 3EAS | 623EAS | 後湖博愛線 623E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.623E_ES | 623E(後博線) ES | LINE69 |  |  |  |  | CDC | 92 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 93 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 94 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | DS3 | 663 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0391 | 392 | 0033 | 1-3A-04 | 1-3A-05 | 1-20 | LINE-5 3AS | 663AS | 博愛鐵嘉白線 663 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.663_DS | 663(博鐵白線) DS | LINE69 |  |  |  |  | CDC | 95 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | ES3 | 663E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0393 | 394 | 0034 | 1-3A-06 | 1-3A-07 | 1-21 | LINE-5 3EAS | 663EAS | 博愛鐵嘉白線 663E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.663E_ES | 663E(博鐵白線) ES | LINE69 |  |  |  |  | CDC | 96 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 97 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 98 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | DS3 | 653 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0399 | 400 | 0037 | 1-3A-12 | 1-3A-13 | 1-24 | LINE-6 3AS | 653AS | 博愛鐵嘉紅線 653 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.653_DS | 653(博鐵紅線) DS | LINE69 |  |  |  |  | CDC | 99 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | ES3 | 653E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0401 | 402 | 0038 | 1-3A-14 | 1-3A-15 | 1-25 | LINE-6 3EAS | 653EAS | 博愛鐵嘉紅線 653E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.653E_ES | 653E(博鐵紅線) ES | LINE69 |  |  |  |  | CDC | 100 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.650LE | 650LE (非取樣點) | LINE69 | [5 empty] | 101 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 102 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | DS3 | 673 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0407 | 408 | 0041 | 1-3B-04 | 1-3B-05 | 1-28 | #2TR 1AS | 673AS | 嘉義博愛線 673 ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.673_DS | 673(嘉博線) DS | LINE69 |  |  |  |  | CDC | 103 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | ES3 | 673E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0409 | 410 | 0042 | 1-3B-06 | 1-3B-07 | 1-29 | #2TR 2AS | 673EAS | 嘉義博愛線 673E ABS ON |  |  | B2/S23_A1 | [8 empty] | 博愛SS.673E_ES | 673E(嘉博線) ES | LINE69 |  |  |  |  | CDC | 104 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 105 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 106 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十一線KVAR | 11KV博十一線 KVAR | FEEDER |  |  |  |  | CDC | 107 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F20 KWH(+) | JB40 | Power Meter 6720 Plus |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 108 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十二線KVAR | 11KV博十二線 KVAR | FEEDER |  |  |  |  | CDC | 109 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F19 KWH(+) | JB39 | Power Meter 6720 Plus |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 110 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十三線KVAR | 11KV博十三線 KVAR | FEEDER |  |  |  |  | CDC | 111 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F18 KWH(+) | JB38 | Power Meter 6720 Plus |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 112 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十四線KVAR | 11KV博十四線 KVAR | FEEDER |  |  |  |  | CDC | 113 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F17 KWH(+) | JB37 | Power Meter 6720 Plus |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 114 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十五線KVAR | 11KV博十五線 KVAR | FEEDER |  |  |  |  | CDC | 115 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F16 KWH(+) | JB36 | Power Meter 6720 Plus |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 116 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB26) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | JB36 | VAR | 博十六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線KVAR | 11KV博十六線 KVAR | FEEDER |  |  |  |  | CDC | 117 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | JB36 | A1 | 博十六線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線A1 | 11KV博十六線 R相AMP | FEEDER |  |  |  |  | CDC | 118 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | JB36 | A2 | 博十六線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線A2 | 11KV博十六線 S相AMP | FEEDER |  |  |  |  | CDC | 119 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | JB36 | A3 | 博十六線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線A3 | 11KV博十六線 T相AMP | FEEDER |  |  |  |  | CDC | 120 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | JB36 | NA | 博十六線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線A0 | 11KV博十六線 N相AMP | FEEDER |  |  |  |  | CDC | 121 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB27) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | JB37 | VAR | 博十七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線KVAR | 11KV博十七線 KVAR | FEEDER |  |  |  |  | CDC | 122 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | JB37 | A1 | 博十七線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線A1 | 11KV博十七線 R相AMP | FEEDER |  |  |  |  | CDC | 123 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | JB37 | A2 | 博十七線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線A2 | 11KV博十七線 S相AMP | FEEDER |  |  |  |  | CDC | 124 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | JB37 | A3 | 博十七線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線A3 | 11KV博十七線 T相AMP | FEEDER |  |  |  |  | CDC | 125 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | JB37 | NA | 博十七線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線A0 | 11KV博十七線 N相AMP | FEEDER |  |  |  |  | CDC | 126 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB28) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | JB38 | VAR | 博十八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線KVAR | 11KV博十八線 KVAR | FEEDER |  |  |  |  | CDC | 127 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | JB38 | A1 | 博十八線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線A1 | 11KV博十八線 R相AMP | FEEDER |  |  |  |  | CDC | 128 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | JB38 | A2 | 博十八線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線A2 | 11KV博十八線 S相AMP | FEEDER |  |  |  |  | CDC | 129 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | JB38 | A3 | 博十八線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線A3 | 11KV博十八線 T相AMP | FEEDER |  |  |  |  | CDC | 130 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | JB38 | NA | 博十八線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線A0 | 11KV博十八線 N相AMP | FEEDER |  |  |  |  | CDC | 131 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB29) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | JB39 | VAR | 博十九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線KVAR | 11KV博十九線 KVAR | FEEDER |  |  |  |  | CDC | 132 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | JB39 | A1 | 博十九線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線A1 | 11KV博十九線 R相AMP | FEEDER |  |  |  |  | CDC | 133 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | JB39 | A2 | 博十九線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線A2 | 11KV博十九線 S相AMP | FEEDER |  |  |  |  | CDC | 134 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | JB39 | A3 | 博十九線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線A3 | 11KV博十九線 T相AMP | FEEDER |  |  |  |  | CDC | 135 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | JB39 | NA | 博十九線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線A0 | 11KV博十九線 N相AMP | FEEDER |  |  |  |  | CDC | 136 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB30) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | JB40 | VAR | 博二十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線KVAR | 11KV博二十線 KVAR | FEEDER |  |  |  |  | CDC | 137 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | JB40 | A1 | 博二十線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線A1 | 11KV博二十線 R相AMP | FEEDER |  |  |  |  | CDC | 138 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | JB40 | A2 | 博二十線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線A2 | 11KV博二十線 S相AMP | FEEDER |  |  |  |  | CDC | 139 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | JB40 | A3 | 博二十線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線A3 | 11KV博二十線 T相AMP | FEEDER |  |  |  |  | CDC | 140 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | JB40 | NA | 博二十線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線A0 | 11KV博二十線 N相AMP | FEEDER |  |  |  |  | CDC | 141 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | F1(JB21) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB21_PHA | 11KV博一線(JB21) 相間RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | F1(JB21) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB21_GDA | 11KV博一線(JB21) 接地RY | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0282 |  | 0061 | 1-33-07 |  | 1-3C | JB21 | 79S U/L | 博一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB21_79UL | 11KV博一線(JB21) 79RY U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0323 |  | 0113 | 1-36-00 |  | 1-70 | JB21 | ADJ(U/L) | 博一線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB21_ADJ | 11KV博一線(JB21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-03 |  |  | F2(JB22) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB22_PHA | 11KV博二線(JB22) 相間RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | F2(JB22) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB22_GDA | 11KV博二線(JB22) 接地RY | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0283 |  | 0062 | 1-33-08 |  | 1-3D | JB22 | 79S U/L | 博二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB22_79UL | 11KV博二線(JB22) 79RY U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0324 |  | 0114 | 1-36-01 |  | 1-71 | JB22 | ADJ(U/L) | 博二線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB22_ADJ | 11KV博二線(JB22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | F3(JB23) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB23_PHA | 11KV博三線(JB23) 相間RY | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0D-06 |  |  | F3(JB23) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB23_GDA | 11KV博三線(JB23) 接地RY | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0284 |  | 0063 | 1-33-09 |  | 1-3E | JB23 | 79S U/L | 博三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB23_79UL | 11KV博三線(JB23) 79RY U/L | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0325 |  | 0115 | 1-36-02 |  | 1-72 | JB23 | ADJ(U/L) | 博三線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB23_ADJ | 11KV博三線(JB23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | F4(JB24) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB24_PHA | 11KV博四線(JB24) 相間RY | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | F4(JB24) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB24_GDA | 11KV博四線(JB24) 接地RY | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0285 |  | 0064 | 1-33-10 |  | 1-3F | JB24 | 79S U/L | 博四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB24_79UL | 11KV博四線(JB24) 79RY U/L | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0326 |  | 0116 | 1-36-03 |  | 1-73 | JB24 | ADJ(U/L) | 博四線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB24_ADJ | 11KV博四線(JB24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-01 |  |  | F5(JB25) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB25_PHA | 11KV博五線(JB25) 相間RY | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | F5(JB25) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB25_GDA | 11KV博五線(JB25) 接地RY | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0286 |  | 0065 | 1-33-11 |  | 1-40 | JB25 | 79S U/L | 博五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB25_79UL | 11KV博五線(JB25) 79RY U/L | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0327 |  | 0117 | 1-36-04 |  | 1-74 | JB25 | ADJ(U/L) | 博五線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB25_ADJ | 11KV博五線(JB25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | F6(JB26) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB26_PHA | 11KV博六線(JB26) 相間RY | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | F6(JB26) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB26_GDA | 11KV博六線(JB26) 接地RY | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0298 |  | 0082 | 1-34-07 |  | 1-51 | JB26 | 79S U/L | 博六線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB26_79UL | 11KV博六線(JB26) 79RY U/L | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0328 |  | 0118 | 1-36-05 |  | 1-75 | JB26 | ADJ(U/L) | 博六線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB26_ADJ | 11KV博六線(JB26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | F7(JB27) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB27_PHA | 11KV博七線(JB27) 相間RY | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | F7(JB27) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB27_GDA | 11KV博七線(JB27) 接地RY | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0299 |  | 0083 | 1-34-08 |  | 1-52 | JB27 | 79S U/L | 博七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB27_79UL | 11KV博七線(JB27) 79RY U/L | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0329 |  | 0119 | 1-36-06 |  | 1-76 | JB27 | ADJ(U/L) | 博七線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB27_ADJ | 11KV博七線(JB27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | F8(JB28) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB28_PHA | 11KV博八線(JB28) 相間RY | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | F8(JB28) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB28_GDA | 11KV博八線(JB28) 接地RY | FEEDER |  |  |  |  | CDC | 171 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0300 |  | 0084 | 1-34-09 |  | 1-53 | JB28 | 79S U/L | 博八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB28_79UL | 11KV博八線(JB28) 79RY U/L | FEEDER |  |  |  |  | CDC | 172 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0330 |  | 0120 | 1-36-07 |  | 1-77 | JB28 | ADJ(U/L) | 博八線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB28_ADJ | 11KV博八線(JB28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 173 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | F9(JB29) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB29_PHA | 11KV博九線(JB29) 相間RY | FEEDER |  |  |  |  | CDC | 174 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | F9(JB29) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB29_GDA | 11KV博九線(JB29) 接地RY | FEEDER |  |  |  |  | CDC | 175 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0301 |  | 0085 | 1-34-10 |  | 1-54 | JB29 | 79S U/L | 博九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB29_79UL | 11KV博九線(JB29) 79RY U/L | FEEDER |  |  |  |  | CDC | 176 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0331 |  | 0121 | 1-36-08 |  | 1-78 | JB29 | ADJ(U/L) | 博九線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB29_ADJ | 11KV博九線(JB29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 177 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | F10(JB30) | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB30_PHA | 11KV博十線(JB30) 相間RY | FEEDER |  |  |  |  | CDC | 178 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | F10(JB30) | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB30_GDA | 11KV博十線(JB30) 接地RY | FEEDER |  |  |  |  | CDC | 179 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0302 |  | 0086 | 1-34-11 |  | 1-55 | JB30 | 79S U/L | 博十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB30_79UL | 11KV博十線(JB30) 79RY U/L | FEEDER |  |  |  |  | CDC | 180 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0332 |  | 0122 | 1-36-09 |  | 1-79 | JB30 | ADJ(U/L) | 博十線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB30_ADJ | 11KV博十線(JB30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 181 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0501 |  |  | 2-0A-02 |  |  | F16(JB36) | PHA | 博十六線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB36_PHA | 11KV博十六線(JB36) 相間RY | FEEDER |  |  |  |  | CDC | 182 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0502 |  |  | 2-0A-03 |  |  | F16(JB36) | GDA | 博十六線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB36_GDA | 11KV博十六線(JB36) 接地RY | FEEDER |  |  |  |  | CDC | 183 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0146 | 2-30-11 |  | 2-11 | JB36 | 79S U/L | 博十六線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB36_79UL | 11KV博十六線(JB36) 79RY U/L | FEEDER |  |  |  |  | CDC | 184 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0531 |  | 0152 | 2-31-00 |  | 2-17 | JB36 | ADJ(U/L) | 博十六線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB36_ADJ | 11KV博十六線(JB36) LCO分流器 | FEEDER |  |  |  |  | CDC | 185 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0499 |  |  | 2-0A-00 |  |  | F17(JB37) | PHA | 博十七線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB37_PHA | 11KV博十七線(JB37) 相間RY | FEEDER |  |  |  |  | CDC | 186 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0500 |  |  | 2-0A-01 |  |  | F17(JB37) | GDA | 博十七線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB37_GDA | 11KV博十七線(JB37) 接地RY | FEEDER |  |  |  |  | CDC | 187 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0525 |  | 0145 | 2-30-10 |  | 2-10 | JB37 | 79S U/L | 博十七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB37_79UL | 11KV博十七線(JB37) 79RY U/L | FEEDER |  |  |  |  | CDC | 188 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0530 |  | 0151 | 2-30-15 |  | 2-16 | JB37 | ADJ(U/L) | 博十七線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB37_ADJ | 11KV博十七線(JB37) LCO分流器 | FEEDER |  |  |  |  | CDC | 189 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0497 |  |  | 2-09-06 |  |  | F18(JB38) | PHA | 博十八線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB38_PHA | 11KV博十八線(JB38) 相間RY | FEEDER |  |  |  |  | CDC | 190 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0498 |  |  | 2-09-07 |  |  | F18(JB38) | GDA | 博十八線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB38_GDA | 11KV博十八線(JB38) 接地RY | FEEDER |  |  |  |  | CDC | 191 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0524 |  | 0144 | 2-30-09 |  | 2-0F | JB38 | 79S U/L | 博十八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB38_79UL | 11KV博十八線(JB38) 79RY U/L | FEEDER |  |  |  |  | CDC | 192 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0529 |  | 0150 | 2-30-14 |  | 2-15 | JB38 | ADJ(U/L) | 博十八線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB38_ADJ | 11KV博十八線(JB38) LCO分流器 | FEEDER |  |  |  |  | CDC | 193 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0495 |  |  | 2-09-04 |  |  | F19(JB39) | PHA | 博十九線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB39_PHA | 11KV博十九線(JB39) 相間RY | FEEDER |  |  |  |  | CDC | 194 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0496 |  |  | 2-09-05 |  |  | F19(JB39) | GDA | 博十九線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB39_GDA | 11KV博十九線(JB39) 接地RY | FEEDER |  |  |  |  | CDC | 195 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  | 0143 | 2-30-08 |  | 2-0E | JB39 | 79S U/L | 博十九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB39_79UL | 11KV博十九線(JB39) 79RY U/L | FEEDER |  |  |  |  | CDC | 196 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0528 |  | 0149 | 2-30-13 |  | 2-14 | JB39 | ADJ(U/L) | 博十九線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB39_ADJ | 11KV博十九線(JB39) LCO分流器 | FEEDER |  |  |  |  | CDC | 197 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0493 |  |  | 2-09-02 |  |  | F20(JB40) | PHA | 博二十線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB40_PHA | 11KV博二十線(JB40) 相間RY | FEEDER |  |  |  |  | CDC | 198 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0494 |  |  | 2-09-03 |  |  | F20(JB40) | GDA | 博二十線 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB40_GDA | 11KV博二十線(JB40) 接地RY | FEEDER |  |  |  |  | CDC | 199 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  | 0142 | 2-30-07 |  | 2-0D | JB40 | 79S U/L | 博二十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB40_79UL | 11KV博二十線(JB40) 79RY U/L | FEEDER |  |  |  |  | CDC | 200 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0527 |  | 0148 | 2-30-12 |  | 2-13 | JB40 | ADJ(U/L) | 博二十線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB40_ADJ | 11KV博二十線(JB40) LCO分流器 | FEEDER |  |  |  |  | CDC | 201 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JB21/T1 |  |  | 0099 |  | 0053 | 1-0C-00 |  | 1-34 | F1(JB21) | 52AS |  |  | aahb | B2/S23_D1 | [8 empty] | 博愛SS.JB21_CB | JB21(11KV博一線) CB | FEEDER |  |  |  |  | CDC | 202 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB21_DS | JB21_DS (非取樣點) | FEEDER | [5 empty] | 203 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB21_ES | JB21_ES (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JB22/T1 |  |  | 0100 |  | 0054 | 1-0C-01 |  | 1-35 | F2(JB22) | 52AS |  |  | aafb | B2/S23_D1 | [8 empty] | 博愛SS.JB22_CB | JB22(11KV博二線) CB | FEEDER |  |  |  |  | CDC | 205 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB22_DS | JB22_DS (非取樣點) | FEEDER | [5 empty] | 206 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB22_ES | JB22_ES (非取樣點) | FEEDER | [5 empty] | 207 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JB23/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | F3(JB23) | 52AS |  |  | aaeb | B2/S23_D1 | [8 empty] | 博愛SS.JB23_CB | JB23(11KV博三線) CB | FEEDER |  |  |  |  | CDC | 208 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB23_DS | JB23_DS (非取樣點) | FEEDER | [5 empty] | 209 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB23_ES | JB23_ES (非取樣點) | FEEDER | [5 empty] | 210 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JB24/T1 |  |  | 0102 |  | 0056 | 1-0C-03 |  | 1-37 | F4(JB24) | 52AS |  |  | aadb | B2/S23_D1 | [8 empty] | 博愛SS.JB24_CB | JB24(11KV博四線) CB | FEEDER |  |  |  |  | CDC | 211 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB24_DS | JB24_DS (非取樣點) | FEEDER | [5 empty] | 212 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB24_ES | JB24_ES (非取樣點) | FEEDER | [5 empty] | 213 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JB25/T1 |  |  | 0103 |  | 0057 | 1-0C-04 |  | 1-38 | F5(JB25) | 52AS |  |  | aacb | B2/S23_D1 | [8 empty] | 博愛SS.JB25_CB | JB25(11KV博五線) CB | FEEDER |  |  |  |  | CDC | 214 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB25_DS | JB25_DS (非取樣點) | FEEDER | [5 empty] | 215 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB25_ES | JB25_ES (非取樣點) | FEEDER | [5 empty] | 216 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JB26/T1 |  |  | 0121 |  | 0074 | 1-0E-06 |  | 1-49 | F6(JB26) | 52AS |  |  | abbb | B2/S23_D1 | [8 empty] | 博愛SS.JB26_CB | JB26(11KV博六線) CB | FEEDER |  |  |  |  | CDC | 217 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB26_DS | JB26_DS (非取樣點) | FEEDER | [5 empty] | 218 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB26_ES | JB26_ES (非取樣點) | FEEDER | [5 empty] | 219 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JB27/T1 |  |  | 0122 |  | 0075 | 1-0E-07 |  | 1-4A | F7(JB27) | 52AS |  |  | abcb | B2/S23_D1 | [8 empty] | 博愛SS.JB27_CB | JB27(11KV博七線) CB | FEEDER |  |  |  |  | CDC | 220 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB27_DS | JB27_DS (非取樣點) | FEEDER | [5 empty] | 221 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB27_ES | JB27_ES (非取樣點) | FEEDER | [5 empty] | 222 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JB28/T1 |  |  | 0123 |  | 0076 | 1-0F-00 |  | 1-4B | F8(JB28) | 52AS |  |  | abdb | B2/S23_D1 | [8 empty] | 博愛SS.JB28_CB | JB28(11KV博八線) CB | FEEDER |  |  |  |  | CDC | 223 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB28_DS | JB28_DS (非取樣點) | FEEDER | [5 empty] | 224 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB28_ES | JB28_ES (非取樣點) | FEEDER | [5 empty] | 225 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JB29/T1 |  |  | 0124 |  | 0077 | 1-0F-01 |  | 1-4C | F9(JB29) | 52AS |  |  | abeb | B2/S23_D1 | [8 empty] | 博愛SS.JB29_CB | JB29(11KV博九線) CB | FEEDER |  |  |  |  | CDC | 226 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB29_DS | JB29_DS (非取樣點) | FEEDER | [5 empty] | 227 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB29_ES | JB29_ES (非取樣點) | FEEDER | [5 empty] | 228 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JB30/T1 |  |  | 0125 |  | 0078 | 1-0F-02 |  | 1-4D | F10(JB30) | 52AS |  |  | abgb | B2/S23_D1 | [8 empty] | 博愛SS.JB30_CB | JB30(11KV博十線) CB | FEEDER |  |  |  |  | CDC | 229 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB30_DS | JB30_DS (非取樣點) | FEEDER | [5 empty] | 230 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB30_ES | JB30_ES (非取樣點) | FEEDER | [5 empty] | 231 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JB36/T1 |  |  | 0488 |  | 0137 | 2-08-05 |  | 2-08 | F16(JB36) | 52AS | 博十六線 11KV |  | acab | B2/S23_D1 | [8 empty] | 博愛SS.JB36_CB | JB36(11KV博十六線) CB | FEEDER |  |  |  |  | CDC | 232 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB36_DS | JB36_DS (非取樣點) | FEEDER | [5 empty] | 233 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB36_ES | JB36_ES (非取樣點) | FEEDER | [5 empty] | 234 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JB37/T1 |  |  | 0487 |  | 0136 | 2-08-04 |  | 2-07 | F17(JB37) | 52AS | 博十七線 11KV |  | acbb | B2/S23_D1 | [8 empty] | 博愛SS.JB37_CB | JB37(11KV博十七線) CB | FEEDER |  |  |  |  | CDC | 235 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB37_DS | JB37_DS (非取樣點) | FEEDER | [5 empty] | 236 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB37_ES | JB37_ES (非取樣點) | FEEDER | [5 empty] | 237 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JB38/T1 |  |  | 0486 |  | 0135 | 2-08-03 |  | 2-06 | F18(JB38) | 52AS | 博十八線 11KV |  | accb | B2/S23_D1 | [8 empty] | 博愛SS.JB38_CB | JB38(11KV博十八線) CB | FEEDER |  |  |  |  | CDC | 238 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB38_DS | JB38_DS (非取樣點) | FEEDER | [5 empty] | 239 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB38_ES | JB38_ES (非取樣點) | FEEDER | [5 empty] | 240 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JB39/T1 |  |  | 0485 |  | 0134 | 2-08-02 |  | 2-05 | F19(JB39) | 52AS | 博十九線 11KV |  | acdb | B2/S23_D1 | [8 empty] | 博愛SS.JB39_CB | JB39(11KV博十九線) CB | FEEDER |  |  |  |  | CDC | 241 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB39_DS | JB39_DS (非取樣點) | FEEDER | [5 empty] | 242 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB39_ES | JB39_ES (非取樣點) | FEEDER | [5 empty] | 243 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JB40/T1 |  |  | 0484 |  | 0133 | 2-08-01 |  | 2-04 | F20(JB40) | 52AS | 博二十線 11KV |  | acfb | B2/S23_D1 | [8 empty] | 博愛SS.JB40_CB | JB40(11KV博二十線) CB | FEEDER |  |  |  |  | CDC | 244 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB40_DS | JB40_DS (非取樣點) | FEEDER | [5 empty] | 245 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB40_ES | JB40_ES (非取樣點) | FEEDER | [5 empty] | 246 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 600 TIE | A | 69KV 600TIE電流 | A_-1200_1200(-2000_2000) |  | B2/S23_A1 | [8 empty] | 博愛SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 247 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE |  |  |  |  | CDC | 248 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE |  |  |  |  | CDC | 249 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE |  |  |  |  | CDC | 250 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | ＃2 TIE | A1 | 二號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 251 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | ＃2 TIE | A2 | 二號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 252 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | ＃2 TIE | A3 | 二號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 253 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | ＃4 TIE | A1 | 四號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE4_A1 | 11KV TIE4 R相AMP | TIE |  |  |  |  | CDC | 254 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | ＃4 TIE | A2 | 四號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE4_A2 | 11KV TIE4 S相AMP | TIE |  |  |  |  | CDC | 255 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | ＃4 TIE | A3 | 四號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.11KV_TIE4_A3 | 11KV TIE4 T相AMP | TIE |  |  |  |  | CDC | 256 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0091 |  | 0009 | 1-0B-00 |  | 1-08 | 600TIE | 600TIE AS |  |  | aafz | B2/S23_A1 | [8 empty] | 博愛SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 257 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0104 |  | 0051 | 1-0C-05 |  | 1-32 | SPARE | 52AS | #3 TIE CB |  | zzzz | B2/S23_D1 | [8 empty] | 博愛SS.TIE3_CB | 11KV TIE3 CB | TIE |  |  |  |  | CDC | 258 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | SPARE | PHA | #3 TIE CB |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE3_51A | 11KV TIE3 51RY | TIE |  |  |  |  | CDC | 259 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-04 |  |  | SPARE | GDA | #3 TIE CB |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE3_51NA | 11KV TIE3 51N RY | TIE |  |  |  |  | CDC | 260 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0126 |  | 0072 | 1-0F-03 |  | 1-47 | #2 TIE | 52AS | #2 TIE CB |  | zzzz | B2/S23_D1 | [8 empty] | 博愛SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 261 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-01 |  |  | #2 TIE | PHA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 262 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-02 |  |  | #2 TIE | GDA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 263 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/4Bus | B/2Bus |  |  | 0489 |  | 0138 | 2-08-06 |  | 2-09 | ＃4 TIE | 52AS | #4 TIE CB |  | zzzz | B2/S23_D1 | [8 empty] | 博愛SS.TIE4_CB | 11KV TIE4 CB | TIE |  |  |  |  | CDC | 264 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0503 |  |  | 2-0A-04 |  |  | ＃4TIE | PHA | #4 TIE CB |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE4_51A | 11KV TIE4 51RY | TIE |  |  |  |  | CDC | 265 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0504 |  |  | 2-0A-05 |  |  | ＃4TIE | GDA | #4 TIE CB |  |  | B2/S23_D1 | [8 empty] | 博愛SS.TIE4_51NA | 11KV TIE4 51N RY | TIE |  |  |  |  | CDC | 266 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0411 | 412 | 0107 | 1-3B-08 | 1-3B-09 | 1-6A | 600TIE 1AS | 601AS | ＃600 TIE 一次側 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 267 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0413 | 414 | 0108 | 1-3B-10 | 1-3B-11 | 1-6B | 600TIE 2AS | 602AS | ＃600 TIE 二次側 |  |  | B2/S23_A1 | [8 empty] | 博愛SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 268 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.601E | 601E (非取樣點) | TIE | [5 empty] | 269 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.602E | 602E (非取樣點) | TIE | [5 empty] | 270 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 271 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 272 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.TIE4_DS | TIE4_DS (非取樣點) | TIE | [5 empty] | 273 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | ＃1 MCB | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 274 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | ＃1 MCB | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 275 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | ＃1 MCB | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 276 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | ＃1 MCB | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 277 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | ＃1 MCB | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 278 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2 MCB | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 279 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | ＃2 MCB | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 280 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | ＃2 MCB | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 281 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | ＃2 MCB | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 282 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | ＃2 MCB | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 283 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | SPARE |  |  | MW_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 284 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | SPARE |  |  | MVAR_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 285 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 286 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 287 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 288 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | ＃4 MCB | MW | 四號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_MW | #4MTR二次側 MW | DTR |  |  |  |  | CDC | 289 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | ＃4 MCB | MVAR | 四號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR |  |  |  |  | CDC | 290 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | ＃4 MCB | A1 | 四號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 291 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | ＃4 MCB | A2 | 四號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 292 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | ＃4 MCB | A3 | 四號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 293 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | ＃1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 294 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 295 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0058 | 1-9B |  | 1-39 | ＃1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 296 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1 MTR | MWH | Power Meter 6760 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 297 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1 MTR | MVARH(+) | Power Meter 6760 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 298 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | ＃2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 299 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | ＃2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 300 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0079 | 1-BF |  | 1-4E | ＃2 MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 301 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2 MTR | MWH | Power Meter 6760 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 302 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2 MTR | MVARH(+) | Power Meter 6760 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 303 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | ＃4 MTR | 油溫 | 四號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_OIL | #4MTR 油溫 | DTR |  |  |  |  | CDC | 304 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | ＃4 MTR | 線溫 | 四號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_COIL | #4MTR 線溫 | DTR |  |  |  |  | CDC | 305 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0168 |  | 0139 | 2-A8 |  | 2-0A | ＃4 MTR | TAP | 四號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_TAP | #4MTR OLTC TAP | DTR |  |  |  |  | CDC | 306 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0043 |  |  | 2-4B |  |  | 620 MVAR(-) | MVAR(-) | 後湖博愛線 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 307 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | MVARH_P |  | Element | [12 empty] | 0044 |  |  | 2-4C |  |  | 660 MVAR(+) | MVAR(+) | 博愛鐵嘉白線 |  |  | B1/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 308 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0004 |  | 0049 | 1-00-01 |  | 1-30 | 750 GIS | 52AS | #1MTR一次側 |  | aacb | B3/S23_D1 | [8 empty] | 博愛SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 309 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 310 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 311 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760 GIS | 52AS | #2MTR一次側 |  | aahb | B3/S23_D1 | [8 empty] | 博愛SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 312 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 313 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 314 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/3MTR |  | 0025 |  | 0089 | 1-02-06 |  | 1-58 | SPARE |  |  |  | not found | B3/S23_D1 | [8 empty] | 博愛SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 315 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 316 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 317 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/4MTR |  | 0453 |  | 0130 | 2-00-02 |  | 2-01 | 780 GIS | 52AS | #4 MTR一次側 |  | aakb | B3/S23_D1 | [8 empty] | 博愛SS.780_CB | 780(#4MTR) CB | DTR |  |  |  |  | CDC | 318 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.780TE | 780TE (非取樣點) | DTR | [5 empty] | 319 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S23_D1 | [8 empty] | 博愛SS.780BE | 780BE (非取樣點) | DTR | [5 empty] | 320 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0005 |  | 0050 | 1-00-02 |  | 1-31 | #1 MCB | 52AS | #1MTR二次側 |  | aaga | B2/S23_D1 | [8 empty] | 博愛SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 321 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2MTR |  |  | 0014 |  | 0070 | 1-01-03 |  | 1-45 | #2 MCB | 52AS | #2MTR二次側 |  | abha | B2/S23_D1 | [8 empty] | 博愛SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 322 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | CB | 3MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABUS | T/3MTR |  |  | 0026 |  | 0090 | 1-02-07 |  | 1-59 | SPARE |  |  |  | not found | B2/S23_D1 | [8 empty] | 博愛SS.3MA_CB | 3MA(#3MTR) CB | DTR |  |  |  |  | CDC | 323 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | CB | 3MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBUS | T/3MTR |  |  | 0027 |  | 0091 | 1-03-00 |  | 1-5A | SPARE |  |  |  | not found | B2/S23_D1 | [8 empty] | 博愛SS.3MB_CB | 3MB(#3MTR) CB | DTR |  |  |  |  | CDC | 324 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M4 | #4MTR(M4) |  | CB | 4M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BUS | T/4MTR |  |  | 0454 |  | 0131 | 2-00-03 |  | 2-02 | #4 MCB | 52AS | #4 MTR二次側 |  | acea | B2/S23_D1 | [8 empty] | 博愛SS.4M_CB | 4M(#4MTR) CB | DTR |  |  |  |  | CDC | 325 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750 GIS | PHA | #1MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 326 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | 750 GIS | 86A | #1MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#1MTR_86A | #1MTR 86A | DTR |  |  |  |  | CDC | 327 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | #1 MTR | 51ZA | #1MTR 51Z RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 328 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | #1 MTR | 87A | #1MTR差動電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 329 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 1-33-03 |  |  | ＃1 MTR | 187S U/L | 一號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 330 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  | 0066 | 1-0C-06 |  | 1-41 | #1MCB | 81A | #1 MCB 81 RY(跳脫＃1 MCB) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 331 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 81UL |  | B2,B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 1-37-11 |  |  | #1 MCB | 181S | 一號主變低頻電驛狀態點 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MTR_81UL | #1MTR 81RY U/L | DTR |  |  |  |  | CDC | 332 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | 760 GIS | PHA | #2MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 333 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | 760 GIS | 86A | #2MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#2MTR_86A | #2MTR 86A | DTR |  |  |  |  | CDC | 334 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | #2 MTR | 51ZA | #2MTR 51Z RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 335 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | #2 MTR | 87A | #2MTR差動電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 336 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-34-03 |  |  | ＃2 MTR | 287S U/L | 二號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 337 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  | 0087 | 1-0F-04 |  | 1-56 | #2 MCB | 81A | #2 MCB 81 RY(跳脫＃2 MCB) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR |  |  |  |  | CDC | 338 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 81UL |  | B2,B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 1-37-12 |  |  | #2 MCB | 281S | 二號主變低頻電驛狀態點 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MTR_81UL | #2MTR 81RY U/L | DTR |  |  |  |  | CDC | 339 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | SPARE |  |  |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 340 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | SPARE |  |  |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 341 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | SPARE |  |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 342 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-04 |  |  | SPARE |  |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 343 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  | 0106 | 1-12-01 |  | 1-69 | SPARE | 81A | #3BUS |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR |  |  |  |  | CDC | 344 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0455 |  |  | 2-00-04 |  |  | 780 GIS | PHA | #4 MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#4MTR_51A | #4MTR 51RY | DTR |  |  |  |  | CDC | 345 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0456 |  |  | 2-00-05 |  |  | 780 GIS | 86A | #4 MTR一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.#4MTR_86A | #4MTR 86A | DTR |  |  |  |  | CDC | 346 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0461 |  |  | 2-01-02 |  |  | #4MTR | M451ZA | #4 MTR 51Z RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_51ZA | #4MTR 51Z RY | DTR |  |  |  |  | CDC | 347 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0458 |  |  | 2-00-07 |  |  | #4 MTR | M487A | #4 MTR差動電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_87A | #4MTR 87RY | DTR |  |  |  |  | CDC | 348 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 2-30-03 |  |  | ＃4 MTR | 487S U/L | 四號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_87UL | #4MTR 87RY U/L | DTR |  |  |  |  | CDC | 349 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0490 |  | 0147 | 2-08-07 |  | 2-12 | #4MCB | 81A | #4 MCB 81 RY(跳脫＃4 MCB) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.#4MTR_81A/S | #4MTR 81RY A/S | DTR |  |  |  |  | CDC | 350 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 81UL |  | B2,B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0352 |  |  | 1-37-13 |  |  | #4 MCB | 481S | 四號主變低頻電驛狀態點 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MTR_81UL | #4MTR 81RY U/L | DTR |  |  |  |  | CDC | 351 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-00-07 |  |  | #1 MCB | PHA | #1MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 352 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0275 |  |  | 1-33-00 |  |  | ＃1 MTR | 1TRA | 一號主變重故障警報 |  | a | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 353 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-33-01 |  |  | ＃1 MTR | 1TRF | 一號主變輕故障警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 354 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-33-04 |  |  | ＃1 MTR | R/L | 一號主變OLTC(中心 / 現場)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 355 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0280 |  | 0059 | 1-33-05 |  | 1-3A | ＃1 MTR | A/M | 一號主變OLTC(自動 / 手動)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 356 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S23 | 博愛SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-01 |  |  | #2 MCB | PHA | #2MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 357 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0291 |  |  | 1-34-00 |  |  | ＃2 MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 358 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0292 |  |  | 1-34-01 |  |  | ＃2 MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 359 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-34-04 |  |  | ＃2 MTR | R/L | 二號主變OLTC(中心 / 現場)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 360 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0080 | 1-34-05 |  | 1-4F | ＃2 MTR | A/M | 二號主變OLTC(自動 / 手動)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 361 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S23 | 博愛SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-03-05 |  |  | SPARE |  |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.3MA_51A | #3MTR二次側(3MA) 51RY | DTR |  |  |  |  | CDC | 362 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-03-07 |  |  | SPARE |  |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.3MB_51A | #3MTR二次側(3MB) 51RY | DTR |  |  |  |  | CDC | 363 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0459 |  |  | 2-01-00 |  |  | #4 MCB | PHA | #4 MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.4M_51A | #4MTR二次側(4M) 51RY | DTR |  |  |  |  | CDC | 364 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0515 |  |  | 2-30-00 |  |  | ＃4 MTR | 4TRA | 四號主變重故障警報 |  | a | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_TRA | #4MTR 重故障 | DTR |  |  |  |  | CDC | 365 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0516 |  |  | 2-30-01 |  |  | ＃4 MTR | 4TRF | 四號主變輕故障警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_TRF | #4MTR 輕故障 | DTR |  |  |  |  | CDC | 366 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 2-30-04 |  |  | ＃4 MTR | R/L | 四號主變OLTC(中心 / 現場)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_S/L | #4MTR OLTC S/L | DTR |  |  |  |  | CDC | 367 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0140 | 2-30-05 |  | 2-0B | ＃4 MTR | A/M | 四號主變OLTC(自動 / 手動)指示 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_A/M | #4MTR OLTC A/M | DTR |  |  |  |  | CDC | 368 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0359 | 360 | 0109 | 1-38-04 | 1-38-05 | 1-6C | LINE-1 3AS | 751AS | ＃1 MTR 一次側BUS1 DS ON |  |  | B3/S23_D1 | [8 empty] | 博愛SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 369 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0361 | 362 | 0110 | 1-38-06 | 1-38-07 | 1-6D | LINE-1 3EAS | 752AS | ＃1 MTR 一次側BUS1 DS ON |  |  | B3/S23_D1 | [8 empty] | 博愛SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 370 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0355 | 356 | 0111 | 1-38-00 | 1-38-01 | 1-6E | LINE-1 1AS | 761AS | ＃2 MTR 一次側BUS1 DS ON |  |  | B3/S23_D1 | [8 empty] | 博愛SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 371 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0357 | 358 | 0112 | 1-38-02 | 1-38-03 | 1-6F | LINE-1 2AS | 762AS | ＃2 MTR 一次側BUS1 DS ON |  |  | B3/S23_D1 | [8 empty] | 博愛SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 372 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0547 | 548 | 0153 | 2-38-00 | 2-38-01 | 2-18 | 781 | 781AS | #4MTR 四號主變一次側 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.781_DS | 781(#4MTR) DS | DTR |  |  |  |  | CDC | 373 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0549 | 550 | 0154 | 2-38-02 | 2-38-03 | 2-19 | 782 | 782AS |  |  |  | B3/S23_D1 | [8 empty] | 博愛SS.782_DS | 782(#4MTR) DS | DTR |  |  |  |  | CDC | 374 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 375 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 376 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | #1 MTR | 96PA | #1MTR 96P RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 377 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 1-33-02 |  |  | ＃1 MTR | 148T | 一號主變OLTC遲滯警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 378 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-33-12 |  |  | ＃1MTR | 127C | 一號主變AC電源欠壓 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 379 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 380 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M2 | #2MTR(M2) |  | E1 | 2M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 381 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | #2 MTR | 96PA | #2MTR 96P RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 382 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-34-02 |  |  | ＃2 MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 383 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 1-34-12 |  |  | ＃2 MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 384 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | 3M(非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 385 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 386 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-03 |  |  | SPARE |  |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 387 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-35-12 |  |  | SPARE |  |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 388 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M4 | #4MTR(M4) |  | DS | 4M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.4M_DS | 4M_DS (非取樣點) | DTR | [5 empty] | 389 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | M4 | #4MTR(M4) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.4M_ES | 4M_ES (非取樣點) | DTR | [5 empty] | 390 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0457 |  |  | 2-00-06 |  |  | #4 MTR | 496PA | #4 MTR 96P RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_96A | #4MTR 96P RY | DTR |  |  |  |  | CDC | 391 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 2-30-02 |  |  | ＃4 MTR | 448T | 四號主變OLTC遲滯警報 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 392 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 2-31-01 |  |  | ＃4MTR | 427C | 四號主變AC電源欠壓 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR |  |  |  |  | CDC | 393 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | C/1SC |  |  | 0098 |  | 0052 | 1-0B-07 |  | 1-33 | #1 11KV SC | 52AS |  |  | aabb | B2/S23_D1 | [8 empty] | 博愛SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 394 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0281 |  | 0060 | 1-33-06 |  | 1-3B | ＃1 SC | Q-CTL A/M | 一號SC乏控器(自動 / 手動)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 395 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 396 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | C/2SC |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | #2 11KV SC | 52AS |  |  | abib | B2/S23_D1 | [8 empty] | 博愛SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 397 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0297 |  | 0081 | 1-34-06 |  | 1-50 | ＃2 SC | Q-CTL A/M | 二號SC乏控器(自動 / 手動)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 398 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 399 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/4BUS | C/4SC |  |  | 0483 |  | 0132 | 2-08-00 |  | 2-03 | ＃4 SC | 52AS | 四號 SC 11KV |  | acgb | B2/S23_D1 | [8 empty] | 博愛SS.240_CB | 240(11KV #4SC) CB | SC |  |  |  |  | CDC | 400 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0521 |  | 0141 | 2-30-06 |  | 2-0C | ＃4 SC | Q-CTL A/M | 四號SC乏控器(自動 / 手動)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.240_A/M | 11KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 401 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 402 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | #1 SC 51、51N | SCA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 403 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-00 |  |  | #1 SC 27、59 RY | UVA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 404 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | #2 SC 51、51N | SCA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 405 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | #2 SC 27、59 RY | UVA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 406 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | SPARE | #3SC | SCA |  |  | B2/S23_D1 | [8 empty] | 博愛SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 407 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 1-12-03 |  |  | SPARE | #3SC | UVA |  |  | B2/S23_D1 | [8 empty] | 博愛SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 408 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0491 |  |  | 2-09-00 |  |  | #4 SC 51、51N | SCA | 四號 SC 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.240_SCA | 11KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 409 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0492 |  |  | 2-09-01 |  |  | #4 SC 27、59 RY | UVA | 四號 SC 11KV |  |  | B2/S23_D1 | [8 empty] | 博愛SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 410 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 411 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 412 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 413 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 414 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.231DS | 231DS (非取樣點) | SC | [5 empty] | 415 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | D2 | 232DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.232DS | 232DS (非取樣點) | SC | [5 empty] | 416 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.241DS | 241DS (非取樣點) | SC | [5 empty] | 417 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | D2 | 242DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.242DS | 242DS (非取樣點) | SC | [5 empty] | 418 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪A I 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 419 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪A I 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 420 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 421 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 422 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 423 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 424 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCL4 |  | B2 | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 425 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | ADCH4 |  | B2 | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 426 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0227 |  | 0001 | 1-30-00 |  | 1-00 | RTU | TEST CB | ON/OFF |  |  | ELEM/ALL | [8 empty] | 博愛SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 427 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0228 |  |  | 1-30-01 |  |  | RTU | L/R | LOCAL/REMOTE(STATUS) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 428 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-30-02 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 429 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0230 |  |  | 1-30-03 |  |  | 通訊充電機 | CHG2 | 通訊充電機故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0231 |  |  | 1-30-04 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0233 |  | 0046 | 1-30-06 |  | 1-2D | 所內開關場 | FLAS | 開關場照明 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0234 |  | 0047 | 1-30-07 |  | 1-2E | 所內配電盤 | FLBS | 市區路燈照明 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-30-08 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0236 |  |  | 1-30-09 |  |  | 充油電纜 | OPA | 油壓電力電纜警報(無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0237 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火災警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.火災警報(1) | [博愛]火警 | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0239 |  |  | 1-30-12 |  |  | 變電所內 | PSF | 所內其他輕故障警報(無接線) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 437 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0240 |  |  | 1-30-13 |  |  | 變電所內 | PSA | 所內其他重故障警報(無接線) |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 438 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0241 |  |  | 1-30-14 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 439 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0242 |  |  | 1-30-15 |  |  | 洩油池泵 | OWF | 洩油池泵警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 440 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0248 |  |  | 1-31-05 |  |  | 門禁警報(1) |  | 無人化門禁警報(1)(無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 441 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0249 |  |  | 1-31-06 |  |  | 門禁警報(2) |  | 無人化門禁警報(2)(無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0250 |  |  | 1-31-07 |  |  | 門禁警報(3) |  | 無人化門禁警報(3)(無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 443 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0252 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 | 6CBF | 69KV CB 輕警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 444 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 1-31-10 |  |  | 69KV CB 重故障 | 6CBA | 69KV CB 重警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0254 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 | 1CBF | 11KV CB NFB跳脫警報 |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-31-12 |  |  | 11KV CB 重故障 | 1CBA | 11KV CB NFB跳脫警報 |  |  | ELEM/S23_D1 | [8 empty] | 博愛SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-31-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報(4TRAL) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-37-00 |  |  | 光纖通訊系統 | ACFA | 通訊設備異常故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊設備AC故障 | 光纖通訊系統 | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0340 |  |  | 1-37-01 |  |  | 光纖通訊系統 | OLTMA | 通訊設備光纖主故障OLTE重故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊OLTE重故障 | 光纖通訊系統 | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0341 |  |  | 1-37-02 |  |  | 光纖通訊系統 | OLTNA | 通訊設備光纖次故障OLTE輕故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊OLTE輕故障 | 光纖通訊系統 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 9A5Other | 通訊PCM警報 |  | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0342 |  |  | 1-37-03 |  |  | 光纖通訊系統 | PCMA | 博碼調變器故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊PCM警報 | 光纖通訊系統 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0232 |  |  | 1-30-05 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0238 |  |  | 1-30-11 |  |  | 安全監控 | SUPA | 所內安全監控(無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Fire3 | MCSG火警 | Element | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0243 |  |  | 1-31-00 |  |  | MCSG火警 |  | 無人化防火警報(1) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.MCSG火警 | MCSG火警 | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Fire4 | MCSG系統故障 | Element | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0244 |  |  | 1-31-01 |  |  | MCSG系統故障 |  | 無人化防火警報(2) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.MCSG系統故障 | MCSG系統故障 | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | COMT |  | B2,B3,Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-31-08 |  |  | 69KV COMT |  | 69KV SC 警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.COMT警報 | COMT警報 | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | GDA |  | B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-04 |  |  | 750 GIS | GDA | #1MTR一次側51N RY(51NA) |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_GDA | #1MTR GDA | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | GDA |  | B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-04-05 |  |  | 760 GIS | GDA | #2MTR一次側51N RY(51NA) |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_GDA | #2MTR GDA | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | GDA |  | B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0466 |  |  | 2-01-07 |  |  | 780 GIS | GDA | #4MTR一次側51N RY |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_GDA | #4MTR GDA | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | #1 MCB | GDA | #1MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#1MAIN51NA | #1MAIN51NA | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | #2 MCB | GDA | #2MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#2MAIN51NA | #2MAIN51NA | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | SPARE |  |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MAIN51NA | #3MAIN51NA | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-00 |  |  | SPARE |  |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#3MBIN51NA | #3MBIN51NA | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0460 |  |  | 2-01-01 |  |  | #4 MCB | GDA | #4 MTR二次側 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#4MAIN51NA | #4MAIN51NA | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Fire2 | 主變火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0245 |  |  | 1-31-02 |  |  | 主變火警 |  | 無人化防盜警報(1) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 466 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0246 |  |  | 1-31-03 |  |  | 細水霧故障 |  | 無人化防盜警報(2) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 467 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0247 |  |  | 1-31-04 |  |  | 細水霧噴灑 |  | 無人化防盜警報(3) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 468 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 維護運轉警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0354 |  |  | 1-37-15 |  |  | 43 R/L |  | 維護運轉 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 469 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 數據機重置 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0162 |  | 0088 | 1-13-07 |  | 1-57 | SPARE | Modem Reset |  |  |  | B3/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 470 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | DD_Light | 路燈電源監視 | Element | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 0346 |  |  | 1-37-07 |  |  | 路燈監視 |  | 路燈操作線電源監視 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.路燈電源監視 | 路燈操作線電源監視 | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室溫度異常 | Element | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0343 |  |  | 1-37-04 |  |  | 光纖通訊系統 |  | 通訊設備溫度異常 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1MTR | 96B1 | #1MTR 樸氣電驛第一段 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | #1MTR | 96B2 | 無接線 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 474 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1MTR | 96D | #1MTR放壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 475 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1MTR | 96P | #1MTR突壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 476 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1MTR | 63Q | #1MTR油流電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 477 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2MTR | 96B1 | #2MTR 樸氣電驛第一段 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | #2MTR | 96B2 | 無接線 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 479 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2MTR | 96D | #2MTR放壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 480 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2MTR | 96P | #2MTR突壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2MTR | 63Q | #2MTR油流電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-02 |  |  | #3MTR | 96B1 | #3MTR 樸氣電驛第一段 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 483 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-03 |  |  | #3MTR | 96B2 | 無接線 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 484 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-04 |  |  | #3MTR | 96D | #3MTR放壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-19-05 |  |  | #3MTR | 96P | #3MTR突壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-19-06 |  |  | #3MTR | 63Q | #3MTR油流電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-19-07 |  |  | #4MTR | 96B1 | #4MTR 樸氣電驛第一段 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR96B1 | #4MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 488 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-00 |  |  | #4MTR | 96B2 | 無接線 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR96B2 | #4MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 489 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-01 |  |  | #4MTR | 96D | #4MTR放壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR96D | #4MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 490 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-02 |  |  | #4MTR | 96P | #4MTR突壓電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR96P | #4MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 491 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-03 |  |  | #4MTR | 63Q | #4MTR油流電驛 |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR63Q | #4MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 492 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | IRFA | IED警報 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-32-15 |  |  | 69KV IED重警報 |  | (無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.69KV_IED警報 | 69KV IED警報 | OTHER |  |  |  |  | CDC | 493 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-01 |  |  | 600TIE 1 | 600TIE PHA1 |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.600PHA(1) | 600(TIE) 67A(B1) | OTHER |  |  |  |  | CDC | 494 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-02 |  |  | 600TIE 1 | 600TIE GDA1 |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.600GDA(1) | 600(TIE) 67NA(B1) | OTHER |  |  |  |  | CDC | 495 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-03 |  |  | 600TIE 2 | 600TIE PHA2 |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.600PHA(2) | 600(TIE) 67A(B2) | OTHER |  |  |  |  | CDC | 496 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-04 |  |  | 600TIE 2 | 600TIE GDA2 |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.600GDA(2) | 600(TIE) 67NA(B2) | OTHER |  |  |  |  | CDC | 497 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0290 |  |  | 1-33-15 |  |  | 750 | RYFA |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_RYFA | #1MTR IED警報 | OTHER |  |  |  |  | CDC | 498 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-34-15 |  |  | 760 | RYFA |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_RYFA | #2MTR IED警報 | OTHER |  |  |  |  | CDC | 499 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0534 |  |  | 2-31-03 |  |  | ＃4MTR | RYFA |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_RYFA | #4MTR IED警報 | OTHER |  |  |  |  | CDC | 500 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-35-00 |  |  | 600TIE | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.600TIE_RYFA | 600 IED警報 | OTHER |  |  |  |  | CDC | 501 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-35-01 |  |  | 650 | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.650紅線_RYFA | 650 IED警報 | OTHER |  |  |  |  | CDC | 502 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0309 |  |  | 1-35-02 |  |  | 620 | CFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620後博線_CFA | 620 通訊故障 | OTHER |  |  |  |  | CDC | 503 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0310 |  |  | 1-35-03 |  |  | 620 | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.620後博線_RYFA | 620 IED警報 | OTHER |  |  |  |  | CDC | 504 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 1-35-04 |  |  | 610 | CFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610水上線_CFA | 610 通訊故障 | OTHER |  |  |  |  | CDC | 505 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0312 |  |  | 1-35-05 |  |  | 610 | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.610水上線_RYFA | 610 IED警報 | OTHER |  |  |  |  | CDC | 506 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0313 |  |  | 1-35-06 |  |  | 660 | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.660白線RYFA | 660 IED警報 | OTHER |  |  |  |  | CDC | 507 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0314 |  |  | 1-35-07 |  |  | 670 | CFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670嘉博線_CFA | 670 通訊故障 | OTHER |  |  |  |  | CDC | 508 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0315 |  |  | 1-35-08 |  |  | 670 | RYFA |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.670嘉博線_RYFA | 670 IED警報 | OTHER |  |  |  |  | CDC | 509 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | BFA | BUSRY_BF | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 1-35-09 |  |  | BUS RY 87BF | RYFA |  |  |  | B3/S23_D1 | [8 empty] | 博愛SS.BUSRY_BF | BUSRY 電驛故障 | OTHER |  |  |  |  | CDC | 510 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | 87CTFA | BUSRY_CTFA | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-35-10 |  |  | BUS RY CTFA | CTFA |  |  |  | B3/S23_D1 | [8 empty] | 博愛SS.BUSRY_CTFA | BUSRY CT回路故障 | OTHER |  |  |  |  | CDC | 511 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0320 |  | 0104 | 1-35-13 |  | 1-67 | 69KV #1BUS | 87 U/L(87B1S) |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 512 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0321 |  | 0105 | 1-35-14 |  | 1-68 | 69KV #1BUS | 87 U/L(87B2S) |  |  |  | B2/S23_A1 | [8 empty] | 博愛SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 513 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 1-33-14 |  |  | #1MTR | 51ZS |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#1MTR_51ZS | #1MTR 51ZS | OTHER |  |  |  |  | CDC | 514 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0305 |  |  | 1-34-14 |  |  | #2 MTR | 51ZS |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#2MTR_51ZS | #2MTR 51ZS | OTHER |  |  |  |  | CDC | 515 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | 51Z_UL |  | B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 2-31-02 |  |  | ＃4MTR | 51ZS |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#4MTR_51ZS | #4MTR 51ZS | OTHER |  |  |  |  | CDC | 516 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | ComPoint |  |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0353 |  |  | 1-37-14 |  |  | PMA |  | (無接線) |  |  | B3/S23_D1 | [8 empty] | 博愛SS.69KV_PMA | 69KV PMA | OTHER |  |  |  |  | CDC | 517 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | CommACF | 4樓通訊室ACA | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0347 |  |  | 1-37-08 |  |  | Locate Empty | 4FACA | 4樓通信室AC故障 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.4樓通訊室ACA | 4樓通訊室AC告警 | OTHER |  |  |  |  | CDC | 518 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | CHG2 | 4樓通訊室CHA | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0348 |  |  | 1-37-09 |  |  | Locate Empty | 4FCHA | 4樓通信室充電機告警 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.4樓通訊室CHA | 4樓通訊室充電機告警 | OTHER |  |  |  |  | CDC | 519 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | JB21 | VAR | F1博一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博一線KVAR | 11KV博一線 KVAR | FEEDER |  |  |  |  | CDC | 520 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | JB21 | A1 | F1博一線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博一線A1 | 11KV博一線 R相AMP | FEEDER |  |  |  |  | CDC | 521 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | JB21 | A2 | F1博一線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博一線A2 | 11KV博一線 S相AMP | FEEDER |  |  |  |  | CDC | 522 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | JB21 | A3 | F1博一線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博一線A3 | 11KV博一線 T相AMP | FEEDER |  |  |  |  | CDC | 523 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | JB21 | NA | F1 博一線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博一線A0 | 11KV博一線 N相AMP | FEEDER |  |  |  |  | CDC | 524 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JB27 | VAR | F7博七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線KVAR | 11KV博七線 KVAR | FEEDER |  |  |  |  | CDC | 525 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JB27 | A1 | F7博七線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線A1 | 11KV博七線 R相AMP | FEEDER |  |  |  |  | CDC | 526 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JB27 | A2 | F7博七線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線A2 | 11KV博七線 S相AMP | FEEDER |  |  |  |  | CDC | 527 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JB27 | A3 | F7博七線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線A3 | 11KV博七線 T相AMP | FEEDER |  |  |  |  | CDC | 528 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JB27 | NA | F7 博七線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線A0 | 11KV博七線 N相AMP | FEEDER |  |  |  |  | CDC | 529 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JB29 | VAR | F9博九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線KVAR | 11KV博九線 KVAR | FEEDER |  |  |  |  | CDC | 530 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JB29 | A1 | F9博九線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線A1 | 11KV博九線 R相AMP | FEEDER |  |  |  |  | CDC | 531 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JB29 | A2 | F9博九線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線A2 | 11KV博九線 S相AMP | FEEDER |  |  |  |  | CDC | 532 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JB29 | A3 | F9博九線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線A3 | 11KV博九線 T相AMP | FEEDER |  |  |  |  | CDC | 533 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JB29 | NA | F9 博九線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線A0 | 11KV博九線 N相AMP | FEEDER |  |  |  |  | CDC | 534 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | JB22 | VAR | F2博二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線KVAR | 11KV博二線 KVAR | FEEDER |  |  |  |  | CDC | 535 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | JB22 | A1 | F2博二線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線A1 | 11KV博二線 R相AMP | FEEDER |  |  |  |  | CDC | 536 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | JB22 | A2 | F2博二線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線A2 | 11KV博二線 S相AMP | FEEDER |  |  |  |  | CDC | 537 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | JB22 | A3 | F2博二線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線A3 | 11KV博二線 T相AMP | FEEDER |  |  |  |  | CDC | 538 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | JB22 | NA | F2 博二線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線A0 | 11KV博二線 N相AMP | FEEDER |  |  |  |  | CDC | 539 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JB28 | VAR | F8博八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線KVAR | 11KV博八線 KVAR | FEEDER |  |  |  |  | CDC | 540 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JB28 | A1 | F8博八線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線A1 | 11KV博八線 R相AMP | FEEDER |  |  |  |  | CDC | 541 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JB28 | A2 | F8博八線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線A2 | 11KV博八線 S相AMP | FEEDER |  |  |  |  | CDC | 542 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JB28 | A3 | F8博八線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線A3 | 11KV博八線 T相AMP | FEEDER |  |  |  |  | CDC | 543 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | JB28 | NA | F8 博八線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線A0 | 11KV博八線 N相AMP | FEEDER |  |  |  |  | CDC | 544 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JB30 | VAR | F10博十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線KVAR | 11KV博十線 KVAR | FEEDER |  |  |  |  | CDC | 545 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JB30 | A1 | F10博十線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線A1 | 11KV博十線 R相AMP | FEEDER |  |  |  |  | CDC | 546 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JB30 | A2 | F10博十線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線A2 | 11KV博十線 S相AMP | FEEDER |  |  |  |  | CDC | 547 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JB30 | A3 | F10博十線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線A3 | 11KV博十線 T相AMP | FEEDER |  |  |  |  | CDC | 548 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JB30 | NA | F10 博十線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線A0 | 11KV博十線 N相AMP | FEEDER |  |  |  |  | CDC | 549 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | JB23 | VAR | F3博三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線KVAR | 11KV博三線 KVAR | FEEDER |  |  |  |  | CDC | 550 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | JB23 | A1 | F3博三線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線A1 | 11KV博三線 R相AMP | FEEDER |  |  |  |  | CDC | 551 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | JB23 | A2 | F3博三線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線A2 | 11KV博三線 S相AMP | FEEDER |  |  |  |  | CDC | 552 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | JB23 | A3 | F3博三線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線A3 | 11KV博三線 T相AMP | FEEDER |  |  |  |  | CDC | 553 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | JB23 | NA | F3 博三線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線A0 | 11KV博三線 N相AMP | FEEDER |  |  |  |  | CDC | 554 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | JB25 | VAR | F5博五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線KVAR | 11KV博五線 KVAR | FEEDER |  |  |  |  | CDC | 555 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | JB25 | A1 | F5博五線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線A1 | 11KV博五線 R相AMP | FEEDER |  |  |  |  | CDC | 556 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | JB25 | A2 | F5博五線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線A2 | 11KV博五線 S相AMP | FEEDER |  |  |  |  | CDC | 557 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JB25 | A3 | F5博五線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線A3 | 11KV博五線 T相AMP | FEEDER |  |  |  |  | CDC | 558 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | JB25 | NA | F5 博五線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線A0 | 11KV博五線 N相AMP | FEEDER |  |  |  |  | CDC | 559 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | JB26 | VAR | F6博六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線KVAR | 11KV博六線 KVAR | FEEDER |  |  |  |  | CDC | 560 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JB26 | A1 | F6博六線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線A1 | 11KV博六線 R相AMP | FEEDER |  |  |  |  | CDC | 561 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JB26 | A2 | F6博六線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線A2 | 11KV博六線 S相AMP | FEEDER |  |  |  |  | CDC | 562 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JB26 | A3 | F6博六線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線A3 | 11KV博六線 T相AMP | FEEDER |  |  |  |  | CDC | 563 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | JB26 | NA | F6 博六線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線A0 | 11KV博六線 N相AMP | FEEDER |  |  |  |  | CDC | 564 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | JB24 | VAR | F4博四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線KVAR | 11KV博四線 KVAR | FEEDER |  |  |  |  | CDC | 565 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | JB24 | A1 | F4博四線R相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線A1 | 11KV博四線 R相AMP | FEEDER |  |  |  |  | CDC | 566 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | JB24 | A2 | F4博四線S相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線A2 | 11KV博四線 S相AMP | FEEDER |  |  |  |  | CDC | 567 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | JB24 | A3 | F4博四線T相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線A3 | 11KV博四線 T相AMP | FEEDER |  |  |  |  | CDC | 568 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | JB24 | NA | F4 博四線零相電流 | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線A0 | 11KV博四線 N相AMP | FEEDER |  |  |  |  | CDC | 569 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | OilTemp |  | INSERT | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | SPARE |  |  | OIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_OIL | #3MTR 油溫 | DTR | [5 empty] | 570 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | CoilTemp |  | INSERT | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | SPARE |  |  | COIL_-120_120(-2000_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_COIL | #3MTR 線溫 | DTR | [5 empty] | 571 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | TapPosMv |  | INSERT | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-61 | SPARE |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | [5 empty] | 572 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 充電機 | DC-V | 配電盤 "MAIN"NFB電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S23_D1 | [8 empty] | 博愛SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 573 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-04 |  |  | SPARE | PHA | F11(JB31) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB31_PHA | 11KV博十一線(JB31) 相間RY | FEEDER | [5 empty] | 574 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-12-05 |  |  | SPARE | GDA | F11(JB31) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB31_GDA | 11KV博十一線(JB31) 接地RY | FEEDER | [5 empty] | 575 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0333 |  | 0123 | 1-36-10 |  | 1-7A | JB31 | ADJ(U/L) | 博十一線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB31_ADJ | 11KV博十一線(JB31) LCO分流器 | FEEDER | [5 empty] | 576 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0143 |  | 0093 | 1-11-04 |  | 1-5C | SPARE | 52AS | F11(JB31) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB31_CB | JB31(11KV博十一線) CB | FEEDER | [5 empty] | 577 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-12-06 |  |  | SPARE | PHA | F12(JB32) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB32_PHA | 11KV博十二線(JB32) 相間RY | FEEDER | [5 empty] | 578 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-12-07 |  |  | SPARE | GDA | F12(JB32) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB32_GDA | 11KV博十二線(JB32) 接地RY | FEEDER | [5 empty] | 579 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0334 |  | 0124 | 1-36-11 |  | 1-7B | JB32 | ADJ(U/L) | 博十二線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB32_ADJ | 11KV博十二線(JB32) LCO分流器 | FEEDER | [5 empty] | 580 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0144 |  | 0094 | 1-11-05 |  | 1-5D | SPARE | 52AS | F12(JB32) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB32_CB | JB32(11KV博十二線) CB | FEEDER | [5 empty] | 581 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | SPARE | PHA | F13(JB33) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB33_PHA | 11KV博十三線(JB33) 相間RY | FEEDER | [5 empty] | 582 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | SPARE | GDA | F13(JB33) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB33_GDA | 11KV博十三線(JB33) 接地RY | FEEDER | [5 empty] | 583 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0335 |  | 0125 | 1-36-12 |  | 1-7C | JB33 | ADJ(U/L) | 博十三線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB33_ADJ | 11KV博十三線(JB33) LCO分流器 | FEEDER | [5 empty] | 584 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0145 |  | 0095 | 1-11-06 |  | 1-5E | SPARE | 52AS | F13(JB33) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB33_CB | JB33(11KV博十三線) CB | FEEDER | [5 empty] | 585 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-02 |  |  | SPARE | PHA | F14(JB34) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB34_PHA | 11KV博十四線(JB34) 相間RY | FEEDER | [5 empty] | 586 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | SPARE | GDA | F14(JB34) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB34_GDA | 11KV博十四線(JB34) 接地RY | FEEDER | [5 empty] | 587 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0336 |  | 0126 | 1-36-13 |  | 1-7D | JB34 | ADJ(U/L) | 博十四線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB34_ADJ | 11KV博十四線(JB34) LCO分流器 | FEEDER | [5 empty] | 588 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0146 |  | 0096 | 1-11-07 |  | 1-5F | SPARE | 52AS | F14(JB34) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB34_CB | JB34(11KV博十四線) CB | FEEDER | [5 empty] | 589 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | SPARE | PHA | F15(JB35) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB35_PHA | 11KV博十五線(JB35) 相間RY | FEEDER | [5 empty] | 590 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-13-05 |  |  | SPARE | GDA | F15(JB35) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB35_GDA | 11KV博十五線(JB35) 接地RY | FEEDER | [5 empty] | 591 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0337 |  | 0127 | 1-36-14 |  | 1-7E | JB35 | ADJ(U/L) | 博十五線分流器(使用 / 閉鎖)指示 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB35_ADJ | 11KV博十五線(JB35) LCO分流器 | FEEDER | [5 empty] | 592 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0147 |  | 0097 | 1-12-00 |  | 1-60 | SPARE | 52AS | F15(JB35) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.JB35_CB | JB35(11KV博十五線) CB | FEEDER | [5 empty] | 593 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 2-3B-11 | [7 empty] | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  | DNP_Mon1_EMPTY,PointList_NULL |  |  |  | 594 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | TRA |  | INSERT | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-3B-14 | [7 empty] | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_TRA | #3MTR 重故障 | DTR |  | DNP_Mon1_EMPTY,PointList_NULL |  |  |  | 595 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | TRF |  | INSERT | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [9 empty] | 2-3B-15 | [7 empty] | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  | DNP_Mon1_EMPTY,PointList_NULL |  |  |  | 596 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | SupLocal |  | INSERT | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [9 empty] | 2-3B-12 | [7 empty] | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  | DNP_Mon1_EMPTY,PointList_NULL |  |  |  | 597 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | Tap Chan |  | INSERT | TapPos |  | Rise/Low | Y | 3 | DI-SP | [8 empty] | 0099 | 2-3B-13 |  | 1-62 | SPARE |  |  |  |  | B1/S23_D1 | [8 empty] | 博愛SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  | DNP_Mon1_EMPTY,DNP_Mon1_NULL |  |  |  | 598 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0142 |  | 0092 | 1-11-03 |  | 1-5B | SPARE | 52AS | #3SC |  |  | B2/S23_D1 | [8 empty] | 博愛SS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 599 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Water1 | 開關場水位警報 | INSERT | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0345 |  |  | 1-37-06 |  |  | Locate Empty |  | 開關場水位第一段警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 600 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | StaDev | 所內設施 |  | Water2 | 開關場水位二段 | INSERT | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0344 |  |  | 1-37-05 |  |  | Locate Empty |  | 開關場水位第二段警報 |  |  | B3/S23_D1 | [8 empty] | 博愛SS.開關場水位二段 | 開關場水位二段警報 | OTHER | [5 empty] | 601 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 1-3F-15 |  |  | 11KV IED重警報 | IEDA | #1 MTR& #4 MTR |  |  | B3/S23_D1 | [8 empty] | 博愛SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 602 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0449 |  |  | 1-3F-14 |  |  | Locate Empty |  | POWER METER (SP) |  |  | B2/S23_D1 | [8 empty] | 博愛SS.PMA | PMA | OTHER | [5 empty] | 603 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0438 |  |  | 1-3F-03 |  |  | JB40 (F20) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博二十線79LOA | 博二十線79LOA | OTHER | [5 empty] | 604 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0435 |  |  | 1-3F-00 |  |  | JB37 (F17) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博十七線79LOA | 博十七線79LOA | OTHER | [5 empty] | 605 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0437 |  |  | 1-3F-02 |  |  | JB39 (F19) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博十九線79LOA | 博十九線79LOA | OTHER | [5 empty] | 606 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0436 |  |  | 1-3F-01 |  |  | JB38 (F18) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博十八線79LOA | 博十八線79LOA | OTHER | [5 empty] | 607 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0434 |  |  | 1-3E-15 |  |  | JB36 (F16) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博十六線79LOA | 博十六線79LOA | OTHER | [5 empty] | 608 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/1SSTR |  |  | 0163 |  | 0067 | 1-14-00 |  | 1-42 | #1 SSTR CB | 52AS | 一號主變所內變壓器 |  | aaab | B2/S23_D1 | [8 empty] | 博愛SS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 609 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-01 |  |  | #1 SSTR CB | PHA | 一號主變所內變壓器 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 610 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-02 |  |  | #1 SSTR CB | GDA | 一號主變所內變壓器 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 611 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0419 |  |  | 1-3E-00 |  |  | JB21 (F1) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博ㄧ線79LOA | 博ㄧ線79LOA | OTHER | [5 empty] | 612 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0420 |  |  | 1-3E-01 |  |  | JB22 (F2) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博二線79LOA | 博二線79LOA | OTHER | [5 empty] | 613 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0421 |  |  | 1-3E-02 |  |  | JB23 (F3) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博三線79LOA | 博三線79LOA | OTHER | [5 empty] | 614 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0423 |  |  | 1-3E-04 |  |  | JB25 (F5) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博五線79LOA | 博五線79LOA | OTHER | [5 empty] | 615 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0422 |  |  | 1-3E-03 |  |  | JB24 (F4) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博四線79LOA | 博四線79LOA | OTHER | [5 empty] | 616 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | T/2SSTR |  |  | 0166 |  | 0068 | 1-14-03 |  | 1-43 | #2 SSTR CB | 52AS | 二號主變所內變壓器 |  | abab | B2/S23_D1 | [8 empty] | 博愛SS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 617 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-04 |  |  | #2 SSTR CB | PHA | 二號主變所內變壓器 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 618 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-14-05 |  |  | #2 SSTR CB | GDA | 二號主變所內變壓器 |  |  | B2/S23_D1 | [8 empty] | 博愛SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 619 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0425 |  |  | 1-3E-06 |  |  | JB27 (F7) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博七線79LOA | 博七線79LOA | OTHER | [5 empty] | 620 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0427 |  |  | 1-3E-08 |  |  | JB29 (F9) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博九線79LOA | 博九線79LOA | OTHER | [5 empty] | 621 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0426 |  |  | 1-3E-07 |  |  | JB28 (F8) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博八線79LOA | 博八線79LOA | OTHER | [5 empty] | 622 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0428 |  |  | 1-3E-09 |  |  | JB30 (F10) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博十線79LOA | 博十線79LOA | OTHER | [5 empty] | 623 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0424 |  |  | 1-3E-05 |  |  | JB26 (F6) | 79LOA |  |  |  | B2/S23_D1 | [8 empty] | 博愛SS.博六線79LOA | 博六線79LOA | OTHER | [5 empty] | 624 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 KWH(+) | JB21 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 625 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 KWH(+) | JB22 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 626 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 KWH(+) | JB23 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 627 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 KWH(+) | JB24 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 628 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 KWH(+) | JB25 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 629 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 KWH(+) | JB26 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 630 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 KWH(+) | JB27 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 631 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 KWH(+) | JB28 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 632 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 KWH(+) | JB29 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 633 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 KWH(+) | JB30 | Power Meter 6760 |  |  | B2/S23_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 634 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十一線A1 | 11KV博十一線 R相AMP | FEEDER | [5 empty] | 635 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十一線A2 | 11KV博十一線 S相AMP | FEEDER | [5 empty] | 636 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十一線A3 | 11KV博十一線 T相AMP | FEEDER | [5 empty] | 637 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十二線A1 | 11KV博十二線 R相AMP | FEEDER | [5 empty] | 638 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十二線A2 | 11KV博十二線 S相AMP | FEEDER | [5 empty] | 639 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十二線A3 | 11KV博十二線 T相AMP | FEEDER | [5 empty] | 640 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十三線A1 | 11KV博十三線 R相AMP | FEEDER | [5 empty] | 641 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十三線A2 | 11KV博十三線 S相AMP | FEEDER | [5 empty] | 642 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十三線A3 | 11KV博十三線 T相AMP | FEEDER | [5 empty] | 643 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十五線A1 | 11KV博十五線 R相AMP | FEEDER | [5 empty] | 644 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十五線A2 | 11KV博十五線 S相AMP | FEEDER | [5 empty] | 645 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十五線A3 | 11KV博十五線 T相AMP | FEEDER | [5 empty] | 646 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十五線A0 | 11KV博十五線 N相AMP | FEEDER | [5 empty] | 647 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十四線A1 | 11KV博十四線 R相AMP | FEEDER | [5 empty] | 648 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十四線A2 | 11KV博十四線 S相AMP | FEEDER | [5 empty] | 649 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S23_D1 | [8 empty] | 博愛SS.博十四線A3 | 11KV博十四線 T相AMP | FEEDER | [5 empty] | 650 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB31_DS | JB31_DS (非取樣點) | FEEDER | [5 empty] | 651 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB31_ES | JB31_ES (非取樣點) | FEEDER | [5 empty] | 652 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB32_DS | JB32_DS (非取樣點) | FEEDER | [5 empty] | 653 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB32_ES | JB32_ES (非取樣點) | FEEDER | [5 empty] | 654 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB33_DS | JB33_DS (非取樣點) | FEEDER | [5 empty] | 655 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB33_ES | JB33_ES (非取樣點) | FEEDER | [5 empty] | 656 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB34_DS | JB34_DS (非取樣點) | FEEDER | [5 empty] | 657 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB34_ES | JB34_ES (非取樣點) | FEEDER | [5 empty] | 658 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB35_DS | JB35_DS (非取樣點) | FEEDER | [5 empty] | 659 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.JB35_ES | JB35_ES (非取樣點) | FEEDER | [5 empty] | 660 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 661 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 69B新1E | #1BUS(69B新1E) |  | E1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_A1 | [8 empty] | 博愛SS.69B新1E | 69B新1E(非取樣點) | BUS | [5 empty] | 662 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 1PT | #1PT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbE | B/1BUS | T/1PT | [12 empty] | aajb | B2/S23_D1 | [8 empty] | 博愛SS.#1PT_DS | #1PT_DS (非取樣點) | OTHER | [5 empty] | 663 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 1PT | #1PT |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.#1PT_ES | #1PT_ES (非取樣點) | OTHER | [5 empty] | 664 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391_DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.391_DS | 391_DS (非取樣點) | OTHER | [5 empty] | 665 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391_ (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.391_ES | 391_ES (非取樣點) | OTHER | [5 empty] | 666 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | BR1 | BR1 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP |  | BayFdrF | B/1Bus | A/1BR | [12 empty] | aajb | B2/S23_D1 | [8 empty] | 博愛SS.BR1_DS | BR1_DS (非取樣點) | OTHER | [5 empty] | 667 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | BR1 | BR1 |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.BR1_ES | BR1_ES (非取樣點) | OTHER | [5 empty] | 668 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 1BE | #1BE |  | BE0 | #1MBUS_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP |  | Bb1EthA | B/1BUS | [13 empty] | aaaa | B2/S23_D1 | [8 empty] | 博愛SS.#1MBUS_ES | #1MBUS_ES (非取樣點) | OTHER | [5 empty] | 669 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 2BE | #2BE |  | BE0 | #2MBUS_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP |  | Bb1EthA | B/2BUS | [13 empty] | abfb | B2/S23_D1 | [8 empty] | 博愛SS.#2MBUS_ES | #2MBUS_ES (非取樣點) | OTHER | [5 empty] | 670 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 2PT | #2PT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbE | B/2BUS | T/2PT | [12 empty] | abjb | B2/S23_D1 | [8 empty] | 博愛SS.#2PT_DS | #2PT_DS (非取樣點) | OTHER | [5 empty] | 671 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 2PT | #2PT |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.#2PT_ES | #2PT_ES (非取樣點) | OTHER | [5 empty] | 672 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491_DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.491_DS | 491_DS (非取樣點) | OTHER | [5 empty] | 673 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491_ (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.491_ES | 491_ES (非取樣點) | OTHER | [5 empty] | 674 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S23_D1 | [8 empty] | 博愛SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | [5 empty] | 675 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S23 | 博愛SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S23_D1 | [12 empty] | 博愛SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S23/69/1BUS/V; OPRD2: S23/69/2BUS/V
S23 | 博愛SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S23_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S23/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S23 | 博愛SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S23_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_10 | OPRD1: S23/11/M1/MW; OPRD2: S23/11/M2/MW; OPRD3: S23/11/M3/MW; OPRD4: S23/11/M4/MW; OPRD5: S23/69/610/MW; OPRD6: S23/69/620/MW; OPRD7: S23/69/640/MW; OPRD8: S23/69/650/MW; OPRD9: S23/69/660/MW; OPRD10: S23/69/670/MW
S23 | 博愛SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S23_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S23/0/CalcPoint/OPRN2_MW
S23 | 博愛SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S23_D1 | [17 empty] | none
S23 | 博愛SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S23_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S23/0/CalcPoint/OPRN1; OPRD2: S23/0/CalcPoint/OPRN2; OPRD3: S23/0/CalcPoint/PRFL_UL
S23 | 博愛SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S23_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S23/11/M1/MW; OPRD2: S23/11/M1/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S23_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S23/11/M2/MW; OPRD2: S23/11/M2/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S23_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S23/11/M3/MW; OPRD2: S23/11/M3/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S23_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S23/11/M4/MW; OPRD2: S23/11/M4/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 610 | 博愛～水上線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.610_AMP | 水上線 AMP | LINE69 | AMP_CAL | C12R0899 | amp_cal | OPRD1: S23/69/610/MW; OPRD2: S23/69/610/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.620_AMP | 後湖線 AMP | LINE69 | AMP_CAL | C12R0880 | amp_cal | OPRD1: S23/69/620/MW; OPRD2: S23/69/620/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 640 | 博愛～溶劑線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.640_AMP | 溶劑線 AMP | LINE69 | AMP_CAL | C12R0880 | amp_cal | OPRD1: S23/69/640/MW; OPRD2: S23/69/640/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 650 | 博愛～鐵嘉紅線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.650_AMP | 博鐵紅線 AMP | LINE69 | AMP_CAL | C12R0880 | amp_cal | OPRD1: S23/69/650/MW; OPRD2: S23/69/650/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 660 | 博愛～鐵嘉白線(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.660_AMP | 博鐵白線 AMP | LINE69 | AMP_CAL | C12R0880 | amp_cal | OPRD1: S23/69/660/MW; OPRD2: S23/69/660/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 69 | 69kV | 670 | 嘉義～博愛線(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S23_A1 | [12 empty] | 博愛SS.670_AMP | 嘉博線 AMP | LINE69 | AMP_CAL | C12R0880 | amp_cal | OPRD1: S23/69/670/MW; OPRD2: S23/69/670/MVAR; OPRD3: S23/0/CalcPoint/Vbs2
S23 | 博愛SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S23_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S23/11/1BUS/V
S23 | 博愛SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S23_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S23/11/2BUS/V
S23 | 博愛SS | 11 | 11kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S23_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S23/11/3ABUS/V
S23 | 博愛SS | 11 | 11kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S23_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S23/11/3BBUS/V
S23 | 博愛SS | 11 | 11kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S23_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S23/11/4BUS/V
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S23_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 博愛SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S23/11/M1/MW; OPRD2: S23/11/M1/MVAR
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S23_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 博愛SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S23/11/M2/MW; OPRD2: S23/11/M2/MVAR
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S23_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 博愛SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S23/11/M3/MW; OPRD2: S23/11/M3/MVAR
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S23_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 博愛SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S23/11/M4/MW; OPRD2: S23/11/M4/MVAR
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S23_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S23//1MTR/MVA; OPRD2: 0
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S23_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S23//2MTR/MVA; OPRD2: 0
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S23_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S23//3MTR/MVA; OPRD2: 0
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/S23_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S23//4MTR/MVA; OPRD2: 0
S23 | 博愛SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S23_D1 | [12 empty] | 博愛SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S23/11/M1/MW; OPRD2: S23/11/M1/MVAR
S23 | 博愛SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S23_D1 | [12 empty] | 博愛SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S23/11/M2/MW; OPRD2: S23/11/M2/MVAR
S23 | 博愛SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S23_D1 | [12 empty] | 博愛SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S23/11/M3/MW; OPRD2: S23/11/M3/MVAR
S23 | 博愛SS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/S23_D1 | [12 empty] | 博愛SS.#4MTR_PF | #4MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S23/11/M4/MW; OPRD2: S23/11/M4/MVAR
S23 | 博愛SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S23_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S23//1MTR/SupLocal; OPRD2: S23//1MTR/Tap Chan; OPRD3: NULL
S23 | 博愛SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S23_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S23//2MTR/SupLocal; OPRD2: S23//2MTR/Tap Chan; OPRD3: NULL
S23 | 博愛SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S23_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S23//3MTR/SupLocal; OPRD2: S23//3MTR/Tap Chan; OPRD3: NULL
S23 | 博愛SS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/S23_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S23//4MTR/SupLocal; OPRD2: S23//4MTR/Tap Chan; OPRD3: NULL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/1BUS/V; OPRD2: S23/11/JB21/I_R; OPRD3: S23/11/JB21/I_S; OPRD4: S23/11/JB21/I_T
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/1BUS/V; OPRD2: S23/11/JB22/I_R; OPRD3: S23/11/JB22/I_S; OPRD4: S23/11/JB22/I_T
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/1BUS/V; OPRD2: S23/11/JB23/I_R; OPRD3: S23/11/JB23/I_S; OPRD4: S23/11/JB23/I_T
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/1BUS/V; OPRD2: S23/11/JB24/I_R; OPRD3: S23/11/JB24/I_S; OPRD4: S23/11/JB24/I_T
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/1BUS/V; OPRD2: S23/11/JB25/I_R; OPRD3: S23/11/JB25/I_S; OPRD4: S23/11/JB25/I_T
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/2BUS/V; OPRD2: S23/11/JB26/I_R; OPRD3: S23/11/JB26/I_S; OPRD4: S23/11/JB26/I_T
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/2BUS/V; OPRD2: S23/11/JB27/I_R; OPRD3: S23/11/JB27/I_S; OPRD4: S23/11/JB27/I_T
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/2BUS/V; OPRD2: S23/11/JB28/I_R; OPRD3: S23/11/JB28/I_S; OPRD4: S23/11/JB28/I_T
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/2BUS/V; OPRD2: S23/11/JB29/I_R; OPRD3: S23/11/JB29/I_S; OPRD4: S23/11/JB29/I_T
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/2BUS/V; OPRD2: S23/11/JB30/I_R; OPRD3: S23/11/JB30/I_S; OPRD4: S23/11/JB30/I_T
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S23/11/JB31/I_R; OPRD3: S23/11/JB31/I_S; OPRD4: S23/11/JB31/I_T
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S23/11/JB32/I_R; OPRD3: S23/11/JB32/I_S; OPRD4: S23/11/JB32/I_T
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S23/11/JB33/I_R; OPRD3: S23/11/JB33/I_S; OPRD4: S23/11/JB33/I_T
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S23/11/JB34/I_R; OPRD3: S23/11/JB34/I_S; OPRD4: S23/11/JB34/I_T
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S23/11/JB35/I_R; OPRD3: S23/11/JB35/I_S; OPRD4: S23/11/JB35/I_T
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/4BUS/V; OPRD2: S23/11/JB36/I_R; OPRD3: S23/11/JB36/I_S; OPRD4: S23/11/JB36/I_T
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/4BUS/V; OPRD2: S23/11/JB37/I_R; OPRD3: S23/11/JB37/I_S; OPRD4: S23/11/JB37/I_T
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/4BUS/V; OPRD2: S23/11/JB38/I_R; OPRD3: S23/11/JB38/I_S; OPRD4: S23/11/JB38/I_T
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/4BUS/V; OPRD2: S23/11/JB39/I_R; OPRD3: S23/11/JB39/I_S; OPRD4: S23/11/JB39/I_T
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S23/11/4BUS/V; OPRD2: S23/11/JB40/I_R; OPRD3: S23/11/JB40/I_S; OPRD4: S23/11/JB40/I_T
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB21/kVA; OPRD2: S23/11/JB21/KVAR
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB22/kVA; OPRD2: S23/11/JB22/KVAR
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB23/kVA; OPRD2: S23/11/JB23/KVAR
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB24/kVA; OPRD2: S23/11/JB24/KVAR
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB25/kVA; OPRD2: S23/11/JB25/KVAR
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB26/kVA; OPRD2: S23/11/JB26/KVAR
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB27/kVA; OPRD2: S23/11/JB27/KVAR
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB28/kVA; OPRD2: S23/11/JB28/KVAR
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB29/kVA; OPRD2: S23/11/JB29/KVAR
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB30/kVA; OPRD2: S23/11/JB30/KVAR
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB31/kVA; OPRD2: S23/11/JB31/KVAR
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB32/kVA; OPRD2: S23/11/JB32/KVAR
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB33/kVA; OPRD2: S23/11/JB33/KVAR
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB34/kVA; OPRD2: S23/11/JB34/KVAR
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB35/kVA; OPRD2: S23/11/JB35/KVAR
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB36/kVA; OPRD2: S23/11/JB36/KVAR
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB37/kVA; OPRD2: S23/11/JB37/KVAR
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB38/kVA; OPRD2: S23/11/JB38/KVAR
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB39/kVA; OPRD2: S23/11/JB39/KVAR
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S23/11/JB40/kVA; OPRD2: S23/11/JB40/KVAR
S23 | 博愛SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S23_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_4 | OPRD1: S23/11/M1/MW; OPRD2: S23/11/M2/MW; OPRD3: S23/11/M3/MW; OPRD4: S23/11/M4/MW
S23 | 博愛SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S23_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_4 | OPRD1: S23/11/M1/MVAR; OPRD2: S23/11/M2/MVAR; OPRD3: S23/11/M3/MVAR; OPRD4: S23/11/M4/MVAR
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S23_D1 | [12 empty] | 博愛SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S23/11/210/CB; OPRD2: 6.9; OPRD3: 0
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S23_D1 | [12 empty] | 博愛SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S23/11/220/CB; OPRD2: 6.9; OPRD3: 0
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S23_D1 | [12 empty] | 博愛SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S23/11/230/CB; OPRD2: 6.9; OPRD3: 0
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S23_D1 | [12 empty] | 博愛SS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S23/11/240/CB; OPRD2: 6.9; OPRD3: 0
S23 | 博愛SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S23_D1 | [12 empty] | 博愛SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_17 |  | com_alarm_37 | S23//1MTR/96B1 | S23//1MTR/96B2 | S23//1MTR/96D | S23//1MTR/96PA | S23//1MTR/GDA | S23//1MTR/TRA | S23//1MTR/63Q | S23//1MTR/87A | S23//1MTR/51ZA | S23//2MTR/96D | S23//2MTR/63Q | S23//2MTR/GDA | S23//2MTR/96B2 | S23//2MTR/96B1 | S23//2MTR/96PA | S23//2MTR/TRA | S23//2MTR/87A | S23//2MTR/51ZA | S23//3MTR/96B1 | S23//3MTR/TRA | S23//3MTR/96PA | S23//3MTR/63Q | S23//3MTR/96D | S23//3MTR/96B2 | S23//3MTR/87A | S23//3MTR/51ZA | S23//4MTR/96B1 | S23//4MTR/TRA | S23//4MTR/96D | S23//4MTR/96B2 | S23//4MTR/GDA | S23//4MTR/63Q | S23//4MTR/96PA | S23//4MTR/87A | S23//4MTR/51ZA | S23/69/1BUS/87A | S23/69/2BUS/87A
S23 | 博愛SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S23_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: S23//1MTR/TRF; OPRD2: S23//2MTR/TRF; OPRD3: S23//3MTR/TRF; OPRD4: S23//4MTR/TRF
S23 | 博愛SS | 11 | 11kV | M1_A1 | #1MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/11/M1/81A
S23 | 博愛SS | 11 | 11kV | M2_A1 | #2MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/11/M2/81A
S23 | 博愛SS | 11 | 11kV | M3_A1 | #3MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/11/M3/81A
S23 | 博愛SS | 11 | 11kV | M4_A1 | #4MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/11/M4/81A
S23 | 博愛SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/0/RTU/RTU_R_L
S23 | 博愛SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/0/StaDev/DCE
S23 | 博愛SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/0/StaDev/PSF
S23 | 博愛SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/0/StaDev/PSA
S23 | 博愛SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S23_A1 | [17 empty] | lamp2CC | OPRD1: S23/0/StaDev/DCA
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/CBF
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/CBA
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/ABS_89A
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/COMT
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | IED警報 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/IRFA
S23 | 博愛SS | 69 | 69kV | ComPoint_D1 |  |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S23_D1 | [17 empty] | lamp2CC | OPRD1: S23/69/ComPoint/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S23 | 博愛SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S23/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.610_AMP | 水上線 AMP | LINE69 | S23/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0899 | 806.400024 | 806.400024 | 899.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 69 | 69kV | 620 | 後湖線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.620_AMP | 後湖線 AMP | LINE69 | S23/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0880 | 792.000000 | 792.000000 | 880.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.670_AMP | 嘉博線 AMP | LINE69 | S23/69/670/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0880 | 792.000000 | 792.000000 | 880.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 0 |  |  |  |  | 博一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博一線KVA | 11KV博一線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博一線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博一線KW | 11KV博一線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博七線KVA | 11KV博七線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博七線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博七線KW | 11KV博七線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博九線KVA | 11KV博九線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博九線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博九線KW | 11KV博九線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博二十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二十線KVA | 11KV博二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博二十線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二十線KW | 11KV博二十線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二線KVA | 11KV博二線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博二線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二線KW | 11KV博二線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博八線KVA | 11KV博八線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博八線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博八線KW | 11KV博八線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十一線KVA | 11KV博十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十一線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十一線KW | 11KV博十一線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十七線KVA | 11KV博十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十七線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十七線KW | 11KV博十七線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十九線KVA | 11KV博十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十九線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十九線KW | 11KV博十九線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十二線KVA | 11KV博十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十二線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十二線KW | 11KV博十二線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十八線KVA | 11KV博十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十八線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十八線KW | 11KV博十八線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十三線KVA | 11KV博十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十三線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十三線KW | 11KV博十三線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十五線KVA | 11KV博十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十五線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十五線KW | 11KV博十五線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十六線KVA | 11KV博十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十六線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十六線KW | 11KV博十六線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十四線KVA | 11KV博十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十四線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十四線KW | 11KV博十四線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十線KVA | 11KV博十線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博十線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十線KW | 11KV博十線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博三線KVA | 11KV博三線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博三線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博三線KW | 11KV博三線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博五線KVA | 11KV博五線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博五線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博五線KW | 11KV博五線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博六線KVA | 11KV博六線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博六線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博六線KW | 11KV博六線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博四線KVA | 11KV博四線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  |  |  |  | 博四線KW | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.博四線KW | 11KV博四線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S23//1MTR/MVA |  | MVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_PF | #1MTR 功率因素 | DTR | S23//1MTR/PF |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S23//2MTR/MVA |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_PF | #2MTR 功率因素 | DTR | S23//2MTR/PF |  | RPDC_PF_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S23//3MTR/MVA |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_PF | #3MTR 功率因素 | DTR | S23//3MTR/PF |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | S23//4MTR/MVA |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_PF | #4MTR 功率因素 | DTR | S23//4MTR/PF |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S23 | 博愛SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S23/11/210/MVAR |  | SC_CAL_11 |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S23/11/220/MVAR |  | SC_CAL_11 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S23/11/230/MVAR |  | SC_CAL_11 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_SC_MVAR | 11KV#4SC MVAR | SC | S23/11/240/MVAR |  | SC_CAL_11 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.650_AMP | 博鐵紅線 AMP | LINE69 | S23/69/650/I |  | AMP_CAL |  |  | 58 | CalcAIPoint | [21 empty] | C12R0880 | 792.000000 | 792.000000 | 880.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.660_AMP | 博鐵白線 AMP | LINE69 | S23/69/660/I |  | AMP_CAL |  |  | 59 | CalcAIPoint | [21 empty] | C12R0880 | 792.000000 | 792.000000 | 880.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 博愛SS.640_AMP | 溶劑線 AMP | LINE69 | S23/69/640/I |  | AMP_CAL |  |  | 60 | CalcAIPoint | [21 empty] | C12R0880 | 792.000000 | 792.000000 | 880.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S23 | 博愛SS | 69 | 69kV | 610_CB | 水上線(610_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.610_CB_2 | 610(水上線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 61 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 620_CB | 後博線(620_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.620_CB_2 | 620(後博線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 62 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 670_CB | 嘉博線(670_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.670_CB_2 | 670(嘉博線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 63 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 64 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 65 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 66 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 博愛SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 67 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S23 | 博愛SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 68 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 博愛SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S23/0/CalcPoint/SUBA |  | STATION_FAULT_17 |  |  | 69 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 70 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_4 |  |  | 71 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610_AMP | 水上線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.610_AMP_A | 水上線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 610_AMP | 水上線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.610_AMP_2 | 水上線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 73 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 620_AMP | 後湖線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.620_AMP_A | 後湖線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 620_AMP | 後湖線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.620_AMP_2 | 後湖線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 75 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 670_AMP | 嘉博線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.670_AMP_A | 嘉博線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 670_AMP | 嘉博線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.670_AMP_2 | 嘉博線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 77 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_MVA_2 | #3MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 4MTR_MVA | #4MTR | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_MVA_2 | #4MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | _IED警報 | IED警報 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_IED警報_A | 69KV IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 86 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650_AMP | 博鐵紅線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.650_AMP_A | 博鐵紅線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 650_AMP | 博鐵紅線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.650_AMP_2 | 博鐵紅線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 88 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 650_CB | 博鐵紅線(650_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.650_CB_2 | 650(博鐵紅線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 89 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 660_AMP | 博鐵白線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.660_AMP_A | 博鐵白線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 660_AMP | 博鐵白線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.660_AMP_2 | 博鐵白線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 91 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 660_CB | 博鐵白線(660_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.660_CB_2 | 660(博鐵白線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 92 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 600_CB | 600(600_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.600_CB_2 | 600 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 93 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | COMT警報 | COMT警報 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.COMT警報_A | COMT警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 94 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | _PMA | PMA | [27 empty] | ADCS_N | [8 empty] | 博愛SS.69KV_PMA_A | 69KV PMA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640_CB | 溶劑線(640_CB) | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.640_CB_2 | 640(溶劑線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 96 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 640_AMP | 溶劑線 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.640_AMP_A | 溶劑線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 69 | 69kV | 640_AMP | 溶劑線 | [27 empty] | DDCS2_2 | [8 empty] | 博愛SS.640_AMP_2 | 溶劑線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 98 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S23 | 博愛SS | 0 |  | 600TIE_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.600TIE_RYFA_A | 600 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 99 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 650_RYFA | 650 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.650_RYFA_A | 650 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 100 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 660_RYFA | 660 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.660_RYFA_A | 660 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 101 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 600_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.600_RYFA_A | 600 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 102 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 610水上_CFA | 610 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.610水上_CFA_A | 610 通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 103 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 610水上_RYFA | 610 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.610水上_RYFA_A | 610 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 104 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 620後博_CFA | 620 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.620後博_CFA_A | 620 通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 620後博_RYFA | 620 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.620後博_RYFA_A | 620 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 106 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 650紅線_RYFA | 650 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.650紅線_RYFA_A | 650 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 107 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 660白線RYFA | 660 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.660白線RYFA_A | 660 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 108 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 670嘉博_CFA | 670 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.670嘉博_CFA_A | 670 通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 109 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 670嘉博_RYFA | 670 | [27 empty] | ADCS_N | [8 empty] | 博愛SS.670嘉博_RYFA_A | 670 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 110 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | BUSRY_BF | BUSRY | [27 empty] | ADCS_N | [8 empty] | 博愛SS.BUSRY_BF_A | BUSRY BF (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 111 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | BUSRY_CTFA | BUSRY | [27 empty] | ADCS_N | [8 empty] | 博愛SS.BUSRY_CTFA_A | BUSRY CTFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 112 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S23/0/RTU/ADCH1 |  |  |  | CDC | 113 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S23/0/RTU/ADCH2 |  |  |  | CDC | 114 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S23/0/RTU/ADCH3 |  |  |  | CDC | 115 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | S23/0/RTU/ADCH4 |  |  |  | CDC | 116 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S23/0/RTU/ADCL1 |  |  |  | CDC | 117 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S23/0/RTU/ADCL2 |  |  |  | CDC | 118 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S23/0/RTU/ADCL3 |  |  |  | CDC | 119 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | S23/0/RTU/ADCL4 |  |  |  | CDC | 120 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S23/69/1BUS/V |  |  |  | CDC | 121 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S23 | 博愛SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S23/11/1BUS/V |  |  |  | CDC | 122 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S23/11/2BUS/V |  |  |  | CDC | 123 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 3ABUS | #3ABUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | S23/11/3ABUS/V |  |  |  | CDC | 124 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-82 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | S23/11/3BBUS/V |  |  |  | CDC | 125 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 11 | 11kV | 4BUS | #4BUS |  | V | [17 empty] | 2-A5 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS | S23/11/4BUS/V |  |  |  | CDC | 126 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.610_MW | 水上線 MW | LINE69 | S23/69/610/MW |  |  |  | CDC | 127 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.610_MVAR | 水上線 MVAR | LINE69 | S23/69/610/MVAR |  |  |  | CDC | 128 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 620 | 後湖線(620) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.620_MW | 後湖線 MW | LINE69 | S23/69/620/MW |  |  |  | CDC | 129 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 620 | 後湖線(620) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.620_MVAR | 後湖線 MVAR | LINE69 | S23/69/620/MVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.670_MW | 嘉博線 MW | LINE69 | S23/69/670/MW |  |  |  | CDC | 131 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.670_MVAR | 嘉博線 MVAR | LINE69 | S23/69/670/MVAR |  |  |  | CDC | 132 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博一線 | 博一線 |  | 博一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博一線KVAR | 11KV博一線 KVAR | FEEDER | S23/11/JB21/KVAR |  |  |  | CDC | 133 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博一線 | 博一線 |  | 博一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博一線A1 | 11KV博一線 R相AMP | FEEDER | S23/11/JB21/I_R |  |  |  | CDC | 134 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博一線 | 博一線 |  | 博一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博一線A2 | 11KV博一線 S相AMP | FEEDER | S23/11/JB21/I_S |  |  |  | CDC | 135 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博一線 | 博一線 |  | 博一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博一線A3 | 11KV博一線 T相AMP | FEEDER | S23/11/JB21/I_T |  |  |  | CDC | 136 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博一線 | 博一線 |  | 博一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博一線A0 | 11KV博一線 N相AMP | FEEDER | S23/11/JB21/I_N |  |  |  | CDC | 137 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博七線 | 博七線 |  | 博七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博七線KVAR | 11KV博七線 KVAR | FEEDER | S23/11/JB27/KVAR |  |  |  | CDC | 138 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博七線 | 博七線 |  | 博七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博七線A1 | 11KV博七線 R相AMP | FEEDER | S23/11/JB27/I_R |  |  |  | CDC | 139 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博七線 | 博七線 |  | 博七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博七線A2 | 11KV博七線 S相AMP | FEEDER | S23/11/JB27/I_S |  |  |  | CDC | 140 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博七線 | 博七線 |  | 博七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博七線A3 | 11KV博七線 T相AMP | FEEDER | S23/11/JB27/I_T |  |  |  | CDC | 141 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博七線 | 博七線 |  | 博七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博七線A0 | 11KV博七線 N相AMP | FEEDER | S23/11/JB27/I_N |  |  |  | CDC | 142 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博九線 | 博九線 |  | 博九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博九線KVAR | 11KV博九線 KVAR | FEEDER | S23/11/JB29/KVAR |  |  |  | CDC | 143 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博九線 | 博九線 |  | 博九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博九線A1 | 11KV博九線 R相AMP | FEEDER | S23/11/JB29/I_R |  |  |  | CDC | 144 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博九線 | 博九線 |  | 博九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博九線A2 | 11KV博九線 S相AMP | FEEDER | S23/11/JB29/I_S |  |  |  | CDC | 145 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博九線 | 博九線 |  | 博九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博九線A3 | 11KV博九線 T相AMP | FEEDER | S23/11/JB29/I_T |  |  |  | CDC | 146 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博九線 | 博九線 |  | 博九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博九線A0 | 11KV博九線 N相AMP | FEEDER | S23/11/JB29/I_N |  |  |  | CDC | 147 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二十線 | 博二十線 |  | 博二十線KVAR | [17 empty] | 2-AE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二十線KVAR | 11KV博二十線 KVAR | FEEDER | S23/11/JB40/KVAR |  |  |  | CDC | 148 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二十線 | 博二十線 |  | 博二十線A1 | [17 empty] | 2-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二十線A1 | 11KV博二十線 R相AMP | FEEDER | S23/11/JB40/I_R |  |  |  | CDC | 149 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二十線 | 博二十線 |  | 博二十線A2 | [17 empty] | 2-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二十線A2 | 11KV博二十線 S相AMP | FEEDER | S23/11/JB40/I_S |  |  |  | CDC | 150 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二十線 | 博二十線 |  | 博二十線A3 | [17 empty] | 2-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二十線A3 | 11KV博二十線 T相AMP | FEEDER | S23/11/JB40/I_T |  |  |  | CDC | 151 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二十線 | 博二十線 |  | 博二十線A0 | [17 empty] | 2-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二十線A0 | 11KV博二十線 N相AMP | FEEDER | S23/11/JB40/I_N |  |  |  | CDC | 152 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二線 | 博二線 |  | 博二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二線KVAR | 11KV博二線 KVAR | FEEDER | S23/11/JB22/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二線 | 博二線 |  | 博二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二線A1 | 11KV博二線 R相AMP | FEEDER | S23/11/JB22/I_R |  |  |  | CDC | 154 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二線 | 博二線 |  | 博二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二線A2 | 11KV博二線 S相AMP | FEEDER | S23/11/JB22/I_S |  |  |  | CDC | 155 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二線 | 博二線 |  | 博二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二線A3 | 11KV博二線 T相AMP | FEEDER | S23/11/JB22/I_T |  |  |  | CDC | 156 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博二線 | 博二線 |  | 博二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博二線A0 | 11KV博二線 N相AMP | FEEDER | S23/11/JB22/I_N |  |  |  | CDC | 157 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博八線 | 博八線 |  | 博八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博八線KVAR | 11KV博八線 KVAR | FEEDER | S23/11/JB28/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博八線 | 博八線 |  | 博八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博八線A1 | 11KV博八線 R相AMP | FEEDER | S23/11/JB28/I_R |  |  |  | CDC | 159 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博八線 | 博八線 |  | 博八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博八線A2 | 11KV博八線 S相AMP | FEEDER | S23/11/JB28/I_S |  |  |  | CDC | 160 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博八線 | 博八線 |  | 博八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博八線A3 | 11KV博八線 T相AMP | FEEDER | S23/11/JB28/I_T |  |  |  | CDC | 161 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博八線 | 博八線 |  | 博八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博八線A0 | 11KV博八線 N相AMP | FEEDER | S23/11/JB28/I_N |  |  |  | CDC | 162 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十一線 | 博十一線 |  | 博十一線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十一線KVAR | 11KV博十一線 KVAR | FEEDER | S23/11/JB31/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十一線 | 博十一線 |  | 博十一線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十一線A1 | 11KV博十一線 R相AMP | FEEDER | S23/11/JB31/I_R |  |  |  | CDC | 164 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十一線 | 博十一線 |  | 博十一線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十一線A2 | 11KV博十一線 S相AMP | FEEDER | S23/11/JB31/I_S |  |  |  | CDC | 165 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十一線 | 博十一線 |  | 博十一線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十一線A3 | 11KV博十一線 T相AMP | FEEDER | S23/11/JB31/I_T |  |  |  | CDC | 166 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十七線 | 博十七線 |  | 博十七線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十七線KVAR | 11KV博十七線 KVAR | FEEDER | S23/11/JB37/KVAR |  |  |  | CDC | 167 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十七線 | 博十七線 |  | 博十七線A1 | [17 empty] | 2-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十七線A1 | 11KV博十七線 R相AMP | FEEDER | S23/11/JB37/I_R |  |  |  | CDC | 168 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十七線 | 博十七線 |  | 博十七線A2 | [17 empty] | 2-BC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十七線A2 | 11KV博十七線 S相AMP | FEEDER | S23/11/JB37/I_S |  |  |  | CDC | 169 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十七線 | 博十七線 |  | 博十七線A3 | [17 empty] | 2-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十七線A3 | 11KV博十七線 T相AMP | FEEDER | S23/11/JB37/I_T |  |  |  | CDC | 170 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十七線 | 博十七線 |  | 博十七線A0 | [17 empty] | 2-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十七線A0 | 11KV博十七線 N相AMP | FEEDER | S23/11/JB37/I_N |  |  |  | CDC | 171 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十九線 | 博十九線 |  | 博十九線KVAR | [17 empty] | 2-B2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十九線KVAR | 11KV博十九線 KVAR | FEEDER | S23/11/JB39/KVAR |  |  |  | CDC | 172 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十九線 | 博十九線 |  | 博十九線A1 | [17 empty] | 2-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十九線A1 | 11KV博十九線 R相AMP | FEEDER | S23/11/JB39/I_R |  |  |  | CDC | 173 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十九線 | 博十九線 |  | 博十九線A2 | [17 empty] | 2-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十九線A2 | 11KV博十九線 S相AMP | FEEDER | S23/11/JB39/I_S |  |  |  | CDC | 174 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十九線 | 博十九線 |  | 博十九線A3 | [17 empty] | 2-B5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十九線A3 | 11KV博十九線 T相AMP | FEEDER | S23/11/JB39/I_T |  |  |  | CDC | 175 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十九線 | 博十九線 |  | 博十九線A0 | [17 empty] | 2-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十九線A0 | 11KV博十九線 N相AMP | FEEDER | S23/11/JB39/I_N |  |  |  | CDC | 176 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十二線 | 博十二線 |  | 博十二線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十二線KVAR | 11KV博十二線 KVAR | FEEDER | S23/11/JB32/KVAR |  |  |  | CDC | 177 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十二線 | 博十二線 |  | 博十二線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十二線A1 | 11KV博十二線 R相AMP | FEEDER | S23/11/JB32/I_R |  |  |  | CDC | 178 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十二線 | 博十二線 |  | 博十二線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十二線A2 | 11KV博十二線 S相AMP | FEEDER | S23/11/JB32/I_S |  |  |  | CDC | 179 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十二線 | 博十二線 |  | 博十二線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十二線A3 | 11KV博十二線 T相AMP | FEEDER | S23/11/JB32/I_T |  |  |  | CDC | 180 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十八線 | 博十八線 |  | 博十八線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十八線KVAR | 11KV博十八線 KVAR | FEEDER | S23/11/JB38/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十八線 | 博十八線 |  | 博十八線A1 | [17 empty] | 2-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十八線A1 | 11KV博十八線 R相AMP | FEEDER | S23/11/JB38/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十八線 | 博十八線 |  | 博十八線A2 | [17 empty] | 2-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十八線A2 | 11KV博十八線 S相AMP | FEEDER | S23/11/JB38/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十八線 | 博十八線 |  | 博十八線A3 | [17 empty] | 2-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十八線A3 | 11KV博十八線 T相AMP | FEEDER | S23/11/JB38/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十八線 | 博十八線 |  | 博十八線A0 | [17 empty] | 2-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十八線A0 | 11KV博十八線 N相AMP | FEEDER | S23/11/JB38/I_N |  |  |  | CDC | 185 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十三線 | 博十三線 |  | 博十三線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十三線KVAR | 11KV博十三線 KVAR | FEEDER | S23/11/JB33/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十三線 | 博十三線 |  | 博十三線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十三線A1 | 11KV博十三線 R相AMP | FEEDER | S23/11/JB33/I_R |  |  |  | CDC | 187 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十三線 | 博十三線 |  | 博十三線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十三線A2 | 11KV博十三線 S相AMP | FEEDER | S23/11/JB33/I_S |  |  |  | CDC | 188 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十三線 | 博十三線 |  | 博十三線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十三線A3 | 11KV博十三線 T相AMP | FEEDER | S23/11/JB33/I_T |  |  |  | CDC | 189 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十五線 | 博十五線 |  | 博十五線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十五線KVAR | 11KV博十五線 KVAR | FEEDER | S23/11/JB35/KVAR |  |  |  | CDC | 190 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十五線 | 博十五線 |  | 博十五線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十五線A1 | 11KV博十五線 R相AMP | FEEDER | S23/11/JB35/I_R |  |  |  | CDC | 191 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十五線 | 博十五線 |  | 博十五線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十五線A2 | 11KV博十五線 S相AMP | FEEDER | S23/11/JB35/I_S |  |  |  | CDC | 192 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十五線 | 博十五線 |  | 博十五線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十五線A3 | 11KV博十五線 T相AMP | FEEDER | S23/11/JB35/I_T |  |  |  | CDC | 193 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十五線 | 博十五線 |  | 博十五線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十五線A0 | 11KV博十五線 N相AMP | FEEDER | S23/11/JB35/I_N |  |  |  | CDC | 194 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十六線 | 博十六線 |  | 博十六線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十六線KVAR | 11KV博十六線 KVAR | FEEDER | S23/11/JB36/KVAR |  |  |  | CDC | 195 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十六線 | 博十六線 |  | 博十六線A1 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十六線A1 | 11KV博十六線 R相AMP | FEEDER | S23/11/JB36/I_R |  |  |  | CDC | 196 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十六線 | 博十六線 |  | 博十六線A2 | [17 empty] | 2-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十六線A2 | 11KV博十六線 S相AMP | FEEDER | S23/11/JB36/I_S |  |  |  | CDC | 197 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十六線 | 博十六線 |  | 博十六線A3 | [17 empty] | 2-C3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十六線A3 | 11KV博十六線 T相AMP | FEEDER | S23/11/JB36/I_T |  |  |  | CDC | 198 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十六線 | 博十六線 |  | 博十六線A0 | [17 empty] | 2-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十六線A0 | 11KV博十六線 N相AMP | FEEDER | S23/11/JB36/I_N |  |  |  | CDC | 199 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十四線 | 博十四線 |  | 博十四線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十四線KVAR | 11KV博十四線 KVAR | FEEDER | S23/11/JB34/KVAR |  |  |  | CDC | 200 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十四線 | 博十四線 |  | 博十四線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十四線A1 | 11KV博十四線 R相AMP | FEEDER | S23/11/JB34/I_R |  |  |  | CDC | 201 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十四線 | 博十四線 |  | 博十四線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十四線A2 | 11KV博十四線 S相AMP | FEEDER | S23/11/JB34/I_S |  |  |  | CDC | 202 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十四線 | 博十四線 |  | 博十四線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十四線A3 | 11KV博十四線 T相AMP | FEEDER | S23/11/JB34/I_T |  |  |  | CDC | 203 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十線 | 博十線 |  | 博十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十線KVAR | 11KV博十線 KVAR | FEEDER | S23/11/JB30/KVAR |  |  |  | CDC | 204 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十線 | 博十線 |  | 博十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十線A1 | 11KV博十線 R相AMP | FEEDER | S23/11/JB30/I_R |  |  |  | CDC | 205 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十線 | 博十線 |  | 博十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十線A2 | 11KV博十線 S相AMP | FEEDER | S23/11/JB30/I_S |  |  |  | CDC | 206 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十線 | 博十線 |  | 博十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十線A3 | 11KV博十線 T相AMP | FEEDER | S23/11/JB30/I_T |  |  |  | CDC | 207 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博十線 | 博十線 |  | 博十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博十線A0 | 11KV博十線 N相AMP | FEEDER | S23/11/JB30/I_N |  |  |  | CDC | 208 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博三線 | 博三線 |  | 博三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博三線KVAR | 11KV博三線 KVAR | FEEDER | S23/11/JB23/KVAR |  |  |  | CDC | 209 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博三線 | 博三線 |  | 博三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博三線A1 | 11KV博三線 R相AMP | FEEDER | S23/11/JB23/I_R |  |  |  | CDC | 210 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博三線 | 博三線 |  | 博三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博三線A2 | 11KV博三線 S相AMP | FEEDER | S23/11/JB23/I_S |  |  |  | CDC | 211 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博三線 | 博三線 |  | 博三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博三線A3 | 11KV博三線 T相AMP | FEEDER | S23/11/JB23/I_T |  |  |  | CDC | 212 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博三線 | 博三線 |  | 博三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博三線A0 | 11KV博三線 N相AMP | FEEDER | S23/11/JB23/I_N |  |  |  | CDC | 213 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博五線 | 博五線 |  | 博五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博五線KVAR | 11KV博五線 KVAR | FEEDER | S23/11/JB25/KVAR |  |  |  | CDC | 214 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博五線 | 博五線 |  | 博五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博五線A1 | 11KV博五線 R相AMP | FEEDER | S23/11/JB25/I_R |  |  |  | CDC | 215 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博五線 | 博五線 |  | 博五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博五線A2 | 11KV博五線 S相AMP | FEEDER | S23/11/JB25/I_S |  |  |  | CDC | 216 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博五線 | 博五線 |  | 博五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博五線A3 | 11KV博五線 T相AMP | FEEDER | S23/11/JB25/I_T |  |  |  | CDC | 217 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博五線 | 博五線 |  | 博五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博五線A0 | 11KV博五線 N相AMP | FEEDER | S23/11/JB25/I_N |  |  |  | CDC | 218 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博六線 | 博六線 |  | 博六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博六線KVAR | 11KV博六線 KVAR | FEEDER | S23/11/JB26/KVAR |  |  |  | CDC | 219 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博六線 | 博六線 |  | 博六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博六線A1 | 11KV博六線 R相AMP | FEEDER | S23/11/JB26/I_R |  |  |  | CDC | 220 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博六線 | 博六線 |  | 博六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博六線A2 | 11KV博六線 S相AMP | FEEDER | S23/11/JB26/I_S |  |  |  | CDC | 221 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博六線 | 博六線 |  | 博六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博六線A3 | 11KV博六線 T相AMP | FEEDER | S23/11/JB26/I_T |  |  |  | CDC | 222 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博六線 | 博六線 |  | 博六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博六線A0 | 11KV博六線 N相AMP | FEEDER | S23/11/JB26/I_N |  |  |  | CDC | 223 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博四線 | 博四線 |  | 博四線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博四線KVAR | 11KV博四線 KVAR | FEEDER | S23/11/JB24/KVAR |  |  |  | CDC | 224 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博四線 | 博四線 |  | 博四線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博四線A1 | 11KV博四線 R相AMP | FEEDER | S23/11/JB24/I_R |  |  |  | CDC | 225 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博四線 | 博四線 |  | 博四線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博四線A2 | 11KV博四線 S相AMP | FEEDER | S23/11/JB24/I_S |  |  |  | CDC | 226 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博四線 | 博四線 |  | 博四線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博四線A3 | 11KV博四線 T相AMP | FEEDER | S23/11/JB24/I_T |  |  |  | CDC | 227 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | 博四線 | 博四線 |  | 博四線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.博四線A0 | 11KV博四線 N相AMP | FEEDER | S23/11/JB24/I_N |  |  |  | CDC | 228 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S23/11/TIE2/I_R |  |  |  | CDC | 229 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S23/11/TIE2/I_S |  |  |  | CDC | 230 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S23/11/TIE2/I_T |  |  |  | CDC | 231 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE | S23/11/TIE3/I_R |  |  |  | CDC | 232 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE | S23/11/TIE3/I_S |  |  |  | CDC | 233 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE | S23/11/TIE3/I_T |  |  |  | CDC | 234 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE4 | TIE4 |  | I_R | [17 empty] | 2-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE4_A1 | 11KV TIE4 R相AMP | TIE | S23/11/TIE4/I_R |  |  |  | CDC | 235 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE4 | TIE4 |  | I_S | [17 empty] | 2-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE4_A2 | 11KV TIE4 S相AMP | TIE | S23/11/TIE4/I_S |  |  |  | CDC | 236 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 11 | 11kV | _TIE4 | TIE4 |  | I_T | [17 empty] | 2-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.11KV_TIE4_A3 | 11KV TIE4 T相AMP | TIE | S23/11/TIE4/I_T |  |  |  | CDC | 237 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_MW | #1MTR二次側 MW | DTR | S23/11/M1/MW |  |  |  | CDC | 238 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S23/11/M1/MVAR |  |  |  | CDC | 239 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S23/11/M1/I_R |  |  |  | CDC | 240 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S23/11/M1/I_S |  |  |  | CDC | 241 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S23/11/M1/I_T |  |  |  | CDC | 242 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_OIL | #1MTR 油溫 | DTR | S23//1MTR/OilTemp |  |  |  | CDC | 243 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_COIL | #1MTR 線溫 | DTR | S23//1MTR/CoilTemp |  |  |  | CDC | 244 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S23//1MTR/TapPosMv |  |  |  | CDC | 245 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_MW | #2MTR二次側 MW | DTR | S23/11/M2/MW |  |  |  | CDC | 246 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S23/11/M2/MVAR |  |  |  | CDC | 247 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S23/11/M2/I_R |  |  |  | CDC | 248 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S23/11/M2/I_S |  |  |  | CDC | 249 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S23/11/M2/I_T |  |  |  | CDC | 250 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_OIL | #2MTR 油溫 | DTR | S23//2MTR/OilTemp |  |  |  | CDC | 251 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_COIL | #2MTR 線溫 | DTR | S23//2MTR/CoilTemp |  |  |  | CDC | 252 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S23//2MTR/TapPosMv |  |  |  | CDC | 253 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_MW | #3MTR二次側 MW | DTR | S23/11/M3/MW |  |  |  | CDC | 254 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S23/11/M3/MVAR |  |  |  | CDC | 255 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S23/11/M3/I_R |  |  |  | CDC | 256 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S23/11/M3/I_S |  |  |  | CDC | 257 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S23/11/M3/I_T |  |  |  | CDC | 258 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_OIL | #3MTR 油溫 | DTR | S23//3MTR/OilTemp |  |  |  | CDC | 259 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_COIL | #3MTR 線溫 | DTR | S23//3MTR/CoilTemp |  |  |  | CDC | 260 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S23//3MTR/TapPosMv |  |  |  | CDC | 261 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 2-A9 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_MW | #4MTR二次側 MW | DTR | S23/11/M4/MW |  |  |  | CDC | 262 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 2-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR | S23/11/M4/MVAR |  |  |  | CDC | 263 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | I_R | [17 empty] | 2-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR | S23/11/M4/I_R |  |  |  | CDC | 264 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | I_S | [17 empty] | 2-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR | S23/11/M4/I_S |  |  |  | CDC | 265 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR二次側 |  | I_T | [17 empty] | 2-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR | S23/11/M4/I_T |  |  |  | CDC | 266 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 2-A7 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_OIL | #4MTR 油溫 | DTR | S23//4MTR/OilTemp |  |  |  | CDC | 267 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 2-A6 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_COIL | #4MTR 線溫 | DTR | S23//4MTR/CoilTemp |  |  |  | CDC | 268 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 2-A8 |  | 2-0A |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_TAP | #4MTR OLTC TAP | DTR | S23//4MTR/TapPosMv |  |  |  | CDC | 269 | GENERICAIPoint | SS203_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S23 | 博愛SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS2_2 | [8 empty] | 博愛SS.直流電源電壓 | 直流電源電壓 | OTHER | S23/0/StaDev/DCV |  |  |  | CDC | 270 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.650_MW | 博鐵紅線 MW | LINE69 | S23/69/650/MW |  |  |  | CDC | 271 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.650_MVAR | 博鐵紅線 MVAR | LINE69 | S23/69/650/MVAR |  |  |  | CDC | 272 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.660_MW | 博鐵白線 MW | LINE69 | S23/69/660/MW |  |  |  | CDC | 273 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.660_MVAR | 博鐵白線 MVAR | LINE69 | S23/69/660/MVAR |  |  |  | CDC | 274 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-E0 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.600TIE_AMP | 600TIE AMP | TIE | S23/69/600/I |  |  |  | CDC | 275 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-DF | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S23/69/2BUS/V |  |  |  | CDC | 276 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.640_MW | 溶劑線 MW | LINE69 | S23/69/640/MW |  |  |  | CDC | 277 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 博愛SS.640_MVAR | 溶劑線 MVAR | LINE69 | S23/69/640/MVAR |  |  |  | CDC | 278 | GENERICAIPoint | SS203_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.610_PHA | 水上線(610) 相間RY | LINE69 | S23/69/610/PHA |  |  |  | CDC | 279 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.610_GDA | 水上線(610) 接地RY | LINE69 | S23/69/610/GDA |  |  |  | CDC | 280 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.610_CB | 610(水上線) CB | LINE69 | S23/69/610/CB |  |  |  | CDC | 281 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.620_PHA | 後博線(620) 相間RY | LINE69 | S23/69/620/PHA |  |  |  | CDC | 282 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.620_GDA | 後博線(620) 接地RY | LINE69 | S23/69/620/GDA |  |  |  | CDC | 283 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | 74A | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.620_74A | 後博線(620) 74RY | LINE69 | S23/69/620/74A |  |  |  | CDC | 284 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.620_CB | 620(後博線) CB | LINE69 | S23/69/620/CB |  |  |  | CDC | 285 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | PHA | [17 empty] | 1-0A-06 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.670_PHA | 嘉博線(670) 相間RY | LINE69 | S23/69/670/PHA |  |  |  | CDC | 286 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | GDA | [17 empty] | 1-0A-07 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.670_GDA | 嘉博線(670) 接地RY | LINE69 | S23/69/670/GDA |  |  |  | CDC | 287 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | 74A | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.670_74A | 嘉博線(670) 74RY | LINE69 | S23/69/670/74A |  |  |  | CDC | 288 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | CB | [17 empty] | 1-0A-04 |  | 1-06 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.670_CB | 670(嘉博線) CB | LINE69 | S23/69/670/CB |  |  |  | CDC | 289 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_PHA | 11KV博一線(JB21) 相間RY | FEEDER | S23/11/JB21/PHA |  |  |  | CDC | 290 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_GDA | 11KV博一線(JB21) 接地RY | FEEDER | S23/11/JB21/GDA |  |  |  | CDC | 291 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_79UL | 11KV博一線(JB21) 79RY U/L | FEEDER | S23/11/JB21/79UL |  |  |  | CDC | 292 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB21 | 博一線(JB21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_ADJ | 11KV博一線(JB21) LCO分流器 U/L | FEEDER | S23/11/JB21/ADJ |  |  |  | CDC | 293 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB21 | JB21(11KV博一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_CB | JB21(11KV博一線) CB | FEEDER | S23/11/JB21/CB |  |  |  | CDC | 294 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_PHA | 11KV博二線(JB22) 相間RY | FEEDER | S23/11/JB22/PHA |  |  |  | CDC | 295 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_GDA | 11KV博二線(JB22) 接地RY | FEEDER | S23/11/JB22/GDA |  |  |  | CDC | 296 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_79UL | 11KV博二線(JB22) 79RY U/L | FEEDER | S23/11/JB22/79UL |  |  |  | CDC | 297 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB22 | 博二線(JB22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_ADJ | 11KV博二線(JB22) LCO分流器 U/L | FEEDER | S23/11/JB22/ADJ |  |  |  | CDC | 298 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB22 | JB22(11KV博二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_CB | JB22(11KV博二線) CB | FEEDER | S23/11/JB22/CB |  |  |  | CDC | 299 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_PHA | 11KV博三線(JB23) 相間RY | FEEDER | S23/11/JB23/PHA |  |  |  | CDC | 300 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_GDA | 11KV博三線(JB23) 接地RY | FEEDER | S23/11/JB23/GDA |  |  |  | CDC | 301 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_79UL | 11KV博三線(JB23) 79RY U/L | FEEDER | S23/11/JB23/79UL |  |  |  | CDC | 302 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB23 | 博三線(JB23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_ADJ | 11KV博三線(JB23) LCO分流器 U/L | FEEDER | S23/11/JB23/ADJ |  |  |  | CDC | 303 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB23 | JB23(11KV博三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_CB | JB23(11KV博三線) CB | FEEDER | S23/11/JB23/CB |  |  |  | CDC | 304 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_PHA | 11KV博四線(JB24) 相間RY | FEEDER | S23/11/JB24/PHA |  |  |  | CDC | 305 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_GDA | 11KV博四線(JB24) 接地RY | FEEDER | S23/11/JB24/GDA |  |  |  | CDC | 306 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_79UL | 11KV博四線(JB24) 79RY U/L | FEEDER | S23/11/JB24/79UL |  |  |  | CDC | 307 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB24 | 博四線(JB24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_ADJ | 11KV博四線(JB24) LCO分流器 U/L | FEEDER | S23/11/JB24/ADJ |  |  |  | CDC | 308 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB24 | JB24(11KV博四線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_CB | JB24(11KV博四線) CB | FEEDER | S23/11/JB24/CB |  |  |  | CDC | 309 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_PHA | 11KV博五線(JB25) 相間RY | FEEDER | S23/11/JB25/PHA |  |  |  | CDC | 310 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_GDA | 11KV博五線(JB25) 接地RY | FEEDER | S23/11/JB25/GDA |  |  |  | CDC | 311 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_79UL | 11KV博五線(JB25) 79RY U/L | FEEDER | S23/11/JB25/79UL |  |  |  | CDC | 312 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB25 | 博五線(JB25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_ADJ | 11KV博五線(JB25) LCO分流器 U/L | FEEDER | S23/11/JB25/ADJ |  |  |  | CDC | 313 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB25 | JB25(11KV博五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_CB | JB25(11KV博五線) CB | FEEDER | S23/11/JB25/CB |  |  |  | CDC | 314 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_PHA | 11KV博六線(JB26) 相間RY | FEEDER | S23/11/JB26/PHA |  |  |  | CDC | 315 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_GDA | 11KV博六線(JB26) 接地RY | FEEDER | S23/11/JB26/GDA |  |  |  | CDC | 316 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_79UL | 11KV博六線(JB26) 79RY U/L | FEEDER | S23/11/JB26/79UL |  |  |  | CDC | 317 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB26 | 博六線(JB26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_ADJ | 11KV博六線(JB26) LCO分流器 U/L | FEEDER | S23/11/JB26/ADJ |  |  |  | CDC | 318 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB26 | JB26(11KV博六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_CB | JB26(11KV博六線) CB | FEEDER | S23/11/JB26/CB |  |  |  | CDC | 319 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_PHA | 11KV博七線(JB27) 相間RY | FEEDER | S23/11/JB27/PHA |  |  |  | CDC | 320 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_GDA | 11KV博七線(JB27) 接地RY | FEEDER | S23/11/JB27/GDA |  |  |  | CDC | 321 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_79UL | 11KV博七線(JB27) 79RY U/L | FEEDER | S23/11/JB27/79UL |  |  |  | CDC | 322 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB27 | 博七線(JB27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_ADJ | 11KV博七線(JB27) LCO分流器 U/L | FEEDER | S23/11/JB27/ADJ |  |  |  | CDC | 323 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB27 | JB27(11KV博七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_CB | JB27(11KV博七線) CB | FEEDER | S23/11/JB27/CB |  |  |  | CDC | 324 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_PHA | 11KV博八線(JB28) 相間RY | FEEDER | S23/11/JB28/PHA |  |  |  | CDC | 325 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_GDA | 11KV博八線(JB28) 接地RY | FEEDER | S23/11/JB28/GDA |  |  |  | CDC | 326 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_79UL | 11KV博八線(JB28) 79RY U/L | FEEDER | S23/11/JB28/79UL |  |  |  | CDC | 327 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB28 | 博八線(JB28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_ADJ | 11KV博八線(JB28) LCO分流器 U/L | FEEDER | S23/11/JB28/ADJ |  |  |  | CDC | 328 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB28 | JB28(11KV博八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_CB | JB28(11KV博八線) CB | FEEDER | S23/11/JB28/CB |  |  |  | CDC | 329 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_PHA | 11KV博九線(JB29) 相間RY | FEEDER | S23/11/JB29/PHA |  |  |  | CDC | 330 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_GDA | 11KV博九線(JB29) 接地RY | FEEDER | S23/11/JB29/GDA |  |  |  | CDC | 331 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_79UL | 11KV博九線(JB29) 79RY U/L | FEEDER | S23/11/JB29/79UL |  |  |  | CDC | 332 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB29 | 博九線(JB29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_ADJ | 11KV博九線(JB29) LCO分流器 U/L | FEEDER | S23/11/JB29/ADJ |  |  |  | CDC | 333 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB29 | JB29(11KV博九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_CB | JB29(11KV博九線) CB | FEEDER | S23/11/JB29/CB |  |  |  | CDC | 334 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_PHA | 11KV博十線(JB30) 相間RY | FEEDER | S23/11/JB30/PHA |  |  |  | CDC | 335 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_GDA | 11KV博十線(JB30) 接地RY | FEEDER | S23/11/JB30/GDA |  |  |  | CDC | 336 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_79UL | 11KV博十線(JB30) 79RY U/L | FEEDER | S23/11/JB30/79UL |  |  |  | CDC | 337 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB30 | 博十線(JB30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_ADJ | 11KV博十線(JB30) LCO分流器 U/L | FEEDER | S23/11/JB30/ADJ |  |  |  | CDC | 338 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB30 | JB30(11KV博十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_CB | JB30(11KV博十線) CB | FEEDER | S23/11/JB30/CB |  |  |  | CDC | 339 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_PHA | 11KV博十一線(JB31) 相間RY | FEEDER | S23/11/JB31/PHA |  |  |  | CDC | 340 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_GDA | 11KV博十一線(JB31) 接地RY | FEEDER | S23/11/JB31/GDA |  |  |  | CDC | 341 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB31 | 博十一線(JB31) |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_ADJ | 11KV博十一線(JB31) LCO分流器 | FEEDER | S23/11/JB31/ADJ |  |  |  | CDC | 342 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB31 | JB31(11KV博十一線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_CB | JB31(11KV博十一線) CB | FEEDER | S23/11/JB31/CB |  |  |  | CDC | 343 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_PHA | 11KV博十二線(JB32) 相間RY | FEEDER | S23/11/JB32/PHA |  |  |  | CDC | 344 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_GDA | 11KV博十二線(JB32) 接地RY | FEEDER | S23/11/JB32/GDA |  |  |  | CDC | 345 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB32 | 博十二線(JB32) |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_ADJ | 11KV博十二線(JB32) LCO分流器 | FEEDER | S23/11/JB32/ADJ |  |  |  | CDC | 346 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB32 | JB32(11KV博十二線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_CB | JB32(11KV博十二線) CB | FEEDER | S23/11/JB32/CB |  |  |  | CDC | 347 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_PHA | 11KV博十三線(JB33) 相間RY | FEEDER | S23/11/JB33/PHA |  |  |  | CDC | 348 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_GDA | 11KV博十三線(JB33) 接地RY | FEEDER | S23/11/JB33/GDA |  |  |  | CDC | 349 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB33 | 博十三線(JB33) |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_ADJ | 11KV博十三線(JB33) LCO分流器 | FEEDER | S23/11/JB33/ADJ |  |  |  | CDC | 350 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB33 | JB33(11KV博十三線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_CB | JB33(11KV博十三線) CB | FEEDER | S23/11/JB33/CB |  |  |  | CDC | 351 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_PHA | 11KV博十四線(JB34) 相間RY | FEEDER | S23/11/JB34/PHA |  |  |  | CDC | 352 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_GDA | 11KV博十四線(JB34) 接地RY | FEEDER | S23/11/JB34/GDA |  |  |  | CDC | 353 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB34 | 博十四線(JB34) |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_ADJ | 11KV博十四線(JB34) LCO分流器 | FEEDER | S23/11/JB34/ADJ |  |  |  | CDC | 354 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB34 | JB34(11KV博十四線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_CB | JB34(11KV博十四線) CB | FEEDER | S23/11/JB34/CB |  |  |  | CDC | 355 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_PHA | 11KV博十五線(JB35) 相間RY | FEEDER | S23/11/JB35/PHA |  |  |  | CDC | 356 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_GDA | 11KV博十五線(JB35) 接地RY | FEEDER | S23/11/JB35/GDA |  |  |  | CDC | 357 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB35 | 博十五線(JB35) |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_ADJ | 11KV博十五線(JB35) LCO分流器 | FEEDER | S23/11/JB35/ADJ |  |  |  | CDC | 358 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB35 | JB35(11KV博十五線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_CB | JB35(11KV博十五線) CB | FEEDER | S23/11/JB35/CB |  |  |  | CDC | 359 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_PHA | 11KV博十六線(JB36) 相間RY | FEEDER | S23/11/JB36/PHA |  |  |  | CDC | 360 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_GDA | 11KV博十六線(JB36) 接地RY | FEEDER | S23/11/JB36/GDA |  |  |  | CDC | 361 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-11 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_79UL | 11KV博十六線(JB36) 79RY U/L | FEEDER | S23/11/JB36/79UL |  |  |  | CDC | 362 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB36 | 博十六線(JB36) |  | ADJ | [17 empty] | 2-31-00 |  | 2-17 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_ADJ | 11KV博十六線(JB36) LCO分流器 | FEEDER | S23/11/JB36/ADJ |  |  |  | CDC | 363 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB36 | JB36(11KV博十六線) |  | CB | [17 empty] | 2-08-05 |  | 2-08 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_CB | JB36(11KV博十六線) CB | FEEDER | S23/11/JB36/CB |  |  |  | CDC | 364 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | PHA | [17 empty] | 2-0A-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_PHA | 11KV博十七線(JB37) 相間RY | FEEDER | S23/11/JB37/PHA |  |  |  | CDC | 365 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | GDA | [17 empty] | 2-0A-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_GDA | 11KV博十七線(JB37) 接地RY | FEEDER | S23/11/JB37/GDA |  |  |  | CDC | 366 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-10 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_79UL | 11KV博十七線(JB37) 79RY U/L | FEEDER | S23/11/JB37/79UL |  |  |  | CDC | 367 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB37 | 博十七線(JB37) |  | ADJ | [17 empty] | 2-30-15 |  | 2-16 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_ADJ | 11KV博十七線(JB37) LCO分流器 | FEEDER | S23/11/JB37/ADJ |  |  |  | CDC | 368 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB37 | JB37(11KV博十七線) |  | CB | [17 empty] | 2-08-04 |  | 2-07 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_CB | JB37(11KV博十七線) CB | FEEDER | S23/11/JB37/CB |  |  |  | CDC | 369 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | PHA | [17 empty] | 2-09-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_PHA | 11KV博十八線(JB38) 相間RY | FEEDER | S23/11/JB38/PHA |  |  |  | CDC | 370 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | GDA | [17 empty] | 2-09-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_GDA | 11KV博十八線(JB38) 接地RY | FEEDER | S23/11/JB38/GDA |  |  |  | CDC | 371 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) 79RY |  | 79UL | [17 empty] | 2-30-09 |  | 2-0F | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_79UL | 11KV博十八線(JB38) 79RY U/L | FEEDER | S23/11/JB38/79UL |  |  |  | CDC | 372 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB38 | 博十八線(JB38) |  | ADJ | [17 empty] | 2-30-14 |  | 2-15 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_ADJ | 11KV博十八線(JB38) LCO分流器 | FEEDER | S23/11/JB38/ADJ |  |  |  | CDC | 373 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB38 | JB38(11KV博十八線) |  | CB | [17 empty] | 2-08-03 |  | 2-06 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_CB | JB38(11KV博十八線) CB | FEEDER | S23/11/JB38/CB |  |  |  | CDC | 374 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_PHA | 11KV博十九線(JB39) 相間RY | FEEDER | S23/11/JB39/PHA |  |  |  | CDC | 375 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_GDA | 11KV博十九線(JB39) 接地RY | FEEDER | S23/11/JB39/GDA |  |  |  | CDC | 376 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-0E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_79UL | 11KV博十九線(JB39) 79RY U/L | FEEDER | S23/11/JB39/79UL |  |  |  | CDC | 377 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB39 | 博十九線(JB39) |  | ADJ | [17 empty] | 2-30-13 |  | 2-14 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_ADJ | 11KV博十九線(JB39) LCO分流器 | FEEDER | S23/11/JB39/ADJ |  |  |  | CDC | 378 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB39 | JB39(11KV博十九線) |  | CB | [17 empty] | 2-08-02 |  | 2-05 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_CB | JB39(11KV博十九線) CB | FEEDER | S23/11/JB39/CB |  |  |  | CDC | 379 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | PHA | [17 empty] | 2-09-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_PHA | 11KV博二十線(JB40) 相間RY | FEEDER | S23/11/JB40/PHA |  |  |  | CDC | 380 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | GDA | [17 empty] | 2-09-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_GDA | 11KV博二十線(JB40) 接地RY | FEEDER | S23/11/JB40/GDA |  |  |  | CDC | 381 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) 79RY |  | 79UL | [17 empty] | 2-30-07 |  | 2-0D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_79UL | 11KV博二十線(JB40) 79RY U/L | FEEDER | S23/11/JB40/79UL |  |  |  | CDC | 382 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 11 | 11kV | JB40 | 博二十線(JB40) |  | ADJ | [17 empty] | 2-30-12 |  | 2-13 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_ADJ | 11KV博二十線(JB40) LCO分流器 | FEEDER | S23/11/JB40/ADJ |  |  |  | CDC | 383 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 11 | 11kV | JB40 | JB40(11KV博二十線) |  | CB | [17 empty] | 2-08-01 |  | 2-04 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_CB | JB40(11KV博二十線) CB | FEEDER | S23/11/JB40/CB |  |  |  | CDC | 384 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE2_CB | 11KV TIE2 CB | TIE | S23/11/TIE2/CB |  |  |  | CDC | 385 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE2_51A | 11KV TIE2 51RY | TIE | S23/11/TIE2/51A |  |  |  | CDC | 386 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S23/11/TIE2/51NA |  |  |  | CDC | 387 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE3_CB | 11KV TIE3 CB | TIE | S23/11/TIE3/CB |  |  |  | CDC | 388 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE3_51A | 11KV TIE3 51RY | TIE | S23/11/TIE3/51A |  |  |  | CDC | 389 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE3_51NA | 11KV TIE3 51N RY | TIE | S23/11/TIE3/51NA |  |  |  | CDC | 390 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE4 |  | CB | [17 empty] | 2-08-06 |  | 2-09 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE4_CB | 11KV TIE4 CB | TIE | S23/11/TIE4/CB |  |  |  | CDC | 391 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE4 |  | 51A | [17 empty] | 2-0A-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE4_51A | 11KV TIE4 51RY | TIE | S23/11/TIE4/51A |  |  |  | CDC | 392 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | TIE4 | TIE4 |  | 51NA | [17 empty] | 2-0A-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE4_51NA | 11KV TIE4 51N RY | TIE | S23/11/TIE4/51NA |  |  |  | CDC | 393 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.750_CB | 750(#1MTR) CB | DTR | S23/69/750/CB |  |  |  | CDC | 394 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.1M_CB | 1M(#1MTR) CB | DTR | S23/11/M1/CB |  |  |  | CDC | 395 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_51A | #1MTR 51RY | DTR | S23/69/750/51A |  |  |  | CDC | 396 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S23//1MTR/51ZA |  |  |  | CDC | 397 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_87A | #1MTR 87RY | DTR | S23//1MTR/87A |  |  |  | CDC | 398 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S23//1MTR/87UL |  |  |  | CDC | 399 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S23/11/M1/81A |  |  |  | CDC | 400 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S23 | 博愛SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S23/11/M1/51A |  |  |  | CDC | 401 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_TRA | #1MTR 重故障 | DTR | S23//1MTR/TRA |  |  |  | CDC | 402 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S23//1MTR/TRF |  |  |  | CDC | 403 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S23//1MTR/SupLocal |  |  |  | CDC | 404 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S23//1MTR/Tap Chan |  |  |  | CDC | 405 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_96A | #1MTR 96P RY | DTR | S23//1MTR/96PA |  |  |  | CDC | 406 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S23//1MTR/OLTC_DLY |  |  |  | CDC | 407 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S23//1MTR/AC_Fault |  |  |  | CDC | 408 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.760_CB | 760(#2MTR) CB | DTR | S23/69/760/CB |  |  |  | CDC | 409 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.2M_CB | 2M(#2MTR) CB | DTR | S23/11/M2/CB |  |  |  | CDC | 410 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_51A | #2MTR 51RY | DTR | S23/69/760/51A |  |  |  | CDC | 411 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S23//2MTR/51ZA |  |  |  | CDC | 412 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_87A | #2MTR 87RY | DTR | S23//2MTR/87A |  |  |  | CDC | 413 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S23//2MTR/87UL |  |  |  | CDC | 414 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S23/11/M2/51A |  |  |  | CDC | 415 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_TRA | #2MTR 重故障 | DTR | S23//2MTR/TRA |  |  |  | CDC | 416 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S23//2MTR/TRF |  |  |  | CDC | 417 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S23//2MTR/SupLocal |  |  |  | CDC | 418 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S23//2MTR/Tap Chan |  |  |  | CDC | 419 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_96A | #2MTR 96P RY | DTR | S23//2MTR/96PA |  |  |  | CDC | 420 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S23//2MTR/OLTC_DLY |  |  |  | CDC | 421 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S23//2MTR/AC_Fault |  |  |  | CDC | 422 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.770_CB | 770(#3MTR) CB | DTR | S23/69/770/CB |  |  |  | CDC | 423 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 3MA | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.3MA_CB | 3MA(#3MTR) CB | DTR | S23/11/M3A/CB |  |  |  | CDC | 424 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 3MB | #3MTR |  | CB | [17 empty] | 1-03-00 |  | 1-5A | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.3MB_CB | 3MB(#3MTR) CB | DTR | S23/11/M3B/CB |  |  |  | CDC | 425 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_51A | #3MTR 51RY | DTR | S23/69/770/51A |  |  |  | CDC | 426 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_51NA | #3MTR 51N RY | DTR | S23/69/770/51NA |  |  |  | CDC | 427 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S23//3MTR/51ZA |  |  |  | CDC | 428 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_87A | #3MTR 87RY | DTR | S23//3MTR/87A |  |  |  | CDC | 429 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 2-3B-11 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S23//3MTR/87UL |  |  |  | CDC | 430 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 3MA | #3MTR二次側(3MA) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.3MA_51A | #3MTR二次側(3MA) 51RY | DTR | S23/11/M3A/51A |  |  |  | CDC | 431 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MB | #3MTR二次側(3MB) |  | 51A | [17 empty] | 1-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.3MB_51A | #3MTR二次側(3MB) 51RY | DTR | S23/11/M3B/51A |  |  |  | CDC | 432 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 2-3B-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_TRA | #3MTR 重故障 | DTR | S23//3MTR/TRA |  |  |  | CDC | 433 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 2-3B-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S23//3MTR/TRF |  |  |  | CDC | 434 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 2-3B-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S23//3MTR/SupLocal |  |  |  | CDC | 435 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 2-3B-13 |  | 1-62 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S23//3MTR/Tap Chan |  |  |  | CDC | 436 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_96A | #3MTR 96P RY | DTR | S23//3MTR/96PA |  |  |  | CDC | 437 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S23//3MTR/AC_Fault |  |  |  | CDC | 438 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 2-00-02 |  | 2-01 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.780_CB | 780(#4MTR) CB | DTR | S23/69/780/CB |  |  |  | CDC | 439 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 4M | #4MTR |  | CB | [17 empty] | 2-00-03 |  | 2-02 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.4M_CB | 4M(#4MTR) CB | DTR | S23/11/M4/CB |  |  |  | CDC | 440 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 51A | [17 empty] | 2-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_51A | #4MTR 51RY | DTR | S23/69/780/51A |  |  |  | CDC | 441 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 2-01-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_51ZA | #4MTR 51Z RY | DTR | S23//4MTR/51ZA |  |  |  | CDC | 442 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 2-00-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_87A | #4MTR 87RY | DTR | S23//4MTR/87A |  |  |  | CDC | 443 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 87UL | [17 empty] | 2-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_87UL | #4MTR 87RY U/L | DTR | S23//4MTR/87UL |  |  |  | CDC | 444 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 4M | #4MTR二次側(4M) |  | 51A | [17 empty] | 2-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.4M_51A | #4MTR二次側(4M) 51RY | DTR | S23/11/M4/51A |  |  |  | CDC | 445 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 2-30-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_TRA | #4MTR 重故障 | DTR | S23//4MTR/TRA |  |  |  | CDC | 446 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 2-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_TRF | #4MTR 輕故障 | DTR | S23//4MTR/TRF |  |  |  | CDC | 447 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 2-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_S/L | #4MTR OLTC S/L | DTR | S23//4MTR/SupLocal |  |  |  | CDC | 448 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 2-30-05 |  | 2-0B | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_A/M | #4MTR OLTC A/M | DTR | S23//4MTR/Tap Chan |  |  |  | CDC | 449 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 2-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_96A | #4MTR 96P RY | DTR | S23//4MTR/96PA |  |  |  | CDC | 450 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | OLTC_DLY | [17 empty] | 2-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR | S23//4MTR/OLTC_DLY |  |  |  | CDC | 451 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR_AC | #4MTR |  | FAULT | [17 empty] | 2-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR | S23//4MTR/AC_Fault |  |  |  | CDC | 452 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_CB | 210(11KV #1SC) CB | SC | S23/11/210/CB |  |  |  | CDC | 453 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S23/11/210/Tap Chan |  |  |  | CDC | 454 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_SCA | 11KV #1SC 51,51N RY | SC | S23/11/210/SCA |  |  |  | CDC | 455 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S23/11/210/UVA |  |  |  | CDC | 456 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_CB | 220(11KV #2SC) CB | SC | S23/11/220/CB |  |  |  | CDC | 457 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S23/11/220/Tap Chan |  |  |  | CDC | 458 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_SCA | 11KV #2SC 51,51N RY | SC | S23/11/220/SCA |  |  |  | CDC | 459 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S23/11/220/UVA |  |  |  | CDC | 460 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_CB | 230(11KV #3SC) CB | SC | S23/11/230/CB |  |  |  | CDC | 461 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_SCA | 11KV #3SC 51,51N RY | SC | S23/11/230/SCA |  |  |  | CDC | 462 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S23/11/230/UVA |  |  |  | CDC | 463 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-08-00 |  | 2-03 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_CB | 240(11KV #4SC) CB | SC | S23/11/240/CB |  |  |  | CDC | 464 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-30-06 |  | 2-0C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_A/M | 11KV #4SC 乏控器 A/M | SC | S23/11/240/Tap Chan |  |  |  | CDC | 465 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-09-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_SCA | 11KV #4SC 51,51N RY | SC | S23/11/240/SCA |  |  |  | CDC | 466 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-09-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | S23/11/240/UVA |  |  |  | CDC | 467 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S23/69/1BUS/BUS_VUA |  |  |  | CDC | 468 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S23/11/ComPoint/CBA |  |  |  | CDC | 469 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S23/11/ComPoint/CBF |  |  |  | CDC | 470 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S23/69/ComPoint/ABS_89A |  |  |  | CDC | 471 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S23/69/ComPoint/CBA |  |  |  | CDC | 472 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S23/69/ComPoint/CBF |  |  |  | CDC | 473 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S23/0/RTU/RTU_R_L |  |  |  | CDC | 474 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S23 | 博愛SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.TEST_CB | TEST CB | OTHER | S23/0/RTU/Test_CB |  |  |  | CDC | 475 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.火災警報(1) | [博愛]火警 | OTHER | S23/0/StaDev/Fire1 |  |  |  | CDC | 476 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S23/0/StaDev/OPA |  |  |  | CDC | 477 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.其他重故障 | 變電所內其他重故障 | OTHER | S23/0/StaDev/PSA |  |  |  | CDC | 478 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S23/0/StaDev/PSF |  |  |  | CDC | 479 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S23/0/StaDev/STUV |  |  |  | CDC | 480 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S23/0/StaDev/CHG1 |  |  |  | CDC | 481 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.直流電源DCA | 直流電源故障警報 | OTHER | S23/0/StaDev/DCA |  |  |  | CDC | 482 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S23/0/StaDev/DCE |  |  |  | CDC | 483 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S23/0/StaDev/OilLeak |  |  |  | CDC | 484 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊OLTE重故障 | 光纖通訊系統 | OTHER | S23/0/StaDev/7A5Other |  |  |  | CDC | 485 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊OLTE輕故障 | 光纖通訊系統 | OTHER | S23/0/StaDev/8A5Other |  |  |  | CDC | 486 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊PCM警報 | 光纖通訊系統 | OTHER | S23/0/StaDev/9A5Other |  |  |  | CDC | 487 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S23/0/StaDev/CHG2 |  |  |  | CDC | 488 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊設備AC故障 | 光纖通訊系統 | OTHER | S23/0/StaDev/CommACF |  |  |  | CDC | 489 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S23/0/StaDev/Door1 |  |  |  | CDC | 490 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S23/0/StaDev/Door2 |  |  |  | CDC | 491 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S23/0/StaDev/Door3 |  |  |  | CDC | 492 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S23 | 博愛SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.開關場照明(A) | 所內開關場照明 | OTHER | S23/0/StaDev/Lights1 |  |  |  | CDC | 493 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S23 | 博愛SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.開關場照明(B) | 路燈照明 | OTHER | S23/0/StaDev/Lights2 |  |  |  | CDC | 494 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S23 | 博愛SS | 0 |  |  |  |  | #1MAIN51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MAIN51NA | #1MAIN51NA | OTHER | S23/11/M1/51NA |  |  |  | CDC | 495 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #2MAIN51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MAIN51NA | #2MAIN51NA | OTHER | S23/11/M2/51NA |  |  |  | CDC | 496 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MAIN51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MAIN51NA | #3MAIN51NA | OTHER | S23/11/M3A/51NA |  |  |  | CDC | 497 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MBIN51NA | [17 empty] | 1-04-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MBIN51NA | #3MBIN51NA | OTHER | S23/11/M3B/51NA |  |  |  | CDC | 498 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #4MAIN51NA | [17 empty] | 2-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MAIN51NA | #4MAIN51NA | OTHER | S23/11/M4/51NA |  |  |  | CDC | 499 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | MCSG火警 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.MCSG火警 | MCSG火警 | OTHER | S23/0/StaDev/Fire3 |  |  |  | CDC | 500 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | MCSG系統故障 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.MCSG系統故障 | MCSG系統故障 | OTHER | S23/0/StaDev/Fire4 |  |  |  | CDC | 501 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.主變火警 | 主變火警 | OTHER | S23/0/StaDev/Fire2 |  |  |  | CDC | 502 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.安全監控 | 安全監控 | OTHER | S23/0/StaDev/Burglar |  |  |  | CDC | 503 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.門禁 | 大門側門 | OTHER | S23/0/StaDev/Door |  |  |  | CDC | 504 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.細水霧故障 | 細水霧故障 | OTHER | S23/0/StaDev/1A5Other |  |  |  | CDC | 505 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S23/0/StaDev/2A5Other |  |  |  | CDC | 506 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.維護運轉警報 | 維護運轉警報 | OTHER | S23/0/StaDev/3A5Other |  |  |  | CDC | 507 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-12-01 |  | 1-69 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S23/11/M3/81A |  |  |  | CDC | 508 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S23//1MTR/63Q |  |  |  | CDC | 509 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S23//1MTR/96B1 |  |  |  | CDC | 510 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S23//1MTR/96B2 |  |  |  | CDC | 511 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S23//1MTR/96D |  |  |  | CDC | 512 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S23//1MTR/96P |  |  |  | CDC | 513 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S23//2MTR/63Q |  |  |  | CDC | 514 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S23//2MTR/96B1 |  |  |  | CDC | 515 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S23//2MTR/96B2 |  |  |  | CDC | 516 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S23//2MTR/96D |  |  |  | CDC | 517 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S23//2MTR/96P |  |  |  | CDC | 518 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 3MTR | #3MTR |  | #3MTR63Q | [17 empty] | 1-19-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER | S23//3MTR/63Q |  |  |  | CDC | 519 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MTR96B1 | [17 empty] | 1-19-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER | S23//3MTR/96B1 |  |  |  | CDC | 520 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MTR96B2 | [17 empty] | 1-19-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER | S23//3MTR/96B2 |  |  |  | CDC | 521 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MTR96D | [17 empty] | 1-19-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER | S23//3MTR/96D |  |  |  | CDC | 522 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #3MTR96P | [17 empty] | 1-19-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER | S23//3MTR/96P |  |  |  | CDC | 523 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | #4MTR63Q | [17 empty] | 1-1A-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR63Q | #4MTR ULTC電驛動作 | OTHER | S23//4MTR/63Q |  |  |  | CDC | 524 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #4MTR96B1 | [17 empty] | 1-19-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR96B1 | #4MTR撲氣電驛警報 | OTHER | S23//4MTR/96B1 |  |  |  | CDC | 525 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #4MTR96B2 | [17 empty] | 1-1A-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR96B2 | #4MTR撲氣電驛動作 | OTHER | S23//4MTR/96B2 |  |  |  | CDC | 526 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #4MTR96D | [17 empty] | 1-1A-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR96D | #4MTR放壓電驛動作 | OTHER | S23//4MTR/96D |  |  |  | CDC | 527 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | #4MTR96P | [17 empty] | 1-1A-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR96P | #4MTR突壓電驛動作 | OTHER | S23//4MTR/96P |  |  |  | CDC | 528 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | 87A | [17 empty] | 1-0A-05 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.670_87A | 嘉博線(670) 87RY | LINE69 | S23/69/670/87A |  |  |  | CDC | 529 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | 87UL | [17 empty] | 1-32-10 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 博愛SS.670_87UL | 嘉博線(670) 87RY U/L | LINE69 | S23/69/670/87UL |  |  |  | CDC | 530 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV |  |  |  | IED警報 | [17 empty] | 1-32-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.69KV_IED警報 | 69KV IED警報 | OTHER | S23/69/ComPoint/IRFA |  |  |  | CDC | 531 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S23/0/StaDev/DD_Light |  |  |  | CDC | 532 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-37-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S23/0/StaDev/R_Temp |  |  |  | CDC | 533 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-0F-04 |  | 1-56 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S23/11/M2/81A |  |  |  | CDC | 534 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.620_87A | 後博線(620) 87RY | LINE69 | S23/69/620/87A |  |  |  | CDC | 535 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 博愛SS.620_87UL | 後博線(620) 87RY U/L | LINE69 | S23/69/620/87UL |  |  |  | CDC | 536 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | DS1 | 621 | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 博愛SS.621_DS | 621(後博線) DS | LINE69 | S23/69/620/DS1 |  |  |  | CDC | 537 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | DS2 | 622 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 博愛SS.622_DS | 622(後博線) DS | LINE69 | S23/69/620/DS2 |  |  |  | CDC | 538 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | DS3 | 623 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 博愛SS.623_DS | 623(後博線) DS | LINE69 | S23/69/620/DS3 |  |  |  | CDC | 539 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.650_PHA | 博鐵紅線(650) 相間RY | LINE69 | S23/69/650/PHA |  |  |  | CDC | 540 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.650_GDA | 博鐵紅線(650) 接地RY | LINE69 | S23/69/650/GDA |  |  |  | CDC | 541 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.650_87A | 博鐵紅線(650) 87RY | LINE69 | S23/69/650/87A |  |  |  | CDC | 542 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | 74A | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.650_74A | 博鐵紅線(650) 74RY | LINE69 | S23/69/650/74A |  |  |  | CDC | 543 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 博愛SS.650_87UL | 博鐵紅線(650) 87RY U/L | LINE69 | S23/69/650/87UL |  |  |  | CDC | 544 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | CB | [17 empty] | 1-0A-00 |  | 1-05 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.650_CB | 650(博鐵紅線) CB | LINE69 | S23/69/650/CB |  |  |  | CDC | 545 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | DS1 | 651 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-22 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.651_DS | 651(博鐵紅線) DS | LINE69 | S23/69/650/DS1 |  |  |  | CDC | 546 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | DS2 | 652 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-23 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.652_DS | 652(博鐵紅線) DS | LINE69 | S23/69/650/DS2 |  |  |  | CDC | 547 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | DS3 | 653 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-24 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.653_DS | 653(博鐵紅線) DS | LINE69 | S23/69/650/DS3 |  |  |  | CDC | 548 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.660_PHA | 博鐵白線(660) 相間RY | LINE69 | S23/69/660/PHA |  |  |  | CDC | 549 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.660_GDA | 博鐵白線(660) 接地RY | LINE69 | S23/69/660/GDA |  |  |  | CDC | 550 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.660_87A | 博鐵白線(660) 87RY | LINE69 | S23/69/660/87A |  |  |  | CDC | 551 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | 74A | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.660_74A | 博鐵白線(660) 74RY | LINE69 | S23/69/660/74A |  |  |  | CDC | 552 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 博愛SS.660_87UL | 博鐵白線(660) 87RY U/L | LINE69 | S23/69/660/87UL |  |  |  | CDC | 553 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.660_CB | 660(博鐵白線) CB | LINE69 | S23/69/660/CB |  |  |  | CDC | 554 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | DS1 | 661 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 博愛SS.661_DS | 661(博鐵白線) DS | LINE69 | S23/69/660/DS1 |  |  |  | CDC | 555 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | DS2 | 662 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 博愛SS.662_DS | 662(博鐵白線) DS | LINE69 | S23/69/660/DS2 |  |  |  | CDC | 556 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | DS3 | 663 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.663_DS | 663(博鐵白線) DS | LINE69 | S23/69/660/DS3 |  |  |  | CDC | 557 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | E3 | 623E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 博愛SS.623E_ES | 623E(後博線) ES | LINE69 | S23/69/620/ES3 |  |  |  | CDC | 558 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | E3 | 653E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-25 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.653E_ES | 653E(博鐵紅線) ES | LINE69 | S23/69/650/ES3 |  |  |  | CDC | 559 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | E3 | 663E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.663E_ES | 663E(博鐵白線) ES | LINE69 | S23/69/660/ES3 |  |  |  | CDC | 560 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | DS1 | 671 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-26 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.671_DS | 671(嘉博線) DS | LINE69 | S23/69/670/DS1 |  |  |  | CDC | 561 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | DS2 | 672 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.672_DS | 672(嘉博線) DS | LINE69 | S23/69/670/DS2 |  |  |  | CDC | 562 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | DS3 | 673 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-28 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.673_DS | 673(嘉博線) DS | LINE69 | S23/69/670/DS3 |  |  |  | CDC | 563 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | E3 | 673E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.673E_ES | 673E(嘉博線) ES | LINE69 | S23/69/670/ES3 |  |  |  | CDC | 564 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-0B-00 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.600_CB | 600(TIE) CB | TIE | S23/69/600/CB |  |  |  | CDC | 565 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 博愛SS.601_DS | 601(TIE) DS | TIE | S23/69/600/DS1 |  |  |  | CDC | 566 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-6B | [5 empty] | ADCS_N | [8 empty] | 博愛SS.602_DS | 602(TIE) DS | TIE | S23/69/600/DS2 |  |  |  | CDC | 567 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 0 |  | TIE | TIE |  | 600GDA(1) | [17 empty] | 1-0B-02 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.600GDA(1) | 600(TIE) 67NA(B1) | OTHER | S23/69/600/GDA1 |  |  |  | CDC | 568 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | TIE | TIE |  | 600GDA(2) | [17 empty] | 1-0B-04 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.600GDA(2) | 600(TIE) 67NA(B2) | OTHER | S23/69/600/GDA2 |  |  |  | CDC | 569 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | TIE | TIE |  | 600PHA(1) | [17 empty] | 1-0B-01 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.600PHA(1) | 600(TIE) 67A(B1) | OTHER | S23/69/600/PHA1 |  |  |  | CDC | 570 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | TIE | TIE |  | 600PHA(2) | [17 empty] | 1-0B-03 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.600PHA(2) | 600(TIE) 67A(B2) | OTHER | S23/69/600/PHA2 |  |  |  | CDC | 571 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S23/69/2BUS/BUS_VUA |  |  |  | CDC | 572 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-04-03 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S23/69/2BUS/87A |  |  |  | CDC | 573 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 692BUS | 69#2BUS |  | 87UL | [17 empty] | 1-35-14 |  | 1-68 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER | S23/69/2BUS/87UL |  |  |  | CDC | 574 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-38-04 | 1-38-05 | 1-6C | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.751_DS | 751(#1MTR) DS | DTR | S23/69/750/DS1 |  |  |  | CDC | 575 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-38-06 | 1-38-07 | 1-6D | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.752_DS | 752(#1MTR) DS | DTR | S23/69/750/DS2 |  |  |  | CDC | 576 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-33-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_RYFA | #1MTR IED警報 | OTHER | S23//1MTR/RYFA |  |  |  | CDC | 577 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-34-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_RYFA | #2MTR IED警報 | OTHER | S23//2MTR/RYFA |  |  |  | CDC | 578 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | RYFA | [17 empty] | 2-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_RYFA | #4MTR IED警報 | OTHER | S23//4MTR/RYFA |  |  |  | CDC | 579 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 660 | 博鐵白線(660) |  | 660白線RYFA | [17 empty] | 1-35-06 | [7 empty] | DDCS2_1 | [8 empty] | 博愛SS.660白線RYFA | 660 IED警報 | OTHER | S23/69/660/RYFA |  |  |  | CDC | 580 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 670嘉博線 | 670 |  | CFA | [17 empty] | 1-35-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.670嘉博線_CFA | 670 通訊故障 | OTHER | S23/69/670/87CFA |  |  |  | CDC | 581 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 670嘉博線 | 670 |  | RYFA | [17 empty] | 1-35-08 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.670嘉博線_RYFA | 670 IED警報 | OTHER | S23/69/670/RYFA |  |  |  | CDC | 582 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 600TIE | 600 |  | RYFA | [17 empty] | 1-35-00 | [7 empty] | DDCS2_1 | [8 empty] | 博愛SS.600TIE_RYFA | 600 IED警報 | OTHER | S23/69/600/RYFA |  |  |  | CDC | 583 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 610水上線 | 610 |  | CFA | [17 empty] | 1-35-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.610水上線_CFA | 610 通訊故障 | OTHER | S23/69/610/87CFA |  |  |  | CDC | 584 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 610水上線 | 610 |  | RYFA | [17 empty] | 1-35-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.610水上線_RYFA | 610 IED警報 | OTHER | S23/69/610/RYFA |  |  |  | CDC | 585 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 650紅線 | 650 |  | RYFA | [17 empty] | 1-35-01 | [7 empty] | DDCS2_1 | [8 empty] | 博愛SS.650紅線_RYFA | 650 IED警報 | OTHER | S23/69/650/RYFA |  |  |  | CDC | 586 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-33-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_51ZS | #1MTR 51ZS | OTHER | S23//1MTR/51Z_UL |  |  |  | CDC | 587 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-34-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_51ZS | #2MTR 51ZS | OTHER | S23//2MTR/51Z_UL |  |  |  | CDC | 588 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_86A | #1MTR 86A | DTR | S23/69/750/51NA |  |  |  | CDC | 589 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | COMT警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.COMT警報 | COMT警報 | OTHER | S23/69/ComPoint/COMT |  |  |  | CDC | 590 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 51Z_UL | [17 empty] | 2-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_51ZS | #4MTR 51ZS | OTHER | S23//4MTR/51Z_UL |  |  |  | CDC | 591 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 620後博線 | 620 |  | CFA | [17 empty] | 1-35-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.620後博線_CFA | 620 通訊故障 | OTHER | S23/69/620/87CFA |  |  |  | CDC | 592 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 620後博線 | 620 |  | RYFA | [17 empty] | 1-35-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.620後博線_RYFA | 620 IED警報 | OTHER | S23/69/620/RYFA |  |  |  | CDC | 593 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | BUSRY | BUSRY |  | BF | [17 empty] | 1-35-09 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.BUSRY_BF | BUSRY 電驛故障 | OTHER | S23/0/StaDev/BFA |  |  |  | CDC | 594 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | BUSRY | BUSRY |  | 87CTFA | [17 empty] | 1-35-10 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.BUSRY_CTFA | BUSRY CT回路故障 | OTHER | S23/0/StaDev/87CTFA |  |  |  | CDC | 595 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV |  |  |  | PMA | [17 empty] | 1-37-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.69KV_PMA | 69KV PMA | OTHER | S23/69/ComPoint/PMA |  |  |  | CDC | 596 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.610_87A | 水上線(610) 87RY | LINE69 | S23/69/610/87A |  |  |  | CDC | 597 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 博愛SS.610_87UL | 水上線(610) 87RY U/L | LINE69 | S23/69/610/87UL |  |  |  | CDC | 598 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | DS1 | 611 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.611_DS | 611(水上線) DS | LINE69 | S23/69/610/DS1 |  |  |  | CDC | 599 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | DS2 | 612 | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.612_DS | 612(水上線) DS | LINE69 | S23/69/610/DS2 |  |  |  | CDC | 600 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | DS3 | 613 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.613_DS | 613(水上線) DS | LINE69 | S23/69/610/DS3 |  |  |  | CDC | 601 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | E3 | 613E | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.613E_ES | 613E(水上線) ES | LINE69 | S23/69/610/ES3 |  |  |  | CDC | 602 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.640_PHA | 溶劑線(640) 相間RY | LINE69 | S23/69/640/PHA |  |  |  | CDC | 603 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.640_GDA | 溶劑線(640) 接地RY | LINE69 | S23/69/640/GDA |  |  |  | CDC | 604 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | 85A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.640_85A | 溶劑線(640) 85RY | LINE69 | S23/69/640/85A |  |  |  | CDC | 605 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | 74A | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 博愛SS.640_74A | 溶劑線(640) 74RY | LINE69 | S23/69/640/74A |  |  |  | CDC | 606 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | 85UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.640_85UL | 溶劑線(640) 85RY U/L | LINE69 | S23/69/640/85UL |  |  |  | CDC | 607 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 博愛SS.640_CB | 640(溶劑線) CB | LINE69 | S23/69/640/CB |  |  |  | CDC | 608 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | DS1 | 641 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.641_DS | 641(溶劑線) DS | LINE69 | S23/69/640/DS1 |  |  |  | CDC | 609 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | DS2 | 642 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.642_DS | 642(溶劑線) DS | LINE69 | S23/69/640/DS2 |  |  |  | CDC | 610 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | DS3 | 643 | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.643_DS | 643(溶劑線) DS | LINE69 | S23/69/640/DS3 |  |  |  | CDC | 611 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | E3 | 643E | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.643E_ES | 643E(溶劑線) ES | LINE69 | S23/69/640/ES3 |  |  |  | CDC | 612 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-02 | [7 empty] | 69KV_N | [8 empty] | 博愛SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S23/69/1BUS/87A |  |  |  | CDC | 613 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-35-13 |  | 1-67 | [5 empty] | ADCS_N | [8 empty] | 博愛SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER | S23/69/1BUS/87UL |  |  |  | CDC | 614 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-38-02 | 1-38-03 | 1-6F | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.762_DS | 762(#2MTR) DS | DTR | S23/69/760/DS2 |  |  |  | CDC | 615 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | [16 empty] | 2-38-00 | 2-38-01 | 2-18 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.781_DS | 781(#4MTR) DS | DTR | S23/69/780/DS1 |  |  |  | CDC | 616 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 | [16 empty] | 2-38-02 | 2-38-03 | 2-19 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.782_DS | 782(#4MTR) DS | DTR | S23/69/780/DS2 |  |  |  | CDC | 617 | GENERICDIPoint | SS203_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_86A | #2MTR 86A | DTR | S23/69/760/51NA |  |  |  | CDC | 618 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | MTR_86A | [17 empty] | 2-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_86A | #4MTR 86A | DTR | S23/69/780/51NA |  |  |  | CDC | 619 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-38-00 | 1-38-01 | 1-6E | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.761_DS | 761(#2MTR) DS | DTR | S23/69/760/DS1 |  |  |  | CDC | 620 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | 81UL | [17 empty] | 1-37-11 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_81UL | #1MTR 81RY U/L | DTR | S23/11/M1/81UL |  |  |  | CDC | 621 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | 81UL | [17 empty] | 1-37-12 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_81UL | #2MTR 81RY U/L | DTR | S23/11/M2/81UL |  |  |  | CDC | 622 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 81UL | [17 empty] | 1-37-13 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_81UL | #4MTR 81RY U/L | DTR | S23/11/M4/81UL |  |  |  | CDC | 623 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | 81AS | [17 empty] | 2-08-07 |  | 2-12 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_81A/S | #4MTR 81RY A/S | DTR | S23/11/M4/81A |  |  |  | CDC | 624 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S23 | 博愛SS | 0 |  | 1MTR | #1MTR |  | GDA | [17 empty] | 1-04-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MTR_GDA | #1MTR GDA | OTHER | S23//1MTR/GDA |  |  |  | CDC | 625 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 1-04-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MTR_GDA | #2MTR GDA | OTHER | S23//2MTR/GDA |  |  |  | CDC | 626 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 4MTR | #4MTR |  | GDA | [17 empty] | 2-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#4MTR_GDA | #4MTR GDA | OTHER | S23//4MTR/GDA |  |  |  | CDC | 627 | GENERICDIPoint | SS203_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 4樓通訊室ACA | [17 empty] | 1-37-08 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.4樓通訊室ACA | 4樓通訊室AC告警 | OTHER | S23/0/StaDev/5A5Other |  |  |  | CDC | 628 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 4樓通訊室CHA | [17 empty] | 1-37-09 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.4樓通訊室CHA | 4樓通訊室充電機告警 | OTHER | S23/0/StaDev/6A5Other |  |  |  | CDC | 629 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.開關場水位警報 | 開關場水位警報 | OTHER | S23/0/StaDev/Water1 |  |  |  | CDC | 630 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S23/0/StaDev/Water2 |  |  |  | CDC | 631 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S23/11/ComPoint/IRFA |  |  |  | CDC | 632 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.PMA | PMA | OTHER | S23/11/PMA/PMA |  |  |  | CDC | 633 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博二十線79LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二十線79LOA | 博二十線79LOA | OTHER | S23/11/JB40/LOA |  |  |  | CDC | 634 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博十七線79LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十七線79LOA | 博十七線79LOA | OTHER | S23/11/JB37/LOA |  |  |  | CDC | 635 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博十九線79LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十九線79LOA | 博十九線79LOA | OTHER | S23/11/JB39/LOA |  |  |  | CDC | 636 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博十八線79LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十八線79LOA | 博十八線79LOA | OTHER | S23/11/JB38/LOA |  |  |  | CDC | 637 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博十六線79LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十六線79LOA | 博十六線79LOA | OTHER | S23/11/JB36/LOA |  |  |  | CDC | 638 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-14-00 |  | 1-42 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.390_CB | 390(#1SSTR) CB | OTHER | S23/11/390/CB |  |  |  | CDC | 639 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-14-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S23/11/390/51A |  |  |  | CDC | 640 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-14-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S23/11/390/51NA |  |  |  | CDC | 641 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博ㄧ線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博ㄧ線79LOA | 博ㄧ線79LOA | OTHER | S23/11/JB21/LOA |  |  |  | CDC | 642 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博二線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博二線79LOA | 博二線79LOA | OTHER | S23/11/JB22/LOA |  |  |  | CDC | 643 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博三線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博三線79LOA | 博三線79LOA | OTHER | S23/11/JB23/LOA |  |  |  | CDC | 644 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博五線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博五線79LOA | 博五線79LOA | OTHER | S23/11/JB25/LOA |  |  |  | CDC | 645 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博四線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博四線79LOA | 博四線79LOA | OTHER | S23/11/JB24/LOA |  |  |  | CDC | 646 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-14-03 |  | 1-43 | [5 empty] | DDCS2_2 | [8 empty] | 博愛SS.490_CB | 490(#2SSTR) CB | OTHER | S23/11/490/CB |  |  |  | CDC | 647 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-14-04 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2SSTR_51A | #2SSTR 51RY | OTHER | S23/11/490/51A |  |  |  | CDC | 648 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-14-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | S23/11/490/51NA |  |  |  | CDC | 649 | GENERICDIPoint | SS203_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博七線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博七線79LOA | 博七線79LOA | OTHER | S23/11/JB27/LOA |  |  |  | CDC | 650 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博九線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博九線79LOA | 博九線79LOA | OTHER | S23/11/JB29/LOA |  |  |  | CDC | 651 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博八線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博八線79LOA | 博八線79LOA | OTHER | S23/11/JB28/LOA |  |  |  | CDC | 652 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博十線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博十線79LOA | 博十線79LOA | OTHER | S23/11/JB30/LOA |  |  |  | CDC | 653 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 0 |  |  |  |  | 博六線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_2 | [8 empty] | 博愛SS.博六線79LOA | 博六線79LOA | OTHER | S23/11/JB26/LOA |  |  |  | CDC | 654 | GENERICDIPoint | SS203_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S23 | 博愛SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 655 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 656 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 657 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 658 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.610LE | 610LE (非取樣點) | LINE69 | S23/69/610/LE0 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.610BE | 610BE (非取樣點) | LINE69 | S23/69/610/BE0 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.620LE | 620LE (非取樣點) | LINE69 | S23/69/620/LE0 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.620BE | 620BE (非取樣點) | LINE69 | S23/69/620/BE0 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | LE0 | 670LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.670LE | 670LE (非取樣點) | LINE69 | S23/69/670/LE0 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | BE0 | 670BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.670BE | 670BE (非取樣點) | LINE69 | S23/69/670/BE0 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB21 | JB21_DS |  | DS1 | JB21_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_DS | JB21_DS (非取樣點) | FEEDER | S23/11/JB21/DS |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB21 | JB21_ES |  | LE0 | JB21_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB21_ES | JB21_ES (非取樣點) | FEEDER | S23/11/JB21/ES |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB22 | JB22_DS |  | DS1 | JB22_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_DS | JB22_DS (非取樣點) | FEEDER | S23/11/JB22/DS |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB22 | JB22_ES |  | LE0 | JB22_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB22_ES | JB22_ES (非取樣點) | FEEDER | S23/11/JB22/ES |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB23 | JB23_DS |  | DS1 | JB23_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_DS | JB23_DS (非取樣點) | FEEDER | S23/11/JB23/DS |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB23 | JB23_ES |  | LE0 | JB23_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB23_ES | JB23_ES (非取樣點) | FEEDER | S23/11/JB23/ES |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB24 | JB24_DS |  | DS1 | JB24_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_DS | JB24_DS (非取樣點) | FEEDER | S23/11/JB24/DS |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB24 | JB24_ES |  | LE0 | JB24_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB24_ES | JB24_ES (非取樣點) | FEEDER | S23/11/JB24/ES |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB25 | JB25_DS |  | DS1 | JB25_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_DS | JB25_DS (非取樣點) | FEEDER | S23/11/JB25/DS |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB25 | JB25_ES |  | LE0 | JB25_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB25_ES | JB25_ES (非取樣點) | FEEDER | S23/11/JB25/ES |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB26 | JB26_DS |  | DS1 | JB26_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_DS | JB26_DS (非取樣點) | FEEDER | S23/11/JB26/DS |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB26 | JB26_ES |  | LE0 | JB26_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB26_ES | JB26_ES (非取樣點) | FEEDER | S23/11/JB26/ES |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB27 | JB27_DS |  | DS1 | JB27_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_DS | JB27_DS (非取樣點) | FEEDER | S23/11/JB27/DS |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB27 | JB27_ES |  | LE0 | JB27_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB27_ES | JB27_ES (非取樣點) | FEEDER | S23/11/JB27/ES |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB28 | JB28_DS |  | DS1 | JB28_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_DS | JB28_DS (非取樣點) | FEEDER | S23/11/JB28/DS |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB28 | JB28_ES |  | LE0 | JB28_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB28_ES | JB28_ES (非取樣點) | FEEDER | S23/11/JB28/ES |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB29 | JB29_DS |  | DS1 | JB29_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_DS | JB29_DS (非取樣點) | FEEDER | S23/11/JB29/DS |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB29 | JB29_ES |  | LE0 | JB29_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB29_ES | JB29_ES (非取樣點) | FEEDER | S23/11/JB29/ES |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB30 | JB30_DS |  | DS1 | JB30_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_DS | JB30_DS (非取樣點) | FEEDER | S23/11/JB30/DS |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB30 | JB30_ES |  | LE0 | JB30_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB30_ES | JB30_ES (非取樣點) | FEEDER | S23/11/JB30/ES |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB31 | JB31_DS |  | DS1 | JB31_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_DS | JB31_DS (非取樣點) | FEEDER | S23/11/JB31/DS |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB31 | JB31_ES |  | LE0 | JB31_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB31_ES | JB31_ES (非取樣點) | FEEDER | S23/11/JB31/ES |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB32 | JB32_DS |  | DS1 | JB32_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_DS | JB32_DS (非取樣點) | FEEDER | S23/11/JB32/DS |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB32 | JB32_ES |  | LE0 | JB32_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB32_ES | JB32_ES (非取樣點) | FEEDER | S23/11/JB32/ES |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB33 | JB33_DS |  | DS1 | JB33_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_DS | JB33_DS (非取樣點) | FEEDER | S23/11/JB33/DS |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB33 | JB33_ES |  | LE0 | JB33_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB33_ES | JB33_ES (非取樣點) | FEEDER | S23/11/JB33/ES |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB34 | JB34_DS |  | DS1 | JB34_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_DS | JB34_DS (非取樣點) | FEEDER | S23/11/JB34/DS |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB34 | JB34_ES |  | LE0 | JB34_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB34_ES | JB34_ES (非取樣點) | FEEDER | S23/11/JB34/ES |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB35 | JB35_DS |  | DS1 | JB35_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_DS | JB35_DS (非取樣點) | FEEDER | S23/11/JB35/DS |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB35 | JB35_ES |  | LE0 | JB35_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB35_ES | JB35_ES (非取樣點) | FEEDER | S23/11/JB35/ES |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB36 | JB36_DS |  | DS1 | JB36_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_DS | JB36_DS (非取樣點) | FEEDER | S23/11/JB36/DS |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB36 | JB36_ES |  | LE0 | JB36_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB36_ES | JB36_ES (非取樣點) | FEEDER | S23/11/JB36/ES |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB37 | JB37_DS |  | DS1 | JB37_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_DS | JB37_DS (非取樣點) | FEEDER | S23/11/JB37/DS |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB37 | JB37_ES |  | LE0 | JB37_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB37_ES | JB37_ES (非取樣點) | FEEDER | S23/11/JB37/ES |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB38 | JB38_DS |  | DS1 | JB38_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_DS | JB38_DS (非取樣點) | FEEDER | S23/11/JB38/DS |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB38 | JB38_ES |  | LE0 | JB38_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB38_ES | JB38_ES (非取樣點) | FEEDER | S23/11/JB38/ES |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB39 | JB39_DS |  | DS1 | JB39_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_DS | JB39_DS (非取樣點) | FEEDER | S23/11/JB39/DS |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB39 | JB39_ES |  | LE0 | JB39_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB39_ES | JB39_ES (非取樣點) | FEEDER | S23/11/JB39/ES |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | JB40 | JB40_DS |  | DS1 | JB40_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_DS | JB40_DS (非取樣點) | FEEDER | S23/11/JB40/DS |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | JB40 | JB40_ES |  | LE0 | JB40_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.JB40_ES | JB40_ES (非取樣點) | FEEDER | S23/11/JB40/ES |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S23/11/TIE2/DS |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S23/11/TIE3/DS |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | TIE4 | TIE4_DS |  | DS1 | TIE4_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE4_DS | TIE4_DS (非取樣點) | TIE | S23/11/TIE4/DS |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.750TE | 750TE (非取樣點) | DTR | S23/69/750/TE0 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.750BE | 750BE (非取樣點) | DTR | S23/69/750/BE0 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.1M_DS | 1M_DS (非取樣點) | DTR | S23/11/M1/DS |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.1M_ES | 1M_ES (非取樣點) | DTR | S23/11/M1/ES |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.760TE | 760TE (非取樣點) | DTR | S23/69/760/TE0 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.760BE | 760BE (非取樣點) | DTR | S23/69/760/BE0 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.2M_DS | 2M_DS (非取樣點) | DTR | S23/11/M2/DS |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.2M_ES | 2M_ES (非取樣點) | DTR | S23/11/M2/ES |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.770TE | 770TE (非取樣點) | DTR | S23/69/770/TE0 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.770BE | 770BE (非取樣點) | DTR | S23/69/770/BE0 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.3M_DS | 3M_DS (非取樣點) | DTR | S23/11/3MTR/DS |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.3M_ES | 3M_ES (非取樣點) | DTR | S23/11/M3/ES |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.780TE | 780TE (非取樣點) | DTR | S23/69/780/TE0 |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.780BE | 780BE (非取樣點) | DTR | S23/69/780/BE0 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 4M | 4M_DS |  | DS1 | 4M_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.4M_DS | 4M_DS (非取樣點) | DTR | S23/11/M4/DS |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 4M | 4M_ES |  | M0 | 4M_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.4M_ES | 4M_ES (非取樣點) | DTR | S23/11/M4/ES |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.210_ES | 210_ES (非取樣點) | SC | S23/11/210/ES |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.211DS | 211DS (非取樣點) | SC | S23/11/210/D1 |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.212DS | 212DS (非取樣點) | SC | S23/11/210/D2 |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.220_ES | 220_ES (非取樣點) | SC | S23/11/220/ES |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.221DS | 221DS (非取樣點) | SC | S23/11/220/D1 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.222DS | 222DS (非取樣點) | SC | S23/11/220/D2 |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.230_ES | 230_ES (非取樣點) | SC | S23/11/230/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 231DS | 231DS |  | 231DS | 231DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.231DS | 231DS (非取樣點) | SC | S23/11/230/D1 |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 232DS | 232DS |  | 232DS | 232DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.232DS | 232DS (非取樣點) | SC | S23/11/230/D2 |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.240_ES | 240_ES (非取樣點) | SC | S23/11/240/ES |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 241DS | 241DS |  | 241DS | 241DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.241DS | 241DS (非取樣點) | SC | S23/11/240/D1 |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 242DS | 242DS |  | 242DS | 242DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.242DS | 242DS (非取樣點) | SC | S23/11/240/D2 |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 博愛SS.69B1E | 69B1E (非取樣點) | BUS | S23/69/1BUS/BE1 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 737 | NotelDIPoint | [38 empty] | START/STOP | STOP
S23 | 博愛SS | 0 |  | 610 | 水上線(610) |  | PW1UL | 610_PW1UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.610_PW1UL | 水上線(610)PW1_UL(非取樣點) | OTHER | [5 empty] | 738 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 610 | 水上線(610) |  | PW2UL | 610_PW2UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.610_PW2UL | 水上線(610)PW2_UL(非取樣點) | OTHER | [5 empty] | 739 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 610 | 水上線(610) |  | HCBUL | 610_HCBUL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.610_HCBUL | 後湖線(610)HCB_UL(非取樣點) | LINE69 | [5 empty] | 740 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 630 | 630 |  | PW1UL | 630_PW1UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.630_PW1UL | 仁臨線(630)PW1_UL(非取樣點) | LINE69 | [5 empty] | 741 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 630 | 630 |  | PW2UL | 630_PW2UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.630_PW2UL | 仁臨線(630)PW2_UL(非取樣點) | LINE69 | [5 empty] | 742 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 69 | 69kV | 630 | 仁臨線(630)HCB_UL |  | HCBUL | 630_HCBUL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.630_HCBUL | 仁臨線(630)HCB_UL (非取樣點) | LINE69 | [5 empty] | 743 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 620 | 後博線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.620_PW1UL | 後博線(620)PW1_UL(非取樣點) | OTHER | [5 empty] | 744 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 0 |  | 620 | 後博線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.620_PW2UL | 後博線(620)PW2_UL(非取樣點) | OTHER | [5 empty] | 745 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 620 | 後博線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.620_HCBUL | 水上線(620)HCB_UL (非取樣點) | LINE69 | [5 empty] | 746 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | PW1UL | 670_PW1UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.670_PW1UL | 嘉義線(670)PW1_UL (非取樣點) | LINE69 | [5 empty] | 747 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 69 | 69kV | 670 | 嘉博線(670) |  | PW2UL | 670_PW2UL | [24 empty] | ADCS_N | [8 empty] | 博愛SS.670_PW2UL | 嘉義線(670)PW2_UL (非取樣點) | LINE69 | [5 empty] | 748 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | LE0 | 650LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.650LE | 650LE (非取樣點) | LINE69 | S23/69/650/LE0 |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 650 | 博鐵紅線(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.650BE | 650BE (非取樣點) | LINE69 | S23/69/650/BE0 |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | LE0 | 660LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.660LE | 660LE (非取樣點) | LINE69 | S23/69/660/LE0 |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 660 | 博鐵白線(660) |  | BE0 | 660BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.660BE | 660BE (非取樣點) | LINE69 | S23/69/660/BE0 |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 博愛SS.601E | 601E (非取樣點) | TIE | S23/69/600/E1 |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 博愛SS.602E | 602E (非取樣點) | TIE | S23/69/600/E2 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 博愛SS.69B2E | 69B2E (非取樣點) | BUS | S23/69/2BUS/BE2 |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  |  |  |  | 69B新1E | 69B新1E | [24 empty] | ADCS_N | [8 empty] | 博愛SS.69B新1E | 69B新1E(非取樣點) | BUS | S23/69/1BUS/E1 |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.640LE | 640LE (非取樣點) | LINE69 | S23/69/640/LE0 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 69 | 69kV | 640 | 溶劑線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 博愛SS.640BE | 640BE (非取樣點) | LINE69 | S23/69/640/BE0 |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 1PT | #1PT_DS |  | DS1 | #1PT_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1PT_DS | #1PT_DS (非取樣點) | OTHER | S23/11/1PT/DS |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 1PT | #1PT_ES |  | PT0 | #1PT_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1PT_ES | #1PT_ES (非取樣點) | OTHER | S23/11/1PT/ES |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 390 | #1SSTR(390) |  | DS1 | 391 | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.391_DS | 391_DS (非取樣點) | OTHER | S23/11/390/D1 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 390 | #1SSTR(390) |  | E1 | 391 | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.391_ES | 391_ES (非取樣點) | OTHER | S23/11/390/E1 |  |  |  |  | 762 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | BR1 | BR1_DS |  | DS1 | BR1_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.BR1_DS | BR1_DS (非取樣點) | OTHER | S23/11/BR1/DS |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | BR1 | BR1_ES |  | LE0 | BR1_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.BR1_ES | BR1_ES (非取樣點) | OTHER | S23/11/BR1/ES |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 1MBUS | #1MBUS_ES |  | MBUS0 | #1MBUS_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#1MBUS_ES | #1MBUS_ES (非取樣點) | OTHER | S23/11/1BUS/ES |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 2MBUS | #2MBUS_ES |  | MBUS0 | #2MBUS_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2MBUS_ES | #2MBUS_ES (非取樣點) | OTHER | S23/11/2BUS/ES |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 2PT | #2PT_DS |  | DS1 | #2PT_DS | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2PT_DS | #2PT_DS (非取樣點) | OTHER | S23/11/2PT/DS |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 2PT | #2PT_ES |  | PT0 | #2PT_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.#2PT_ES | #2PT_ES (非取樣點) | OTHER | S23/11/2PT/ES |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | 490 | #2SSTR(490) |  | DS1 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.491_DS | 491_DS (非取樣點) | OTHER | S23/11/490/D1 |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S23 | 博愛SS | 0 |  | 490 | #2SSTR(490) |  | E1 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.491_ES | 491_ES (非取樣點) | OTHER | S23/11/490/E1 |  |  |  |  | 770 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
S23 | 博愛SS | 0 |  | TIE2 | TIE2_ES |  | LE0 | TIE2_ES | [24 empty] | DDCS2_2 | [8 empty] | 博愛SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | S23/11/TIE2/ES |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo