## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S25 | 頭橋SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 一號 BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S25_A1 | [8 empty] | 頭橋SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S25 | 頭橋SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | ＃1MTR | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | ada | B2/S25_D1 | [8 empty] | 頭橋SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | ＃2MTR | KV | 二號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aaa | B2/S25_D1 | [8 empty] | 頭橋SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | ＃3MTR | KV | 三號主變二次側BUS(3MA) | kV_-9_9(-2000_2000) | aba | B2/S25_D1 | [8 empty] | 頭橋SS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0130 |  |  | 2-82 |  |  | ＃3MTR | KV | 三號主變二次側BUS(3MB) | kV_-9_9(-2000_2000) | aca | B2/S25_D1 | [8 empty] | 頭橋SS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aagb | B2/S25_A1 | [8 empty] | 頭橋SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-13 |  |  | 69KV＃1BUS | 6VUA | 69KV BUS1衡相監視警報 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 650 | MW | 秀林頭橋線有效電力 | MW_-96_96(-2000_2000) |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_MW | 秀林線 MW | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 650 | MVAR | 秀林頭橋線無效電力 | MVAR_-96_96(-2000_2000) |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_MVAR | 秀林線 MVAR | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 650 | 69KV Line1 MWH(+) | 秀林頭橋線 |  |  | B2/S25_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 11 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 630 | MW | 頭橋嘉太線有效電力 | MW_-96_96(-2000_2000) |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_MW | 嘉太線 MW | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 630 | MVAR | 頭橋嘉太線無效電力 | MVAR_-96_96(-2000_2000) |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_MVAR | 嘉太線 MVAR | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 630 | 69KV Line2 MWH(+) | 頭橋嘉太線 |  |  | B2/S25_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 14 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 650 | PHA | 秀林頭橋線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_PHA | 秀林線(650) 相間RY | LINE69 |  |  |  |  | CDC | 15 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 650 | GDA | 秀林頭橋線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_GDA | 秀林線(650) 接地RY | LINE69 |  |  |  |  | CDC | 16 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 650 | 87A | 秀林頭橋線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_87A | 秀林線(650) 87RY | LINE69 |  |  |  |  | CDC | 17 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 630 | PHA | 頭橋嘉太線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_PHA | 嘉太線(630) 相間RY | LINE69 |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 630 | GDA | 頭橋嘉太線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_GDA | 嘉太線(630) 接地RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | 630 | 87A | 頭橋嘉太線 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_87A | 嘉太線(630) 87RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0532 |  | 0010 | 1-32-00 |  | 1-09 | 650 | 87S U/L | 秀林頭橋線 69KV |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_87UL | 秀林線(650) 87RY U/L | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0011 | 1-32-02 |  | 1-0A | 630 | 87S U/L | 頭橋嘉太線 69KV |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_87UL | 嘉太線(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/S24S25/T2 |  |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 650 | CB ON/OFF | 秀林頭橋線 |  | aada | B2/S25_A1 | [8 empty] | 頭橋SS.650_CB | 650(秀林線) CB | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/S25S30/T1 |  |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 630 | CB ON/OFF | 頭橋嘉太線 |  | aaba | B2/S25_A1 | [8 empty] | 頭橋SS.630_CB | 630(嘉太線) CB | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | ABS1 | 651 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 637 | 0019 | 1-38-08 | 1-38-09 | 1-12 | 651 | ABS ON | 秀林頭橋線BUS側 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.651_ABS | 651(秀林線) ABS | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | ABS2 | 652 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0638 | 639 | 0020 | 1-38-10 | 1-38-11 | 1-13 | 652 | ABS ON | 秀林頭橋線線路側 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.652_ABS | 652(秀林線) ABS | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | ABS1 | 631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 | 0022 | 1-38-14 | 1-38-15 | 1-15 | 631 | ABS ON | 頭橋嘉太線BUS側 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.631_ABS | 631(嘉太線) ABS | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | ABS2 | 632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 | 0023 | 1-39-00 | 1-39-01 | 1-16 | 632 | ABS ON | 頭橋嘉太線線路側 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.632_ABS | 632(嘉太線) ABS | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | ES2 | 652E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0640 | 641 | 0021 | 1-38-12 | 1-38-13 | 1-14 | 652E | ABS ON | 秀林頭橋線接地組 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.652E_ES | 652E(秀林線) ES | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_A1 | [8 empty] | 頭橋SS.650LE | 650LE (非取樣點) | LINE69 | [5 empty] | 30 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_A1 | [8 empty] | 頭橋SS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 31 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 | 647 | 0024 | 1-39-02 | 1-39-03 | 1-17 | 632E | ABS ON | 頭橋嘉太線接地組 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.632E_ES | 632E(嘉太線) ES | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_A1 | [8 empty] | 頭橋SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 33 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_A1 | [8 empty] | 頭橋SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 34 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | JP31 | VAR | 橋11線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十一線KVAR | 11KV橋十一線 KVAR | FEEDER |  |  |  |  | CDC | 35 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | JP31 | A1 | 橋11線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十一線A1 | 11KV橋十一線 R相AMP | FEEDER |  |  |  |  | CDC | 36 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | JP31 | A2 | 橋11線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十一線A2 | 11KV橋十一線 S相AMP | FEEDER |  |  |  |  | CDC | 37 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | JP31 | A3 | 橋11線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十一線A3 | 11KV橋十一線 T相AMP | FEEDER |  |  |  |  | CDC | 38 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | JP31 | NA | 橋11線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十一線A0 | 11KV橋十一線 N相AMP | FEEDER |  |  |  |  | CDC | 39 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | JP31 | F11 KWH(+) | 橋十一線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 40 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | JP32 | VAR | 橋12線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線KVAR | 11KV橋十二線 KVAR | FEEDER |  |  |  |  | CDC | 41 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | JP32 | A1 | 橋12線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線A1 | 11KV橋十二線 R相AMP | FEEDER |  |  |  |  | CDC | 42 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | JP32 | A2 | 橋12線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線A2 | 11KV橋十二線 S相AMP | FEEDER |  |  |  |  | CDC | 43 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | JP32 | A3 | 橋12線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線A3 | 11KV橋十二線 T相AMP | FEEDER |  |  |  |  | CDC | 44 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | JP32 | NA | 橋12線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線A0 | 11KV橋十二線 N相AMP | FEEDER |  |  |  |  | CDC | 45 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | JP32 | F12 KWH(+) | 橋十二線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 46 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | JP33 | VAR | 橋13線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線KVAR | 11KV橋十三線 KVAR | FEEDER |  |  |  |  | CDC | 47 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | JP33 | A1 | 橋13線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線A1 | 11KV橋十三線 R相AMP | FEEDER |  |  |  |  | CDC | 48 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | JP33 | A2 | 橋13線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線A2 | 11KV橋十三線 S相AMP | FEEDER |  |  |  |  | CDC | 49 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | JP33 | A3 | 橋13線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線A3 | 11KV橋十三線 T相AMP | FEEDER |  |  |  |  | CDC | 50 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | JP33 | NA | 橋13線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線A0 | 11KV橋十三線 N相AMP | FEEDER |  |  |  |  | CDC | 51 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | JP33 | F13 KWH(+) | 橋十三線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 52 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | JP34 | VAR | 橋14線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線KVAR | 11KV橋十四線 KVAR | FEEDER |  |  |  |  | CDC | 53 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | JP34 | A1 | 橋14線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線A1 | 11KV橋十四線 R相AMP | FEEDER |  |  |  |  | CDC | 54 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | JP34 | A2 | 橋14線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線A2 | 11KV橋十四線 S相AMP | FEEDER |  |  |  |  | CDC | 55 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | JP34 | A3 | 橋14線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線A3 | 11KV橋十四線 T相AMP | FEEDER |  |  |  |  | CDC | 56 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | JP34 | NA | 橋14線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線A0 | 11KV橋十四線 N相AMP | FEEDER |  |  |  |  | CDC | 57 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | JP34 | F14 KWH(+) | 橋十四線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 58 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | JP35 | VAR | 橋15線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線KVAR | 11KV橋十五線 KVAR | FEEDER |  |  |  |  | CDC | 59 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | JP35 | A1 | 橋15線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線A1 | 11KV橋十五線 R相AMP | FEEDER |  |  |  |  | CDC | 60 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | JP35 | A2 | 橋15線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線A2 | 11KV橋十五線 S相AMP | FEEDER |  |  |  |  | CDC | 61 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | JP35 | A3 | 橋15線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線A3 | 11KV橋十五線 T相AMP | FEEDER |  |  |  |  | CDC | 62 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | JP35 | NA | 橋15線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線A0 | 11KV橋十五線 N相AMP | FEEDER |  |  |  |  | CDC | 63 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | JP35 | F15 KWH(+) | 橋十五線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 64 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JP21 | PHA | 橋一線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_PHA | 11KV橋一線(JP21) 相間RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JP21 | GDA | 橋一線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_GDA | 11KV橋一線(JP21) 接地RY | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0061 | 1-33-07 |  | 1-3C | JP21 | 79S U/L | 橋一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_79UL | 11KV橋一線(JP21) 79RY U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0596 |  | 0113 | 1-36-00 |  | 1-70 | JP21 | ADJ(U/L) | 橋一線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_ADJ | 11KV橋一線(JP21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-03 |  |  | JP22 | PHA | 橋二線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_PHA | 11KV橋二線(JP22) 相間RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JP22 | GDA | 橋二線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_GDA | 11KV橋二線(JP22) 接地RY | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0062 | 1-33-08 |  | 1-3D | JP22 | 79S U/L | 橋二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_79UL | 11KV橋二線(JP22) 79RY U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0597 |  | 0114 | 1-36-01 |  | 1-71 | JP22 | ADJ(U/L) | 橋二線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_ADJ | 11KV橋二線(JP22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JP23 | PHA | 橋三線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_PHA | 11KV橋三線(JP23) 相間RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0D-06 |  |  | JP23 | GDA | 橋三線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_GDA | 11KV橋三線(JP23) 接地RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0557 |  | 0063 | 1-33-09 |  | 1-3E | JP23 | 79S U/L | 橋三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_79UL | 11KV橋三線(JP23) 79RY U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0598 |  | 0115 | 1-36-02 |  | 1-72 | JP23 | ADJ(U/L) | 橋三線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_ADJ | 11KV橋三線(JP23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | JP24 | PHA | 橋四線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_PHA | 11KV橋四線(JP24) 相間RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | JP24 | GDA | 橋四線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_GDA | 11KV橋四線(JP24) 接地RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0064 | 1-33-10 |  | 1-3F | JP24 | 79S U/L | 橋四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_79UL | 11KV橋四線(JP24) 79RY U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0599 |  | 0116 | 1-36-03 |  | 1-73 | JP24 | ADJ(U/L) | 橋四線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_ADJ | 11KV橋四線(JP24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-01 |  |  | JP25 | PHA | 橋五線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_PHA | 11KV橋五線(JP25) 相間RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | JP25 | GDA | 橋五線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_GDA | 11KV橋五線(JP25) 接地RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  | 0065 | 1-33-11 |  | 1-40 | JP25 | 79S U/L | 橋五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_79UL | 11KV橋五線(JP25) 79RY U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0600 |  | 0117 | 1-36-04 |  | 1-74 | JP25 | ADJ(U/L) | 橋五線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_ADJ | 11KV橋五線(JP25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JP26 | PHA | 橋六線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_PHA | 11KV橋六線(JP26) 相間RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | JP26 | GDA | 橋六線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_GDA | 11KV橋六線(JP26) 接地RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0571 |  | 0082 | 1-34-07 |  | 1-51 | JP26 | 79S U/L | 橋六線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_79UL | 11KV橋六線(JP26) 79RY U/L | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0601 |  | 0118 | 1-36-05 |  | 1-75 | JP26 | ADJ(U/L) | 橋六線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_ADJ | 11KV橋六線(JP26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | JP27 | PHA | 橋七線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_PHA | 11KV橋七線(JP27) 相間RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JP27 | GDA | 橋七線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_GDA | 11KV橋七線(JP27) 接地RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0572 |  | 0083 | 1-34-08 |  | 1-52 | JP27 | 79S U/L | 橋七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_79UL | 11KV橋七線(JP27) 79RY U/L | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0602 |  | 0119 | 1-36-06 |  | 1-76 | JP27 | ADJ(U/L) | 橋七線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_ADJ | 11KV橋七線(JP27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | JP28 | PHA | 橋八線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_PHA | 11KV橋八線(JP28) 相間RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | JP28 | GDA | 橋八線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_GDA | 11KV橋八線(JP28) 接地RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0573 |  | 0084 | 1-34-09 |  | 1-53 | JP28 | 79S U/L | 橋八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_79UL | 11KV橋八線(JP28) 79RY U/L | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0603 |  | 0120 | 1-36-07 |  | 1-77 | JP28 | ADJ(U/L) | 橋八線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_ADJ | 11KV橋八線(JP28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JP29 | PHA | 橋九線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_PHA | 11KV橋九線(JP29) 相間RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | JP29 | GDA | 橋九線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_GDA | 11KV橋九線(JP29) 接地RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  | 0085 | 1-34-10 |  | 1-54 | JP29 | 79S U/L | 橋九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_79UL | 11KV橋九線(JP29) 79RY U/L | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0604 |  | 0121 | 1-36-08 |  | 1-78 | JP29 | ADJ(U/L) | 橋九線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_ADJ | 11KV橋九線(JP29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | JP30 | PHA | 橋十線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_PHA | 11KV橋十線(JP30) 相間RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JP30 | GDA | 橋十線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_GDA | 11KV橋十線(JP30) 接地RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0575 |  | 0086 | 1-34-11 |  | 1-55 | JP30 | 79S U/L | 橋十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_79UL | 11KV橋十線(JP30) 79RY U/L | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0605 |  | 0122 | 1-36-09 |  | 1-79 | JP30 | ADJ(U/L) | 橋十線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_ADJ | 11KV橋十線(JP30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-04 |  |  | JP31 | PHA | 橋11線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_PHA | 11KV橋十一線(JP31) 相間RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-12-05 |  |  | JP31 | GDA | 橋11線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_GDA | 11KV橋十一線(JP31) 接地RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0587 |  | 0101 | 1-35-07 |  | 1-64 | JP31 | 79S U/L | 橋十一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_79UL | 11KV橋十一線(JP31) 79RY U/L | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0606 |  | 0123 | 1-36-10 |  | 1-7A | JP31 | ADJ(U/L) | 橋十一線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_ADJ | 11KV橋十一線(JP31) LCO分流器 | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-12-06 |  |  | JP32 | PHA | 橋12線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_PHA | 11KV橋十二線(JP32) 相間RY | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-12-07 |  |  | JP32 | GDA | 橋12線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_GDA | 11KV橋十二線(JP32) 接地RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0588 |  | 0102 | 1-35-08 |  | 1-65 | JP32 | 79S U/L | 橋十二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_79UL | 11KV橋十二線(JP32) 79RY U/L | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0607 |  | 0124 | 1-36-11 |  | 1-7B | JP32 | ADJ(U/L) | 橋十二線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_ADJ | 11KV橋十二線(JP32) LCO分流器 | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | JP33 | PHA | 橋13線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_PHA | 11KV橋十三線(JP33) 相間RY | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | JP33 | GDA | 橋13線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_GDA | 11KV橋十三線(JP33) 接地RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0589 |  | 0103 | 1-35-09 |  | 1-66 | JP33 | 79S U/L | 橋十三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_79UL | 11KV橋十三線(JP33) 79RY U/L | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0608 |  | 0125 | 1-36-12 |  | 1-7C | JP33 | ADJ(U/L) | 橋十三線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_ADJ | 11KV橋十三線(JP33) LCO分流器 | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-02 |  |  | JP34 | PHA | 橋14線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_PHA | 11KV橋十四線(JP34) 相間RY | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | JP34 | GDA | 橋14線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_GDA | 11KV橋十四線(JP34) 接地RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0590 |  | 0104 | 1-35-10 |  | 1-67 | JP34 | 79S U/L | 橋十四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_79UL | 11KV橋十四線(JP34) 79RY U/L | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0609 |  | 0126 | 1-36-13 |  | 1-7D | JP34 | ADJ(U/L) | 橋十四線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_ADJ | 11KV橋十四線(JP34) LCO分流器 | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | JP35 | PHA | 橋15線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_PHA | 11KV橋十五線(JP35) 相間RY | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-13-05 |  |  | JP35 | GDA | 橋15線 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_GDA | 11KV橋十五線(JP35) 接地RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0591 |  | 0105 | 1-35-11 |  | 1-68 | JP35 | 79S U/L | 橋十五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_79UL | 11KV橋十五線(JP35) 79RY U/L | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0610 |  | 0127 | 1-36-14 |  | 1-7E | JP35 | ADJ(U/L) | 橋十五線分流器(使用 / 閉鎖)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_ADJ | 11KV橋十五線(JP35) LCO分流器 | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JP21/T1 |  |  | 0099 |  | 0053 | 1-0C-00 |  | 1-34 | JP21 | CB ON/OFF | 橋一線 11KV |  | adfb | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_CB | JP21(11KV橋一線) CB | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_DS | JP21_DS (非取樣點) | FEEDER | [5 empty] | 126 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP21_ES | JP21_ES (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JP22/T1 |  |  | 0100 |  | 0054 | 1-0C-01 |  | 1-35 | JP22 | CB ON/OFF | 橋二線 11KV |  | adeb | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_CB | JP22(11KV橋二線) CB | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_DS | JP22_DS (非取樣點) | FEEDER | [5 empty] | 129 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP22_ES | JP22_ES (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JP23/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | JP23 | CB ON/OFF | 橋三線 11KV |  | addb | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_CB | JP23(11KV橋三線) CB | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_DS | JP23_DS (非取樣點) | FEEDER | [5 empty] | 132 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP23_ES | JP23_ES (非取樣點) | FEEDER | [5 empty] | 133 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JP24/T1 |  |  | 0102 |  | 0056 | 1-0C-03 |  | 1-37 | JP24 | CB ON/OFF | 橋四線 11KV |  | adbb | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_CB | JP24(11KV橋四線) CB | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_DS | JP24_DS (非取樣點) | FEEDER | [5 empty] | 135 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP24_ES | JP24_ES (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | L/JP25/T1 |  |  | 0103 |  | 0057 | 1-0C-04 |  | 1-38 | JP25 | CB ON/OFF | 橋五線 11KV |  | adab | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_CB | JP25(11KV橋五線) CB | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_DS | JP25_DS (非取樣點) | FEEDER | [5 empty] | 138 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP25_ES | JP25_ES (非取樣點) | FEEDER | [5 empty] | 139 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JP26/T1 |  |  | 0121 |  | 0074 | 1-0E-06 |  | 1-49 | JP26 | CB ON/OFF | 橋六線 11KV |  | aacb | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_CB | JP26(11KV橋六線) CB | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_DS | JP26_DS (非取樣點) | FEEDER | [5 empty] | 141 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP26_ES | JP26_ES (非取樣點) | FEEDER | [5 empty] | 142 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JP27/T1 |  |  | 0122 |  | 0075 | 1-0E-07 |  | 1-4A | JP27 | CB ON/OFF | 橋七線 11KV |  | aadb | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_CB | JP27(11KV橋七線) CB | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_DS | JP27_DS (非取樣點) | FEEDER | [5 empty] | 144 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP27_ES | JP27_ES (非取樣點) | FEEDER | [5 empty] | 145 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JP28/T1 |  |  | 0123 |  | 0076 | 1-0F-00 |  | 1-4B | JP28 | CB ON/OFF | 橋八線 11KV |  | aafb | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_CB | JP28(11KV橋八線) CB | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_DS | JP28_DS (非取樣點) | FEEDER | [5 empty] | 147 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP28_ES | JP28_ES (非取樣點) | FEEDER | [5 empty] | 148 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JP29/T1 |  |  | 0124 |  | 0077 | 1-0F-01 |  | 1-4C | JP29 | CB ON/OFF | 橋九線 11KV |  | aagb | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_CB | JP29(11KV橋九線) CB | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_DS | JP29_DS (非取樣點) | FEEDER | [5 empty] | 150 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP29_ES | JP29_ES (非取樣點) | FEEDER | [5 empty] | 151 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JP30/T1 |  |  | 0125 |  | 0078 | 1-0F-02 |  | 1-4D | JP30 | CB ON/OFF | 橋十線 11KV |  | aahb | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_CB | JP30(11KV橋十線) CB | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_DS | JP30_DS (非取樣點) | FEEDER | [5 empty] | 153 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP30_ES | JP30_ES (非取樣點) | FEEDER | [5 empty] | 154 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3ABUS | L/JP31/T1 |  |  | 0143 |  | 0093 | 1-11-04 |  | 1-5C | JP31 | CB ON/OFF | 橋11線 11KV |  | abcb | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_CB | JP31(11KV橋十一線) CB | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_DS | JP31_DS (非取樣點) | FEEDER | [5 empty] | 156 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP31_ES | JP31_ES (非取樣點) | FEEDER | [5 empty] | 157 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3ABUS | L/JP32/T1 |  |  | 0144 |  | 0094 | 1-11-05 |  | 1-5D | JP32 | CB ON/OFF | 橋12線 11KV |  | abbb | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_CB | JP32(11KV橋十二線) CB | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_DS | JP32_DS (非取樣點) | FEEDER | [5 empty] | 159 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP32_ES | JP32_ES (非取樣點) | FEEDER | [5 empty] | 160 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3ABUS | L/JP33/T1 |  |  | 0145 |  | 0095 | 1-11-06 |  | 1-5E | JP33 | CB ON/OFF | 橋13線 11KV |  | abab | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_CB | JP33(11KV橋十三線) CB | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_DS | JP33_DS (非取樣點) | FEEDER | [5 empty] | 162 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP33_ES | JP33_ES (非取樣點) | FEEDER | [5 empty] | 163 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BBUS | L/JP34/T1 |  |  | 0146 |  | 0096 | 1-11-07 |  | 1-5F | JP34 | CB ON/OFF | 橋14線 11KV |  | acdb | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_CB | JP34(11KV橋十四線) CB | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_DS | JP34_DS (非取樣點) | FEEDER | [5 empty] | 165 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP34_ES | JP34_ES (非取樣點) | FEEDER | [5 empty] | 166 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BBUS | L/JP35/T1 |  |  | 0147 |  | 0097 | 1-12-00 |  | 1-60 | JP35 | CB ON/OFF | 橋15線 11KV |  | accb | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_CB | JP35(11KV橋十五線) CB | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_DS | JP35_DS (非取樣點) | FEEDER | [5 empty] | 168 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.JP35_ES | JP35_ES (非取樣點) | FEEDER | [5 empty] | 169 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | ＃2TIE | A1 | 二號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 170 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | ＃2TIE | A2 | 二號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 171 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | ＃2TIE | A3 | 二號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 172 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | ＃3TIE | A1 | 三號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE |  |  |  |  | CDC | 173 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | ＃3TIE | A2 | 三號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE |  |  |  |  | CDC | 174 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | ＃3TIE | A3 | 三號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE |  |  |  |  | CDC | 175 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  | N2為實線 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | B/3ABUS |  |  | 0104 |  | 0051 | 1-0C-05 |  | 1-32 | ＃2 TIE | CB ON/OFF | 二號聯絡斷路器 |  | zzzz | B2/S25_D1 | [8 empty] | 頭橋SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 176 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | ＃2 TIE | PHA | 二號聯絡斷路器 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 177 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-04 |  |  | ＃2 TIE | GDA | 二號聯絡斷路器 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 178 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/3BBUS | B/1BUS |  |  | 0126 |  | 0072 | 1-0F-03 |  | 1-47 | ＃3 TIE | CB ON/OFF | 三號聯絡斷路器 |  | zzzz | B2/S25_D1 | [8 empty] | 頭橋SS.TIE3_CB | 11KV TIE3 CB | TIE |  |  |  |  | CDC | 179 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-01 |  |  | ＃3 TIE | PHA | 三號聯絡斷路器 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.TIE3_51A | 11KV TIE3 51RY | TIE |  |  |  |  | CDC | 180 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-02 |  |  | ＃3 TIE | GDA | 三號聯絡斷路器 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.TIE3_51NA | 11KV TIE3 51N RY | TIE |  |  |  |  | CDC | 181 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 182 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 183 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | TIE2(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | Point Empty | [7 empty] | 184 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D2 | TIE3(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | Point Empty | [7 empty] | 185 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | ＃1MTR | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 186 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | ＃1MTR | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 187 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | ＃1MTR | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 188 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | ＃1MTR | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 189 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | ＃1MTR | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 190 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2MTR | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 191 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | ＃2MTR | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 192 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | ＃2MTR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 193 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | ＃2MTR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 194 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | ＃2MTR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 195 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | ＃3MTR | MW | 三號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 196 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | ＃3MTR | MVAR | 三號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 197 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | ＃3MTR | A1 | 三號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 198 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | ＃3MTR | A2 | 三號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 199 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | ＃3MTR | A3 | 三號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 200 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | ＃1MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 201 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 202 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0058 | 1-9B |  | 1-39 | ＃1MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 203 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1MTR | #1MTR MWH(+) | 一號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 204 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1MTR | #1MTR MVARH(+) | 一號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 205 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | ＃2MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 206 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | ＃2MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 207 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0079 | 1-BF |  | 1-4E | ＃2MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 208 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2MTR | #2MTR MWH(+) | 二號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 209 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2MTR | #2MTR MVARH(+) | 二號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 210 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | ＃3MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 211 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | ＃3MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 212 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-61 | ＃3MTR | TAP | 三號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 213 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3MTR | #3MTR MWH(+) | 三號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 214 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3MTR | #3MTR MVARH(+) | 三號主變 |  |  | B1/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 215 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0004 |  | 0049 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側(50AS) |  | aaeb | B3/S25_D1 | [8 empty] | 頭橋SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 216 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 217 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 218 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側(60AS) |  | aaab | B3/S25_D1 | [8 empty] | 頭橋SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 219 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 220 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 221 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0025 |  | 0089 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aacb | B3/S25_D1 | [8 empty] | 頭橋SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 222 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 223 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S25_D1 | [8 empty] | 頭橋SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 224 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | T/1MTR |  |  | 0005 |  | 0050 | 1-00-02 |  | 1-31 | ＃1MAIN | CB ON/OFF | 一號主變二次側(1MAS) |  | adca | B2/S25_D1 | [8 empty] | 頭橋SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 225 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2MTR |  |  | 0014 |  | 0070 | 1-01-03 |  | 1-45 | ＃2MAIN(A) | CB ON/OFF | 二號主變二次側 |  | aaea | B2/S25_D1 | [8 empty] | 頭橋SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 226 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | CB | 3MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3ABUS | T/3MTR |  |  | 0026 |  | 0090 | 1-02-07 |  | 1-59 | ＃3MAIN(A) | CB ON/OFF | 三號主變二次側 |  | abda | B2/S25_D1 | [8 empty] | 頭橋SS.3MA_CB | 3MA(#3MTR) CB | DTR |  |  |  |  | CDC | 227 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | CB | 3MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BBUS | T/3MTR |  |  | 0027 |  | 0091 | 1-03-00 |  | 1-5A | ＃3MAINB) | CB ON/OFF | 三號主變二次側 |  | acba | B2/S25_D1 | [8 empty] | 頭橋SS.3MB_CB | 3MB(#3MTR) CB | DTR |  |  |  |  | CDC | 228 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750 | 51A | 一號主變一次側(M1PHA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 229 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | 750 | 51NA | 一號主變一次側(M1GDA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 230 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | ＃1MAIN | 51ZA | 一號主變 51Z RY |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 231 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | ＃1MTR | 87A | 一號主變差動電驛 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 232 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-33-03 |  |  | ＃1MTR | 187S U/L | 一號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 233 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | 760 | 51A | 二號主變一次側(M2PHA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 234 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | 760 | 51NA | 二號主變一次側(M2GDA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 235 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | ＃2MAIN | 51ZA | 二號主變 51Z RY |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 236 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | ＃2MTR | 87A | 二號主變差動電驛 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 237 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-34-03 |  |  | ＃2MTR | 287S U/L | 二號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 238 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | 770 | 51A | 三號主變一次側(M3PHA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 239 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | 770 | 51NA | 三號主變一次側(M3GDA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 240 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | ＃3MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 241 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-04 |  |  | ＃3MTR | 87A | 三號主變差動電驛 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 242 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-35-03 |  |  | ＃3MTR | 387S U/L | 三號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 243 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  | 0106 | 1-12-01 |  | 1-69 | #3M | 3 81 A | 三號低頻電驛(跳脫＃3.M CB) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR |  |  |  |  | CDC | 244 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-00-07 |  |  | ＃1MAIN | 51A | 一號主變二次側(PHA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 245 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-33-00 |  |  | ＃1MTR | 1TRA | 一號主變重故障警報 |  | a | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 246 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0549 |  |  | 1-33-01 |  |  | ＃1MTR | 1TRF | 一號主變輕故障警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 247 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-33-04 |  |  | ＃1MTR | 143RS2 (R/L) | 一號主變OLTC(中心 / 現場)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 248 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0059 | 1-33-05 |  | 1-3A | ＃1MTR | A/M | 一號主變OLTC(自動 / 手動)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 249 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-01 |  |  | ＃2MAIN(A) | 51A | 二號主變二次側 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 250 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-34-00 |  |  | ＃2MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 251 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-34-01 |  |  | ＃2MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 252 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-34-04 |  |  | ＃2MTR | 243RS2 (R/L) | 二號主變OLTC(中心 / 現場)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 253 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0569 |  | 0080 | 1-34-05 |  | 1-4F | ＃2MTR | A/M | 二號主變OLTC(自動 / 手動)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 254 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-03-05 |  |  | ＃3M(A) | 51A | 三號主變二次側(3Main(A)PHA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.3MA_51A | #3MTR二次側(3MA) 51RY | DTR |  |  |  |  | CDC | 255 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-03-07 |  |  | ＃3M(B) | 51A | 三號主變二次側(3Main(B)PHA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.3MB_51A | #3MTR二次側(3MB) 51RY | DTR |  |  |  |  | CDC | 256 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 1-35-00 |  |  | ＃3MTR | 3TRA | 三號主變重故障警報 |  | a | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 257 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0581 |  |  | 1-35-01 |  |  | ＃3MTR | 3TRF | 三號主變輕故障警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 258 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-35-04 |  |  | ＃3MTR | 343RS2 (R/L) | 三號主變OLTC(中心 / 現場)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 259 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0585 |  | 0099 | 1-35-05 |  | 1-62 | ＃3MTR | A/M | 三號主變OLTC(自動 / 手動)指示 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 260 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 629 | 0043 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | 1.MTR 一號主變一次側 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 261 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0630 | 631 | 0044 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | 2.MTR 二號主變一次側 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 262 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 633 | 0045 | 1-38-04 | 1-38-05 | 1-2C | 771 | ABS ON | 3.MTR 三號主變一次側 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 263 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | M1(非取樣點) | DEL | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [16 empty] | 264 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | M1_ES(非取樣點) | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [16 empty] | 265 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | ＃1MTR | 96A | 一號主變 96P RY(96PA) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 266 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-33-02 |  |  | ＃1MTR | 148T | 一號主變OLTC遲滯警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 267 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-12 |  |  | ＃1MTR | 127C | 一號主變AC電源欠壓 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 268 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 269 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M2 | #2MTR(M2) |  | E1 | 2M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 270 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | ＃2MTR | 96A | 二號主變 96P RY(96PA) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 271 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-34-02 |  |  | ＃2MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 272 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-12 |  |  | ＃2MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 273 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | DS | 3M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 274 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 275 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-03 |  |  | ＃3MTR | 96A | 三號主變 96P RY(96PA) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 276 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-35-02 |  |  | ＃3MTR | 348T | 三號主變OLTC遲滯警報 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 277 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-12 |  |  | ＃3MTR | 327C | 三號主變AC電源欠壓 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 278 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0095 |  | 0009 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | 69KV SC |  | aafa | B2/S25_A1 | [8 empty] | 頭橋SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 279 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_A1 | [8 empty] | 頭橋SS.810_ES | 810_ES (非取樣點) | SC | [5 empty] | 280 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/1BUS | C/1SC |  |  | 0098 |  | 0052 | 1-0B-07 |  | 1-33 | ＃1 SC | CB ON/OFF | 一號 SC 11KV |  | adgb | B2/S25_D1 | [8 empty] | 頭橋SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 281 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0060 | 1-33-06 |  | 1-3B | ＃1SC | A/M | 一號SC乏控器(自動 / 手動)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 282 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 283 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | C/2SC |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | ＃2 SC | CB ON/OFF | 二號 SC 11KV |  | aabb | B2/S25_D1 | [8 empty] | 頭橋SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 284 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0081 | 1-34-06 |  | 1-50 | ＃2SC | A/M | 二號SC乏控器(自動 / 手動)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 285 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 286 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/3BBUS | C/3SC |  |  | 0142 |  | 0092 | 1-11-03 |  | 1-5B | #3SC | CB ON/OFF | 三號 SC 11KV |  | acab | B2/S25_D1 | [8 empty] | 頭橋SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 287 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0586 |  | 0100 | 1-35-06 |  | 1-63 | ＃3SC | A/M | 三號SC乏控器(自動 / 手動)指示 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 288 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | ES | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 289 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0634 | 635 | 0040 | 1-38-06 | 1-38-07 | 1-27 | 811 | ABS ON | 69KV SC一次側 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 290 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0096 |  |  | 1-0B-05 |  |  | 810 | SCA | 69KV SC |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 291 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0097 |  |  | 1-0B-06 |  |  | 810 | UVA | 69KV SC |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 292 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | ＃1 SC | SCA | 一號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 293 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-00 |  |  | ＃1 SC | UVA | 一號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 294 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | ＃2 SC | SCA | 二號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 295 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | ＃2 SC | UVA | 二號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 296 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | #3SC | SCA | 三號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 297 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 1-12-03 |  |  | #3SC | UVA | 三號 SC 11KV |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 298 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 299 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 300 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 301 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 302 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.231DS | 231DS (非取樣點) | SC | [5 empty] | 303 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | D2 | 232DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.232DS | 232DS (非取樣點) | SC | [5 empty] | 304 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪A I 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 305 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪A I 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 306 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 307 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 308 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0500 |  | 0001 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 頭橋SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 309 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(STATUS) |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 310 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-30-02 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 311 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0503 |  |  | 1-30-03 |  |  | 通訊充電機 | CHG2 | 通訊充電機故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0504 |  |  | 1-30-04 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0506 |  | 0046 | 1-30-06 |  | 1-2D | 所內開關場 | FLA | 開關場照明 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0507 |  | 0047 | 1-30-07 |  | 1-2E | SPARE | FLB | 市區路燈照明 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0508 |  |  | 1-30-08 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0509 |  |  | 1-30-09 |  |  | SPARE | OPA | 油壓電力電纜警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0510 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火災警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.火災警報(1) | [頭橋]火警 | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0512 |  |  | 1-30-12 |  |  | SPARE | PSF | 所內其他輕故障警報 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-13 |  |  | SPARE | PSA | 所內其他重故障警報 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-14 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0515 |  |  | 1-30-15 |  |  | 洩油池幫 | OWF | 洩油池水位警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0521 |  |  | 1-31-05 |  |  | SPARE |  | 無人化門禁警報(1) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0522 |  |  | 1-31-06 |  |  | SPARE |  | 無人化門禁警報(2) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0523 |  |  | 1-31-07 |  |  | SPARE |  | 無人化門禁警報(3) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0525 |  |  | 1-31-09 |  |  | 69KV CB | 6CBF | 69KV CB 輕警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-31-10 |  |  | 69KV CB | 6CBA | 69KV CB 重警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0527 |  |  | 1-31-11 |  |  | 11KV CB | 1CBF | 11KV CB 輕故障警報 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-12 |  |  | 11KV CB | 1CBA | 11KV CB 重故障警報 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-37-00 |  |  | 光纖通訊系統 | ACFA | 通訊設備AC故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0613 |  |  | 1-37-01 |  |  | 光纖通訊系統 | OLTEA | 通訊設備光纖主故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0614 |  |  | 1-37-02 |  |  | 光纖通訊系統 | OLTEF | 通訊設備光纖次故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 通訊PCM警報 |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-37-03 |  |  | 光纖通訊系統 | PCMA | 博碼調變器故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | ＃1MAIN | 51NA | 一號主變二次側(GDA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1MAIN51NA | #1MAIN51NA | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | ＃2MAIN(A) | 51NA | 二號主變二次側 |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2MAIN51NA | #2MAIN51NA | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M3A | #3MTR(A)(M3A) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | ＃3M(A) | 51NA | 三號主變二次側(3Main(A)GDA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MAIN51NA | #3MAIN51NA | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | M3B | #3MTR(B)(M3B) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-00 |  |  | ＃3M(B) | 51NA | 三號主變二次側(3Main(B)GDA) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3MBIN51NA | #3MBIN51NA | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-30-05 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0511 |  |  | 1-30-11 |  |  | SPARE | SUPA | 所內安全監控 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 340 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Fire2 | MCSG火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-31-00 |  |  | MCSG火警 |  | MCSG火警 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.MCSG火警 | MCSG火警 | OTHER |  |  |  |  | CDC | 341 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | MCSG_89A | MCSG系統故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0517 |  |  | 1-31-01 |  |  | MCSG系統警報 |  | MCSG系統警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.MCSG系統故障 | MCSG系統故障 | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-31-08 |  |  | SPARE |  | 69KV SC 警報 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-14 |  |  | SPARE | 6VUA | 69KV BUS2衡相監視警報 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER |  |  |  |  | CDC | 344 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Fire | 主變火警 | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-31-02 |  |  | 主變火警 |  | 主變火警 |  |  | ELEM/S25_D1 | [8 empty] | 頭橋SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 345 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0519 |  |  | 1-31-03 |  |  | 細水霧故障 |  | 細水霧故障 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 346 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0520 |  |  | 1-31-04 |  |  | 細水霧噴灑 |  | 細水霧噴灑 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 347 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 維護運轉警報 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-15 |  |  | 維護運轉警報 | 43R R/L | 維護運轉警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 348 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 數據機重置 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0595 |  | 0088 | 1-35-15 |  | 1-57 | SPARE | modem reset | 數據機重置 |  |  | B3/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 349 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1MTR | 196B1 | 樸氣電驛第一段動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR96B1 | #1MT撲氣電驛警報 | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | SPARE | 196B2 | 樸氣電驛第二段動作 (SPARE) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR96B2 | #1MT撲氣電驛動作 | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1MTR | 196D | 放壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR96D | #1MT放壓電驛動作 | OTHER |  |  |  |  | CDC | 352 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1MTR | 196P | 突壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR96P | #1MT突壓電驛動作 | OTHER |  |  |  |  | CDC | 353 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1MTR | 163Q | 油流電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR63Q | #1MT ULTC電驛動作 | OTHER |  |  |  |  | CDC | 354 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2MTR | 296B1 | 樸氣電驛第一段動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 355 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | SPARE | 296B2 | 樸氣電驛第二段動作 (SPARE) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 356 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2MTR | 296D | 放壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2MTR | 296P | 突壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2MTR | 263Q | 油流電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-02 |  |  | #3MTR | 396B1 | 樸氣電驛第一段動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-03 |  |  | SPARE | 396B2 | 樸氣電驛第二段動作 (SPARE) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-04 |  |  | #3MTR | 396D | 放壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-19-05 |  |  | #3MTR | 396P | 突壓電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS |  |  | 3MTR | #3MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-19-06 |  |  | #3MTR | 363Q | 油流電驛動作 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | JP21 | VAR | 橋一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋一線KVAR | 11KV橋一線 KVAR | FEEDER |  |  |  |  | CDC | 365 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | JP21 | A1 | 橋一線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋一線A1 | 11KV橋一線 R相AMP | FEEDER |  |  |  |  | CDC | 366 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | JP21 | A2 | 橋一線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋一線A2 | 11KV橋一線 S相AMP | FEEDER |  |  |  |  | CDC | 367 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | JP21 | A3 | 橋一線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋一線A3 | 11KV橋一線 T相AMP | FEEDER |  |  |  |  | CDC | 368 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | JP21 | NA | 橋一線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋一線A0 | 11KV橋一線 N相AMP | FEEDER |  |  |  |  | CDC | 369 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JP27 | VAR | 橋七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線KVAR | 11KV橋七線 KVAR | FEEDER |  |  |  |  | CDC | 370 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JP27 | A1 | 橋七線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線A1 | 11KV橋七線 R相AMP | FEEDER |  |  |  |  | CDC | 371 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JP27 | A2 | 橋七線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線A2 | 11KV橋七線 S相AMP | FEEDER |  |  |  |  | CDC | 372 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JP27 | A3 | 橋七線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線A3 | 11KV橋七線 T相AMP | FEEDER |  |  |  |  | CDC | 373 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JP27 | NA | 橋七線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線A0 | 11KV橋七線 N相AMP | FEEDER |  |  |  |  | CDC | 374 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JP29 | VAR | 橋九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線KVAR | 11KV橋九線 KVAR | FEEDER |  |  |  |  | CDC | 375 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JP29 | A1 | 橋九線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線A1 | 11KV橋九線 R相AMP | FEEDER |  |  |  |  | CDC | 376 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JP29 | A2 | 橋九線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線A2 | 11KV橋九線 S相AMP | FEEDER |  |  |  |  | CDC | 377 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JP29 | A3 | 橋九線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線A3 | 11KV橋九線 T相AMP | FEEDER |  |  |  |  | CDC | 378 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JP29 | NA | 橋九線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線A0 | 11KV橋九線 N相AMP | FEEDER |  |  |  |  | CDC | 379 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | JP22 | VAR | 橋二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線KVAR | 11KV橋二線 KVAR | FEEDER |  |  |  |  | CDC | 380 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | JP22 | A1 | 橋二線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線A1 | 11KV橋二線 R相AMP | FEEDER |  |  |  |  | CDC | 381 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | JP22 | A2 | 橋二線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線A2 | 11KV橋二線 S相AMP | FEEDER |  |  |  |  | CDC | 382 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | JP22 | A3 | 橋二線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線A3 | 11KV橋二線 T相AMP | FEEDER |  |  |  |  | CDC | 383 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | JP22 | NA | 橋二線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線A0 | 11KV橋二線 N相AMP | FEEDER |  |  |  |  | CDC | 384 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JP28 | VAR | 橋八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線KVAR | 11KV橋八線 KVAR | FEEDER |  |  |  |  | CDC | 385 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JP28 | A1 | 橋八線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線A1 | 11KV橋八線 R相AMP | FEEDER |  |  |  |  | CDC | 386 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JP28 | A2 | 橋八線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線A2 | 11KV橋八線 S相AMP | FEEDER |  |  |  |  | CDC | 387 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JP28 | A3 | 橋八線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線A3 | 11KV橋八線 T相AMP | FEEDER |  |  |  |  | CDC | 388 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | JP28 | NA | 橋八線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線A0 | 11KV橋八線 N相AMP | FEEDER |  |  |  |  | CDC | 389 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JP30 | VAR | 橋十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線KVAR | 11KV橋十線 KVAR | FEEDER |  |  |  |  | CDC | 390 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JP30 | A1 | 橋十線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線A1 | 11KV橋十線 R相AMP | FEEDER |  |  |  |  | CDC | 391 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JP30 | A2 | 橋十線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線A2 | 11KV橋十線 S相AMP | FEEDER |  |  |  |  | CDC | 392 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JP30 | A3 | 橋十線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線A3 | 11KV橋十線 T相AMP | FEEDER |  |  |  |  | CDC | 393 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JP30 | NA | 橋十線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線A0 | 11KV橋十線 N相AMP | FEEDER |  |  |  |  | CDC | 394 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | JP23 | VAR | 橋三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線KVAR | 11KV橋三線 KVAR | FEEDER |  |  |  |  | CDC | 395 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | JP23 | A1 | 橋三線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線A1 | 11KV橋三線 R相AMP | FEEDER |  |  |  |  | CDC | 396 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | JP23 | A2 | 橋三線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線A2 | 11KV橋三線 S相AMP | FEEDER |  |  |  |  | CDC | 397 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | JP23 | A3 | 橋三線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線A3 | 11KV橋三線 T相AMP | FEEDER |  |  |  |  | CDC | 398 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | JP23 | NA | 橋三線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線A0 | 11KV橋三線 N相AMP | FEEDER |  |  |  |  | CDC | 399 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | JP25 | VAR | 橋五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線KVAR | 11KV橋五線 KVAR | FEEDER |  |  |  |  | CDC | 400 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | JP25 | A1 | 橋五線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線A1 | 11KV橋五線 R相AMP | FEEDER |  |  |  |  | CDC | 401 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | JP25 | A2 | 橋五線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線A2 | 11KV橋五線 S相AMP | FEEDER |  |  |  |  | CDC | 402 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JP25 | A3 | 橋五線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線A3 | 11KV橋五線 T相AMP | FEEDER |  |  |  |  | CDC | 403 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | JP25 | NA | 橋五線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線A0 | 11KV橋五線 N相AMP | FEEDER |  |  |  |  | CDC | 404 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | JP26 | VAR | 橋六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線KVAR | 11KV橋六線 KVAR | FEEDER |  |  |  |  | CDC | 405 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JP26 | A1 | 橋六線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線A1 | 11KV橋六線 R相AMP | FEEDER |  |  |  |  | CDC | 406 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JP26 | A2 | 橋六線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線A2 | 11KV橋六線 S相AMP | FEEDER |  |  |  |  | CDC | 407 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JP26 | A3 | 橋六線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線A3 | 11KV橋六線 T相AMP | FEEDER |  |  |  |  | CDC | 408 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | JP26 | NA | 橋六線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線A0 | 11KV橋六線 N相AMP | FEEDER |  |  |  |  | CDC | 409 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | JP24 | VAR | 橋四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線KVAR | 11KV橋四線 KVAR | FEEDER |  |  |  |  | CDC | 410 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | JP24 | A1 | 橋四線R相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線A1 | 11KV橋四線 R相AMP | FEEDER |  |  |  |  | CDC | 411 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | JP24 | A2 | 橋四線S相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線A2 | 11KV橋四線 S相AMP | FEEDER |  |  |  |  | CDC | 412 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | JP24 | A3 | 橋四線T相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線A3 | 11KV橋四線 T相AMP | FEEDER |  |  |  |  | CDC | 413 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | JP24 | NA | 橋四線零相電流 | A_-500_500(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線A0 | 11KV橋四線 N相AMP | FEEDER |  |  |  |  | CDC | 414 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 充電機 | DC-V | 配電盤 "MAIN"NFB電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 415 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCH3 |  | INSERT | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 416 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | RTU | RTU |  | ADCL3 |  | INSERT | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S25_D1 | [8 empty] | 頭橋SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 417 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | #1SC組 | A1 | 11KV#1SC組A1 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1SC組A1 | 11KV#1SC組 R相AMP | FEEDER | [5 empty] | 418 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | #1SC組 | A2 | 11KV#1SC組A2 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1SC組A2 | 11KV#1SC組 S相AMP | FEEDER | [5 empty] | 419 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | #1SC組 | A3 | 11KV#1SC組A3 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#1SC組A3 | 11KV#1SC組 T相AMP | FEEDER | [5 empty] | 420 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | #2SC組 | A1 | 11KV#2SC組A1 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2SC組A1 | 11KV#2SC組 R相AMP | FEEDER | [5 empty] | 421 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | #2SC組 | A2 | 11KV#2SC組A2 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2SC組A2 | 11KV#2SC組 S相AMP | FEEDER | [5 empty] | 422 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | #2SC組 | A3 | 11KV#2SC組A3 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#2SC組A3 | 11KV#2SC組 T相AMP | FEEDER | [5 empty] | 423 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | #3SC組 | A1 | 11KV#3SC組A1 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3SC組A1 | 11KV#3SC組 R相AMP | FEEDER | [5 empty] | 424 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | #3SC組 | A2 | 11KV#3SC組A2 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3SC組A2 | 11KV#3SC組 S相AMP | FEEDER | [5 empty] | 425 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | #3SC組 | A3 | 11KV#3SC組A3 | A_-400_400(-2000_2000) |  | B2/S25_D1 | [8 empty] | 頭橋SS.#3SC組A3 | 11KV#3SC組 T相AMP | FEEDER | [5 empty] | 426 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  | 0087 | 1-0F-04 |  | 1-56 | #2M | 81A | 二號低頻電驛 |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR |  |  |  |  | CDC | 427 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  | 0066 | 1-0C-06 |  | 1-41 | #1M | 81A | 一號低頻電驛(跳脫＃1.M CB) |  |  | B1/S25_D1 | [8 empty] | 頭橋SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 428 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | 9A5Other | 通訊室溫度異常 | INSERT | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0616 |  |  | 1-37-04 |  |  | 通訊室溫度 |  | 通訊室溫度異常 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | [5 empty] | 429 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Lights3 | 路燈電源監視 | INSERT | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0619 |  |  | 1-37-07 |  |  | SPARE |  | 路燈電源監視 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 430 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Water1 | 開關場水位警報 | INSERT | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0626 |  |  | 1-37-14 |  |  | 開關場水位一段 |  | 開關場水位一段警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 431 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-32-03 |  |  | 630 | 74A(CFA) | 頭橋嘉太線通信故障 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_CFA | 嘉太線(630) 通訊故障 | LINE69 | [5 empty] | 432 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-37-09 |  |  | 630 | RYFA | 630 IED警報 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.630_RYFA | 630 嘉太線IED警報 | OTHER | [5 empty] | 433 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-32-01 |  |  | 650 | 74A(CFA) | 秀林頭橋線通信故障 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_CFA | 秀林線(650) 通訊故障 | LINE69 | [5 empty] | 434 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0622 |  |  | 1-37-10 |  |  | 650 | RYFA | 650 IED警報 |  |  | B2/S25_A1 | [8 empty] | 頭橋SS.650_RYFA | 650 秀林線IED警報 | OTHER | [5 empty] | 435 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0755 |  |  | 1-3F-15 |  |  | RYFA | 11KV IEDA | IED重警報 (含 81RYFA) |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 436 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | StaDev | 所內設施 |  | Water2 | 開關場水位二段 | INSERT | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0625 |  |  | 1-37-13 |  |  | 開關場水位二段 |  | 開關場水位二段警報 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.開關場水位二段 | 開關場水位二段警報 | OTHER | [5 empty] | 437 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 2PT | #2PT |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-05-07 |  |  | SPARE | PHA | 11KV#2BUS PT-2 (大系統有規劃) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.PT-2_51A | PT-2 51RY | OTHER | [5 empty] | 438 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 2PT | #2PT |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-00 |  |  | SPARE | GDA | 11KV#2BUS PT-2 (大系統有規劃) |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.PT-2_51NA | PT-2 51N RY | OTHER | [5 empty] | 439 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | T/2SSTR |  |  | 0039 |  | 0068 | 1-04-04 |  | 1-43 | SSTR-2 | 52AS ON/OFF | 所內電源 #2 SSTR 490CB |  | aaab | B2/S25_D1 | [8 empty] | 頭橋SS.490_CB | 490(SSTR-2) CB | OTHER | [5 empty] | 440 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | SSTR-2 | PHA | 所內電源 #2 SSTR 490CB |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.SSTR-2_51A | SSTR-2 51RY | OTHER | [5 empty] | 441 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | SSTR-2 | GDA | 所內電源 #2 SSTR 490CB |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.SSTR-2_51NA | SSTR-2 51N RY | OTHER | [5 empty] | 442 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0754 |  |  | 1-3F-14 |  |  | Ladder 14,1 | PMA | POWER METER異常 |  |  | B3/S25_D1 | [8 empty] | 頭橋SS.PMA | PMA | OTHER | [5 empty] | 443 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0724 |  |  | 1-3E-00 |  |  | JP21 | 79 LOA | 橋一線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋ㄧ線79LOA | 橋ㄧ線79LOA | OTHER | [5 empty] | 444 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0730 |  |  | 1-3E-06 |  |  | JP27 | 79 LOA | 橋七線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋七線79LOA | 橋七線79LOA | OTHER | [5 empty] | 445 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0732 |  |  | 1-3E-08 |  |  | JP29 | 79 LOA | 橋九線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋九線79LOA | 橋九線79LOA | OTHER | [5 empty] | 446 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0725 |  |  | 1-3E-01 |  |  | JP22 | 79 LOA | 橋二線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋二線79LOA | 橋二線79LOA | OTHER | [5 empty] | 447 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0731 |  |  | 1-3E-07 |  |  | JP28 | 79 LOA | 橋八線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋八線79LOA | 橋八線79LOA | OTHER | [5 empty] | 448 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0734 |  |  | 1-3E-10 |  |  | JP31 | 79 LOA | 橋十一線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十ㄧ線79LOA | 橋十ㄧ線79LOA | OTHER | [5 empty] | 449 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0735 |  |  | 1-3E-11 |  |  | JP32 | 79 LOA | 橋十二線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十二線79LOA | 橋十二線79LOA | OTHER | [5 empty] | 450 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0736 |  |  | 1-3E-12 |  |  | JP33 | 79 LOA | 橋十三線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十三線79LOA | 橋十三線79LOA | OTHER | [5 empty] | 451 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0738 |  |  | 1-3E-14 |  |  | JP35 | 79 LOA | 橋十五線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十五線79LOA | 橋十五線79LOA | OTHER | [5 empty] | 452 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0737 |  |  | 1-3E-13 |  |  | JP34 | 79 LOA | 橋十四線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十四線79LOA | 橋十四線79LOA | OTHER | [5 empty] | 453 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0733 |  |  | 1-3E-09 |  |  | JP30 | 79 LOA | 橋十線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋十線79LOA | 橋十線79LOA | OTHER | [5 empty] | 454 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0726 |  |  | 1-3E-02 |  |  | JP23 | 79 LOA | 橋三線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋三線79LOA | 橋三線79LOA | OTHER | [5 empty] | 455 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0728 |  |  | 1-3E-04 |  |  | JP25 | 79 LOA | 橋五線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋五線79LOA | 橋五線79LOA | OTHER | [5 empty] | 456 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0729 |  |  | 1-3E-05 |  |  | JP26 | 79 LOA | 橋六線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋六線79LOA | 橋六線79LOA | OTHER | [5 empty] | 457 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0727 |  |  | 1-3E-03 |  |  | JP24 | 79 LOA | 橋四線復閉電驛LOA |  |  | B2/S25_D1 | [8 empty] | 頭橋SS.橋四線79LOA | 橋四線79LOA | OTHER | [5 empty] | 458 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JP21 | F1 KWH(+) | 橋一線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 459 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JP22 | F2 KWH(+) | 橋二線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 460 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JP23 | F3 KWH(+) | 橋三線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 461 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JP24 | F4 KWH(+) | 橋四線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 462 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JP25 | F5 KWH(+) | 橋五線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 463 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | JP26 | F6 KWH(+) | 橋六線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 464 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | JP27 | F7 KWH(+) | 橋七線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 465 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | JP28 | F8 KWH(+) | 橋八線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 466 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | JP29 | F9 KWH(+) | 橋九線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 467 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | JP30 | F10 KWH(+) | 橋十線 |  |  | B2/S25_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 468 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 469 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 470 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | [5 empty] | 471 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 2PT | #2PT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.PT-2_DS | PT-2_DS (非取樣點) | OTHER | [5 empty] | 472 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 2PT | #2PT |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.PT-2_ES | PT-2_ES (非取樣點) | OTHER | [5 empty] | 473 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491_DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.491_DS | 491_DS (非取樣點) | OTHER | [5 empty] | 474 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491_ (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S25_D1 | [8 empty] | 頭橋SS.491_ES | 491_ES (非取樣點) | OTHER | [5 empty] | 475 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S25_D1 | [12 empty] | 頭橋SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S25/69/1BUS/V
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S25_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S25/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S25_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S25/11/M1/MW; OPRD2: S25/11/M2/MW; OPRD3: S25/69/630/MW; OPRD4: S25/69/650/MW
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S25_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S25/0/CalcPoint/OPRN2_MW
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S25_D1 | [17 empty] | none
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S25_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S25/0/CalcPoint/OPRN1; OPRD2: S25/0/CalcPoint/OPRN2; OPRD3: S25/0/CalcPoint/PRFL_UL
S25 | 頭橋SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S25_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S25/11/M1/MW; OPRD2: S25/11/M1/MVAR; OPRD3: S25/0/CalcPoint/Vbs1
S25 | 頭橋SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S25_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S25/11/M2/MW; OPRD2: S25/11/M2/MVAR; OPRD3: S25/0/CalcPoint/Vbs1
S25 | 頭橋SS | 69 | 69kV | 630 | 頭橋～嘉太線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S25_A1 | [12 empty] | 頭橋SS.630_AMP | 嘉太線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S25/69/630/MW; OPRD2: S25/69/630/MVAR; OPRD3: S25/0/CalcPoint/Vbs1
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林～頭橋線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S25_A1 | [12 empty] | 頭橋SS.650_AMP | 秀林線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S25/69/650/MW; OPRD2: S25/69/650/MVAR; OPRD3: S25/0/CalcPoint/Vbs1
S25 | 頭橋SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S25_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S25/11/1BUS/V
S25 | 頭橋SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S25_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S25/11/2BUS/V
S25 | 頭橋SS | 11 | 11kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S25_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S25/11/3ABUS/V
S25 | 頭橋SS | 11 | 11kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S25_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S25/11/3BBUS/V
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S25_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 頭橋SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S25/11/M1/MW; OPRD2: S25/11/M1/MVAR
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S25_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 頭橋SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S25/11/M2/MW; OPRD2: S25/11/M2/MVAR
S25 | 頭橋SS |  |  | 3MTR(A) | #3MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S25_D1 | [15 empty] | MVA_CAL |  | va_million | OPRD1: S25/11/M3A/MW; OPRD2: S25/11/M3A/MVAR
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S25_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S25//1MTR/MVA; OPRD2: 0
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S25_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S25//2MTR/MVA; OPRD2: 0
S25 | 頭橋SS |  |  | 3MTR(A) | #3MTR(A) |  | LOAD | [9 empty] | B1/S25_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S25//3MTR(A)/MVA; OPRD2: 0
S25 | 頭橋SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S25_D1 | [12 empty] | 頭橋SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S25/11/M1/MW; OPRD2: S25/11/M1/MVAR
S25 | 頭橋SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S25_D1 | [12 empty] | 頭橋SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S25/11/M2/MW; OPRD2: S25/11/M2/MVAR
S25 | 頭橋SS |  |  | 3MTR(A) | #3MTR(A) |  | PF | [9 empty] | B1/S25_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S25/11/M3A/MW; OPRD2: S25/11/M3A/MVAR
S25 | 頭橋SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S25_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S25//1MTR/SupLocal; OPRD2: S25//1MTR/Tap Chan; OPRD3: NULL
S25 | 頭橋SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S25_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S25//2MTR/SupLocal; OPRD2: S25//2MTR/Tap Chan; OPRD3: NULL
S25 | 頭橋SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S25_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S25//3MTR/SupLocal; OPRD2: S25//3MTR/Tap Chan; OPRD3: NULL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/1BUS/V; OPRD2: S25/11/JP21/I_R; OPRD3: S25/11/JP21/I_S; OPRD4: S25/11/JP21/I_T
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/1BUS/V; OPRD2: S25/11/JP22/I_R; OPRD3: S25/11/JP22/I_S; OPRD4: S25/11/JP22/I_T
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/1BUS/V; OPRD2: S25/11/JP23/I_R; OPRD3: S25/11/JP23/I_S; OPRD4: S25/11/JP23/I_T
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/1BUS/V; OPRD2: S25/11/JP24/I_R; OPRD3: S25/11/JP24/I_S; OPRD4: S25/11/JP24/I_T
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/1BUS/V; OPRD2: S25/11/JP25/I_R; OPRD3: S25/11/JP25/I_S; OPRD4: S25/11/JP25/I_T
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/2BUS/V; OPRD2: S25/11/JP26/I_R; OPRD3: S25/11/JP26/I_S; OPRD4: S25/11/JP26/I_T
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/2BUS/V; OPRD2: S25/11/JP27/I_R; OPRD3: S25/11/JP27/I_S; OPRD4: S25/11/JP27/I_T
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/2BUS/V; OPRD2: S25/11/JP28/I_R; OPRD3: S25/11/JP28/I_S; OPRD4: S25/11/JP28/I_T
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/2BUS/V; OPRD2: S25/11/JP29/I_R; OPRD3: S25/11/JP29/I_S; OPRD4: S25/11/JP29/I_T
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/2BUS/V; OPRD2: S25/11/JP30/I_R; OPRD3: S25/11/JP30/I_S; OPRD4: S25/11/JP30/I_T
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/3ABUS/V; OPRD2: S25/11/JP31/I_R; OPRD3: S25/11/JP31/I_S; OPRD4: S25/11/JP31/I_T
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/3ABUS/V; OPRD2: S25/11/JP32/I_R; OPRD3: S25/11/JP32/I_S; OPRD4: S25/11/JP32/I_T
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/3ABUS/V; OPRD2: S25/11/JP33/I_R; OPRD3: S25/11/JP33/I_S; OPRD4: S25/11/JP33/I_T
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/3BBUS/V; OPRD2: S25/11/JP34/I_R; OPRD3: S25/11/JP34/I_S; OPRD4: S25/11/JP34/I_T
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S25/11/3BBUS/V; OPRD2: S25/11/JP35/I_R; OPRD3: S25/11/JP35/I_S; OPRD4: S25/11/JP35/I_T
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP21/kVA; OPRD2: S25/11/JP21/KVAR
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP22/kVA; OPRD2: S25/11/JP22/KVAR
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP23/kVA; OPRD2: S25/11/JP23/KVAR
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP24/kVA; OPRD2: S25/11/JP24/KVAR
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP25/kVA; OPRD2: S25/11/JP25/KVAR
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP26/kVA; OPRD2: S25/11/JP26/KVAR
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP27/kVA; OPRD2: S25/11/JP27/KVAR
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP28/kVA; OPRD2: S25/11/JP28/KVAR
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP29/kVA; OPRD2: S25/11/JP29/KVAR
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP30/kVA; OPRD2: S25/11/JP30/KVAR
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十ㄧ線(JP31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP31/kVA; OPRD2: S25/11/JP31/KVAR
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP32/kVA; OPRD2: S25/11/JP32/KVAR
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP33/kVA; OPRD2: S25/11/JP33/KVAR
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP34/kVA; OPRD2: S25/11/JP34/KVAR
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S25/11/JP35/kVA; OPRD2: S25/11/JP35/KVAR
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S25_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S25/11/M1/MW; OPRD2: S25/11/M2/MW
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S25_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S25/11/M1/MVAR; OPRD2: S25/11/M2/MVAR
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S25_D1 | [12 empty] | 頭橋SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S25/11/210/CB; OPRD2: 6.9; OPRD3: 0
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S25_D1 | [12 empty] | 頭橋SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S25/11/220/CB; OPRD2: 6.9; OPRD3: 0
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S25_D1 | [12 empty] | 頭橋SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S25/11/230/CB; OPRD2: 6.9; OPRD3: 0
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S25_A1 | [12 empty] | 頭橋SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S25/69/810/CB; OPRD2: 69; OPRD3: 0
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S25_D1 | [12 empty] | 頭橋SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_24 | OPRD1: S25//1MTR/96B1; OPRD2: S25//1MTR/96PA; OPRD3: S25//1MTR/TRA; OPRD4: S25//1MTR/63Q; OPRD5: S25//1MTR/96D; OPRD6: S25//1MTR/96B2; OPRD7: S25//1MTR/51ZA; OPRD8: S25//1MTR/87A; OPRD9: S25//2MTR/51ZA; OPRD10: S25//2MTR/96B1; OPRD11: S25//2MTR/63Q; OPRD12: S25//2MTR/96D; OPRD13: S25//2MTR/96B2; OPRD14: S25//2MTR/96PA; OPRD15: S25//2MTR/TRA; OPRD16: S25//2MTR/87A; OPRD17: S25//3MTR/96D; OPRD18: S25//3MTR/96B2; OPRD19: S25//3MTR/96B1; OPRD20: S25//3MTR/63Q; OPRD21: S25//3MTR/87A; OPRD22: S25//3MTR/51ZA; OPRD23: S25//3MTR/96PA; OPRD24: S25//3MTR/TRA
S25 | 頭橋SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S25_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S25//1MTR/TRF; OPRD2: S25//2MTR/TRF; OPRD3: S25//3MTR/TRF
S25 | 頭橋SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/RTU/RTU_R_L
S25 | 頭橋SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/StaDev/DCE
S25 | 頭橋SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/StaDev/PSF
S25 | 頭橋SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/StaDev/PSA
S25 | 頭橋SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/StaDev/DCA
S25 | 頭橋SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S25_D1 | [17 empty] | lamp2CC | OPRD1: S25/69/ComPoint/CBF
S25 | 頭橋SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S25_D1 | [17 empty] | lamp2CC | OPRD1: S25/69/ComPoint/CBA
S25 | 頭橋SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S25_D1 | [17 empty] | lamp2CC | OPRD1: S25/69/ComPoint/ABS_89A
S25 | 頭橋SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 主變火警 |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S25_A1 | [17 empty] | lamp2CC | OPRD1: S25/0/StaDev/Fire

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S25 | 頭橋SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 頭橋SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S25/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 頭橋SS.630_AMP | 嘉太線 AMP | LINE69 | S25/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 頭橋SS.650_AMP | 秀林線 AMP | LINE69 | S25/69/650/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋一線KVA | 11KV橋一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋一線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋一線KW | 11KV橋一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋七線KVA | 11KV橋七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋七線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋七線KW | 11KV橋七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋九線KVA | 11KV橋九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋九線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋九線KW | 11KV橋九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋二線KVA | 11KV橋二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋二線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋二線KW | 11KV橋二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋八線KVA | 11KV橋八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋八線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋八線KW | 11KV橋八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線KVA | 11KV橋十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十一線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線KW | 11KV橋十一線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線KVA | 11KV橋十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十二線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線KW | 11KV橋十二線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線KVA | 11KV橋十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十三線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線KW | 11KV橋十三線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線KVA | 11KV橋十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十五線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線KW | 11KV橋十五線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線KVA | 11KV橋十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十四線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線KW | 11KV橋十四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十線KVA | 11KV橋十線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋十線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十線KW | 11KV橋十線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋三線KVA | 11KV橋三線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋三線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋三線KW | 11KV橋三線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋五線KVA | 11KV橋五線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋五線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋五線KW | 11KV橋五線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋六線KVA | 11KV橋六線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋六線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋六線KW | 11KV橋六線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋四線KVA | 11KV橋四線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  |  |  |  | 橋四線KW | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋四線KW | 11KV橋四線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S25//1MTR/MVA |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_PF | #1MTR 功率因素 | DTR | S25//1MTR/PF |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S25//2MTR/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_PF | #2MTR 功率因素 | DTR | S25//2MTR/PF |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_MVA | #3MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_PF | #3MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S25 | 頭橋SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S25/11/210/MVAR |  | SC_CAL_11 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S25/11/220/MVAR |  | SC_CAL_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S25/11/230/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S25/69/810/MVAR |  | SC_CAL_69 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 69 | 69kV | 630_CB | 嘉太線(630_CB) | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.630_CB_2 | 630(嘉太線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 45 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650_CB | 秀林線(650_CB) | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.650_CB_2 | 650(秀林線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 46 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810_CB | #1SC(810_CB) | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.810_CB_2 | 810(69KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 48 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 49 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 50 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 51 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S25 | 頭橋SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 52 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | BUS2VUA | BUS#2VUA | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.69KVBUS#2VUA_A | 69KVBUS#2VUA (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 53 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 54 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 頭橋SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S25/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_3 |  |  | 57 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630_AMP | 嘉太線 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.630_AMP_A | 嘉太線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630_AMP | 嘉太線 | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.630_AMP_2 | 嘉太線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 59 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650_AMP | 秀林線 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.650_AMP_A | 秀林線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650_AMP | 秀林線 | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.650_AMP_2 | 秀林線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_MVA_2 | #3MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 66 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S25 | 頭橋SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.630_RYFA_A | 630 嘉太線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 68 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 650_RYFA | 650 | [27 empty] | ADCS_N | [8 empty] | 頭橋SS.650_RYFA_A | 650 秀林線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 69 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S25/0/RTU/ADCH1 |  |  |  | CDC | 70 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S25/0/RTU/ADCH2 |  |  |  | CDC | 71 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S25/0/RTU/ADCL1 |  |  |  | CDC | 72 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S25/0/RTU/ADCL2 |  |  |  | CDC | 73 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 頭橋SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S25/69/1BUS/V |  |  |  | CDC | 74 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S25 | 頭橋SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S25/11/1BUS/V |  |  |  | CDC | 75 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S25/11/2BUS/V |  |  |  | CDC | 76 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 3ABUS | #3ABUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | S25/11/3ABUS/V |  |  |  | CDC | 77 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 11 | 11kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-82 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | S25/11/3BBUS/V |  |  |  | CDC | 78 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 頭橋SS.630_MW | 嘉太線 MW | LINE69 | S25/69/630/MW |  |  |  | CDC | 79 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 頭橋SS.630_MVAR | 嘉太線 MVAR | LINE69 | S25/69/630/MVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 頭橋SS.650_MW | 秀林線 MW | LINE69 | S25/69/650/MW |  |  |  | CDC | 81 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 頭橋SS.650_MVAR | 秀林線 MVAR | LINE69 | S25/69/650/MVAR |  |  |  | CDC | 82 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋一線 | 橋一線 |  | 橋一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋一線KVAR | 11KV橋一線 KVAR | FEEDER | S25/11/JP21/KVAR |  |  |  | CDC | 83 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋一線 | 橋一線 |  | 橋一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋一線A1 | 11KV橋一線 R相AMP | FEEDER | S25/11/JP21/I_R |  |  |  | CDC | 84 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋一線 | 橋一線 |  | 橋一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋一線A2 | 11KV橋一線 S相AMP | FEEDER | S25/11/JP21/I_S |  |  |  | CDC | 85 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋一線 | 橋一線 |  | 橋一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋一線A3 | 11KV橋一線 T相AMP | FEEDER | S25/11/JP21/I_T |  |  |  | CDC | 86 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋一線 | 橋一線 |  | 橋一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋一線A0 | 11KV橋一線 N相AMP | FEEDER | S25/11/JP21/I_N |  |  |  | CDC | 87 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋七線 | 橋七線 |  | 橋七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋七線KVAR | 11KV橋七線 KVAR | FEEDER | S25/11/JP27/KVAR |  |  |  | CDC | 88 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋七線 | 橋七線 |  | 橋七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋七線A1 | 11KV橋七線 R相AMP | FEEDER | S25/11/JP27/I_R |  |  |  | CDC | 89 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋七線 | 橋七線 |  | 橋七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋七線A2 | 11KV橋七線 S相AMP | FEEDER | S25/11/JP27/I_S |  |  |  | CDC | 90 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋七線 | 橋七線 |  | 橋七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋七線A3 | 11KV橋七線 T相AMP | FEEDER | S25/11/JP27/I_T |  |  |  | CDC | 91 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋七線 | 橋七線 |  | 橋七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋七線A0 | 11KV橋七線 N相AMP | FEEDER | S25/11/JP27/I_N |  |  |  | CDC | 92 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋九線 | 橋九線 |  | 橋九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋九線KVAR | 11KV橋九線 KVAR | FEEDER | S25/11/JP29/KVAR |  |  |  | CDC | 93 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋九線 | 橋九線 |  | 橋九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋九線A1 | 11KV橋九線 R相AMP | FEEDER | S25/11/JP29/I_R |  |  |  | CDC | 94 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋九線 | 橋九線 |  | 橋九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋九線A2 | 11KV橋九線 S相AMP | FEEDER | S25/11/JP29/I_S |  |  |  | CDC | 95 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋九線 | 橋九線 |  | 橋九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋九線A3 | 11KV橋九線 T相AMP | FEEDER | S25/11/JP29/I_T |  |  |  | CDC | 96 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋九線 | 橋九線 |  | 橋九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋九線A0 | 11KV橋九線 N相AMP | FEEDER | S25/11/JP29/I_N |  |  |  | CDC | 97 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋二線 | 橋二線 |  | 橋二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋二線KVAR | 11KV橋二線 KVAR | FEEDER | S25/11/JP22/KVAR |  |  |  | CDC | 98 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋二線 | 橋二線 |  | 橋二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋二線A1 | 11KV橋二線 R相AMP | FEEDER | S25/11/JP22/I_R |  |  |  | CDC | 99 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋二線 | 橋二線 |  | 橋二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋二線A2 | 11KV橋二線 S相AMP | FEEDER | S25/11/JP22/I_S |  |  |  | CDC | 100 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋二線 | 橋二線 |  | 橋二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋二線A3 | 11KV橋二線 T相AMP | FEEDER | S25/11/JP22/I_T |  |  |  | CDC | 101 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋二線 | 橋二線 |  | 橋二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋二線A0 | 11KV橋二線 N相AMP | FEEDER | S25/11/JP22/I_N |  |  |  | CDC | 102 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋八線 | 橋八線 |  | 橋八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋八線KVAR | 11KV橋八線 KVAR | FEEDER | S25/11/JP28/KVAR |  |  |  | CDC | 103 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋八線 | 橋八線 |  | 橋八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋八線A1 | 11KV橋八線 R相AMP | FEEDER | S25/11/JP28/I_R |  |  |  | CDC | 104 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋八線 | 橋八線 |  | 橋八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋八線A2 | 11KV橋八線 S相AMP | FEEDER | S25/11/JP28/I_S |  |  |  | CDC | 105 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋八線 | 橋八線 |  | 橋八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋八線A3 | 11KV橋八線 T相AMP | FEEDER | S25/11/JP28/I_T |  |  |  | CDC | 106 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋八線 | 橋八線 |  | 橋八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋八線A0 | 11KV橋八線 N相AMP | FEEDER | S25/11/JP28/I_N |  |  |  | CDC | 107 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十一線 | 橋十一線 |  | 橋十一線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線KVAR | 11KV橋十一線 KVAR | FEEDER | S25/11/JP31/KVAR |  |  |  | CDC | 108 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十一線 | 橋十一線 |  | 橋十一線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線A1 | 11KV橋十一線 R相AMP | FEEDER | S25/11/JP31/I_R |  |  |  | CDC | 109 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十一線 | 橋十一線 |  | 橋十一線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線A2 | 11KV橋十一線 S相AMP | FEEDER | S25/11/JP31/I_S |  |  |  | CDC | 110 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十一線 | 橋十一線 |  | 橋十一線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線A3 | 11KV橋十一線 T相AMP | FEEDER | S25/11/JP31/I_T |  |  |  | CDC | 111 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十一線 | 橋十一線 |  | 橋十一線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十一線A0 | 11KV橋十一線 N相AMP | FEEDER | S25/11/JP31/I_N |  |  |  | CDC | 112 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十二線 | 橋十二線 |  | 橋十二線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線KVAR | 11KV橋十二線 KVAR | FEEDER | S25/11/JP32/KVAR |  |  |  | CDC | 113 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十二線 | 橋十二線 |  | 橋十二線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線A1 | 11KV橋十二線 R相AMP | FEEDER | S25/11/JP32/I_R |  |  |  | CDC | 114 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十二線 | 橋十二線 |  | 橋十二線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線A2 | 11KV橋十二線 S相AMP | FEEDER | S25/11/JP32/I_S |  |  |  | CDC | 115 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十二線 | 橋十二線 |  | 橋十二線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線A3 | 11KV橋十二線 T相AMP | FEEDER | S25/11/JP32/I_T |  |  |  | CDC | 116 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十二線 | 橋十二線 |  | 橋十二線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線A0 | 11KV橋十二線 N相AMP | FEEDER | S25/11/JP32/I_N |  |  |  | CDC | 117 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十三線 | 橋十三線 |  | 橋十三線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線KVAR | 11KV橋十三線 KVAR | FEEDER | S25/11/JP33/KVAR |  |  |  | CDC | 118 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十三線 | 橋十三線 |  | 橋十三線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線A1 | 11KV橋十三線 R相AMP | FEEDER | S25/11/JP33/I_R |  |  |  | CDC | 119 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十三線 | 橋十三線 |  | 橋十三線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線A2 | 11KV橋十三線 S相AMP | FEEDER | S25/11/JP33/I_S |  |  |  | CDC | 120 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十三線 | 橋十三線 |  | 橋十三線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線A3 | 11KV橋十三線 T相AMP | FEEDER | S25/11/JP33/I_T |  |  |  | CDC | 121 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十三線 | 橋十三線 |  | 橋十三線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線A0 | 11KV橋十三線 N相AMP | FEEDER | S25/11/JP33/I_N |  |  |  | CDC | 122 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十五線 | 橋十五線 |  | 橋十五線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線KVAR | 11KV橋十五線 KVAR | FEEDER | S25/11/JP35/KVAR |  |  |  | CDC | 123 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十五線 | 橋十五線 |  | 橋十五線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線A1 | 11KV橋十五線 R相AMP | FEEDER | S25/11/JP35/I_R |  |  |  | CDC | 124 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十五線 | 橋十五線 |  | 橋十五線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線A2 | 11KV橋十五線 S相AMP | FEEDER | S25/11/JP35/I_S |  |  |  | CDC | 125 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十五線 | 橋十五線 |  | 橋十五線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線A3 | 11KV橋十五線 T相AMP | FEEDER | S25/11/JP35/I_T |  |  |  | CDC | 126 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十五線 | 橋十五線 |  | 橋十五線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線A0 | 11KV橋十五線 N相AMP | FEEDER | S25/11/JP35/I_N |  |  |  | CDC | 127 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十四線 | 橋十四線 |  | 橋十四線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線KVAR | 11KV橋十四線 KVAR | FEEDER | S25/11/JP34/KVAR |  |  |  | CDC | 128 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十四線 | 橋十四線 |  | 橋十四線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線A1 | 11KV橋十四線 R相AMP | FEEDER | S25/11/JP34/I_R |  |  |  | CDC | 129 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十四線 | 橋十四線 |  | 橋十四線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線A2 | 11KV橋十四線 S相AMP | FEEDER | S25/11/JP34/I_S |  |  |  | CDC | 130 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十四線 | 橋十四線 |  | 橋十四線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線A3 | 11KV橋十四線 T相AMP | FEEDER | S25/11/JP34/I_T |  |  |  | CDC | 131 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十四線 | 橋十四線 |  | 橋十四線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線A0 | 11KV橋十四線 N相AMP | FEEDER | S25/11/JP34/I_N |  |  |  | CDC | 132 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十線 | 橋十線 |  | 橋十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十線KVAR | 11KV橋十線 KVAR | FEEDER | S25/11/JP30/KVAR |  |  |  | CDC | 133 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十線 | 橋十線 |  | 橋十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十線A1 | 11KV橋十線 R相AMP | FEEDER | S25/11/JP30/I_R |  |  |  | CDC | 134 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十線 | 橋十線 |  | 橋十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十線A2 | 11KV橋十線 S相AMP | FEEDER | S25/11/JP30/I_S |  |  |  | CDC | 135 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十線 | 橋十線 |  | 橋十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十線A3 | 11KV橋十線 T相AMP | FEEDER | S25/11/JP30/I_T |  |  |  | CDC | 136 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋十線 | 橋十線 |  | 橋十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋十線A0 | 11KV橋十線 N相AMP | FEEDER | S25/11/JP30/I_N |  |  |  | CDC | 137 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋三線 | 橋三線 |  | 橋三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋三線KVAR | 11KV橋三線 KVAR | FEEDER | S25/11/JP23/KVAR |  |  |  | CDC | 138 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋三線 | 橋三線 |  | 橋三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋三線A1 | 11KV橋三線 R相AMP | FEEDER | S25/11/JP23/I_R |  |  |  | CDC | 139 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋三線 | 橋三線 |  | 橋三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋三線A2 | 11KV橋三線 S相AMP | FEEDER | S25/11/JP23/I_S |  |  |  | CDC | 140 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋三線 | 橋三線 |  | 橋三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋三線A3 | 11KV橋三線 T相AMP | FEEDER | S25/11/JP23/I_T |  |  |  | CDC | 141 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋三線 | 橋三線 |  | 橋三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋三線A0 | 11KV橋三線 N相AMP | FEEDER | S25/11/JP23/I_N |  |  |  | CDC | 142 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋五線 | 橋五線 |  | 橋五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋五線KVAR | 11KV橋五線 KVAR | FEEDER | S25/11/JP25/KVAR |  |  |  | CDC | 143 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋五線 | 橋五線 |  | 橋五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋五線A1 | 11KV橋五線 R相AMP | FEEDER | S25/11/JP25/I_R |  |  |  | CDC | 144 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋五線 | 橋五線 |  | 橋五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋五線A2 | 11KV橋五線 S相AMP | FEEDER | S25/11/JP25/I_S |  |  |  | CDC | 145 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋五線 | 橋五線 |  | 橋五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋五線A3 | 11KV橋五線 T相AMP | FEEDER | S25/11/JP25/I_T |  |  |  | CDC | 146 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋五線 | 橋五線 |  | 橋五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋五線A0 | 11KV橋五線 N相AMP | FEEDER | S25/11/JP25/I_N |  |  |  | CDC | 147 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋六線 | 橋六線 |  | 橋六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋六線KVAR | 11KV橋六線 KVAR | FEEDER | S25/11/JP26/KVAR |  |  |  | CDC | 148 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋六線 | 橋六線 |  | 橋六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋六線A1 | 11KV橋六線 R相AMP | FEEDER | S25/11/JP26/I_R |  |  |  | CDC | 149 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋六線 | 橋六線 |  | 橋六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋六線A2 | 11KV橋六線 S相AMP | FEEDER | S25/11/JP26/I_S |  |  |  | CDC | 150 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋六線 | 橋六線 |  | 橋六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋六線A3 | 11KV橋六線 T相AMP | FEEDER | S25/11/JP26/I_T |  |  |  | CDC | 151 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋六線 | 橋六線 |  | 橋六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋六線A0 | 11KV橋六線 N相AMP | FEEDER | S25/11/JP26/I_N |  |  |  | CDC | 152 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋四線 | 橋四線 |  | 橋四線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋四線KVAR | 11KV橋四線 KVAR | FEEDER | S25/11/JP24/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋四線 | 橋四線 |  | 橋四線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋四線A1 | 11KV橋四線 R相AMP | FEEDER | S25/11/JP24/I_R |  |  |  | CDC | 154 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋四線 | 橋四線 |  | 橋四線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋四線A2 | 11KV橋四線 S相AMP | FEEDER | S25/11/JP24/I_S |  |  |  | CDC | 155 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋四線 | 橋四線 |  | 橋四線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋四線A3 | 11KV橋四線 T相AMP | FEEDER | S25/11/JP24/I_T |  |  |  | CDC | 156 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 橋四線 | 橋四線 |  | 橋四線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.橋四線A0 | 11KV橋四線 N相AMP | FEEDER | S25/11/JP24/I_N |  |  |  | CDC | 157 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S25/11/TIE2/I_R |  |  |  | CDC | 158 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S25/11/TIE2/I_S |  |  |  | CDC | 159 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S25/11/TIE2/I_T |  |  |  | CDC | 160 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE | S25/11/TIE3/I_R |  |  |  | CDC | 161 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE | S25/11/TIE3/I_S |  |  |  | CDC | 162 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE | S25/11/TIE3/I_T |  |  |  | CDC | 163 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_MW | #1MTR二次側 MW | DTR | S25/11/M1/MW |  |  |  | CDC | 164 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S25/11/M1/MVAR |  |  |  | CDC | 165 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S25/11/M1/I_R |  |  |  | CDC | 166 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S25/11/M1/I_S |  |  |  | CDC | 167 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S25/11/M1/I_T |  |  |  | CDC | 168 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_OIL | #1MTR 油溫 | DTR | S25//1MTR/OilTemp |  |  |  | CDC | 169 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_COIL | #1MTR 線溫 | DTR | S25//1MTR/CoilTemp |  |  |  | CDC | 170 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S25//1MTR/TapPosMv |  |  |  | CDC | 171 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_MW | #2MTR二次側 MW | DTR | S25/11/M2/MW |  |  |  | CDC | 172 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S25/11/M2/MVAR |  |  |  | CDC | 173 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S25/11/M2/I_R |  |  |  | CDC | 174 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S25/11/M2/I_S |  |  |  | CDC | 175 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S25/11/M2/I_T |  |  |  | CDC | 176 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_OIL | #2MTR 油溫 | DTR | S25//2MTR/OilTemp |  |  |  | CDC | 177 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_COIL | #2MTR 線溫 | DTR | S25//2MTR/CoilTemp |  |  |  | CDC | 178 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S25//2MTR/TapPosMv |  |  |  | CDC | 179 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_MW | #3MTR二次側 MW | DTR | S25/11/M3A/MW |  |  |  | CDC | 180 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S25/11/M3A/MVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S25/11/M3A/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S25/11/M3A/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S25/11/M3A/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_OIL | #3MTR 油溫 | DTR | S25//3MTR/OilTemp |  |  |  | CDC | 185 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_COIL | #3MTR 線溫 | DTR | S25//3MTR/CoilTemp |  |  |  | CDC | 186 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S25//3MTR/TapPosMv |  |  |  | CDC | 187 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S25 | 頭橋SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.直流電源電壓 | 直流電源電壓 | OTHER | S25/0/StaDev/DCV |  |  |  | CDC | 188 | GENERICAIPoint | SS205_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S25/0/RTU/ADCH3 |  |  |  | CDC | 189 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S25/0/RTU/ADCL3 |  |  |  | CDC | 190 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 1SC組 | #1SC組 |  | #1SC組A1 | [17 empty] | 2-84 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1SC組A1 | 11KV#1SC組 R相AMP | FEEDER | S25/11/210/I_R |  |  |  | CDC | 191 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 1SC組 | #1SC組 |  | #1SC組A2 | [17 empty] | 2-85 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1SC組A2 | 11KV#1SC組 S相AMP | FEEDER | S25/11/210/I_S |  |  |  | CDC | 192 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 1SC組 | #1SC組 |  | #1SC組A3 | [17 empty] | 2-86 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#1SC組A3 | 11KV#1SC組 T相AMP | FEEDER | S25/11/210/I_T |  |  |  | CDC | 193 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 2SC組 | #2SC組 |  | #2SC組A1 | [17 empty] | 2-87 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2SC組A1 | 11KV#2SC組 R相AMP | FEEDER | S25/11/220/I_R |  |  |  | CDC | 194 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 2SC組 | #2SC組 |  | #2SC組A2 | [17 empty] | 2-88 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2SC組A2 | 11KV#2SC組 S相AMP | FEEDER | S25/11/220/I_S |  |  |  | CDC | 195 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 2SC組 | #2SC組 |  | #2SC組A3 | [17 empty] | 2-89 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#2SC組A3 | 11KV#2SC組 T相AMP | FEEDER | S25/11/220/I_T |  |  |  | CDC | 196 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 3SC組 | #3SC組 |  | #3SC組A1 | [17 empty] | 2-8A | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3SC組A1 | 11KV#3SC組 R相AMP | FEEDER | S25/11/230/I_R |  |  |  | CDC | 197 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 3SC組 | #3SC組 |  | #3SC組A2 | [17 empty] | 2-8B | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3SC組A2 | 11KV#3SC組 S相AMP | FEEDER | S25/11/230/I_S |  |  |  | CDC | 198 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 11 | 11kV | 3SC組 | #3SC組 |  | #3SC組A3 | [17 empty] | 2-8C | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 頭橋SS.#3SC組A3 | 11KV#3SC組 T相AMP | FEEDER | S25/11/230/I_T |  |  |  | CDC | 199 | GENERICAIPoint | SS205_L2 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.630_PHA | 嘉太線(630) 相間RY | LINE69 | S25/69/630/PHA |  |  |  | CDC | 200 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.630_GDA | 嘉太線(630) 接地RY | LINE69 | S25/69/630/GDA |  |  |  | CDC | 201 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 頭橋SS.630_CB | 630(嘉太線) CB | LINE69 | S25/69/630/CB |  |  |  | CDC | 202 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | ABS1 | 631 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.631_ABS | 631(嘉太線) ABS | LINE69 | S25/69/630/ABS1 |  |  |  | CDC | 203 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | ABS2 | 632 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.632_ABS | 632(嘉太線) ABS | LINE69 | S25/69/630/ABS2 |  |  |  | CDC | 204 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | E2 | 632E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.632E_ES | 632E(嘉太線) ES | LINE69 | S25/69/630/ES2 |  |  |  | CDC | 205 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.650_PHA | 秀林線(650) 相間RY | LINE69 | S25/69/650/PHA |  |  |  | CDC | 206 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.650_GDA | 秀林線(650) 接地RY | LINE69 | S25/69/650/GDA |  |  |  | CDC | 207 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 頭橋SS.650_CB | 650(秀林線) CB | LINE69 | S25/69/650/CB |  |  |  | CDC | 208 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | ABS1 | 651 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.651_ABS | 651(秀林線) ABS | LINE69 | S25/69/650/ABS1 |  |  |  | CDC | 209 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | ABS2 | 652 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.652_ABS | 652(秀林線) ABS | LINE69 | S25/69/650/ABS2 |  |  |  | CDC | 210 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | E2 | 652E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.652E_ES | 652E(秀林線) ES | LINE69 | S25/69/650/ES2 |  |  |  | CDC | 211 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_PHA | 11KV橋一線(JP21) 相間RY | FEEDER | S25/11/JP21/PHA |  |  |  | CDC | 212 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_GDA | 11KV橋一線(JP21) 接地RY | FEEDER | S25/11/JP21/GDA |  |  |  | CDC | 213 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_79UL | 11KV橋一線(JP21) 79RY U/L | FEEDER | S25/11/JP21/79UL |  |  |  | CDC | 214 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP21 | 橋一線(JP21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_ADJ | 11KV橋一線(JP21) LCO分流器 U/L | FEEDER | S25/11/JP21/ADJ |  |  |  | CDC | 215 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP21 | JP21(11KV橋一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_CB | JP21(11KV橋一線) CB | FEEDER | S25/11/JP21/CB |  |  |  | CDC | 216 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_PHA | 11KV橋二線(JP22) 相間RY | FEEDER | S25/11/JP22/PHA |  |  |  | CDC | 217 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_GDA | 11KV橋二線(JP22) 接地RY | FEEDER | S25/11/JP22/GDA |  |  |  | CDC | 218 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_79UL | 11KV橋二線(JP22) 79RY U/L | FEEDER | S25/11/JP22/79UL |  |  |  | CDC | 219 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP22 | 橋二線(JP22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_ADJ | 11KV橋二線(JP22) LCO分流器 U/L | FEEDER | S25/11/JP22/ADJ |  |  |  | CDC | 220 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP22 | JP22(11KV橋二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_CB | JP22(11KV橋二線) CB | FEEDER | S25/11/JP22/CB |  |  |  | CDC | 221 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_PHA | 11KV橋三線(JP23) 相間RY | FEEDER | S25/11/JP23/PHA |  |  |  | CDC | 222 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_GDA | 11KV橋三線(JP23) 接地RY | FEEDER | S25/11/JP23/GDA |  |  |  | CDC | 223 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_79UL | 11KV橋三線(JP23) 79RY U/L | FEEDER | S25/11/JP23/79UL |  |  |  | CDC | 224 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP23 | 橋三線(JP23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_ADJ | 11KV橋三線(JP23) LCO分流器 U/L | FEEDER | S25/11/JP23/ADJ |  |  |  | CDC | 225 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP23 | JP23(11KV橋三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_CB | JP23(11KV橋三線) CB | FEEDER | S25/11/JP23/CB |  |  |  | CDC | 226 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_PHA | 11KV橋四線(JP24) 相間RY | FEEDER | S25/11/JP24/PHA |  |  |  | CDC | 227 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_GDA | 11KV橋四線(JP24) 接地RY | FEEDER | S25/11/JP24/GDA |  |  |  | CDC | 228 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_79UL | 11KV橋四線(JP24) 79RY U/L | FEEDER | S25/11/JP24/79UL |  |  |  | CDC | 229 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP24 | 橋四線(JP24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_ADJ | 11KV橋四線(JP24) LCO分流器 U/L | FEEDER | S25/11/JP24/ADJ |  |  |  | CDC | 230 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP24 | JP24(11KV橋四線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_CB | JP24(11KV橋四線) CB | FEEDER | S25/11/JP24/CB |  |  |  | CDC | 231 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_PHA | 11KV橋五線(JP25) 相間RY | FEEDER | S25/11/JP25/PHA |  |  |  | CDC | 232 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_GDA | 11KV橋五線(JP25) 接地RY | FEEDER | S25/11/JP25/GDA |  |  |  | CDC | 233 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_79UL | 11KV橋五線(JP25) 79RY U/L | FEEDER | S25/11/JP25/79UL |  |  |  | CDC | 234 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP25 | 橋五線(JP25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_ADJ | 11KV橋五線(JP25) LCO分流器 U/L | FEEDER | S25/11/JP25/ADJ |  |  |  | CDC | 235 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP25 | JP25(11KV橋五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_CB | JP25(11KV橋五線) CB | FEEDER | S25/11/JP25/CB |  |  |  | CDC | 236 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_PHA | 11KV橋六線(JP26) 相間RY | FEEDER | S25/11/JP26/PHA |  |  |  | CDC | 237 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_GDA | 11KV橋六線(JP26) 接地RY | FEEDER | S25/11/JP26/GDA |  |  |  | CDC | 238 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_79UL | 11KV橋六線(JP26) 79RY U/L | FEEDER | S25/11/JP26/79UL |  |  |  | CDC | 239 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP26 | 橋六線(JP26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_ADJ | 11KV橋六線(JP26) LCO分流器 U/L | FEEDER | S25/11/JP26/ADJ |  |  |  | CDC | 240 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP26 | JP26(11KV橋六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_CB | JP26(11KV橋六線) CB | FEEDER | S25/11/JP26/CB |  |  |  | CDC | 241 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_PHA | 11KV橋七線(JP27) 相間RY | FEEDER | S25/11/JP27/PHA |  |  |  | CDC | 242 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_GDA | 11KV橋七線(JP27) 接地RY | FEEDER | S25/11/JP27/GDA |  |  |  | CDC | 243 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_79UL | 11KV橋七線(JP27) 79RY U/L | FEEDER | S25/11/JP27/79UL |  |  |  | CDC | 244 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP27 | 橋七線(JP27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_ADJ | 11KV橋七線(JP27) LCO分流器 U/L | FEEDER | S25/11/JP27/ADJ |  |  |  | CDC | 245 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP27 | JP27(11KV橋七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_CB | JP27(11KV橋七線) CB | FEEDER | S25/11/JP27/CB |  |  |  | CDC | 246 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_PHA | 11KV橋八線(JP28) 相間RY | FEEDER | S25/11/JP28/PHA |  |  |  | CDC | 247 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_GDA | 11KV橋八線(JP28) 接地RY | FEEDER | S25/11/JP28/GDA |  |  |  | CDC | 248 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_79UL | 11KV橋八線(JP28) 79RY U/L | FEEDER | S25/11/JP28/79UL |  |  |  | CDC | 249 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP28 | 橋八線(JP28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_ADJ | 11KV橋八線(JP28) LCO分流器 U/L | FEEDER | S25/11/JP28/ADJ |  |  |  | CDC | 250 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP28 | JP28(11KV橋八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_CB | JP28(11KV橋八線) CB | FEEDER | S25/11/JP28/CB |  |  |  | CDC | 251 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_PHA | 11KV橋九線(JP29) 相間RY | FEEDER | S25/11/JP29/PHA |  |  |  | CDC | 252 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_GDA | 11KV橋九線(JP29) 接地RY | FEEDER | S25/11/JP29/GDA |  |  |  | CDC | 253 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_79UL | 11KV橋九線(JP29) 79RY U/L | FEEDER | S25/11/JP29/79UL |  |  |  | CDC | 254 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP29 | 橋九線(JP29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_ADJ | 11KV橋九線(JP29) LCO分流器 U/L | FEEDER | S25/11/JP29/ADJ |  |  |  | CDC | 255 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP29 | JP29(11KV橋九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_CB | JP29(11KV橋九線) CB | FEEDER | S25/11/JP29/CB |  |  |  | CDC | 256 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_PHA | 11KV橋十線(JP30) 相間RY | FEEDER | S25/11/JP30/PHA |  |  |  | CDC | 257 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_GDA | 11KV橋十線(JP30) 接地RY | FEEDER | S25/11/JP30/GDA |  |  |  | CDC | 258 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_79UL | 11KV橋十線(JP30) 79RY U/L | FEEDER | S25/11/JP30/79UL |  |  |  | CDC | 259 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP30 | 橋十線(JP30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_ADJ | 11KV橋十線(JP30) LCO分流器 U/L | FEEDER | S25/11/JP30/ADJ |  |  |  | CDC | 260 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP30 | JP30(11KV橋十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_CB | JP30(11KV橋十線) CB | FEEDER | S25/11/JP30/CB |  |  |  | CDC | 261 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十一線(JP31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_PHA | 11KV橋十一線(JP31) 相間RY | FEEDER | S25/11/JP31/PHA |  |  |  | CDC | 262 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十一線(JP31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_GDA | 11KV橋十一線(JP31) 接地RY | FEEDER | S25/11/JP31/GDA |  |  |  | CDC | 263 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十一線(JP31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_79UL | 11KV橋十一線(JP31) 79RY U/L | FEEDER | S25/11/JP31/79UL |  |  |  | CDC | 264 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP31 | 橋十一線(JP31) |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_ADJ | 11KV橋十一線(JP31) LCO分流器 | FEEDER | S25/11/JP31/ADJ |  |  |  | CDC | 265 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP31 | JP31(11KV橋十一線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_CB | JP31(11KV橋十一線) CB | FEEDER | S25/11/JP31/CB |  |  |  | CDC | 266 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_PHA | 11KV橋十二線(JP32) 相間RY | FEEDER | S25/11/JP32/PHA |  |  |  | CDC | 267 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_GDA | 11KV橋十二線(JP32) 接地RY | FEEDER | S25/11/JP32/GDA |  |  |  | CDC | 268 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_79UL | 11KV橋十二線(JP32) 79RY U/L | FEEDER | S25/11/JP32/79UL |  |  |  | CDC | 269 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP32 | 橋十二線(JP32) |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_ADJ | 11KV橋十二線(JP32) LCO分流器 | FEEDER | S25/11/JP32/ADJ |  |  |  | CDC | 270 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP32 | JP32(11KV橋十二線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_CB | JP32(11KV橋十二線) CB | FEEDER | S25/11/JP32/CB |  |  |  | CDC | 271 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_PHA | 11KV橋十三線(JP33) 相間RY | FEEDER | S25/11/JP33/PHA |  |  |  | CDC | 272 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_GDA | 11KV橋十三線(JP33) 接地RY | FEEDER | S25/11/JP33/GDA |  |  |  | CDC | 273 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_79UL | 11KV橋十三線(JP33) 79RY U/L | FEEDER | S25/11/JP33/79UL |  |  |  | CDC | 274 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP33 | 橋十三線(JP33) |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_ADJ | 11KV橋十三線(JP33) LCO分流器 | FEEDER | S25/11/JP33/ADJ |  |  |  | CDC | 275 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP33 | JP33(11KV橋十三線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_CB | JP33(11KV橋十三線) CB | FEEDER | S25/11/JP33/CB |  |  |  | CDC | 276 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_PHA | 11KV橋十四線(JP34) 相間RY | FEEDER | S25/11/JP34/PHA |  |  |  | CDC | 277 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_GDA | 11KV橋十四線(JP34) 接地RY | FEEDER | S25/11/JP34/GDA |  |  |  | CDC | 278 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_79UL | 11KV橋十四線(JP34) 79RY U/L | FEEDER | S25/11/JP34/79UL |  |  |  | CDC | 279 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP34 | 橋十四線(JP34) |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_ADJ | 11KV橋十四線(JP34) LCO分流器 | FEEDER | S25/11/JP34/ADJ |  |  |  | CDC | 280 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP34 | JP34(11KV橋十四線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_CB | JP34(11KV橋十四線) CB | FEEDER | S25/11/JP34/CB |  |  |  | CDC | 281 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_PHA | 11KV橋十五線(JP35) 相間RY | FEEDER | S25/11/JP35/PHA |  |  |  | CDC | 282 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_GDA | 11KV橋十五線(JP35) 接地RY | FEEDER | S25/11/JP35/GDA |  |  |  | CDC | 283 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_79UL | 11KV橋十五線(JP35) 79RY U/L | FEEDER | S25/11/JP35/79UL |  |  |  | CDC | 284 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 11 | 11kV | JP35 | 橋十五線(JP35) |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_ADJ | 11KV橋十五線(JP35) LCO分流器 | FEEDER | S25/11/JP35/ADJ |  |  |  | CDC | 285 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S25 | 頭橋SS | 11 | 11kV | JP35 | JP35(11KV橋十五線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_CB | JP35(11KV橋十五線) CB | FEEDER | S25/11/JP35/CB |  |  |  | CDC | 286 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE2_CB | 11KV TIE2 CB | TIE | S25/11/TIE2/CB |  |  |  | CDC | 287 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE2_51A | 11KV TIE2 51RY | TIE | S25/11/TIE2/51A |  |  |  | CDC | 288 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S25/11/TIE2/51NA |  |  |  | CDC | 289 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE3_CB | 11KV TIE3 CB | TIE | S25/11/TIE3/CB |  |  |  | CDC | 290 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE3_51A | 11KV TIE3 51RY | TIE | S25/11/TIE3/51A |  |  |  | CDC | 291 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE3_51NA | 11KV TIE3 51N RY | TIE | S25/11/TIE3/51NA |  |  |  | CDC | 292 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.750_CB | 750(#1MTR) CB | DTR | S25/69/750/CB |  |  |  | CDC | 293 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.1M_CB | 1M(#1MTR) CB | DTR | S25/11/M1/CB |  |  |  | CDC | 294 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_51A | #1MTR 51RY | DTR | S25/69/750/51A |  |  |  | CDC | 295 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_51NA | #1MTR 51N RY | DTR | S25/69/750/51NA |  |  |  | CDC | 296 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S25//1MTR/51ZA |  |  |  | CDC | 297 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_87A | #1MTR 87RY | DTR | S25//1MTR/87A |  |  |  | CDC | 298 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S25//1MTR/87UL |  |  |  | CDC | 299 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S25/11/M1/51A |  |  |  | CDC | 300 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_TRA | #1MTR 重故障 | DTR | S25//1MTR/TRA |  |  |  | CDC | 301 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S25//1MTR/TRF |  |  |  | CDC | 302 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S25//1MTR/SupLocal |  |  |  | CDC | 303 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S25//1MTR/Tap Chan |  |  |  | CDC | 304 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.751_ABS | 751(#1MTR) ABS | DTR | S25/69/750/ABS1 |  |  |  | CDC | 305 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_96A | #1MTR 96P RY | DTR | S25//1MTR/96PA |  |  |  | CDC | 306 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S25//1MTR/OLTC_DLY |  |  |  | CDC | 307 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S25//1MTR/AC_Fault |  |  |  | CDC | 308 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.760_CB | 760(#2MTR) CB | DTR | S25/69/760/CB |  |  |  | CDC | 309 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.2M_CB | 2M(#2MTR) CB | DTR | S25/11/M2/CB |  |  |  | CDC | 310 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_51A | #2MTR 51RY | DTR | S25/69/760/51A |  |  |  | CDC | 311 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_51NA | #2MTR 51N RY | DTR | S25/69/760/51NA |  |  |  | CDC | 312 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S25//2MTR/51ZA |  |  |  | CDC | 313 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_87A | #2MTR 87RY | DTR | S25//2MTR/87A |  |  |  | CDC | 314 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S25//2MTR/87UL |  |  |  | CDC | 315 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-0F-04 |  | 1-56 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S25//2MTR/81AS |  |  |  | CDC | 316 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S25 | 頭橋SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S25/11/M2/51A |  |  |  | CDC | 317 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_TRA | #2MTR 重故障 | DTR | S25//2MTR/TRA |  |  |  | CDC | 318 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S25//2MTR/TRF |  |  |  | CDC | 319 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S25//2MTR/SupLocal |  |  |  | CDC | 320 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S25//2MTR/Tap Chan |  |  |  | CDC | 321 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.761_ABS | 761(#2MTR) ABS | DTR | S25/69/760/ABS1 |  |  |  | CDC | 322 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_96A | #2MTR 96P RY | DTR | S25//2MTR/96PA |  |  |  | CDC | 323 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S25//2MTR/OLTC_DLY |  |  |  | CDC | 324 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S25//2MTR/AC_Fault |  |  |  | CDC | 325 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.770_CB | 770(#3MTR) CB | DTR | S25/69/770/CB |  |  |  | CDC | 326 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 3MA | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3MA_CB | 3MA(#3MTR) CB | DTR | S25/11/M3A/CB |  |  |  | CDC | 327 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 3MB | #3MTR |  | CB | [17 empty] | 1-03-00 |  | 1-5A | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3MB_CB | 3MB(#3MTR) CB | DTR | S25/11/M3B/CB |  |  |  | CDC | 328 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_51A | #3MTR 51RY | DTR | S25/69/770/51A |  |  |  | CDC | 329 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_51NA | #3MTR 51N RY | DTR | S25/69/770/51NA |  |  |  | CDC | 330 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S25//3MTR/51ZA |  |  |  | CDC | 331 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_87A | #3MTR 87RY | DTR | S25//3MTR/87A |  |  |  | CDC | 332 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S25//3MTR/87UL |  |  |  | CDC | 333 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 0 |  | 3MA | #3MTR二次側(3MA) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3MA_51A | #3MTR二次側(3MA) 51RY | DTR | S25/11/M3A/51A |  |  |  | CDC | 334 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MB | #3MTR二次側(3MB) |  | 51A | [17 empty] | 1-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3MB_51A | #3MTR二次側(3MB) 51RY | DTR | S25/11/M3B/51A |  |  |  | CDC | 335 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_TRA | #3MTR 重故障 | DTR | S25//3MTR/TRA |  |  |  | CDC | 336 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S25//3MTR/TRF |  |  |  | CDC | 337 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S25//3MTR/SupLocal |  |  |  | CDC | 338 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S25//3MTR/Tap Chan |  |  |  | CDC | 339 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.771_ABS | 771(#3MTR) ABS | DTR | S25/69/770/ABS1 |  |  |  | CDC | 340 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_96A | #3MTR 96P RY | DTR | S25//3MTR/96PA |  |  |  | CDC | 341 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S25//3MTR/OLTC_DLY |  |  |  | CDC | 342 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S25//3MTR/AC_Fault |  |  |  | CDC | 343 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_CB | 210(11KV #1SC) CB | SC | S25/11/210/CB |  |  |  | CDC | 344 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S25/11/210/Tap Chan |  |  |  | CDC | 345 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_SCA | 11KV #1SC 51,51N RY | SC | S25/11/210/SCA |  |  |  | CDC | 346 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S25/11/210/UVA |  |  |  | CDC | 347 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_CB | 220(11KV #2SC) CB | SC | S25/11/220/CB |  |  |  | CDC | 348 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S25/11/220/Tap Chan |  |  |  | CDC | 349 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_SCA | 11KV #2SC 51,51N RY | SC | S25/11/220/SCA |  |  |  | CDC | 350 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S25/11/220/UVA |  |  |  | CDC | 351 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_CB | 230(11KV #3SC) CB | SC | S25/11/230/CB |  |  |  | CDC | 352 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S25/11/230/Tap Chan |  |  |  | CDC | 353 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_SCA | 11KV #3SC 51,51N RY | SC | S25/11/230/SCA |  |  |  | CDC | 354 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S25/11/230/UVA |  |  |  | CDC | 355 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 頭橋SS.810_CB | 810(69KV #1SC) CB | SC | S25/69/810/CB |  |  |  | CDC | 356 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.811_ABS | 811(69KV #1SC) ABS | SC | S25/69/810/ABS1 |  |  |  | CDC | 357 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.810_SCA | 69KV #1SC 51,51N RY | SC | S25/69/810/SCA |  |  |  | CDC | 358 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.810_OUVA | 69KV #1SC 27,59RY | SC | S25/69/810/UVA |  |  |  | CDC | 359 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 頭橋SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S25/69/1BUS/BUS_VUA |  |  |  | CDC | 360 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S25/11/ComPoint/CBA |  |  |  | CDC | 361 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S25/11/ComPoint/CBF |  |  |  | CDC | 362 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S25/69/ComPoint/ABS_89A |  |  |  | CDC | 363 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S25/69/ComPoint/CBA |  |  |  | CDC | 364 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S25/69/ComPoint/CBF |  |  |  | CDC | 365 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S25/0/RTU/RTU_R_L |  |  |  | CDC | 366 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S25 | 頭橋SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TEST_CB | TEST CB | OTHER | S25/0/RTU/Test_CB |  |  |  | CDC | 367 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.火災警報(1) | [頭橋]火警 | OTHER | S25/0/StaDev/Fire1 |  |  |  | CDC | 368 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S25/0/StaDev/OPA |  |  |  | CDC | 369 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.其他重故障 | 變電所內其他重故障 | OTHER | S25/0/StaDev/PSA |  |  |  | CDC | 370 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S25/0/StaDev/PSF |  |  |  | CDC | 371 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S25/0/StaDev/STUV |  |  |  | CDC | 372 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S25/0/StaDev/CHG1 |  |  |  | CDC | 373 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.直流電源DCA | 直流電源故障警報 | OTHER | S25/0/StaDev/DCA |  |  |  | CDC | 374 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S25/0/StaDev/DCE |  |  |  | CDC | 375 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S25/0/StaDev/OilLeak |  |  |  | CDC | 376 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S25/0/StaDev/6A5Other |  |  |  | CDC | 377 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S25/0/StaDev/7A5Other |  |  |  | CDC | 378 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S25/0/StaDev/8A5Other |  |  |  | CDC | 379 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S25/0/StaDev/CHG2 |  |  |  | CDC | 380 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S25/0/StaDev/CommACF |  |  |  | CDC | 381 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S25/0/StaDev/Door1 |  |  |  | CDC | 382 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S25/0/StaDev/Door2 |  |  |  | CDC | 383 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S25/0/StaDev/Door3 |  |  |  | CDC | 384 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S25 | 頭橋SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.開關場照明(A) | 所內開關場照明 | OTHER | S25/0/StaDev/Lights1 |  |  |  | CDC | 385 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S25 | 頭橋SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.開關場照明(B) | 路燈照明 | OTHER | S25/0/StaDev/Lights2 |  |  |  | CDC | 386 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S25 | 頭橋SS | 0 |  |  |  |  | #1MAIN51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MAIN51NA | #1MAIN51NA | OTHER | S25/11/M1/51NA |  |  |  | CDC | 387 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #2MAIN51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MAIN51NA | #2MAIN51NA | OTHER | S25/11/M2A/51NA |  |  |  | CDC | 388 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MAIN51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MAIN51NA | #3MAIN51NA | OTHER | S25/11/M3A/51NA |  |  |  | CDC | 389 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MBIN51NA | [17 empty] | 1-04-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MBIN51NA | #3MBIN51NA | OTHER | S25/11/M3B/51NA |  |  |  | CDC | 390 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 69KVBUS#2VUA | [17 empty] | 1-31-14 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER | S25/69/2BUS/BUS_VUA |  |  |  | CDC | 391 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.69KVSC警報 | 69KVSC警報 | OTHER | S25/69/810/60A |  |  |  | CDC | 392 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | MCSG火警 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.MCSG火警 | MCSG火警 | OTHER | S25/0/StaDev/Fire2 |  |  |  | CDC | 393 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | MCSG系統故障 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.MCSG系統故障 | MCSG系統故障 | OTHER | S25/0/StaDev/1A5Other |  |  |  | CDC | 394 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.主變火警 | 主變火警 | OTHER | S25/0/StaDev/Fire |  |  |  | CDC | 395 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.安全監控 | 安全監控 | OTHER | S25/0/StaDev/Burglar |  |  |  | CDC | 396 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.門禁 | 大門側門 | OTHER | S25/0/StaDev/Door |  |  |  | CDC | 397 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.細水霧故障 | 細水霧故障 | OTHER | S25/0/StaDev/2A5Other |  |  |  | CDC | 398 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S25/0/StaDev/3A5Other |  |  |  | CDC | 399 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.維護運轉警報 | 維護運轉警報 | OTHER | S25/0/StaDev/4A5Other |  |  |  | CDC | 400 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 1MT | #1MT |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR63Q | #1MT ULTC電驛動作 | OTHER | S25//1MTR/63Q |  |  |  | CDC | 401 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR96B1 | #1MT撲氣電驛警報 | OTHER | S25//1MTR/96B1 |  |  |  | CDC | 402 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR96B2 | #1MT撲氣電驛動作 | OTHER | S25//1MTR/96B2 |  |  |  | CDC | 403 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR96D | #1MT放壓電驛動作 | OTHER | S25//1MTR/96D |  |  |  | CDC | 404 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR96P | #1MT突壓電驛動作 | OTHER | S25//1MTR/96P |  |  |  | CDC | 405 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S25//2MTR/63Q |  |  |  | CDC | 406 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S25//2MTR/96B1 |  |  |  | CDC | 407 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S25//2MTR/96B2 |  |  |  | CDC | 408 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S25//2MTR/96D |  |  |  | CDC | 409 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S25//2MTR/96P |  |  |  | CDC | 410 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | #3MTR63Q | [17 empty] | 1-19-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER | S25//3MTR/63Q |  |  |  | CDC | 411 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MTR96B1 | [17 empty] | 1-19-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER | S25//3MTR/96B1 |  |  |  | CDC | 412 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MTR96B2 | [17 empty] | 1-19-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER | S25//3MTR/96B2 |  |  |  | CDC | 413 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MTR96D | [17 empty] | 1-19-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER | S25//3MTR/96D |  |  |  | CDC | 414 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | #3MTR96P | [17 empty] | 1-19-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER | S25//3MTR/96P |  |  |  | CDC | 415 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-12-01 |  | 1-69 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S25/11/M3A/81AS |  |  |  | CDC | 416 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S25 | 頭橋SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS2_2 | [8 empty] | 頭橋SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S25//1MTR/81AS |  |  |  | CDC | 417 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S25 | 頭橋SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-37-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S25/0/StaDev/9A5Other |  |  |  | CDC | 418 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S25/0/StaDev/Lights3 |  |  |  | CDC | 419 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-14 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.開關場水位警報 | 開關場水位警報 | OTHER | S25/0/StaDev/Water1 |  |  |  | CDC | 420 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.630_87A | 嘉太線(630) 87RY | LINE69 | S25/69/630/85A |  |  |  | CDC | 421 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | CFA | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 頭橋SS.630_CFA | 嘉太線(630) 通訊故障 | LINE69 | S25/69/630/87CFA |  |  |  | CDC | 422 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.630_87UL | 嘉太線(630) 87RY U/L | LINE69 | S25/69/630/85UL |  |  |  | CDC | 423 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 0 |  | 630 | 嘉太線(630) |  | RYFA | [17 empty] | 1-37-09 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.630_RYFA | 630 嘉太線IED警報 | OTHER | S25/69/630/RYFA |  |  |  | CDC | 424 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 頭橋SS.650_87A | 秀林線(650) 87RY | LINE69 | S25/69/650/85A |  |  |  | CDC | 425 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | CFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 頭橋SS.650_CFA | 秀林線(650) 通訊故障 | LINE69 | S25/69/650/87CFA |  |  |  | CDC | 426 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 頭橋SS.650_87UL | 秀林線(650) 87RY U/L | LINE69 | S25/69/650/85UL |  |  |  | CDC | 427 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S25 | 頭橋SS | 0 |  | 650 | 秀林線(650) |  | RYFA | [17 empty] | 1-37-10 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.650_RYFA | 650 秀林線IED警報 | OTHER | S25/69/650/RYFA |  |  |  | CDC | 428 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S25/11/ComPoint/IRFA |  |  |  | CDC | 429 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S25/0/StaDev/Water2 |  |  |  | CDC | 430 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | PT-2 | PT-2 |  | 51A | [17 empty] | 1-05-07 | [7 empty] | DDCS2_1 | [8 empty] | 頭橋SS.PT-2_51A | PT-2 51RY | OTHER | S25/11/2PT/51A |  |  |  | CDC | 431 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | PT-2 | PT-2 |  | 51NA | [17 empty] | 1-06-00 | [7 empty] | DDCS2_1 | [8 empty] | 頭橋SS.PT-2_51NA | PT-2 51N RY | OTHER | S25/11/2PT/51NA |  |  |  | CDC | 432 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | 490 | SSTR-2(490) |  | CB | [17 empty] | 1-04-04 |  | 1-43 | [5 empty] | DDCS2_1 | [8 empty] | 頭橋SS.490_CB | 490(SSTR-2) CB | OTHER | S25/11/490/CB |  |  |  | CDC | 433 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | SSTR-2 | SSTR-2 |  | 51A | [17 empty] | 1-05-00 | [7 empty] | DDCS2_1 | [8 empty] | 頭橋SS.SSTR-2_51A | SSTR-2 51RY | OTHER | S25/11/490/51A |  |  |  | CDC | 434 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  | SSTR-2 | SSTR-2 |  | 51NA | [17 empty] | 1-05-01 | [7 empty] | DDCS2_1 | [8 empty] | 頭橋SS.SSTR-2_51NA | SSTR-2 51N RY | OTHER | S25/11/490/51NA |  |  |  | CDC | 435 | GENERICDIPoint | SS205_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.PMA | PMA | OTHER | S25/11/ComPoint/PMA |  |  |  | CDC | 436 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋ㄧ線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋ㄧ線79LOA | 橋ㄧ線79LOA | OTHER | S25/11/JP21/LOA |  |  |  | CDC | 437 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋七線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋七線79LOA | 橋七線79LOA | OTHER | S25/11/JP27/LOA |  |  |  | CDC | 438 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋九線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋九線79LOA | 橋九線79LOA | OTHER | S25/11/JP29/LOA |  |  |  | CDC | 439 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋二線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋二線79LOA | 橋二線79LOA | OTHER | S25/11/JP22/LOA |  |  |  | CDC | 440 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋八線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋八線79LOA | 橋八線79LOA | OTHER | S25/11/JP28/LOA |  |  |  | CDC | 441 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十ㄧ線79LOA | [17 empty] | 1-3E-10 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十ㄧ線79LOA | 橋十ㄧ線79LOA | OTHER | S25/11/JP31/LOA |  |  |  | CDC | 442 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十二線79LOA | [17 empty] | 1-3E-11 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十二線79LOA | 橋十二線79LOA | OTHER | S25/11/JP32/LOA |  |  |  | CDC | 443 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十三線79LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十三線79LOA | 橋十三線79LOA | OTHER | S25/11/JP33/LOA |  |  |  | CDC | 444 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十五線79LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十五線79LOA | 橋十五線79LOA | OTHER | S25/11/JP35/LOA |  |  |  | CDC | 445 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十四線79LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十四線79LOA | 橋十四線79LOA | OTHER | S25/11/JP34/LOA |  |  |  | CDC | 446 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋十線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋十線79LOA | 橋十線79LOA | OTHER | S25/11/JP30/LOA |  |  |  | CDC | 447 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋三線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋三線79LOA | 橋三線79LOA | OTHER | S25/11/JP23/LOA |  |  |  | CDC | 448 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋五線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋五線79LOA | 橋五線79LOA | OTHER | S25/11/JP25/LOA |  |  |  | CDC | 449 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋六線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋六線79LOA | 橋六線79LOA | OTHER | S25/11/JP26/LOA |  |  |  | CDC | 450 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 0 |  |  |  |  | 橋四線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_2 | [8 empty] | 頭橋SS.橋四線79LOA | 橋四線79LOA | OTHER | S25/11/JP24/LOA |  |  |  | CDC | 451 | GENERICDIPoint | SS205_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S25 | 頭橋SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 452 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 453 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 454 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 頭橋SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 455 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.630LE | 630LE (非取樣點) | LINE69 | S25/69/630/LE0 |  |  |  |  | 456 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 630 | 嘉太線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.630BE | 630BE (非取樣點) | LINE69 | S25/69/630/BE0 |  |  |  |  | 457 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | LE0 | 650LE | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.650LE | 650LE (非取樣點) | LINE69 | S25/69/650/LE0 |  |  |  |  | 458 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 650 | 秀林線(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.650BE | 650BE (非取樣點) | LINE69 | S25/69/650/BE0 |  |  |  |  | 459 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP21 | JP21_DS |  | DS1 | JP21_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_DS | JP21_DS (非取樣點) | FEEDER | S25/11/JP21/DS |  |  |  |  | 460 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP21 | JP21_ES |  | LE0 | JP21_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP21_ES | JP21_ES (非取樣點) | FEEDER | S25/11/JP21/ES |  |  |  |  | 461 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP22 | JP22_DS |  | DS1 | JP22_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_DS | JP22_DS (非取樣點) | FEEDER | S25/11/JP22/DS |  |  |  |  | 462 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP22 | JP22_ES |  | LE0 | JP22_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP22_ES | JP22_ES (非取樣點) | FEEDER | S25/11/JP22/ES |  |  |  |  | 463 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP23 | JP23_DS |  | DS1 | JP23_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_DS | JP23_DS (非取樣點) | FEEDER | S25/11/JP23/DS |  |  |  |  | 464 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP23 | JP23_ES |  | LE0 | JP23_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP23_ES | JP23_ES (非取樣點) | FEEDER | S25/11/JP23/ES |  |  |  |  | 465 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP24 | JP24_DS |  | DS1 | JP24_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_DS | JP24_DS (非取樣點) | FEEDER | S25/11/JP24/DS |  |  |  |  | 466 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP24 | JP24_ES |  | LE0 | JP24_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP24_ES | JP24_ES (非取樣點) | FEEDER | S25/11/JP24/ES |  |  |  |  | 467 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP25 | JP25_DS |  | DS1 | JP25_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_DS | JP25_DS (非取樣點) | FEEDER | S25/11/JP25/DS |  |  |  |  | 468 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP25 | JP25_ES |  | LE0 | JP25_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP25_ES | JP25_ES (非取樣點) | FEEDER | S25/11/JP25/ES |  |  |  |  | 469 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP26 | JP26_DS |  | DS1 | JP26_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_DS | JP26_DS (非取樣點) | FEEDER | S25/11/JP26/DS |  |  |  |  | 470 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP26 | JP26_ES |  | LE0 | JP26_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP26_ES | JP26_ES (非取樣點) | FEEDER | S25/11/JP26/ES |  |  |  |  | 471 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP27 | JP27_DS |  | DS1 | JP27_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_DS | JP27_DS (非取樣點) | FEEDER | S25/11/JP27/DS |  |  |  |  | 472 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP27 | JP27_ES |  | LE0 | JP27_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP27_ES | JP27_ES (非取樣點) | FEEDER | S25/11/JP27/ES |  |  |  |  | 473 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP28 | JP28_DS |  | DS1 | JP28_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_DS | JP28_DS (非取樣點) | FEEDER | S25/11/JP28/DS |  |  |  |  | 474 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP28 | JP28_ES |  | LE0 | JP28_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP28_ES | JP28_ES (非取樣點) | FEEDER | S25/11/JP28/ES |  |  |  |  | 475 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP29 | JP29_DS |  | DS1 | JP29_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_DS | JP29_DS (非取樣點) | FEEDER | S25/11/JP29/DS |  |  |  |  | 476 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP29 | JP29_ES |  | LE0 | JP29_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP29_ES | JP29_ES (非取樣點) | FEEDER | S25/11/JP29/ES |  |  |  |  | 477 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP30 | JP30_DS |  | DS1 | JP30_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_DS | JP30_DS (非取樣點) | FEEDER | S25/11/JP30/DS |  |  |  |  | 478 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP30 | JP30_ES |  | LE0 | JP30_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP30_ES | JP30_ES (非取樣點) | FEEDER | S25/11/JP30/ES |  |  |  |  | 479 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP31 | JP31_DS |  | DS1 | JP31_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_DS | JP31_DS (非取樣點) | FEEDER | S25/11/JP31/DS |  |  |  |  | 480 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP31 | JP31_ES |  | LE0 | JP31_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP31_ES | JP31_ES (非取樣點) | FEEDER | S25/11/JP31/ES |  |  |  |  | 481 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP32 | JP32_DS |  | DS1 | JP32_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_DS | JP32_DS (非取樣點) | FEEDER | S25/11/JP32/DS |  |  |  |  | 482 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP32 | JP32_ES |  | LE0 | JP32_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP32_ES | JP32_ES (非取樣點) | FEEDER | S25/11/JP32/ES |  |  |  |  | 483 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP33 | JP33_DS |  | DS1 | JP33_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_DS | JP33_DS (非取樣點) | FEEDER | S25/11/JP33/DS |  |  |  |  | 484 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP33 | JP33_ES |  | LE0 | JP33_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP33_ES | JP33_ES (非取樣點) | FEEDER | S25/11/JP33/ES |  |  |  |  | 485 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP34 | JP34_DS |  | DS1 | JP34_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_DS | JP34_DS (非取樣點) | FEEDER | S25/11/JP34/DS |  |  |  |  | 486 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP34 | JP34_ES |  | LE0 | JP34_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP34_ES | JP34_ES (非取樣點) | FEEDER | S25/11/JP34/ES |  |  |  |  | 487 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | JP35 | JP35_DS |  | DS1 | JP35_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_DS | JP35_DS (非取樣點) | FEEDER | S25/11/JP35/DS |  |  |  |  | 488 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | JP35 | JP35_ES |  | LE0 | JP35_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.JP35_ES | JP35_ES (非取樣點) | FEEDER | S25/11/JP35/ES |  |  |  |  | 489 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S25/11/TIE2/D1 |  |  |  |  | 490 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S25/11/TIE3/D1 |  |  |  |  | 491 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.750TE | 750TE (非取樣點) | DTR | S25/69/750/TE0 |  |  |  |  | 492 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.750BE | 750BE (非取樣點) | DTR | S25/69/750/BE0 |  |  |  |  | 493 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.1M_DS | 1M_DS (非取樣點) | DTR | S25/11/M1/DS |  |  |  |  | 494 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.1M_ES | 1M_ES (非取樣點) | DTR | S25/11/M1/ES |  |  |  |  | 495 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.760TE | 760TE (非取樣點) | DTR | S25/69/760/TE0 |  |  |  |  | 496 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.760BE | 760BE (非取樣點) | DTR | S25/69/760/BE0 |  |  |  |  | 497 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.2M_DS | 2M_DS (非取樣點) | DTR | S25/11/M2/DS |  |  |  |  | 498 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.2M_ES | 2M_ES (非取樣點) | DTR | S25/11/M2/ES |  |  |  |  | 499 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.770TE | 770TE (非取樣點) | DTR | S25/69/770/TE0 |  |  |  |  | 500 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.770BE | 770BE (非取樣點) | DTR | S25/69/770/BE0 |  |  |  |  | 501 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3M_DS | 3M_DS (非取樣點) | DTR | S25/11/M3A/DS |  |  |  |  | 502 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.3M_ES | 3M_ES (非取樣點) | DTR | S25/11/M3A/ES |  |  |  |  | 503 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.210_ES | 210_ES (非取樣點) | SC | S25/11/210/ES |  |  |  |  | 504 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.211DS | 211DS (非取樣點) | SC | S25/11/210/D1 |  |  |  |  | 505 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.212DS | 212DS (非取樣點) | SC | S25/11/210/D2 |  |  |  |  | 506 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.220_ES | 220_ES (非取樣點) | SC | S25/11/220/ES |  |  |  |  | 507 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.221DS | 221DS (非取樣點) | SC | S25/11/220/D1 |  |  |  |  | 508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.222DS | 222DS (非取樣點) | SC | S25/11/220/D2 |  |  |  |  | 509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.230_ES | 230_ES (非取樣點) | SC | S25/11/230/ES |  |  |  |  | 510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 231DS | 231DS |  | 231DS | 231DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.231DS | 231DS (非取樣點) | SC | S25/11/230/D1 |  |  |  |  | 511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 232DS | 232DS |  | 232DS | 232DS | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.232DS | 232DS (非取樣點) | SC | S25/11/230/D2 |  |  |  |  | 512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810_ES | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.810_ES | 810_ES (非取樣點) | SC | S25/69/810/ES |  |  |  |  | 513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.69B1E | 69B1E (非取樣點) | BUS | S25/69/1BUS/BE1 |  |  |  |  | 514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 515 | NotelDIPoint | [38 empty] | START/STOP | STOP
S25 | 頭橋SS | 0 |  | TIE2 | TIE2_ES |  | LE0 | TIE2_ES | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | S25/11/TIE2/ES |  |  |  |  | 516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | PT-2 | PT-2_DS |  | DS1 | PT-2_DS | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.PT-2_DS | PT-2_DS (非取樣點) | OTHER | S25/11/2PT/DS |  |  |  |  | 517 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | PT-2 | PT-2_ES |  | LE0 | PT-2_ES | [24 empty] | ADCS_N | [8 empty] | 頭橋SS.PT-2_ES | PT-2_ES (非取樣點) | OTHER | S25/11/2PT/ES |  |  |  |  | 518 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S25 | 頭橋SS | 0 |  | 490 | SSTR-2(490) |  | DS1 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.491_DS | 491_DS (非取樣點) | OTHER | S25/11/490/D1 |  |  |  |  | 519 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S25 | 頭橋SS | 0 |  | 490 | SSTR-2(490) |  | E1 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 頭橋SS.491_ES | 491_ES (非取樣點) | OTHER | S25/11/490/E1 |  |  |  |  | 520 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo