## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S26 | 後湖SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV #1BUS | KV | 一號 BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S26_A1 | [8 empty] | 後湖SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S26 | 後湖SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 MTR | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | aba | B2/S26_D1 | [8 empty] | 後湖SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S26 | 後湖SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2MTR | KV | 二號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aaa | B2/S26_D1 | [8 empty] | 後湖SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S26 | 後湖SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaeb | B2/S26_A1 | [8 empty] | 後湖SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 5 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-13 |  |  | 69KV #1BUS | 6VUA | 69KV BUS衡相監視警報 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 6 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-14 |  |  | SPARE | 6VUA | 69KV BUS衡相監視警報 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 610 | MW | 嘉義後湖線 有效電力 | MW_-144_144(-2000_2000) |  | B2/S26_A1 | [8 empty] | 後湖SS.610_MW | 嘉義線 MW | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 610 | MVAR | 嘉義後湖線 無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S26_A1 | [8 empty] | 後湖SS.610_MVAR | 嘉義線 MVAR | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 69KV 610 | MWH (+) | 610 嘉義後湖線 瓦時計量值 |  |  | B2/S26_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 10 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 620 | MW | 後湖博愛線 有效電力 | MW_-120_120(-2000_2000) |  | B2/S26_A1 | [8 empty] | 後湖SS.620_MW | 博愛線 MW | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 620 | MVAR | 後湖博愛線 無效電力 | MVAR_-120_120(-2000_2000) |  | B2/S26_A1 | [8 empty] | 後湖SS.620_MVAR | 博愛線 MVAR | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 69KV 620 | MWH (+) | 620 後湖博愛線 瓦時計量值 |  |  | B2/S26_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 13 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 610 | PHA | 嘉義後湖線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610_PHA | 嘉義線(610) 相間RY | LINE69 |  |  |  |  | CDC | 14 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 610 | GDA | 嘉義後湖線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610_GDA | 嘉義線(610) 接地RY | LINE69 |  |  |  |  | CDC | 15 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 610 | 87A | 嘉義後湖線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610_87A | 嘉義線(610) 87RY | LINE69 |  |  |  |  | CDC | 16 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0533 |  |  | 1-32-01 |  |  | 610 | 174A | 嘉義後湖線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610_87CFA | 嘉義線(610)87RY通訊故障 | LINE69 |  |  |  |  | CDC | 17 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-02 |  |  | 620 | PHA | 後湖博愛線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620_PHA | 博愛線(620) 相間RY | LINE69 |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-03 |  |  | 620 | GDA | 後湖博愛線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620_GDA | 博愛線(620) 接地RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-01 |  |  | 620 | 85A | 後湖博愛線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620_87A | 博愛線(620) 87RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0537 |  |  | 1-32-05 |  |  | 620 | 374A | 後湖博愛線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620_74A | 博愛線(620) 74RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0532 |  | 0010 | 1-32-00 |  | 1-09 | 610 | 185S U/L | 嘉義後湖線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610_87UL | 嘉義線(610) 87RY U/L | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0536 |  | 0012 | 1-32-04 |  | 1-0B | 620 | 385S U/L | 後湖博愛線 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620_87UL | 博愛線(620) 87RY U/L | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/P05S26/T2 |  |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 610 | CB ON/OFF | 嘉義後湖線 |  | aaca | B2/S26_A1 | [8 empty] | 後湖SS.610_CB | 610(嘉義線) CB | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L/S26S23/T1 |  |  | 0075 |  | 0004 | 1-09-00 |  | 1-03 | 620 | CB ON/OFF | 後湖博愛線 |  | aabd | B2/S26_A1 | [8 empty] | 後湖SS.620_CB | 620(博愛線) CB | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | ABS1 | 611 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 637 | 0019 | 1-38-08 | 1-38-09 | 1-12 | 611 | ABS ON | 嘉義後湖線 BUS側 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.611_ABS | 611(嘉義線) ABS | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | ABS2 | 612 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0638 | 639 | 0020 | 1-38-10 | 1-38-11 | 1-13 | 612 | ABS ON | 嘉義後湖線 線路側 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.612_ABS | 612(嘉義線) ABS | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 | 0025 | 1-39-04 | 1-39-05 | 1-18 | 621 | ABS ON | 後湖博愛線 BUS側 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.621_ABS | 621(博愛線) ABS | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 | 0026 | 1-39-06 | 1-39-07 | 1-19 | 622 | ABS ON | 後湖博愛線 線路側 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.622_ABS | 622(博愛線) ABS | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0640 | 641 | 0021 | 1-38-12 | 1-38-13 | 1-14 | 612E | ABS ON | 嘉義後湖線 接地組 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.612E_ES | 612E(嘉義線) ES | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_A1 | [8 empty] | 後湖SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 31 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_A1 | [8 empty] | 後湖SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 32 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0652 | 653 | 0027 | 1-39-08 | 1-39-09 | 1-1A | 622E | ABS ON | 後湖博愛線 接地組 |  |  | B2/S26_A1 | [8 empty] | 後湖SS.622E_ES | 622E(博愛線) ES | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_A1 | [8 empty] | 後湖SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 34 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_A1 | [8 empty] | 後湖SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 35 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JR21 | PHA | 後一線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR21_PHA | 11KV後ㄧ線(JR21) 相間RY | FEEDER |  |  |  |  | CDC | 36 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JR21 | GDA | 後一線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR21_GDA | 11KV後ㄧ線(JR21) 接地RY | FEEDER |  |  |  |  | CDC | 37 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0061 | 1-33-07 |  | 1-3C | JR21 | 79S U/L | 後一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR21_79UL | 11KV後ㄧ線(JR21) 79RY U/L | FEEDER |  |  |  |  | CDC | 38 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0596 |  | 0113 | 1-36-00 |  | 1-70 | JR21 | ADJ(U/L) | 後一線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR21_ADJ | 11KV後ㄧ線(JR21) LCO分流器 | FEEDER |  |  |  |  | CDC | 39 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-03 |  |  | JR22 | PHA | 後二線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR22_PHA | 11KV後二線(JR22) 相間RY | FEEDER |  |  |  |  | CDC | 40 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JR22 | GDA | 後二線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR22_GDA | 11KV後二線(JR22) 接地RY | FEEDER |  |  |  |  | CDC | 41 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0062 | 1-33-08 |  | 1-3D | JR22 | 79S U/L | 後二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR22_79UL | 11KV後二線(JR22) 79RY U/L | FEEDER |  |  |  |  | CDC | 42 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0597 |  | 0114 | 1-36-01 |  | 1-71 | JR22 | ADJ(U/L) | 後二線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR22_ADJ | 11KV後二線(JR22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 43 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JR23 | PHA | 後三線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR23_PHA | 11KV後三線(JR23) 相間RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0D-06 |  |  | JR23 | GDA | 後三線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR23_GDA | 11KV後三線(JR23) 接地RY | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0557 |  | 0063 | 1-33-09 |  | 1-3E | JR23 | 79S U/L | 後三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR23_79UL | 11KV後三線(JR23) 79RY U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0598 |  | 0115 | 1-36-02 |  | 1-72 | JR23 | ADJ(U/L) | 後三線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR23_ADJ | 11KV後三線(JR23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | JR24 | PHA | 後四線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR24_PHA | 11KV後四線(JR24) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | JR24 | GDA | 後四線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR24_GDA | 11KV後四線(JR24) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0064 | 1-33-10 |  | 1-3F | JR24 | 79S U/L | 後四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR24_79UL | 11KV後四線(JR24) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0599 |  | 0116 | 1-36-03 |  | 1-73 | JR24 | ADJ(U/L) | 後四線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR24_ADJ | 11KV後四線(JR24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-01 |  |  | JR25 | PHA | 後五線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR25_PHA | 11KV後五線(JR25) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | JR25 | GDA | 後五線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR25_GDA | 11KV後五線(JR25) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  | 0065 | 1-33-11 |  | 1-40 | JR25 | 79S U/L | 後五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR25_79UL | 11KV後五線(JR25) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0600 |  | 0117 | 1-36-04 |  | 1-74 | JR25 | ADJ(U/L) | 後五線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR25_ADJ | 11KV後五線(JR25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JR26 | PHA | 後六線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR26_PHA | 11KV後六線(JR26) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | JR26 | GDA | 後六線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR26_GDA | 11KV後六線(JR26) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0571 |  | 0082 | 1-34-07 |  | 1-51 | JR26 | 79S U/L | 後六線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR26_79UL | 11KV後六線(JR26) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0601 |  | 0118 | 1-36-05 |  | 1-75 | JR26 | ADJ(U/L) | 後六線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR26_ADJ | 11KV後六線(JR26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | JR27 | PHA | 後七線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR27_PHA | 11KV後七線(JR27) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JR27 | GDA | 後七線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR27_GDA | 11KV後七線(JR27) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0572 |  | 0083 | 1-34-08 |  | 1-52 | JR27 | 79S U/L | 後七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR27_79UL | 11KV後七線(JR27) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0602 |  | 0119 | 1-36-06 |  | 1-76 | JR27 | ADJ(U/L) | 後七線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR27_ADJ | 11KV後七線(JR27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | JR28 | PHA | 後八線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR28_PHA | 11KV後八線(JR28) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | JR28 | GDA | 後八線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR28_GDA | 11KV後八線(JR28) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0573 |  | 0084 | 1-34-09 |  | 1-53 | JR28 | 79S U/L | 後八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR28_79UL | 11KV後八線(JR28) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0603 |  | 0120 | 1-36-07 |  | 1-77 | JR28 | ADJ(U/L) | 後八線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR28_ADJ | 11KV後八線(JR28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JR29 | PHA | 後九線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR29_PHA | 11KV後九線(JR29) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | JR29 | GDA | 後九線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR29_GDA | 11KV後九線(JR29) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  | 0085 | 1-34-10 |  | 1-54 | JR29 | 79S U/L | 後九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR29_79UL | 11KV後九線(JR29) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0604 |  | 0121 | 1-36-08 |  | 1-78 | JR29 | ADJ(U/L) | 後九線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR29_ADJ | 11KV後九線(JR29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | JR30 | PHA | 後十線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR30_PHA | 11KV後十線(JR30) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JR30 | GDA | 後十線 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR30_GDA | 11KV後十線(JR30) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0575 |  | 0086 | 1-34-11 |  | 1-55 | JR30 | 79S U/L | 後十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR30_79UL | 11KV後十線(JR30) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0605 |  | 0122 | 1-36-09 |  | 1-79 | JR30 | ADJ(U/L) | 後十線分流器(使用 / 閉鎖)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.JR30_ADJ | 11KV後十線(JR30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JR21/T1 |  |  | 0099 |  | 0053 | 1-0C-00 |  | 1-34 | JR21 | CB ON/OFF | 後一線 11KV |  | abab | B2/S26_D1 | [8 empty] | 後湖SS.JR21_CB | JR21(11KV後ㄧ線) CB | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR21_DS | JR21_DS (非取樣點) | FEEDER | [5 empty] | 77 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR21_ES | JR21_ES (非取樣點) | FEEDER | [5 empty] | 78 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JR22/T1 |  |  | 0100 |  | 0054 | 1-0C-01 |  | 1-35 | JR22 | CB ON/OFF | 後二線 11KV |  | abbb | B2/S26_D1 | [8 empty] | 後湖SS.JR22_CB | JR22(11KV後二線) CB | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR22_DS | JR22_DS (非取樣點) | FEEDER | [5 empty] | 80 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR22_ES | JR22_ES (非取樣點) | FEEDER | [5 empty] | 81 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JR23/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | JR23 | CB ON/OFF | 後三線 11KV |  | abcb | B2/S26_D1 | [8 empty] | 後湖SS.JR23_CB | JR23(11KV後三線) CB | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR23_DS | JR23_DS (非取樣點) | FEEDER | [5 empty] | 83 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR23_ES | JR23_ES (非取樣點) | FEEDER | [5 empty] | 84 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JR24/T1 |  |  | 0102 |  | 0056 | 1-0C-03 |  | 1-37 | JR24 | CB ON/OFF | 後四線 11KV |  | abeb | B2/S26_D1 | [8 empty] | 後湖SS.JR24_CB | JR24(11KV後四線) CB | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR24_DS | JR24_DS (非取樣點) | FEEDER | [5 empty] | 86 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR24_ES | JR24_ES (非取樣點) | FEEDER | [5 empty] | 87 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | L/JR25/T1 |  |  | 0103 |  | 0057 | 1-0C-04 |  | 1-38 | JR25 | CB ON/OFF | 後五線 11KV |  | abfb | B2/S26_D1 | [8 empty] | 後湖SS.JR25_CB | JR25(11KV後五線) CB | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR25_DS | JR25_DS (非取樣點) | FEEDER | [5 empty] | 89 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR25_ES | JR25_ES (非取樣點) | FEEDER | [5 empty] | 90 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JR26/T1 |  |  | 0121 |  | 0074 | 1-0E-06 |  | 1-49 | JR26 | CB ON/OFF | 後六線 11KV |  | aahb | B2/S26_D1 | [8 empty] | 後湖SS.JR26_CB | JR26(11KV後六線) CB | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR26_DS | JR26_DS (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR26_ES | JR26_ES (非取樣點) | FEEDER | [5 empty] | 93 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JR27/T1 |  |  | 0122 |  | 0075 | 1-0E-07 |  | 1-4A | JR27 | CB ON/OFF | 後七線 11KV |  | aagb | B2/S26_D1 | [8 empty] | 後湖SS.JR27_CB | JR27(11KV後七線) CB | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR27_DS | JR27_DS (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR27_ES | JR27_ES (非取樣點) | FEEDER | [5 empty] | 96 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JR28/T1 |  |  | 0123 |  | 0076 | 1-0F-00 |  | 1-4B | JR28 | CB ON/OFF | 後八線 11KV |  | aafb | B2/S26_D1 | [8 empty] | 後湖SS.JR28_CB | JR28(11KV後八線) CB | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR28_DS | JR28_DS (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR28_ES | JR28_ES (非取樣點) | FEEDER | [5 empty] | 99 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JR29/T1 |  |  | 0124 |  | 0077 | 1-0F-01 |  | 1-4C | JR29 | CB ON/OFF | 後九線 11KV |  | aadb | B2/S26_D1 | [8 empty] | 後湖SS.JR29_CB | JR29(11KV後九線) CB | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR29_DS | JR29_DS (非取樣點) | FEEDER | [5 empty] | 101 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR29_ES | JR29_ES (非取樣點) | FEEDER | [5 empty] | 102 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | L/JR30/T1 |  |  | 0125 |  | 0078 | 1-0F-02 |  | 1-4D | JR30 | CB ON/OFF | 後十線 11KV |  | aacb | B2/S26_D1 | [8 empty] | 後湖SS.JR30_CB | JR30(11KV後十線) CB | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR30_DS | JR30_DS (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.JR30_ES | JR30_ES (非取樣點) | FEEDER | [5 empty] | 105 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BUS | B/2BUS |  |  | 0104 |  | 0051 | 1-0C-05 |  | 1-32 | #2 TIE (200) | CB ON/OFF | 二號聯絡斷路器 |  | zzzz | B2/S26_D1 | [8 empty] | 後湖SS.200TIE_CB | 200TIE(TIE) CB | TIE |  |  |  |  | CDC | 106 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | #2 TIE(200) | PHA | 二號聯絡斷路器 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.200TIE_51A | 11KV TIE(200TIE) 51RY | TIE |  |  |  |  | CDC | 107 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-04 |  |  | #2 TIE(200) | GDA | 二號聯絡斷路器 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.200TIE_51NA | 11KV TIE(200TIE) 51N RY | TIE |  |  |  |  | CDC | 108 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | TIE1(非取樣點) | Del | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | Point Empty | [7 empty] | 109 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | TIE1(非取樣點) | Del | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | Point Empty | [7 empty] | 110 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 MTR | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 111 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 MTR | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 112 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 MTR | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 113 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 MTR | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 114 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 MTR | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 115 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2MTR | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 116 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2MTR | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 117 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2MTR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 118 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2MTR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 119 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2MTR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 120 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 121 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 122 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0058 | 1-9B |  | 1-39 | #1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 123 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1.MTR | KWH | 一號主變 瓦時計量值 |  |  | B1/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 124 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1.MTR | MVARH (+) | 一號主變 乏時計量值 |  |  | B1/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 125 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 126 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 127 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0079 | 1-BF |  | 1-4E | #2MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 128 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2.MTR | MWH | 二號主變 瓦時計量值 |  |  | B1/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 129 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2.MTR | MVARH (+) | 二號主變 乏時計量值 |  |  | B1/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 130 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0004 |  | 0049 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aadb | B3/S26_D1 | [8 empty] | 後湖SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 131 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S26_D1 | [8 empty] | 後湖SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 132 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S26_D1 | [8 empty] | 後湖SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 133 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aaab | B3/S26_D1 | [8 empty] | 後湖SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 134 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S26_D1 | [8 empty] | 後湖SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 135 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S26_D1 | [8 empty] | 後湖SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 136 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0005 |  | 0050 | 1-00-02 |  | 1-31 | #1 MCB | CB ON/OFF | 一號主變二次側 |  | abda | B2/S26_D1 | [8 empty] | 後湖SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 137 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2MTR |  |  | 0014 |  | 0070 | 1-01-03 |  | 1-45 | #2 MCB | CB ON/OFF | 二號主變二次側 |  | aaea | B2/S26_D1 | [8 empty] | 後湖SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 138 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750 | 51A | 一號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 139 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | 750 | 51NA | 一號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 140 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | #1 MCB | 51ZA | 一號主變 51ZA RY |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 141 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | #1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 142 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-33-03 |  |  | #1 MTR | 187S U/L | 一號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 143 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | 760 | 51A | 二號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 144 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | 760 | 51NA | 二號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 145 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | #2 MCB | 51ZA | 二號主變 51Z RY |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 146 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | #2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 147 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-34-03 |  |  | #2 MTR | 287S U/L | 二號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 148 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-00-07 |  |  | #1 MCB | 51A | 一號主變二次側 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 149 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-33-00 |  |  | #1 MTR | 1TRA | 一號主變重故障警報 |  | a | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 150 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0549 |  |  | 1-33-01 |  |  | #1 MTR | 1TRF | 一號主變輕故障警報 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 151 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-33-04 |  |  | #1 MTR | R/L | 一號主變OLTC(中心 / 現場)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 152 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0059 | 1-33-05 |  | 1-3A | #1 MTR | A/M | 一號主變OLTC(自動 / 手動)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 153 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S26 | 後湖SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-01 |  |  | #2 MCB | 51A | 二號主變二次側 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 154 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-34-00 |  |  | #2 MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 155 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-34-01 |  |  | #2 MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 156 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-34-04 |  |  | #2 MTR | R/L | 二號主變OLTC(中心 / 現場)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 157 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0569 |  | 0080 | 1-34-05 |  | 1-4F | #2 MTR | A/M | 二號主變OLTC(自動 / 手動)指示 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 158 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 629 | 0043 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | #1 MTR 一號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 159 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0630 | 631 | 0044 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | #2 MTR 二號主變一次側 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 160 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 161 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 162 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | #1 MTR | 96A | 一號主變 96P RY |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 163 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-33-02 |  |  | #1 MTR | 148T | 一號主變OLTC遲滯警報 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 164 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-12 |  |  | #1 MTR | 127C | 一號主變AC電源欠壓 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 165 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 166 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | M2 | #2MTR(M2) |  | E1 | 2M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 167 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | #2 MTR | 96A | 二號主變 96P RY |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 168 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-34-02 |  |  | #2 MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 169 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-12 |  |  | #2 MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 170 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | C/1SC |  |  | 0098 |  | 0052 | 1-0B-07 |  | 1-33 | #1 SC | CB ON/OFF | 一號 SC 11KV |  | abgb | B2/S26_D1 | [8 empty] | 後湖SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 171 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0060 | 1-33-06 |  | 1-3B | #1 SC | A/M | 一號SC乏控器(自動 / 手動)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 172 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 173 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | C/2SC |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | #2 SC | CB ON/OFF | 二號 SC 11KV |  | aabb | B2/S26_D1 | [8 empty] | 後湖SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 174 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0081 | 1-34-06 |  | 1-50 | #2 SC | A/M | 二號SC乏控器(自動 / 手動)指示 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 175 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 176 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | #1 SC | SCA | 一號 SC 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 177 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-00 |  |  | #1 SC | UVA | 一號 SC 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 178 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | #2 SC | SCA | 二號 SC 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 179 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | #2 SC | UVA | 二號 SC 11KV |  |  | B2/S26_D1 | [8 empty] | 後湖SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 180 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S26_D1 | [8 empty] | 後湖SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 181 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪AI 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S26_D1 | [8 empty] | 後湖SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 182 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S26_D1 | [8 empty] | 後湖SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 183 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪AI 轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S26_D1 | [8 empty] | 後湖SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 184 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0500 |  | 0001 | 1-30-00 |  | 1-00 | TEST_CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 後湖SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 185 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(STATUS) |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 186 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-30-02 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 187 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0503 |  |  | 1-30-03 |  |  | 通訊充電機 | CHG2 (？) | 通訊充電機故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 188 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0504 |  |  | 1-30-04 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 189 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0506 |  | 0046 | 1-30-06 |  | 1-2D | 所內開關場 | FLA | 開關場照明 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 190 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0507 |  | 0047 | 1-30-07 |  | 1-2E | 所內配電盤 | FLB | 市區路燈照明(SPACE) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 191 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0508 |  |  | 1-30-08 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 192 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0509 |  |  | 1-30-09 |  |  | 充油電纜 | OPA (SPACE) | 油壓電力電纜警報(SPACE) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 193 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0510 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火災警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.火災警報(1) | [後湖]火警 | OTHER |  |  |  |  | CDC | 194 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0512 |  |  | 1-30-12 |  |  | 變電所內 | PSF (SPACE) | 所內其他輕故障警報(SPACE) |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 195 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-13 |  |  | 變電所內 | PSA (SPACE) | 所內其他重故障警報(SPACE) |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 196 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-14 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 197 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0515 |  |  | 1-30-15 |  |  | 洩油池幫 | OWF | 洩油池幫警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 198 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0521 |  |  | 1-31-05 |  |  | 門禁警報(1) |  | 無人化門禁警報(1) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 199 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0522 |  |  | 1-31-06 |  |  | 門禁警報(2) |  | 無人化門禁警報(2) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 200 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0523 |  |  | 1-31-07 |  |  | 門禁警報(3) |  | 無人化門禁警報(3) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 201 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0525 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 | 6CBF | 69KV CB 輕警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 202 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-31-10 |  |  | 69KV CB 重故障 | 6CBA | 69KV CB 重警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 203 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | ComPoint |  |  | CBF |  | B2 | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0527 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 | 1CBF | 11KV CB NFB跳脫警報 |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 204 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | ComPoint |  |  | CBA |  | B2 | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-12 |  |  | 11KV CB 重故障 | 1CBA | 11KV CB NFB跳脫警報 |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER |  |  |  |  | CDC | 205 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-37-00 |  |  | 光纖通訊系統 | ACFA | 通訊設備AC故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 206 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0613 |  |  | 1-37-01 |  |  | 光纖通訊系統 | OLTMA | 通訊設備光纖主故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 207 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0614 |  |  | 1-37-02 |  |  | 光纖通訊系統 | OLTNA | 通訊設備光纖次故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 208 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 通訊PCM警報 |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-37-03 |  |  | 光纖通訊系統 | PCMA | 博碼調變器故障 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 209 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Door | (大門側門) |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-30-05 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.門禁 | (大門側門) | OTHER |  |  |  |  | CDC | 210 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0511 |  |  | 1-30-11 |  |  | 安全監控 | SUPA (SPACE) | 所內安全監控(SPACE) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 211 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Fire2 | MCSG火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-31-00 |  |  | 防火警報(1) | FMG警報 | 無人化防火警報(1) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.MCSG火警 | MCSG火警 | OTHER |  |  |  |  | CDC | 212 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | MCSG_89A | MCSG系統故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0517 |  |  | 1-31-01 |  |  | 防火警報(2) | FMG故障 | 無人化防火警報(2) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.MCSG系統故障 | MCSG系統故障 | OTHER |  |  |  |  | CDC | 213 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | ComPoint |  |  | SCA | SC警報 | Element | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-31-08 |  |  | 69KV SC |  | 69KV SC 警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.69KV_SC警報 | 69KV SC警報 | OTHER |  |  |  |  | CDC | 214 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.69KV_ABS_89A | 69KV ABS 89A | OTHER |  |  |  |  | CDC | 215 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | #1 MCB | 51NA | 一號主變二次側 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.1M_51NA | 1M 51NA | OTHER |  |  |  |  | CDC | 216 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | #2 MCB | 51NA | 二號主變二次側 |  |  | B2/S26_D1 | [8 empty] | 後湖SS.2M_51NA | 2M 51NA | OTHER |  |  |  |  | CDC | 217 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Fire | 主變火警 | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-31-02 |  |  | 防盜警報(1) | FW警報 | 無人化防盜警報(1) |  |  | ELEM/S26_D1 | [8 empty] | 後湖SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 218 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0519 |  |  | 1-31-03 |  |  | 防盜警報(2) | FW故障 | 無人化防盜警報(2) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 219 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0520 |  |  | 1-31-04 |  |  | 防盜警報(3) | FW噴灑 | 無人化防盜警報(3) |  |  | B3/S26_D1 | [8 empty] | 後湖SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 220 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 維護運轉警報 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-15 |  |  | SPARE | 43 R/L | 維護運轉警報 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 221 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 數據機重置 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0595 |  | 0088 | 1-35-15 |  | 1-57 | SPARE |  |  |  |  | B3/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 222 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室溫度異常 | Element | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0616 |  |  | 1-37-04 |  |  | SPARE | 溫度異常 | 溫度異常 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER |  |  |  |  | CDC | 223 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1 MTR | 196B1 |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 224 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | SPARE | 196B2 |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 225 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1 MTR | 196D |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 226 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1 MTR | 196P |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 227 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1 MTR | 163Q |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 228 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2 MTR | 296B1 |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 229 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | SPARE | 296B2 |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 230 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2 MTR | 296D |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 231 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2 MTR | 296P |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 232 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2 MTR | 263Q |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 233 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-15 |  |  | SPARE |  |  |  |  | B2/S26_A1 | [8 empty] | 後湖SS.610嘉義線_RYFA | 610 IED警報 | OTHER |  |  |  |  | CDC | 234 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0620 |  |  | 1-37-08 |  |  | 620 | 87 CFA | 620 後湖博愛線 87CFA |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620博愛線_CFA | 620 通訊故障 | OTHER |  |  |  |  | CDC | 235 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-37-09 |  |  | 620 | RYFA | 620 後湖博愛線 RYFA |  |  | B2/S26_A1 | [8 empty] | 後湖SS.620博愛線_RYFA | 620 IED警報 | OTHER |  |  |  |  | CDC | 236 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | JR21 | VAR | 後一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線KVAR | 11KV後ㄧ線 KVAR | FEEDER |  |  |  |  | CDC | 237 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | JR21 | A1 | 後一線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線A1 | 11KV後ㄧ線 R相AMP | FEEDER |  |  |  |  | CDC | 238 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | JR21 | A2 | 後一線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線A2 | 11KV後ㄧ線 S相AMP | FEEDER |  |  |  |  | CDC | 239 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | JR21 | A3 | 後一線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線A3 | 11KV後ㄧ線 T相AMP | FEEDER |  |  |  |  | CDC | 240 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | JR21 | NA | 後一線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線A0 | 11KV後ㄧ線 N相AMP | FEEDER |  |  |  |  | CDC | 241 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JR27 | VAR | 後七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線KVAR | 11KV後七線 KVAR | FEEDER |  |  |  |  | CDC | 242 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JR27 | A1 | 後七線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線A1 | 11KV後七線 R相AMP | FEEDER |  |  |  |  | CDC | 243 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JR27 | A2 | 後七線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線A2 | 11KV後七線 S相AMP | FEEDER |  |  |  |  | CDC | 244 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JR27 | A3 | 後七線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線A3 | 11KV後七線 T相AMP | FEEDER |  |  |  |  | CDC | 245 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JR27 | NA | 後七線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線A0 | 11KV後七線 N相AMP | FEEDER |  |  |  |  | CDC | 246 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JR29 | VAR | 後九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線KVAR | 11KV後九線 KVAR | FEEDER |  |  |  |  | CDC | 247 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JR29 | A1 | 後九線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線A1 | 11KV後九線 R相AMP | FEEDER |  |  |  |  | CDC | 248 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JR29 | A2 | 後九線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線A2 | 11KV後九線 S相AMP | FEEDER |  |  |  |  | CDC | 249 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JR29 | A3 | 後九線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線A3 | 11KV後九線 T相AMP | FEEDER |  |  |  |  | CDC | 250 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JR29 | NA | 後九線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線A0 | 11KV後九線 N相AMP | FEEDER |  |  |  |  | CDC | 251 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | JR22 | VAR | 後二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線KVAR | 11KV後二線 KVAR | FEEDER |  |  |  |  | CDC | 252 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | JR22 | A1 | 後二線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線A1 | 11KV後二線 R相AMP | FEEDER |  |  |  |  | CDC | 253 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | JR22 | A2 | 後二線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線A2 | 11KV後二線 S相AMP | FEEDER |  |  |  |  | CDC | 254 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | JR22 | A3 | 後二線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線A3 | 11KV後二線 T相AMP | FEEDER |  |  |  |  | CDC | 255 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | JR22 | NA | 後二線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線A0 | 11KV後二線 N相AMP | FEEDER |  |  |  |  | CDC | 256 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JR28 | VAR | 後八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線KVAR | 11KV後八線 KVAR | FEEDER |  |  |  |  | CDC | 257 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JR28 | A1 | 後八線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線A1 | 11KV後八線 R相AMP | FEEDER |  |  |  |  | CDC | 258 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JR28 | A2 | 後八線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線A2 | 11KV後八線 S相AMP | FEEDER |  |  |  |  | CDC | 259 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JR28 | A3 | 後八線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線A3 | 11KV後八線 T相AMP | FEEDER |  |  |  |  | CDC | 260 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | JR28 | NA | 後八線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線A0 | 11KV後八線 N相AMP | FEEDER |  |  |  |  | CDC | 261 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JR30 | VAR | 後十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線KVAR | 11KV後十線 KVAR | FEEDER |  |  |  |  | CDC | 262 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JR30 | A1 | 後十線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線A1 | 11KV後十線 R相AMP | FEEDER |  |  |  |  | CDC | 263 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JR30 | A2 | 後十線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線A2 | 11KV後十線 S相AMP | FEEDER |  |  |  |  | CDC | 264 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JR30 | A3 | 後十線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線A3 | 11KV後十線 T相AMP | FEEDER |  |  |  |  | CDC | 265 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JR30 | NA | 後十線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線A0 | 11KV後十線 N相AMP | FEEDER |  |  |  |  | CDC | 266 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | JR23 | VAR | 後三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線KVAR | 11KV後三線 KVAR | FEEDER |  |  |  |  | CDC | 267 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | JR23 | A1 | 後三線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線A1 | 11KV後三線 R相AMP | FEEDER |  |  |  |  | CDC | 268 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | JR23 | A2 | 後三線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線A2 | 11KV後三線 S相AMP | FEEDER |  |  |  |  | CDC | 269 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | JR23 | A3 | 後三線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線A3 | 11KV後三線 T相AMP | FEEDER |  |  |  |  | CDC | 270 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | JR23 | NA | 後三線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線A0 | 11KV後三線 N相AMP | FEEDER |  |  |  |  | CDC | 271 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | JR25 | VAR | 後五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線KVAR | 11KV後五線 KVAR | FEEDER |  |  |  |  | CDC | 272 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | JR25 | A1 | 後五線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線A1 | 11KV後五線 R相AMP | FEEDER |  |  |  |  | CDC | 273 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | JR25 | A2 | 後五線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線A2 | 11KV後五線 S相AMP | FEEDER |  |  |  |  | CDC | 274 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JR25 | A3 | 後五線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線A3 | 11KV後五線 T相AMP | FEEDER |  |  |  |  | CDC | 275 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | JR25 | NA | 後五線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線A0 | 11KV後五線 N相AMP | FEEDER |  |  |  |  | CDC | 276 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | JR26 | VAR | 後六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線KVAR | 11KV後六線 KVAR | FEEDER |  |  |  |  | CDC | 277 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JR26 | A1 | 後六線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線A1 | 11KV後六線 R相AMP | FEEDER |  |  |  |  | CDC | 278 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JR26 | A2 | 後六線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線A2 | 11KV後六線 S相AMP | FEEDER |  |  |  |  | CDC | 279 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JR26 | A3 | 後六線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線A3 | 11KV後六線 T相AMP | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | JR26 | NA | 後六線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線A0 | 11KV後六線 N相AMP | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | JR24 | VAR | 後四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線KVAR | 11KV後四線 KVAR | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | JR24 | A1 | 後四線R相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線A1 | 11KV後四線 R相AMP | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | JR24 | A2 | 後四線S相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線A2 | 11KV後四線 S相AMP | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | JR24 | A3 | 後四線T相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線A3 | 11KV後四線 T相AMP | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | JR24 | NA | 後四線零相電流 | A_-500_500(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線A0 | 11KV後四線 N相AMP | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 充電機 | DC-V | 配電盤 "MAIN" NFB電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S26_D1 | [8 empty] | 後湖SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #2 TIE (200) | A1 | 二號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 288 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #2 TIE (200) | A2 | 二號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 289 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #2 TIE (200) | A3 | 二號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S26_D1 | [8 empty] | 後湖SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 290 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  | 0066 | 1-0C-06 |  | 1-41 | SPARE | 81A | 一號低頻電驛(跳脫#1 MCB) |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 291 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  | 0087 | 1-0F-04 |  | 1-56 | SPARE |  |  |  |  | B1/S26_D1 | [8 empty] | 後湖SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | [5 empty] | 292 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Lights3 | 路燈電源監視 | INSERT | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0619 |  |  | 1-37-07 |  |  | SPARE |  |  |  |  | B3/S26_D1 | [8 empty] | 後湖SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 293 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Water1 | 開關場水位警報 | INSERT | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0626 |  |  | 1-37-14 |  |  | SPARE |  | 水位警報開關 |  |  | B3/S26_D1 | [8 empty] | 後湖SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 294 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/1SSTR |  |  | 0039 |  | 0048 | 1-04-04 |  | 1-2F | #1 SSTR(390) | CB | SSTR-1 CB 52AS |  | abhb | B2/S26_D1 | [8 empty] | 後湖SS.390_CB | 390(SSTR-1) CB | OTHER | [5 empty] | 295 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-04-05 |  |  | #1 SSTR(390) | 51A | SSTR-1 CB PHA |  |  | B2/S26_D1 | [8 empty] | 後湖SS.SSTR-1_51A | SSTR-1 51RY | OTHER | [5 empty] | 296 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-04-06 |  |  | #1 SSTR(390) | 51NA | SSTR-1 CB GDA |  |  | B2/S26_D1 | [8 empty] | 後湖SS.SSTR-1_51NA | SSTR-1 51N RY | OTHER | [5 empty] | 297 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0755 |  |  | 1-3F-15 |  |  | RYFA | 11KV IEDA |  |  |  | B3/S26_D1 | [8 empty] | 後湖SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 298 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0724 |  |  | 1-3E-00 |  |  | F1 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後ㄧ線79LOA | 後ㄧ線79LOA | OTHER | [5 empty] | 299 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0725 |  |  | 1-3E-01 |  |  | F2 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後二線79LOA | 後二線79LOA | OTHER | [5 empty] | 300 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0726 |  |  | 1-3E-02 |  |  | F3 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後三線79LOA | 後三線79LOA | OTHER | [5 empty] | 301 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0727 |  |  | 1-3E-03 |  |  | F4 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後四線79LOA | 後四線79LOA | OTHER | [5 empty] | 302 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0728 |  |  | 1-3E-04 |  |  | F5 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後五線79LOA | 後五線79LOA | OTHER | [5 empty] | 303 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0729 |  |  | 1-3E-05 |  |  | F6 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後六線79LOA | 後六線79LOA | OTHER | [5 empty] | 304 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0730 |  |  | 1-3E-06 |  |  | F7 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後七線79LOA | 後七線79LOA | OTHER | [5 empty] | 305 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0731 |  |  | 1-3E-07 |  |  | F8 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後八線79LOA | 後八線79LOA | OTHER | [5 empty] | 306 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0732 |  |  | 1-3E-08 |  |  | F9 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後九線79LOA | 後九線79LOA | OTHER | [5 empty] | 307 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0733 |  |  | 1-3E-09 |  |  | F10 LOA |  |  |  |  | B2/S26_D1 | [8 empty] | 後湖SS.後十線79LOA | 後十線79LOA | OTHER | [5 empty] | 308 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0754 |  |  | 1-3F-14 |  |  | Locate Empty | PMA |  |  |  | B3/S26_D1 | [8 empty] | 後湖SS.PMA | PMA | OTHER | [5 empty] | 309 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | StaDev | 所內設施 |  | Water2 | 開關場水位二段 | INSERT | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0625 |  |  | 1-37-13 |  |  | SPARE |  |  |  |  | B3/S26_D1 | [8 empty] | 後湖SS.開關場水位二段 | 開關場水位二段警報 | OTHER | [5 empty] | 310 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/2SSTR |  |  | 0043 |  | 0068 | 1-05-00 |  | 1-43 | #2 SSTR(490) | CB | SSTR-2 CB 52AS |  | aaab | B2/S26_D1 | [8 empty] | 後湖SS.490_CB | 490(SSTR-2) CB | OTHER | [5 empty] | 311 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | #2 SSTR(490) | 51A | SSTR-2 CB PHA |  |  | B2/S26_D1 | [8 empty] | 後湖SS.SSTR-2_51A | SSTR-2 51RY | OTHER | [5 empty] | 312 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 490 | #2SSTR(490) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-02 |  |  | #2 SSTR(490) | 51NA | SSTR-2 CB GDA |  |  | B2/S26_D1 | [8 empty] | 後湖SS.SSTR-2_51NA | SSTR-2 51N RY | OTHER | [5 empty] | 313 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JR21 | KWH | 後一線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 314 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JR22 | KWH | 後二線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 315 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JR23 | KWH | 後三線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 316 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JR24 | KWH | 後四線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 317 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JR25 | KWH | 後五線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 318 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | JR26 | KWH | 後六線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 319 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | JR27 | KWH | 後七線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 320 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | JR28 | KWH | 後八線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 321 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | JR29 | KWH | 後九線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 322 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | JR30 | KWH | 後十線 瓦時計量值 |  |  | B2/S26_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 323 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S26 | 後湖SS | 69 | 69kV | 2BUS | #2BUS |  | BE2 | 69B2E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_A1 | [8 empty] | 後湖SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 324 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 1PT | #1PT |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.#1PT_DS | #1PT_DS (非取樣點) | OTHER | [5 empty] | 325 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 1PT | #1PT |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.#1PT_ES | #1PT_ES (非取樣點) | OTHER | [5 empty] | 326 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391_DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.391_DS | 391_DS (非取樣點) | OTHER | [5 empty] | 327 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391_ (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.391_ES | 391_ES (非取樣點) | OTHER | [5 empty] | 328 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 11BE1 | #1BUS(11BE1) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaab | B2/S26_D1 | [8 empty] | 後湖SS.11BE1 | 11BE1 (非取樣點) | BUS | [5 empty] | 329 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 330 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 331 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | 201 (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.201ES | 201ES (非取樣點) | TIE | [5 empty] | 332 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E2 | 202 (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.202ES | 202ES (非取樣點) | TIE | [5 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | 201DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.201DS | 201DS (非取樣點) | TIE | [5 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | 202DS (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.202DS | 202DS (非取樣點) | TIE | [5 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491_DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.491_DS | 491_DS (非取樣點) | OTHER | [5 empty] | 336 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491_ (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S26_D1 | [8 empty] | 後湖SS.491_ES | 491_ES (非取樣點) | OTHER | [5 empty] | 337 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S26 | 後湖SS | 11 | 11kV | 11BE2 | #2BUS(11BE2) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/2Bus | [13 empty] | abib | B2/S26_D1 | [8 empty] | 後湖SS.11BE2 | 11BE2 (非取樣點) | BUS | [5 empty] | 338 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S26 | 後湖SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S26_D1 | [12 empty] | 後湖SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S26/69/1BUS/V
S26 | 後湖SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S26_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S26/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S26 | 後湖SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S26_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S26/11/M1/MW; OPRD2: S26/11/M2/MW; OPRD3: S26/69/610/MW; OPRD4: S26/69/620/MW
S26 | 後湖SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S26_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S26/0/CalcPoint/OPRN2_MW
S26 | 後湖SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S26_D1 | [17 empty] | none
S26 | 後湖SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S26_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S26/0/CalcPoint/OPRN1; OPRD2: S26/0/CalcPoint/OPRN2; OPRD3: S26/0/CalcPoint/PRFL_UL
S26 | 後湖SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S26_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S26/11/M1/MW; OPRD2: S26/11/M1/MVAR; OPRD3: S26/0/CalcPoint/Vbs1
S26 | 後湖SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S26_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S26/11/M2/MW; OPRD2: S26/11/M2/MVAR; OPRD3: S26/0/CalcPoint/Vbs1
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義～後湖線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S26_A1 | [12 empty] | 後湖SS.610_AMP | 嘉義線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: S26/69/610/MW; OPRD2: S26/69/610/MVAR; OPRD3: S26/0/CalcPoint/Vbs1
S26 | 後湖SS | 69 | 69kV | 620 | 後湖～博愛線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S26_A1 | [12 empty] | 後湖SS.620_AMP | 博愛線 AMP | LINE69 | AMP_CAL | C10R0880 | amp_cal | OPRD1: S26/69/620/MW; OPRD2: S26/69/620/MVAR; OPRD3: S26/0/CalcPoint/Vbs1
S26 | 後湖SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S26_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S26/11/1BUS/V
S26 | 後湖SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S26_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S26/11/2BUS/V
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S26_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 後湖SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S26/11/M1/MW; OPRD2: S26/11/M1/MVAR
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S26_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 後湖SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S26/11/M2/MW; OPRD2: S26/11/M2/MVAR
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S26_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S26//1MTR/MVA; OPRD2: 0
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S26_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S26//2MTR/MVA; OPRD2: 0
S26 | 後湖SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S26_D1 | [12 empty] | 後湖SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S26/11/M1/MW; OPRD2: S26/11/M1/MVAR
S26 | 後湖SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S26_D1 | [12 empty] | 後湖SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S26/11/M2/MW; OPRD2: S26/11/M2/MVAR
S26 | 後湖SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S26_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S26//1MTR/SupLocal; OPRD2: S26//1MTR/Tap Chan; OPRD3: NULL
S26 | 後湖SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S26_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S26//2MTR/SupLocal; OPRD2: S26//2MTR/Tap Chan; OPRD3: NULL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/1BUS/V; OPRD2: S26/11/JR21/I_R; OPRD3: S26/11/JR21/I_S; OPRD4: S26/11/JR21/I_T
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/1BUS/V; OPRD2: S26/11/JR22/I_R; OPRD3: S26/11/JR22/I_S; OPRD4: S26/11/JR22/I_T
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/1BUS/V; OPRD2: S26/11/JR23/I_R; OPRD3: S26/11/JR23/I_S; OPRD4: S26/11/JR23/I_T
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/1BUS/V; OPRD2: S26/11/JR24/I_R; OPRD3: S26/11/JR24/I_S; OPRD4: S26/11/JR24/I_T
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/1BUS/V; OPRD2: S26/11/JR25/I_R; OPRD3: S26/11/JR25/I_S; OPRD4: S26/11/JR25/I_T
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/2BUS/V; OPRD2: S26/11/JR26/I_R; OPRD3: S26/11/JR26/I_S; OPRD4: S26/11/JR26/I_T
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/2BUS/V; OPRD2: S26/11/JR27/I_R; OPRD3: S26/11/JR27/I_S; OPRD4: S26/11/JR27/I_T
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/2BUS/V; OPRD2: S26/11/JR28/I_R; OPRD3: S26/11/JR28/I_S; OPRD4: S26/11/JR28/I_T
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/2BUS/V; OPRD2: S26/11/JR29/I_R; OPRD3: S26/11/JR29/I_S; OPRD4: S26/11/JR29/I_T
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S26/11/2BUS/V; OPRD2: S26/11/JR30/I_R; OPRD3: S26/11/JR30/I_S; OPRD4: S26/11/JR30/I_T
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR21/kVA; OPRD2: S26/11/JR21/KVAR
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR22/kVA; OPRD2: S26/11/JR22/KVAR
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR23/kVA; OPRD2: S26/11/JR23/KVAR
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR24/kVA; OPRD2: S26/11/JR24/KVAR
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR25/kVA; OPRD2: S26/11/JR25/KVAR
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR26/kVA; OPRD2: S26/11/JR26/KVAR
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR27/kVA; OPRD2: S26/11/JR27/KVAR
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR28/kVA; OPRD2: S26/11/JR28/KVAR
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR29/kVA; OPRD2: S26/11/JR29/KVAR
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S26/11/JR30/kVA; OPRD2: S26/11/JR30/KVAR
S26 | 後湖SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S26_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S26/11/M1/MW; OPRD2: S26/11/M2/MW
S26 | 後湖SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S26_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S26/11/M1/MVAR; OPRD2: S26/11/M2/MVAR
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S26_D1 | [12 empty] | 後湖SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S26/11/210/CB; OPRD2: 6.9; OPRD3: 0
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S26_D1 | [12 empty] | 後湖SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S26/11/220/CB; OPRD2: 6.9; OPRD3: 0
S26 | 後湖SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S26_D1 | [12 empty] | 後湖SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_8 |  | com_alarm_16 | OPRD1: S26//1MTR/96B2; OPRD2: S26//1MTR/TRA; OPRD3: S26//1MTR/96B1; OPRD4: S26//1MTR/96PA; OPRD5: S26//1MTR/87A; OPRD6: S26//1MTR/51ZA; OPRD7: S26//1MTR/96D; OPRD8: S26//1MTR/63Q; OPRD9: S26//2MTR/96D; OPRD10: S26//2MTR/63Q; OPRD11: S26//2MTR/96B1; OPRD12: S26//2MTR/96B2; OPRD13: S26//2MTR/87A; OPRD14: S26//2MTR/51ZA; OPRD15: S26//2MTR/96PA; OPRD16: S26//2MTR/TRA
S26 | 後湖SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S26_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S26//1MTR/TRF; OPRD2: S26//2MTR/TRF
S26 | 後湖SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/RTU/RTU_R_L
S26 | 後湖SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/StaDev/DCE
S26 | 後湖SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/StaDev/PSF
S26 | 後湖SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/StaDev/PSA
S26 | 後湖SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/StaDev/DCA
S26 | 後湖SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S26_D1 | [17 empty] | lamp2CC | OPRD1: S26/69/ComPoint/CBF
S26 | 後湖SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S26_D1 | [17 empty] | lamp2CC | OPRD1: S26/69/ComPoint/CBA
S26 | 後湖SS | 69 | 69kV | ComPoint_D1 |  |  | SCA | SC警報 |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP |  | B3/S26_D1 | [17 empty] | lamp2CC | OPRD1: S26/69/ComPoint/SCA
S26 | 後湖SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S26_D1 | [17 empty] | lamp2CC | OPRD1: S26/69/ComPoint/ABS_89A
S26 | 後湖SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 主變火警 |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S26_A1 | [17 empty] | lamp2CC | OPRD1: S26/0/StaDev/Fire

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S26 | 後湖SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 後湖SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S26/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 後湖SS.610_AMP | 嘉義線 AMP | LINE69 | S26/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 後湖SS.620_AMP | 博愛線 AMP | LINE69 | S26/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C10R0880 | 792.000000 | 792.000000 | 880.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S26 | 後湖SS | 0 |  |  |  |  | 後ㄧ線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線KVA | 11KV後ㄧ線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後ㄧ線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線KW | 11KV後ㄧ線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後七線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後七線KVA | 11KV後七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後七線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後七線KW | 11KV後七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後九線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後九線KVA | 11KV後九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後九線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後九線KW | 11KV後九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後二線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後二線KVA | 11KV後二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後二線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後二線KW | 11KV後二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後八線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後八線KVA | 11KV後八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後八線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後八線KW | 11KV後八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後十線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後十線KVA | 11KV後十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後十線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後十線KW | 11KV後十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後三線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後三線KVA | 11KV後三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後三線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後三線KW | 11KV後三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後五線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後五線KVA | 11KV後五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後五線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後五線KW | 11KV後五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後六線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後六線KVA | 11KV後六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後六線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後六線KW | 11KV後六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後四線KVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後四線KVA | 11KV後四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  |  |  |  | 後四線KW | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.後四線KW | 11KV後四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S26//1MTR/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_PF | #1MTR 功率因素 | DTR | S26//1MTR/PF |  | RPDC_PF_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S26//2MTR/MVA |  | MVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_PF | #2MTR 功率因素 | DTR | S26//2MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S26 | 後湖SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S26/11/210/MVAR |  | SC_CAL_11 |  |  | 29 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S26/11/220/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 69 | 69kV | 610_CB | 嘉義線(610_CB) | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.610_CB_2 | 610(嘉義線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 31 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 620_CB | 博愛線(620_CB) | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.620_CB_2 | 620(博愛線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 32 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 後湖SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 33 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 後湖SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 34 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 後湖SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 35 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S26 | 後湖SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 36 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 後湖SS.69KV_ABS_89A_A | 69KV ABS 89A (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 37 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | _SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.69KV_SC警報_A | 69KV SC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 38 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 後湖SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S26/0/CalcPoint/SUBA |  | STATION_FAULT_8 |  |  | 39 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 40 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 41 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610_AMP | 嘉義線 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.610_AMP_A | 嘉義線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 42 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 69 | 69kV | 610_AMP | 嘉義線 | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.610_AMP_2 | 嘉義線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 43 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 69 | 69kV | 620_AMP | 博愛線 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.620_AMP_A | 博愛線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 44 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 69 | 69kV | 620_AMP | 博愛線 | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.620_AMP_2 | 博愛線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 45 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 49 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S26 | 後湖SS | 0 |  | 610_87CFA | 嘉義線(610)87RY通訊故障 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.610_87CFA_A | 嘉義線(610)87RY通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 50 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 610_RYFA | 610 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.610_RYFA_A | 610 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 51 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620_CFA | 620 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.620_CFA_A | 620 通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 52 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620_RYFA | 620 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.620_RYFA_A | 620 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 53 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 610後湖_RYFA | 610嘉義線 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.610後湖_RYFA_A | 610嘉義線 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620博愛_CFA | 620博愛線 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.620博愛_CFA_A | 620博愛線 通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620博愛_RYFA | 620博愛線 | [27 empty] | ADCS_N | [8 empty] | 後湖SS.620博愛_RYFA_A | 620博愛線 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S26/0/RTU/ADCH1 |  |  |  | CDC | 57 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S26/0/RTU/ADCH2 |  |  |  | CDC | 58 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S26/0/RTU/ADCL1 |  |  |  | CDC | 59 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S26/0/RTU/ADCL2 |  |  |  | CDC | 60 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 後湖SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S26/69/1BUS/V |  |  |  | CDC | 61 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S26 | 後湖SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S26/11/1BUS/V |  |  |  | CDC | 62 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S26 | 後湖SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S26/11/2BUS/V |  |  |  | CDC | 63 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 後湖SS.610_MW | 嘉義線 MW | LINE69 | S26/69/610/MW |  |  |  | CDC | 64 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 後湖SS.610_MVAR | 嘉義線 MVAR | LINE69 | S26/69/610/MVAR |  |  |  | CDC | 65 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 後湖SS.620_MW | 博愛線 MW | LINE69 | S26/69/620/MW |  |  |  | CDC | 66 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 後湖SS.620_MVAR | 博愛線 MVAR | LINE69 | S26/69/620/MVAR |  |  |  | CDC | 67 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後ㄧ線 | 後ㄧ線 |  | 後ㄧ線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線KVAR | 11KV後ㄧ線 KVAR | FEEDER | S26/11/JR21/KVAR |  |  |  | CDC | 68 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後ㄧ線 | 後ㄧ線 |  | 後ㄧ線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線A1 | 11KV後ㄧ線 R相AMP | FEEDER | S26/11/JR21/I_R |  |  |  | CDC | 69 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後ㄧ線 | 後ㄧ線 |  | 後ㄧ線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線A2 | 11KV後ㄧ線 S相AMP | FEEDER | S26/11/JR21/I_S |  |  |  | CDC | 70 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後ㄧ線 | 後ㄧ線 |  | 後ㄧ線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線A3 | 11KV後ㄧ線 T相AMP | FEEDER | S26/11/JR21/I_T |  |  |  | CDC | 71 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後ㄧ線 | 後ㄧ線 |  | 後ㄧ線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線A0 | 11KV後ㄧ線 N相AMP | FEEDER | S26/11/JR21/I_N |  |  |  | CDC | 72 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後七線 | 後七線 |  | 後七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後七線KVAR | 11KV後七線 KVAR | FEEDER | S26/11/JR27/KVAR |  |  |  | CDC | 73 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後七線 | 後七線 |  | 後七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後七線A1 | 11KV後七線 R相AMP | FEEDER | S26/11/JR27/I_R |  |  |  | CDC | 74 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後七線 | 後七線 |  | 後七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後七線A2 | 11KV後七線 S相AMP | FEEDER | S26/11/JR27/I_S |  |  |  | CDC | 75 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後七線 | 後七線 |  | 後七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後七線A3 | 11KV後七線 T相AMP | FEEDER | S26/11/JR27/I_T |  |  |  | CDC | 76 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後七線 | 後七線 |  | 後七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後七線A0 | 11KV後七線 N相AMP | FEEDER | S26/11/JR27/I_N |  |  |  | CDC | 77 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後九線 | 後九線 |  | 後九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後九線KVAR | 11KV後九線 KVAR | FEEDER | S26/11/JR29/KVAR |  |  |  | CDC | 78 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後九線 | 後九線 |  | 後九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後九線A1 | 11KV後九線 R相AMP | FEEDER | S26/11/JR29/I_R |  |  |  | CDC | 79 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後九線 | 後九線 |  | 後九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後九線A2 | 11KV後九線 S相AMP | FEEDER | S26/11/JR29/I_S |  |  |  | CDC | 80 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後九線 | 後九線 |  | 後九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後九線A3 | 11KV後九線 T相AMP | FEEDER | S26/11/JR29/I_T |  |  |  | CDC | 81 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後九線 | 後九線 |  | 後九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後九線A0 | 11KV後九線 N相AMP | FEEDER | S26/11/JR29/I_N |  |  |  | CDC | 82 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後二線 | 後二線 |  | 後二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後二線KVAR | 11KV後二線 KVAR | FEEDER | S26/11/JR22/KVAR |  |  |  | CDC | 83 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後二線 | 後二線 |  | 後二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後二線A1 | 11KV後二線 R相AMP | FEEDER | S26/11/JR22/I_R |  |  |  | CDC | 84 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後二線 | 後二線 |  | 後二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後二線A2 | 11KV後二線 S相AMP | FEEDER | S26/11/JR22/I_S |  |  |  | CDC | 85 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後二線 | 後二線 |  | 後二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後二線A3 | 11KV後二線 T相AMP | FEEDER | S26/11/JR22/I_T |  |  |  | CDC | 86 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後二線 | 後二線 |  | 後二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後二線A0 | 11KV後二線 N相AMP | FEEDER | S26/11/JR22/I_N |  |  |  | CDC | 87 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後八線 | 後八線 |  | 後八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後八線KVAR | 11KV後八線 KVAR | FEEDER | S26/11/JR28/KVAR |  |  |  | CDC | 88 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後八線 | 後八線 |  | 後八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後八線A1 | 11KV後八線 R相AMP | FEEDER | S26/11/JR28/I_R |  |  |  | CDC | 89 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後八線 | 後八線 |  | 後八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後八線A2 | 11KV後八線 S相AMP | FEEDER | S26/11/JR28/I_S |  |  |  | CDC | 90 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後八線 | 後八線 |  | 後八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後八線A3 | 11KV後八線 T相AMP | FEEDER | S26/11/JR28/I_T |  |  |  | CDC | 91 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後八線 | 後八線 |  | 後八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後八線A0 | 11KV後八線 N相AMP | FEEDER | S26/11/JR28/I_N |  |  |  | CDC | 92 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後十線 | 後十線 |  | 後十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後十線KVAR | 11KV後十線 KVAR | FEEDER | S26/11/JR30/KVAR |  |  |  | CDC | 93 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後十線 | 後十線 |  | 後十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後十線A1 | 11KV後十線 R相AMP | FEEDER | S26/11/JR30/I_R |  |  |  | CDC | 94 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後十線 | 後十線 |  | 後十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後十線A2 | 11KV後十線 S相AMP | FEEDER | S26/11/JR30/I_S |  |  |  | CDC | 95 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後十線 | 後十線 |  | 後十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後十線A3 | 11KV後十線 T相AMP | FEEDER | S26/11/JR30/I_T |  |  |  | CDC | 96 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後十線 | 後十線 |  | 後十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後十線A0 | 11KV後十線 N相AMP | FEEDER | S26/11/JR30/I_N |  |  |  | CDC | 97 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後三線 | 後三線 |  | 後三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後三線KVAR | 11KV後三線 KVAR | FEEDER | S26/11/JR23/KVAR |  |  |  | CDC | 98 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後三線 | 後三線 |  | 後三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後三線A1 | 11KV後三線 R相AMP | FEEDER | S26/11/JR23/I_R |  |  |  | CDC | 99 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後三線 | 後三線 |  | 後三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後三線A2 | 11KV後三線 S相AMP | FEEDER | S26/11/JR23/I_S |  |  |  | CDC | 100 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後三線 | 後三線 |  | 後三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後三線A3 | 11KV後三線 T相AMP | FEEDER | S26/11/JR23/I_T |  |  |  | CDC | 101 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後三線 | 後三線 |  | 後三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後三線A0 | 11KV後三線 N相AMP | FEEDER | S26/11/JR23/I_N |  |  |  | CDC | 102 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後五線 | 後五線 |  | 後五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後五線KVAR | 11KV後五線 KVAR | FEEDER | S26/11/JR25/KVAR |  |  |  | CDC | 103 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後五線 | 後五線 |  | 後五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後五線A1 | 11KV後五線 R相AMP | FEEDER | S26/11/JR25/I_R |  |  |  | CDC | 104 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後五線 | 後五線 |  | 後五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後五線A2 | 11KV後五線 S相AMP | FEEDER | S26/11/JR25/I_S |  |  |  | CDC | 105 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後五線 | 後五線 |  | 後五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後五線A3 | 11KV後五線 T相AMP | FEEDER | S26/11/JR25/I_T |  |  |  | CDC | 106 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後五線 | 後五線 |  | 後五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後五線A0 | 11KV後五線 N相AMP | FEEDER | S26/11/JR25/I_N |  |  |  | CDC | 107 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後六線 | 後六線 |  | 後六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後六線KVAR | 11KV後六線 KVAR | FEEDER | S26/11/JR26/KVAR |  |  |  | CDC | 108 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後六線 | 後六線 |  | 後六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後六線A1 | 11KV後六線 R相AMP | FEEDER | S26/11/JR26/I_R |  |  |  | CDC | 109 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後六線 | 後六線 |  | 後六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後六線A2 | 11KV後六線 S相AMP | FEEDER | S26/11/JR26/I_S |  |  |  | CDC | 110 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後六線 | 後六線 |  | 後六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後六線A3 | 11KV後六線 T相AMP | FEEDER | S26/11/JR26/I_T |  |  |  | CDC | 111 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後六線 | 後六線 |  | 後六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後六線A0 | 11KV後六線 N相AMP | FEEDER | S26/11/JR26/I_N |  |  |  | CDC | 112 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後四線 | 後四線 |  | 後四線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後四線KVAR | 11KV後四線 KVAR | FEEDER | S26/11/JR24/KVAR |  |  |  | CDC | 113 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後四線 | 後四線 |  | 後四線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後四線A1 | 11KV後四線 R相AMP | FEEDER | S26/11/JR24/I_R |  |  |  | CDC | 114 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後四線 | 後四線 |  | 後四線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後四線A2 | 11KV後四線 S相AMP | FEEDER | S26/11/JR24/I_S |  |  |  | CDC | 115 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後四線 | 後四線 |  | 後四線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後四線A3 | 11KV後四線 T相AMP | FEEDER | S26/11/JR24/I_T |  |  |  | CDC | 116 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | 後四線 | 後四線 |  | 後四線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.後四線A0 | 11KV後四線 N相AMP | FEEDER | S26/11/JR24/I_N |  |  |  | CDC | 117 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_MW | #1MTR二次側 MW | DTR | S26/11/M1/MW |  |  |  | CDC | 118 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S26/11/M1/MVAR |  |  |  | CDC | 119 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S26/11/M1/I_R |  |  |  | CDC | 120 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S26/11/M1/I_S |  |  |  | CDC | 121 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S26/11/M1/I_T |  |  |  | CDC | 122 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_OIL | #1MTR 油溫 | DTR | S26//1MTR/OilTemp |  |  |  | CDC | 123 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_COIL | #1MTR 線溫 | DTR | S26//1MTR/CoilTemp |  |  |  | CDC | 124 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S26//1MTR/TapPosMv |  |  |  | CDC | 125 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_MW | #2MTR二次側 MW | DTR | S26/11/M2/MW |  |  |  | CDC | 126 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S26/11/M2/MVAR |  |  |  | CDC | 127 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S26/11/M2/I_R |  |  |  | CDC | 128 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S26/11/M2/I_S |  |  |  | CDC | 129 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S26/11/M2/I_T |  |  |  | CDC | 130 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_OIL | #2MTR 油溫 | DTR | S26//2MTR/OilTemp |  |  |  | CDC | 131 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_COIL | #2MTR 線溫 | DTR | S26//2MTR/CoilTemp |  |  |  | CDC | 132 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S26//2MTR/TapPosMv |  |  |  | CDC | 133 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S26 | 後湖SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.直流電源電壓 | 直流電源電壓 | OTHER | S26/0/StaDev/DCV |  |  |  | CDC | 134 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S26 | 後湖SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S26/11/TIE2/I_R |  |  |  | CDC | 135 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S26/11/TIE2/I_S |  |  |  | CDC | 136 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 後湖SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S26/11/TIE2/I_T |  |  |  | CDC | 137 | GENERICAIPoint | SS206_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.610_PHA | 嘉義線(610) 相間RY | LINE69 | S26/69/610/PHA |  |  |  | CDC | 138 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.610_GDA | 嘉義線(610) 接地RY | LINE69 | S26/69/610/GDA |  |  |  | CDC | 139 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 後湖SS.610_CB | 610(嘉義線) CB | LINE69 | S26/69/610/CB |  |  |  | CDC | 140 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | ABS1 | 611 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.611_ABS | 611(嘉義線) ABS | LINE69 | S26/69/610/ABS1 |  |  |  | CDC | 141 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | ABS2 | 612 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.612_ABS | 612(嘉義線) ABS | LINE69 | S26/69/610/ABS2 |  |  |  | CDC | 142 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | E2 | 612E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.612E_ES | 612E(嘉義線) ES | LINE69 | S26/69/610/ES2 |  |  |  | CDC | 143 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.620_PHA | 博愛線(620) 相間RY | LINE69 | S26/69/620/PHA |  |  |  | CDC | 144 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.620_GDA | 博愛線(620) 接地RY | LINE69 | S26/69/620/GDA |  |  |  | CDC | 145 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | 74A | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 後湖SS.620_74A | 博愛線(620) 74RY | LINE69 | S26/69/620/74A |  |  |  | CDC | 146 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 後湖SS.620_CB | 620(博愛線) CB | LINE69 | S26/69/620/CB |  |  |  | CDC | 147 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | ABS1 | 621 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.621_ABS | 621(博愛線) ABS | LINE69 | S26/69/620/ABS1 |  |  |  | CDC | 148 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | ABS2 | 622 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.622_ABS | 622(博愛線) ABS | LINE69 | S26/69/620/ABS2 |  |  |  | CDC | 149 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | E2 | 622E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 後湖SS.622E_ES | 622E(博愛線) ES | LINE69 | S26/69/620/ES2 |  |  |  | CDC | 150 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_PHA | 11KV後ㄧ線(JR21) 相間RY | FEEDER | S26/11/JR21/PHA |  |  |  | CDC | 151 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_GDA | 11KV後ㄧ線(JR21) 接地RY | FEEDER | S26/11/JR21/GDA |  |  |  | CDC | 152 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_79UL | 11KV後ㄧ線(JR21) 79RY U/L | FEEDER | S26/11/JR21/79UL |  |  |  | CDC | 153 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR21 | 後ㄧ線(JR21) |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_ADJ | 11KV後ㄧ線(JR21) LCO分流器 | FEEDER | S26/11/JR21/ADJ |  |  |  | CDC | 154 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR21 | JR21(11KV後ㄧ線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_CB | JR21(11KV後ㄧ線) CB | FEEDER | S26/11/JR21/CB |  |  |  | CDC | 155 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_PHA | 11KV後二線(JR22) 相間RY | FEEDER | S26/11/JR22/PHA |  |  |  | CDC | 156 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_GDA | 11KV後二線(JR22) 接地RY | FEEDER | S26/11/JR22/GDA |  |  |  | CDC | 157 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_79UL | 11KV後二線(JR22) 79RY U/L | FEEDER | S26/11/JR22/79UL |  |  |  | CDC | 158 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR22 | 後二線(JR22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_ADJ | 11KV後二線(JR22) LCO分流器 U/L | FEEDER | S26/11/JR22/ADJ |  |  |  | CDC | 159 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR22 | JR22(11KV後二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_CB | JR22(11KV後二線) CB | FEEDER | S26/11/JR22/CB |  |  |  | CDC | 160 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_PHA | 11KV後三線(JR23) 相間RY | FEEDER | S26/11/JR23/PHA |  |  |  | CDC | 161 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_GDA | 11KV後三線(JR23) 接地RY | FEEDER | S26/11/JR23/GDA |  |  |  | CDC | 162 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_79UL | 11KV後三線(JR23) 79RY U/L | FEEDER | S26/11/JR23/79UL |  |  |  | CDC | 163 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR23 | 後三線(JR23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_ADJ | 11KV後三線(JR23) LCO分流器 U/L | FEEDER | S26/11/JR23/ADJ |  |  |  | CDC | 164 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR23 | JR23(11KV後三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_CB | JR23(11KV後三線) CB | FEEDER | S26/11/JR23/CB |  |  |  | CDC | 165 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_PHA | 11KV後四線(JR24) 相間RY | FEEDER | S26/11/JR24/PHA |  |  |  | CDC | 166 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_GDA | 11KV後四線(JR24) 接地RY | FEEDER | S26/11/JR24/GDA |  |  |  | CDC | 167 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_79UL | 11KV後四線(JR24) 79RY U/L | FEEDER | S26/11/JR24/79UL |  |  |  | CDC | 168 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR24 | 後四線(JR24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_ADJ | 11KV後四線(JR24) LCO分流器 U/L | FEEDER | S26/11/JR24/ADJ |  |  |  | CDC | 169 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR24 | JR24(11KV後四線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_CB | JR24(11KV後四線) CB | FEEDER | S26/11/JR24/CB |  |  |  | CDC | 170 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_PHA | 11KV後五線(JR25) 相間RY | FEEDER | S26/11/JR25/PHA |  |  |  | CDC | 171 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_GDA | 11KV後五線(JR25) 接地RY | FEEDER | S26/11/JR25/GDA |  |  |  | CDC | 172 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_79UL | 11KV後五線(JR25) 79RY U/L | FEEDER | S26/11/JR25/79UL |  |  |  | CDC | 173 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR25 | 後五線(JR25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_ADJ | 11KV後五線(JR25) LCO分流器 U/L | FEEDER | S26/11/JR25/ADJ |  |  |  | CDC | 174 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR25 | JR25(11KV後五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_CB | JR25(11KV後五線) CB | FEEDER | S26/11/JR25/CB |  |  |  | CDC | 175 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_PHA | 11KV後六線(JR26) 相間RY | FEEDER | S26/11/JR26/PHA |  |  |  | CDC | 176 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_GDA | 11KV後六線(JR26) 接地RY | FEEDER | S26/11/JR26/GDA |  |  |  | CDC | 177 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_79UL | 11KV後六線(JR26) 79RY U/L | FEEDER | S26/11/JR26/79UL |  |  |  | CDC | 178 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR26 | 後六線(JR26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_ADJ | 11KV後六線(JR26) LCO分流器 U/L | FEEDER | S26/11/JR26/ADJ |  |  |  | CDC | 179 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR26 | JR26(11KV後六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_CB | JR26(11KV後六線) CB | FEEDER | S26/11/JR26/CB |  |  |  | CDC | 180 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_PHA | 11KV後七線(JR27) 相間RY | FEEDER | S26/11/JR27/PHA |  |  |  | CDC | 181 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_GDA | 11KV後七線(JR27) 接地RY | FEEDER | S26/11/JR27/GDA |  |  |  | CDC | 182 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_79UL | 11KV後七線(JR27) 79RY U/L | FEEDER | S26/11/JR27/79UL |  |  |  | CDC | 183 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR27 | 後七線(JR27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_ADJ | 11KV後七線(JR27) LCO分流器 U/L | FEEDER | S26/11/JR27/ADJ |  |  |  | CDC | 184 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR27 | JR27(11KV後七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_CB | JR27(11KV後七線) CB | FEEDER | S26/11/JR27/CB |  |  |  | CDC | 185 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_PHA | 11KV後八線(JR28) 相間RY | FEEDER | S26/11/JR28/PHA |  |  |  | CDC | 186 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_GDA | 11KV後八線(JR28) 接地RY | FEEDER | S26/11/JR28/GDA |  |  |  | CDC | 187 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_79UL | 11KV後八線(JR28) 79RY U/L | FEEDER | S26/11/JR28/79UL |  |  |  | CDC | 188 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR28 | 後八線(JR28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_ADJ | 11KV後八線(JR28) LCO分流器 U/L | FEEDER | S26/11/JR28/ADJ |  |  |  | CDC | 189 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR28 | JR28(11KV後八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_CB | JR28(11KV後八線) CB | FEEDER | S26/11/JR28/CB |  |  |  | CDC | 190 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_PHA | 11KV後九線(JR29) 相間RY | FEEDER | S26/11/JR29/PHA |  |  |  | CDC | 191 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_GDA | 11KV後九線(JR29) 接地RY | FEEDER | S26/11/JR29/GDA |  |  |  | CDC | 192 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_79UL | 11KV後九線(JR29) 79RY U/L | FEEDER | S26/11/JR29/79UL |  |  |  | CDC | 193 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR29 | 後九線(JR29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_ADJ | 11KV後九線(JR29) LCO分流器 U/L | FEEDER | S26/11/JR29/ADJ |  |  |  | CDC | 194 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR29 | JR29(11KV後九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_CB | JR29(11KV後九線) CB | FEEDER | S26/11/JR29/CB |  |  |  | CDC | 195 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_PHA | 11KV後十線(JR30) 相間RY | FEEDER | S26/11/JR30/PHA |  |  |  | CDC | 196 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_GDA | 11KV後十線(JR30) 接地RY | FEEDER | S26/11/JR30/GDA |  |  |  | CDC | 197 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_79UL | 11KV後十線(JR30) 79RY U/L | FEEDER | S26/11/JR30/79UL |  |  |  | CDC | 198 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 11 | 11kV | JR30 | 後十線(JR30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_ADJ | 11KV後十線(JR30) LCO分流器 U/L | FEEDER | S26/11/JR30/ADJ |  |  |  | CDC | 199 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 11 | 11kV | JR30 | JR30(11KV後十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_CB | JR30(11KV後十線) CB | FEEDER | S26/11/JR30/CB |  |  |  | CDC | 200 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.750_CB | 750(#1MTR) CB | DTR | S26/69/750/CB |  |  |  | CDC | 201 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.1M_CB | 1M(#1MTR) CB | DTR | S26/11/M1/CB |  |  |  | CDC | 202 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_51A | #1MTR 51RY | DTR | S26/69/750/51A |  |  |  | CDC | 203 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_51NA | #1MTR 51N RY | DTR | S26/69/750/51NA |  |  |  | CDC | 204 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S26//1MTR/51ZA |  |  |  | CDC | 205 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_87A | #1MTR 87RY | DTR | S26//1MTR/87A |  |  |  | CDC | 206 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S26//1MTR/87UL |  |  |  | CDC | 207 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S26/11/M1/51A |  |  |  | CDC | 208 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_TRA | #1MTR 重故障 | DTR | S26//1MTR/TRA |  |  |  | CDC | 209 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S26//1MTR/TRF |  |  |  | CDC | 210 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S26//1MTR/SupLocal |  |  |  | CDC | 211 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S26//1MTR/Tap Chan |  |  |  | CDC | 212 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.751_ABS | 751(#1MTR) ABS | DTR | S26/69/750/ABS1 |  |  |  | CDC | 213 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_96A | #1MTR 96P RY | DTR | S26//1MTR/96PA |  |  |  | CDC | 214 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S26//1MTR/OLTC_DLY |  |  |  | CDC | 215 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S26//1MTR/AC_Fault |  |  |  | CDC | 216 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.760_CB | 760(#2MTR) CB | DTR | S26/69/760/CB |  |  |  | CDC | 217 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.2M_CB | 2M(#2MTR) CB | DTR | S26/11/M2/CB |  |  |  | CDC | 218 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_51A | #2MTR 51RY | DTR | S26/69/760/51A |  |  |  | CDC | 219 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_51NA | #2MTR 51N RY | DTR | S26/69/760/51NA |  |  |  | CDC | 220 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S26//2MTR/51ZA |  |  |  | CDC | 221 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_87A | #2MTR 87RY | DTR | S26//2MTR/87A |  |  |  | CDC | 222 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S26//2MTR/87UL |  |  |  | CDC | 223 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S26/11/M2/51A |  |  |  | CDC | 224 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_TRA | #2MTR 重故障 | DTR | S26//2MTR/TRA |  |  |  | CDC | 225 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S26//2MTR/TRF |  |  |  | CDC | 226 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S26//2MTR/SupLocal |  |  |  | CDC | 227 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S26//2MTR/Tap Chan |  |  |  | CDC | 228 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.761_ABS | 761(#2MTR) ABS | DTR | S26/69/760/ABS1 |  |  |  | CDC | 229 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_96A | #2MTR 96P RY | DTR | S26//2MTR/96PA |  |  |  | CDC | 230 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S26//2MTR/OLTC_DLY |  |  |  | CDC | 231 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S26//2MTR/AC_Fault |  |  |  | CDC | 232 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_CB | 210(11KV #1SC) CB | SC | S26/11/210/CB |  |  |  | CDC | 233 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S26/11/210/Tap Chan |  |  |  | CDC | 234 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_SCA | 11KV #1SC 51,51N RY | SC | S26/11/210/SCA |  |  |  | CDC | 235 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S26/11/210/UVA |  |  |  | CDC | 236 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_CB | 220(11KV #2SC) CB | SC | S26/11/220/CB |  |  |  | CDC | 237 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S26/11/220/Tap Chan |  |  |  | CDC | 238 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_SCA | 11KV #2SC 51,51N RY | SC | S26/11/220/SCA |  |  |  | CDC | 239 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S26/11/220/UVA |  |  |  | CDC | 240 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 後湖SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S26/69/1BUS/BUS_VUA |  |  |  | CDC | 241 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 後湖SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S26/69/2BUS/BUS_VUA |  |  |  | CDC | 242 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | S26/11/ComPoint/CBA |  |  |  | CDC | 243 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | S26/11/ComPoint/CBF |  |  |  | CDC | 244 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S26/69/ComPoint/CBA |  |  |  | CDC | 245 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S26/69/ComPoint/CBF |  |  |  | CDC | 246 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S26/0/RTU/RTU_R_L |  |  |  | CDC | 247 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S26 | 後湖SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.TEST_CB | TEST CB | OTHER | S26/0/RTU/Test_CB |  |  |  | CDC | 248 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.火災警報(1) | [後湖]火警 | OTHER | S26/0/StaDev/Fire1 |  |  |  | CDC | 249 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S26/0/StaDev/OPA |  |  |  | CDC | 250 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.其他重故障 | 變電所內其他重故障 | OTHER | S26/0/StaDev/PSA |  |  |  | CDC | 251 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S26/0/StaDev/PSF |  |  |  | CDC | 252 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S26/0/StaDev/STUV |  |  |  | CDC | 253 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S26/0/StaDev/CHG1 |  |  |  | CDC | 254 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.直流電源DCA | 直流電源故障警報 | OTHER | S26/0/StaDev/DCA |  |  |  | CDC | 255 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S26/0/StaDev/DCE |  |  |  | CDC | 256 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S26/0/StaDev/OilLeak |  |  |  | CDC | 257 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S26/0/StaDev/6A5Other |  |  |  | CDC | 258 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S26/0/StaDev/7A5Other |  |  |  | CDC | 259 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S26/0/StaDev/8A5Other |  |  |  | CDC | 260 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S26/0/StaDev/CHG2 |  |  |  | CDC | 261 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S26/0/StaDev/CommACF |  |  |  | CDC | 262 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S26/0/StaDev/Door1 |  |  |  | CDC | 263 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S26/0/StaDev/Door2 |  |  |  | CDC | 264 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S26/0/StaDev/Door3 |  |  |  | CDC | 265 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S26 | 後湖SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.開關場照明(A) | 所內開關場照明 | OTHER | S26/0/StaDev/Lights1 |  |  |  | CDC | 266 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S26 | 後湖SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.開關場照明(B) | 路燈照明 | OTHER | S26/0/StaDev/Lights2 |  |  |  | CDC | 267 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S26 | 後湖SS | 0 |  | 1M | 1M |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.1M_51NA | 1M 51NA | OTHER | S26/11/M1/51NA |  |  |  | CDC | 268 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2M | 2M |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.2M_51NA | 2M 51NA | OTHER | S26/11/M2/51NA |  |  |  | CDC | 269 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.69KV_ABS_89A | 69KV ABS 89A | OTHER | S26/69/ComPoint/ABS_89A |  |  |  | CDC | 270 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV |  |  |  | SC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.69KV_SC警報 | 69KV SC警報 | OTHER | S26/69/ComPoint/SCA |  |  |  | CDC | 271 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | MCSG火警 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.MCSG火警 | MCSG火警 | OTHER | S26/0/StaDev/Fire2 |  |  |  | CDC | 272 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | MCSG系統故障 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.MCSG系統故障 | MCSG系統故障 | OTHER | S26/0/StaDev/1A5Other |  |  |  | CDC | 273 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.主變火警 | 主變火警 | OTHER | S26/0/StaDev/Fire |  |  |  | CDC | 274 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.安全監控 | 安全監控 | OTHER | S26/0/StaDev/Burglar |  |  |  | CDC | 275 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.門禁 | (大門側門) | OTHER | S26/0/StaDev/Door |  |  |  | CDC | 276 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.細水霧故障 | 細水霧故障 | OTHER | S26/0/StaDev/2A5Other |  |  |  | CDC | 277 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S26/0/StaDev/3A5Other |  |  |  | CDC | 278 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.維護運轉警報 | 維護運轉警報 | OTHER | S26/0/StaDev/4A5Other |  |  |  | CDC | 279 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S26//1MTR/81AS |  |  |  | CDC | 280 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S26 | 後湖SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S26//1MTR/63Q |  |  |  | CDC | 281 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S26//1MTR/96B1 |  |  |  | CDC | 282 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S26//1MTR/96B2 |  |  |  | CDC | 283 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S26//1MTR/96D |  |  |  | CDC | 284 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S26//1MTR/96P |  |  |  | CDC | 285 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S26//2MTR/63Q |  |  |  | CDC | 286 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S26//2MTR/96B1 |  |  |  | CDC | 287 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S26//2MTR/96B2 |  |  |  | CDC | 288 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S26//2MTR/96D |  |  |  | CDC | 289 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S26//2MTR/96P |  |  |  | CDC | 290 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-0F-04 |  | 1-56 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S26//2MTR/81AS |  |  |  | CDC | 291 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.610_87A | 嘉義線(610) 87RY | LINE69 | S26/69/610/87A |  |  |  | CDC | 292 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | 87CFA | [17 empty] | 1-32-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.610_87CFA | 嘉義線(610)87RY通訊故障 | LINE69 | S26/69/610/74A |  |  |  | CDC | 293 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 後湖SS.610_87UL | 嘉義線(610) 87RY U/L | LINE69 | S26/69/610/87UL |  |  |  | CDC | 294 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-37-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S26/0/StaDev/R_Temp |  |  |  | CDC | 295 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 後湖SS.620_87A | 博愛線(620) 87RY | LINE69 | S26/69/620/87A |  |  |  | CDC | 296 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 後湖SS.620_87UL | 博愛線(620) 87RY U/L | LINE69 | S26/69/620/87UL |  |  |  | CDC | 297 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S26 | 後湖SS | 0 |  | 610嘉義線 | 610 |  | RYFA | [17 empty] | 1-32-15 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.610嘉義線_RYFA | 610 IED警報 | OTHER | S26/69/610/RYFA |  |  |  | CDC | 298 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620博愛線 | 620 |  | CFA | [17 empty] | 1-37-08 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.620博愛線_CFA | 620 通訊故障 | OTHER | S26/69/620/87CFA |  |  |  | CDC | 299 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 620博愛線 | 620 |  | RYFA | [17 empty] | 1-37-09 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.620博愛線_RYFA | 620 IED警報 | OTHER | S26/69/620/RYFA |  |  |  | CDC | 300 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S26/0/StaDev/Lights3 |  |  |  | CDC | 301 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-14 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.開關場水位警報 | 開關場水位警報 | OTHER | S26/0/StaDev/Water1 |  |  |  | CDC | 302 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 390 | SSTR-1(390) |  | CB | [17 empty] | 1-04-04 |  | 1-2F | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.390_CB | 390(SSTR-1) CB | OTHER | S26/11/390/CB |  |  |  | CDC | 303 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | SSTR-1 | SSTR-1 |  | 51A | [17 empty] | 1-04-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.SSTR-1_51A | SSTR-1 51RY | OTHER | S26/11/390/51A |  |  |  | CDC | 304 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | SSTR-1 | SSTR-1 |  | 51NA | [17 empty] | 1-04-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.SSTR-1_51NA | SSTR-1 51N RY | OTHER | S26/11/390/51NA |  |  |  | CDC | 305 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S26/11/ComPoint/IRFA |  |  |  | CDC | 306 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後ㄧ線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後ㄧ線79LOA | 後ㄧ線79LOA | OTHER | S26/11/JR21/LOA |  |  |  | CDC | 307 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後二線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後二線79LOA | 後二線79LOA | OTHER | S26/11/JR22/LOA |  |  |  | CDC | 308 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後三線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後三線79LOA | 後三線79LOA | OTHER | S26/11/JR23/LOA |  |  |  | CDC | 309 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後四線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後四線79LOA | 後四線79LOA | OTHER | S26/11/JR24/LOA |  |  |  | CDC | 310 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後五線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後五線79LOA | 後五線79LOA | OTHER | S26/11/JR25/LOA |  |  |  | CDC | 311 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後六線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後六線79LOA | 後六線79LOA | OTHER | S26/11/JR26/LOA |  |  |  | CDC | 312 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後七線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後七線79LOA | 後七線79LOA | OTHER | S26/11/JR27/LOA |  |  |  | CDC | 313 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後八線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後八線79LOA | 後八線79LOA | OTHER | S26/11/JR28/LOA |  |  |  | CDC | 314 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後九線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後九線79LOA | 後九線79LOA | OTHER | S26/11/JR29/LOA |  |  |  | CDC | 315 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 後十線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.後十線79LOA | 後十線79LOA | OTHER | S26/11/JR30/LOA |  |  |  | CDC | 316 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.PMA | PMA | OTHER | S26/0/ComPoint/PMA |  |  |  | CDC | 317 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S26/0/StaDev/Water2 |  |  |  | CDC | 318 | GENERICDIPoint | SS206_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 200TIE | TIE |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.200TIE_CB | 200TIE(TIE) CB | TIE | S26/11/TIE1/CB |  |  |  | CDC | 319 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 200TIE | 200TIE |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.200TIE_51A | 11KV TIE(200TIE) 51RY | TIE | S26/11/TIE1/51A |  |  |  | CDC | 320 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 200TIE | 200TIE |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.200TIE_51NA | 11KV TIE(200TIE) 51N RY | TIE | S26/11/TIE1/51NA |  |  |  | CDC | 321 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | 490 | SSTR-2(490) |  | CB | [17 empty] | 1-05-00 |  | 1-43 | [5 empty] | DDCS2_1 | [8 empty] | 後湖SS.490_CB | 490(SSTR-2) CB | OTHER | S26/11/490/CB |  |  |  | CDC | 322 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | SSTR-2 | SSTR-2 |  | 51A | [17 empty] | 1-05-01 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.SSTR-2_51A | SSTR-2 51RY | OTHER | S26/11/490/51A |  |  |  | CDC | 323 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 0 |  | SSTR-2 | SSTR-2 |  | 51NA | [17 empty] | 1-05-02 | [7 empty] | DDCS2_1 | [8 empty] | 後湖SS.SSTR-2_51NA | SSTR-2 51N RY | OTHER | S26/11/490/51NA |  |  |  | CDC | 324 | GENERICDIPoint | SS206_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S26 | 後湖SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 325 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 326 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 後湖SS.610LE | 610LE (非取樣點) | LINE69 | S26/69/610/LE0 |  |  |  |  | 327 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 後湖SS.610BE | 610BE (非取樣點) | LINE69 | S26/69/610/BE0 |  |  |  |  | 328 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 後湖SS.620LE | 620LE (非取樣點) | LINE69 | S26/69/620/LE0 |  |  |  |  | 329 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 後湖SS.620BE | 620BE (非取樣點) | LINE69 | S26/69/620/BE0 |  |  |  |  | 330 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR21 | JR21_DS |  | DS1 | JR21_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_DS | JR21_DS (非取樣點) | FEEDER | S26/11/JR21/DS |  |  |  |  | 331 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR21 | JR21_ES |  | LE0 | JR21_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR21_ES | JR21_ES (非取樣點) | FEEDER | S26/11/JR21/ES |  |  |  |  | 332 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR22 | JR22_DS |  | DS1 | JR22_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_DS | JR22_DS (非取樣點) | FEEDER | S26/11/JR22/DS |  |  |  |  | 333 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR22 | JR22_ES |  | LE0 | JR22_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR22_ES | JR22_ES (非取樣點) | FEEDER | S26/11/JR22/ES |  |  |  |  | 334 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR23 | JR23_DS |  | DS1 | JR23_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_DS | JR23_DS (非取樣點) | FEEDER | S26/11/JR23/DS |  |  |  |  | 335 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR23 | JR23_ES |  | LE0 | JR23_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR23_ES | JR23_ES (非取樣點) | FEEDER | S26/11/JR23/ES |  |  |  |  | 336 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR24 | JR24_DS |  | DS1 | JR24_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_DS | JR24_DS (非取樣點) | FEEDER | S26/11/JR24/DS |  |  |  |  | 337 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR24 | JR24_ES |  | LE0 | JR24_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR24_ES | JR24_ES (非取樣點) | FEEDER | S26/11/JR24/ES |  |  |  |  | 338 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR25 | JR25_DS |  | DS1 | JR25_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_DS | JR25_DS (非取樣點) | FEEDER | S26/11/JR25/DS |  |  |  |  | 339 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR25 | JR25_ES |  | LE0 | JR25_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR25_ES | JR25_ES (非取樣點) | FEEDER | S26/11/JR25/ES |  |  |  |  | 340 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR26 | JR26_DS |  | DS1 | JR26_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_DS | JR26_DS (非取樣點) | FEEDER | S26/11/JR26/DS |  |  |  |  | 341 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR26 | JR26_ES |  | LE0 | JR26_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR26_ES | JR26_ES (非取樣點) | FEEDER | S26/11/JR26/ES |  |  |  |  | 342 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR27 | JR27_DS |  | DS1 | JR27_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_DS | JR27_DS (非取樣點) | FEEDER | S26/11/JR27/DS |  |  |  |  | 343 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR27 | JR27_ES |  | LE0 | JR27_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR27_ES | JR27_ES (非取樣點) | FEEDER | S26/11/JR27/ES |  |  |  |  | 344 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR28 | JR28_DS |  | DS1 | JR28_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_DS | JR28_DS (非取樣點) | FEEDER | S26/11/JR28/DS |  |  |  |  | 345 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR28 | JR28_ES |  | LE0 | JR28_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR28_ES | JR28_ES (非取樣點) | FEEDER | S26/11/JR28/ES |  |  |  |  | 346 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR29 | JR29_DS |  | DS1 | JR29_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_DS | JR29_DS (非取樣點) | FEEDER | S26/11/JR29/DS |  |  |  |  | 347 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR29 | JR29_ES |  | LE0 | JR29_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR29_ES | JR29_ES (非取樣點) | FEEDER | S26/11/JR29/ES |  |  |  |  | 348 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | JR30 | JR30_DS |  | DS1 | JR30_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_DS | JR30_DS (非取樣點) | FEEDER | S26/11/JR30/DS |  |  |  |  | 349 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | JR30 | JR30_ES |  | LE0 | JR30_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.JR30_ES | JR30_ES (非取樣點) | FEEDER | S26/11/JR30/ES |  |  |  |  | 350 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.750TE | 750TE (非取樣點) | DTR | S26/69/750/TE0 |  |  |  |  | 351 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.750BE | 750BE (非取樣點) | DTR | S26/69/750/BE0 |  |  |  |  | 352 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.1M_DS | 1M_DS (非取樣點) | DTR | S26/11/M1/DS |  |  |  |  | 353 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.1M_ES | 1M_ES (非取樣點) | DTR | S26/11/M1/ES |  |  |  |  | 354 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.760TE | 760TE (非取樣點) | DTR | S26/69/760/TE0 |  |  |  |  | 355 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.760BE | 760BE (非取樣點) | DTR | S26/69/760/BE0 |  |  |  |  | 356 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.2M_DS | 2M_DS (非取樣點) | DTR | S26/11/M2/DS |  |  |  |  | 357 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.2M_ES | 2M_ES (非取樣點) | DTR | S26/11/M2/ES |  |  |  |  | 358 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_ES | 210_ES (非取樣點) | SC | S26/11/210/ES |  |  |  |  | 359 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_ES | 220_ES (非取樣點) | SC | S26/11/220/ES |  |  |  |  | 360 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 後湖SS.69B1E | 69B1E (非取樣點) | BUS | S26/69/1BUS/BE1 |  |  |  |  | 361 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 後湖SS.69B2E | 69B2E (非取樣點) | BUS | S26/69/2BUS/BE2 |  |  |  |  | 362 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 363 | NotelDIPoint | [38 empty] | START/STOP | STOP
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | PW1UL | 610_PW1UL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.610_PW1UL | 嘉義線(610)PW1_UL (非取樣點) | LINE69 | [5 empty] | 364 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | PW2UL | 610_PW2UL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.610_PW2UL | 嘉義線(610)PW2_UL (非取樣點) | LINE69 | [5 empty] | 365 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 69 | 69kV | 610 | 嘉義線(610) |  | HCBUL | 610_HCBUL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.610_HCBUL | 嘉義線(610)HCB_UL(非取樣點) | LINE69 | [5 empty] | 366 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.620_PW1UL | 博愛線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 367 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.620_PW2UL | 博愛線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 368 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S26 | 後湖SS | 69 | 69kV | 620 | 博愛線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_N | [8 empty] | 後湖SS.620_HCBUL | 博愛線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 369 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S26 | 後湖SS | 0 |  | 1PT | #1PT_DS |  | DS1 | #1PT_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1PT_DS | #1PT_DS (非取樣點) | OTHER | S26/11/1PT/DS |  |  |  |  | 370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 1PT | #1PT_ES |  | PT0 | #1PT_ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.#1PT_ES | #1PT_ES (非取樣點) | OTHER | S26/11/1PT/ES |  |  |  |  | 371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 390 | SSTR-1(390) |  | DS1 | 391 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.391_DS | 391_DS (非取樣點) | OTHER | S26/11/390/D1 |  |  |  |  | 372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 390 | SSTR-1(390) |  | E1 | 391 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.391_ES | 391_ES (非取樣點) | OTHER | S26/11/390/E1 |  |  |  |  | 373 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 11BE1 | 11BE1 |  | BE10 | 11BE1 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.11BE1 | 11BE1 (非取樣點) | BUS | S26/11/1BUS/BE1 |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.210_DS | 210_DS (非取樣點) | SC | S26/11/210/DS |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.220_DS | 220_DS (非取樣點) | SC | S26/11/220/DS |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 200 | 200 |  | E1 | 201ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.201ES | 201ES (非取樣點) | TIE | S26/11/TIE2/E1 |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 200 | 200 |  | E2 | 202ES | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.202ES | 202ES (非取樣點) | TIE | S26/11/TIE2/E2 |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 200 | 200 |  | DS1 | 201DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.201DS | 201DS (非取樣點) | TIE | S26/11/TIE2/D1 |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 200 | 200 |  | DS2 | 202DS | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.202DS | 202DS (非取樣點) | TIE | S26/11/TIE2/D2 |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 490 | SSTR-2(490) |  | DS1 | 491 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.491_DS | 491_DS (非取樣點) | OTHER | S26/11/490/D1 |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S26 | 後湖SS | 0 |  | 490 | SSTR-2(490) |  | E1 | 491 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.491_ES | 491_ES (非取樣點) | OTHER | S26/11/490/E1 |  |  |  |  | 382 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
S26 | 後湖SS | 0 |  | 11BE2 | 11BE2 |  | BE20 | 11BE2 | [24 empty] | DDCS2_1 | [8 empty] | 後湖SS.11BE2 | 11BE2 (非取樣點) | BUS | S26/11/1BUS/BE2 |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo