## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S31 | 朴子SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 一號 BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S31_A1 | [8 empty] | 朴子SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S31 | 朴子SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | ＃1 MTR | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | ada | B2/S31_D1 | [8 empty] | 朴子SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | ＃2 MTR | KV | 二號主變二次側11KV BUS(A) | kV_-9_9(-2000_2000) | aba | B2/S31_D1 | [8 empty] | 朴子SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | ＃3 MTR | KV | 三號主變二次側BUS(MA) | kV_-9_9(-2000_2000) | aca | B2/S31_D1 | [8 empty] | 朴子SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 4BUS | #4BUS |  | V |  | DELETE | MvMoment | kV |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | SPARE |  |  | kV_-9_9(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S31_A1 | [8 empty] | 朴子SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0288 |  |  | 1-31-13 |  |  | 69KV＃1 BUS | 6VUA | 69KV BUS#1衡相監視警報 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 610 | MW | 嘉太朴子線有效電力 | MW_-120_120(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.610_MW | 嘉太線 MW | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 610 | MVAR | 嘉太朴子線無效電力 | MVAR_-120_120(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.610_MVAR | 嘉太線 MVAR | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 610 | MWH(＋) | 嘉太朴子線瓦時(正)計量值 |  |  | B2/S31_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 11 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 620 | MW | 朴子鹿草線有效電力 | MW_-48_48(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.620_MW | 朴子鹿草線 MW | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.096 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 620 | MVAR | 朴子鹿草線無效電力 | MVAR_-48_48(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.620_MVAR | 朴子鹿草線 MVAR | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.096 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 620 | MWH(＋) | 朴子鹿草線瓦時(正)計量值 |  |  | B2/S31_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 14 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 640 | MW | 北港朴子線有效電力 | MW_-120_120(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.640_MW | 北港線 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 640 | MVAR | 北港朴子線無效電力 | MVAR_-120_120(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.640_MVAR | 北港線 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 640 | MWH(＋) | 北港朴子線瓦時(正)計量值 |  |  | B2/S31_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 630 | MW | 東石朴子線有效電力 | MW_-144_144(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.630_MW | 東石線 MW | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 630 | MVAR | 東石朴子線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S31_A1 | [8 empty] | 朴子SS.630_MVAR | 東石線 MVAR | LINE69 |  |  |  |  | CDC | 19 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | 630 | MWH(＋) | 東石朴子線瓦時(正)計量值 |  |  | B2/S31_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 20 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 610 | 51A(PHA) | 嘉太朴子線(610) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_PHA | 嘉太線(610) 相間RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 610 | 51NA(GDA) | 嘉太朴子線(610) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_GDA | 嘉太線(610) 接地RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-02 |  |  | 620 | 51A(PHA) | 朴子鹿草線(620) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.620_PHA | 朴子鹿草線(620) 相間RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-03 |  |  | 620 | 51NA(GDA) | 朴子鹿草線(620) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.620_GDA | 朴子鹿草線(620) 接地RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-09-06 |  |  | 640 | 51A(PHA) | 北港朴子線(640) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_PHA | 北港線(640) 相間RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-09-07 |  |  | 640 | 51NA(GDA) | 北港朴子線(640) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_GDA | 北港線(640) 接地RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-02 |  |  | 630 | 51A(PHA) | 東石朴子線(630) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_PHA | 東石線(630) 相間RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-03 |  |  | 630 | 51NA(GDA) | 東石朴子線(630) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_GDA | 東石線(630) 接地RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 610 | CB ON/OFF | 嘉太朴子線(610) |  | aaca | B2/S31_A1 | [8 empty] | 朴子SS.610_CB | 610(嘉太線) CB | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0075 |  | 0004 | 1-09-00 |  | 1-03 | 620 | CB ON/OFF | 朴子鹿草線(620) |  | aaba | B2/S31_A1 | [8 empty] | 朴子SS.620_CB | 620(朴子鹿草線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0079 |  | 0005 | 1-09-04 |  | 1-04 | 640 | CB ON/OFF | 北港朴子線(640) |  | aaga | B2/S31_A1 | [8 empty] | 朴子SS.640_CB | 640(北港線) CB | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0083 |  | 0006 | 1-0A-00 |  | 1-05 | 630 | CB ON/OFF | 東石朴子線(630) |  | aaea | B2/S31_A1 | [8 empty] | 朴子SS.630_CB | 630(東石線) CB | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | ABS1 | 611 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0401 | 402 | 0022 | 1-38-14 | 1-38-15 | 1-15 | 611 | ABS ON | 嘉太朴子線BUS側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.611_ABS | 611(嘉太線) ABS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | ABS2 | 612 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0403 | 404 | 0023 | 1-39-00 | 1-39-01 | 1-16 | 612 | ABS ON | 嘉太朴子線線路側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.612_ABS | 612(嘉太線) ABS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0407 | 408 | 0025 | 1-39-04 | 1-39-05 | 1-18 | 621 | ABS ON | 朴子鹿草線BUS側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.621_ABS | 621(朴子鹿草線) ABS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0409 | 410 | 0026 | 1-39-06 | 1-39-07 | 1-19 | 622 | ABS ON | 朴子鹿草線線路側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.622_ABS | 622(朴子鹿草線) ABS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ABS1 | 641 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0413 | 414 | 0028 | 1-39-10 | 1-39-11 | 1-1B | 641 | ABS ON | 北港朴子線BUS側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.641_ABS | 641(北港線) ABS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ABS2 | 642 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0415 | 416 | 0029 | 1-39-12 | 1-39-13 | 1-1C | 642 | ABS ON | 北港朴子線線路側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.642_ABS | 642(北港線) ABS | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | ABS1 | 631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0419 | 420 | 0031 | 1-3A-00 | 1-3A-01 | 1-1E | 631 | ABS ON | 東石朴子線BUS側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.631_ABS | 631(東石線) ABS | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | ABS2 | 632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0421 | 422 | 0032 | 1-3A-02 | 1-3A-03 | 1-1F | 632 | ABS ON | 東石朴子線線路側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.632_ABS | 632(東石線) ABS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0405 | 406 | 0024 | 1-39-02 | 1-39-03 | 1-17 | 612E | ABS ON | 嘉太朴子線接地組 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.612E_ES | 612E(嘉太線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | LE0 | 610LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | BE0 | 610BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0411 | 412 | 0027 | 1-39-08 | 1-39-09 | 1-1A | 622E | ABS ON | 朴子鹿草線接地組 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.622E_ES | 622E(朴子鹿草線) ES | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | LE0 | 620LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 45 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | BE0 | 620BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 46 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ES2 | 642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0417 | 418 | 0030 | 1-39-14 | 1-39-15 | 1-1D | 642E | ABS ON | 北港朴子線接地組 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.642E_ES | 642E(北港線) ES | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | LE0 | 640LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 48 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | BE0 | 640BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 49 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0423 | 424 | 0033 | 1-3A-04 | 1-3A-05 | 1-20 | 632E | ABS ON | 東石朴子線接地組 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.632E_ES | 632E(東石線) ES | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | LE0 | 630LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 51 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | BE0 | 630BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 52 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | JD31 | VAR | 朴十一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線KVAR | 11KV朴十一線 KVAR | FEEDER |  |  |  |  | CDC | 53 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | JD31 | A1 | 朴十一線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線A1 | 11KV朴十一線 R相AMP | FEEDER |  |  |  |  | CDC | 54 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | JD31 | A2 | 朴十一線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線A2 | 11KV朴十一線 S相AMP | FEEDER |  |  |  |  | CDC | 55 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | JD31 | A3 | 朴十一線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線A3 | 11KV朴十一線 T相AMP | FEEDER |  |  |  |  | CDC | 56 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | JD31 | NA | 朴十一線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線A0 | 11KV朴十一線 N相AMP | FEEDER |  |  |  |  | CDC | 57 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | JD31 | KWH(＋) | 朴十一線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 58 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | JD32 | VAR | 朴十二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線KVAR | 11KV朴十二線 KVAR | FEEDER |  |  |  |  | CDC | 59 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | JD32 | A1 | 朴十二線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線A1 | 11KV朴十二線 R相AMP | FEEDER |  |  |  |  | CDC | 60 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | JD32 | A2 | 朴十二線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線A2 | 11KV朴十二線 S相AMP | FEEDER |  |  |  |  | CDC | 61 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | JD32 | A3 | 朴十二線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線A3 | 11KV朴十二線 T相AMP | FEEDER |  |  |  |  | CDC | 62 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | JD32 | NA | 朴十二線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線A0 | 11KV朴十二線 N相AMP | FEEDER |  |  |  |  | CDC | 63 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | JD32 | KWH(＋) | 朴十二線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 64 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | JD33 | VAR | 朴十三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線KVAR | 11KV朴十三線 KVAR | FEEDER |  |  |  |  | CDC | 65 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | JD33 | A1 | 朴十三線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線A1 | 11KV朴十三線 R相AMP | FEEDER |  |  |  |  | CDC | 66 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | JD33 | A2 | 朴十三線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線A2 | 11KV朴十三線 S相AMP | FEEDER |  |  |  |  | CDC | 67 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | JD33 | A3 | 朴十三線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線A3 | 11KV朴十三線 T相AMP | FEEDER |  |  |  |  | CDC | 68 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | JD33 | NA | 朴十三線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線A0 | 11KV朴十三線 N相AMP | FEEDER |  |  |  |  | CDC | 69 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | JD33 | KWH(＋) | 朴十三線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 70 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | JD34 | VAR | 朴十四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線KVAR | 11KV朴十四線 KVAR | FEEDER |  |  |  |  | CDC | 71 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | JD34 | A1 | 朴十四線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線A1 | 11KV朴十四線 R相AMP | FEEDER |  |  |  |  | CDC | 72 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | JD34 | A2 | 朴十四線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線A2 | 11KV朴十四線 S相AMP | FEEDER |  |  |  |  | CDC | 73 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | JD34 | A3 | 朴十四線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線A3 | 11KV朴十四線 T相AMP | FEEDER |  |  |  |  | CDC | 74 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | JD34 | NA | 朴十四線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線A0 | 11KV朴十四線 N相AMP | FEEDER |  |  |  |  | CDC | 75 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | JD34 | KWH(＋) | 朴十四線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 76 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | JD35 | VAR | 朴十五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線KVAR | 11KV朴十五線 KVAR | FEEDER |  |  |  |  | CDC | 77 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | JD35 | A1 | 朴十五線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線A1 | 11KV朴十五線 R相AMP | FEEDER |  |  |  |  | CDC | 78 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | JD35 | A2 | 朴十五線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線A2 | 11KV朴十五線 S相AMP | FEEDER |  |  |  |  | CDC | 79 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | JD35 | A3 | 朴十五線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線A3 | 11KV朴十五線 T相AMP | FEEDER |  |  |  |  | CDC | 80 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | JD35 | NA | 朴十五線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線A0 | 11KV朴十五線 N相AMP | FEEDER |  |  |  |  | CDC | 81 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | JD35 | KWH(＋) | 朴十五線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 82 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線KVAR | 11KV朴十六線 KVAR | FEEDER |  |  |  |  | CDC | 83 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線A1 | 11KV朴十六線 R相AMP | FEEDER |  |  |  |  | CDC | 84 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線A2 | 11KV朴十六線 S相AMP | FEEDER |  |  |  |  | CDC | 85 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線A3 | 11KV朴十六線 T相AMP | FEEDER |  |  |  |  | CDC | 86 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線A0 | 11KV朴十六線 N相AMP | FEEDER |  |  |  |  | CDC | 87 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | kWh |  | DELETE | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0038 |  |  | 2-46 |  |  | 69KV LINE1 | SPARE |  |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 88 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線KVAR | 11KV朴十七線 KVAR | FEEDER |  |  |  |  | CDC | 89 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線A1 | 11KV朴十七線 R相AMP | FEEDER |  |  |  |  | CDC | 90 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線A2 | 11KV朴十七線 S相AMP | FEEDER |  |  |  |  | CDC | 91 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線A3 | 11KV朴十七線 T相AMP | FEEDER |  |  |  |  | CDC | 92 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線A0 | 11KV朴十七線 N相AMP | FEEDER |  |  |  |  | CDC | 93 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | kWh |  | DELETE | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0039 |  |  | 2-47 |  |  | 69KV LINE1 | SPARE |  |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 94 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線KVAR | 11KV朴十八線 KVAR | FEEDER |  |  |  |  | CDC | 95 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線A1 | 11KV朴十八線 R相AMP | FEEDER |  |  |  |  | CDC | 96 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線A2 | 11KV朴十八線 S相AMP | FEEDER |  |  |  |  | CDC | 97 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線A3 | 11KV朴十八線 T相AMP | FEEDER |  |  |  |  | CDC | 98 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線A0 | 11KV朴十八線 N相AMP | FEEDER |  |  |  |  | CDC | 99 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | kWh |  | DELETE | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0040 |  |  | 2-48 |  |  | 610 | MVARH(＋) | 嘉太朴子線乏時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 100 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線KVAR | 11KV朴十九線 KVAR | FEEDER |  |  |  |  | CDC | 101 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線A1 | 11KV朴十九線 R相AMP | FEEDER |  |  |  |  | CDC | 102 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線A2 | 11KV朴十九線 S相AMP | FEEDER |  |  |  |  | CDC | 103 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線A3 | 11KV朴十九線 T相AMP | FEEDER |  |  |  |  | CDC | 104 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線A0 | 11KV朴十九線 N相AMP | FEEDER |  |  |  |  | CDC | 105 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | kWh |  | DELETE | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0041 |  |  | 2-49 |  |  | 610 | MVARH(－) | 嘉太朴子線乏時(負)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 106 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | SPARE |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線KVAR | 11KV朴二十線 KVAR | FEEDER |  |  |  |  | CDC | 107 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線A1 | 11KV朴二十線 R相AMP | FEEDER |  |  |  |  | CDC | 108 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線A2 | 11KV朴二十線 S相AMP | FEEDER |  |  |  |  | CDC | 109 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線A3 | 11KV朴二十線 T相AMP | FEEDER |  |  |  |  | CDC | 110 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | SPARE |  |  | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線A0 | 11KV朴二十線 N相AMP | FEEDER |  |  |  |  | CDC | 111 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | kWh |  | DELETE | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0042 |  |  | 2-4A |  |  | 620 | MVARH(＋) | 朴子鹿草線乏時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 112 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JD21 | 51A(PHA) | 朴一線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD21_PHA | 11KV朴一線(JD21) 相間RY | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JD21 | 51NA(GDA) | 朴一線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD21_GDA | 11KV朴一線(JD21) 接地RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0061 | 1-33-07 |  | 1-3C | JD21 | F1 79RY U/L | 朴一線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD21_79UL | 11KV朴一線(JD21) 79RY U/L | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0113 | 1-36-00 |  | 1-70 | JD21 LCO ADJ | ADJ(U/L) | 朴一線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD21_ADJ | 11KV朴一線(JD21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-03 |  |  | JD22 | 51A(PHA) | 朴二線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD22_PHA | 11KV朴二線(JD22) 相間RY | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JD22 | 51NA(GDA) | 朴二線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD22_GDA | 11KV朴二線(JD22) 接地RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0062 | 1-33-08 |  | 1-3D | JD22 | F2 79RY U/L | 朴二線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD22_79UL | 11KV朴二線(JD22) 79RY U/L | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0114 | 1-36-01 |  | 1-71 | JD22 LCO ADJ | ADJ(U/L) | 朴二線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD22_ADJ | 11KV朴二線(JD22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JD23 | 51A(PHA) | 朴三線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD23_PHA | 11KV朴三線(JD23) 相間RY | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0D-06 |  |  | JD23 | 51NA(GDA) | 朴三線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD23_GDA | 11KV朴三線(JD23) 接地RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0316 |  | 0063 | 1-33-09 |  | 1-3E | JD23 | F3 79RY U/L | 朴三線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD23_79UL | 11KV朴三線(JD23) 79RY U/L | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0115 | 1-36-02 |  | 1-72 | JD23 LCO ADJ | ADJ(U/L) | 朴三線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD23_ADJ | 11KV朴三線(JD23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | JD24 | 51A(PHA) | 朴四線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD24_PHA | 11KV朴四線(JD24) 相間RY | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | JD24 | 51NA(GDA) | 朴四線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD24_GDA | 11KV朴四線(JD24) 接地RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0064 | 1-33-10 |  | 1-3F | JD24 | F4 79RY U/L | 朴四線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD24_79UL | 11KV朴四線(JD24) 79RY U/L | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0116 | 1-36-03 |  | 1-73 | JD24 LCO ADJ | ADJ(U/L) | 朴四線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD24_ADJ | 11KV朴四線(JD24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-01 |  |  | JD25 | 51A(PHA) | 朴五線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD25_PHA | 11KV朴五線(JD25) 相間RY | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | JD25 | 51NA(GDA) | 朴五線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD25_GDA | 11KV朴五線(JD25) 接地RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0318 |  | 0065 | 1-33-11 |  | 1-40 | JD25 | F5 79RY U/L | 朴五線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD25_79UL | 11KV朴五線(JD25) 79RY U/L | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0117 | 1-36-04 |  | 1-74 | JD25 LCO ADJ | ADJ(U/L) | 朴五線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD25_ADJ | 11KV朴五線(JD25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JS26 | 51A(PHA) | 朴六線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD26_PHA | 11KV朴六線(JD26) 相間RY | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | JD26 | 51NA(GDA) | 朴六線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD26_GDA | 11KV朴六線(JD26) 接地RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0082 | 1-34-07 |  | 1-51 | JD26 | F6 79RY U/L | 朴六線復閉電驛(使用 / 閉鎖) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD26_79UL | 11KV朴六線(JD26) 79RY U/L | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0118 | 1-36-05 |  | 1-75 | JD26 LCO ADJ | ADJ(U/L) | 朴六線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD26_ADJ | 11KV朴六線(JD26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | JD27 | 51A(PHA) | 朴七線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD27_PHA | 11KV朴七線(JD27) 相間RY | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JD27 | 51NA(GDA) | 朴七線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD27_GDA | 11KV朴七線(JD27) 接地RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0083 | 1-34-08 |  | 1-52 | JD27 | F7 79RY U/L | 朴七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD27_79UL | 11KV朴七線(JD27) 79RY U/L | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0119 | 1-36-06 |  | 1-76 | JD27 LCO ADJ | ADJ(U/L) | 朴七線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD27_ADJ | 11KV朴七線(JD27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | JD28 | 51A(PHA) | 朴八線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD28_PHA | 11KV朴八線(JD28) 相間RY | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | JD28 | 51NA(GDA) | 朴八線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD28_GDA | 11KV朴八線(JD28) 接地RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0332 |  | 0084 | 1-34-09 |  | 1-53 | JD28 | F8 79RY U/L | 朴八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD28_79UL | 11KV朴八線(JD28) 79RY U/L | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0120 | 1-36-07 |  | 1-77 | JD28 LCO ADJ | ADJ(U/L) | 朴八線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD28_ADJ | 11KV朴八線(JD28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JD29 | 51A(PHA) | 朴九線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD29_PHA | 11KV朴九線(JD29) 相間RY | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | JD29 | 51NA(GDA) | 朴九線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD29_GDA | 11KV朴九線(JD29) 接地RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0085 | 1-34-10 |  | 1-54 | JD29 | F9 79RY U/L | 朴九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD29_79UL | 11KV朴九線(JD29) 79RY U/L | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0121 | 1-36-08 |  | 1-78 | JD29 LCO ADJ | ADJ(U/L) | 朴九線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD29_ADJ | 11KV朴九線(JD29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | JD30 | 51A(PHA) | 朴十線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD30_PHA | 11KV朴十線(JD30) 相間RY | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JD30 | 51NA(GDA) | 朴十線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD30_GDA | 11KV朴十線(JD30) 接地RY | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0334 |  | 0086 | 1-34-11 |  | 1-55 | JD30 | F10 79RY U/L | 朴十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD30_79UL | 11KV朴十線(JD30) 79RY U/L | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0122 | 1-36-09 |  | 1-79 | JD30 LCO ADJ | ADJ(U/L) | 朴十線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD30_ADJ | 11KV朴十線(JD30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-04 |  |  | JD31 | 51A(PHA) | 朴十一線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD31_PHA | 11KV朴十一線(JD31) 相間RY | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-12-05 |  |  | JD31 | 51NA(GDA) | 朴十一線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD31_GDA | 11KV朴十一線(JD31) 接地RY | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0101 | 1-35-07 |  | 1-64 | JD31 | F11 79S U/L | 朴十一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD31_79UL | 11KV朴十一線(JD31) 79RY U/L | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0123 | 1-36-10 |  | 1-7A | JD31 LCO ADJ | ADJ(U/L) | 朴十一線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD31_ADJ | 11KV朴十一線(JD31) LCO分流器 | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-12-06 |  |  | JD32 | 51A(PHA) | 朴十二線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD32_PHA | 11KV朴十二線(JD32) 相間RY | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-12-07 |  |  | JD32 | 51NA(GDA) | 朴十二線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD32_GDA | 11KV朴十二線(JD32) 接地RY | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0102 | 1-35-08 |  | 1-65 | JD32 | F12 79S U/L | 朴十二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD32_79UL | 11KV朴十二線(JD32) 79RY U/L | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0124 | 1-36-11 |  | 1-7B | JD32 LCO ADJ | ADJ(U/L) | 朴十二線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD32_ADJ | 11KV朴十二線(JD32) LCO分流器 | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | JD33 | 51A(PHA) | 朴十三線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD33_PHA | 11KV朴十三線(JD33) 相間RY | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | JD33 | 51NA(GDA) | 朴十三線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD33_GDA | 11KV朴十三線(JD33) 接地RY | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0348 |  | 0103 | 1-35-09 |  | 1-66 | JD33 | F13 79S U/L | 朴十三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD33_79UL | 11KV朴十三線(JD33) 79RY U/L | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0367 |  | 0125 | 1-36-12 |  | 1-7C | JD33 LCO ADJ | ADJ(U/L) | 朴十三線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD33_ADJ | 11KV朴十三線(JD33) LCO分流器 | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-02 |  |  | JD34 | 51A(PHA) | 朴十四線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD34_PHA | 11KV朴十四線(JD34) 相間RY | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | JD34 | 51NA(GDA) | 朴十四線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD34_GDA | 11KV朴十四線(JD34) 接地RY | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0104 | 1-35-10 |  | 1-67 | JD34 | F14 79S U/L | 朴十四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD34_79UL | 11KV朴十四線(JD34) 79RY U/L | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0368 |  | 0126 | 1-36-13 |  | 1-7D | JD34 LCO ADJ | ADJ(U/L) | 朴十四線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD34_ADJ | 11KV朴十四線(JD34) LCO分流器 | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | JD35 | 51A(PHA) | 朴十五線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD35_PHA | 11KV朴十五線(JD35) 相間RY | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-13-05 |  |  | JD35 | 51NA(GDA) | 朴十五線 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD35_GDA | 11KV朴十五線(JD35) 接地RY | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0350 |  | 0105 | 1-35-11 |  | 1-68 | JD35 | F15 79S U/L | 朴十五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD35_79UL | 11KV朴十五線(JD35) 79RY U/L | FEEDER |  |  |  |  | CDC | 171 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0369 |  | 0127 | 1-36-14 |  | 1-7E | JD35 LCO ADJ | ADJ(U/L) | 朴十五線分流器(使用 / 閉鎖)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD35_ADJ | 11KV朴十五線(JD35) LCO分流器 | FEEDER |  |  |  |  | CDC | 172 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0525 |  |  | 2-09-02 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD36_PHA | 11KV朴十六線(JD36) 相間RY | FEEDER |  |  |  |  | CDC | 173 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0526 |  |  | 2-09-03 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD36_GDA | 11KV朴十六線(JD36) 接地RY | FEEDER |  |  |  |  | CDC | 174 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0142 | 2-30-07 |  | 2-0D | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD36_79UL | 11KV朴十六線(JD36) 79RY U/L | FEEDER |  |  |  |  | CDC | 175 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0559 |  | 0148 | 2-30-12 |  | 2-13 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD36_ADJ | 11KV朴十六線(JD36) LCO分流器 | FEEDER |  |  |  |  | CDC | 176 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0527 |  |  | 2-09-04 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD37_PHA | 11KV朴十七線(JD37) 相間RY | FEEDER |  |  |  |  | CDC | 177 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0528 |  |  | 2-09-05 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD37_GDA | 11KV朴十七線(JD37) 接地RY | FEEDER |  |  |  |  | CDC | 178 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0143 | 2-30-08 |  | 2-0E | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD37_79UL | 11KV朴十七線(JD37) 79RY U/L | FEEDER |  |  |  |  | CDC | 179 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0560 |  | 0149 | 2-30-13 |  | 2-14 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD37_ADJ | 11KV朴十七線(JD37) LCO分流器 | FEEDER |  |  |  |  | CDC | 180 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0529 |  |  | 2-09-06 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD38_PHA | 11KV朴十八線(JD38) 相間RY | FEEDER |  |  |  |  | CDC | 181 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0530 |  |  | 2-09-07 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD38_GDA | 11KV朴十八線(JD38) 接地RY | FEEDER |  |  |  |  | CDC | 182 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0144 | 2-30-09 |  | 2-0F | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD38_79UL | 11KV朴十八線(JD38) 79RY U/L | FEEDER |  |  |  |  | CDC | 183 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0561 |  | 0150 | 2-30-14 |  | 2-15 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD38_ADJ | 11KV朴十八線(JD38) LCO分流器 | FEEDER |  |  |  |  | CDC | 184 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0531 |  |  | 2-0A-00 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD39_PHA | 11KV朴十九線(JD39) 相間RY | FEEDER |  |  |  |  | CDC | 185 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0532 |  |  | 2-0A-01 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD39_GDA | 11KV朴十九線(JD39) 接地RY | FEEDER |  |  |  |  | CDC | 186 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0557 |  | 0145 | 2-30-10 |  | 2-10 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD39_79UL | 11KV朴十九線(JD39) 79RY U/L | FEEDER |  |  |  |  | CDC | 187 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0562 |  | 0151 | 2-30-15 |  | 2-16 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD39_ADJ | 11KV朴十九線(JD39) LCO分流器 | FEEDER |  |  |  |  | CDC | 188 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0533 |  |  | 2-0A-02 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD40_PHA | 11KV朴二十線(JD40) 相間RY | FEEDER |  |  |  |  | CDC | 189 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0534 |  |  | 2-0A-03 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD40_GDA | 11KV朴二十線(JD40) 接地RY | FEEDER |  |  |  |  | CDC | 190 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0146 | 2-30-11 |  | 2-11 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD40_79UL | 11KV朴二十線(JD40) 79RY U/L | FEEDER |  |  |  |  | CDC | 191 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0563 |  | 0152 | 2-31-00 |  | 2-17 | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.JD40_ADJ | 11KV朴二十線(JD40) LCO分流器 | FEEDER |  |  |  |  | CDC | 192 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JD21/T1 |  |  | 0099 |  | 0053 | 1-0C-00 |  | 1-34 | JD21 | CB ON/OFF | 朴一線 11KV |  | adbb | B2/S31_D1 | [8 empty] | 朴子SS.JD21_CB | JD21(11KV朴一線) CB | FEEDER |  |  |  |  | CDC | 193 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD21_DS | JD21_DS (非取樣點) | FEEDER | [5 empty] | 194 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | E1 | JD21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD21_ES | JD21_ES (非取樣點) | FEEDER | [5 empty] | 195 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JD22/T1 |  |  | 0100 |  | 0054 | 1-0C-01 |  | 1-35 | JD22 | CB ON/OFF | 朴二線 11KV |  | adcb | B2/S31_D1 | [8 empty] | 朴子SS.JD22_CB | JD22(11KV朴二線) CB | FEEDER |  |  |  |  | CDC | 196 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD22_DS | JD22_DS (非取樣點) | FEEDER | [5 empty] | 197 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | E1 | JD22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD22_ES | JD22_ES (非取樣點) | FEEDER | [5 empty] | 198 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JD23/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | JD23 | CB ON/OFF | 朴三線 11KV |  | addb | B2/S31_D1 | [8 empty] | 朴子SS.JD23_CB | JD23(11KV朴三線) CB | FEEDER |  |  |  |  | CDC | 199 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD23_DS | JD23_DS (非取樣點) | FEEDER | [5 empty] | 200 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | E1 | JD23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD23_ES | JD23_ES (非取樣點) | FEEDER | [5 empty] | 201 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JD24/T1 |  |  | 0102 |  | 0056 | 1-0C-03 |  | 1-37 | JD24 | CB ON/OFF | 朴四線 11KV |  | adeb | B2/S31_D1 | [8 empty] | 朴子SS.JD24_CB | JD24(11KV朴四線) CB | FEEDER |  |  |  |  | CDC | 202 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD24_DS | JD24_DS (非取樣點) | FEEDER | [5 empty] | 203 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | E1 | JD24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD24_ES | JD24_ES (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JD25/T1 |  |  | 0103 |  | 0057 | 1-0C-04 |  | 1-38 | JD25 | CB ON/OFF | 朴五線 11KV |  | adfb | B2/S31_D1 | [8 empty] | 朴子SS.JD25_CB | JD25(11KV朴五線) CB | FEEDER |  |  |  |  | CDC | 205 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD25_DS | JD25_DS (非取樣點) | FEEDER | [5 empty] | 206 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | E1 | JD25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD25_ES | JD25_ES (非取樣點) | FEEDER | [5 empty] | 207 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/JD26/T1 |  |  | 0121 |  | 0074 | 1-0E-06 |  | 1-49 | JD26 | CB ON/OFF | 朴六線 11KV |  | abab | B2/S31_D1 | [8 empty] | 朴子SS.JD26_CB | JD26(11KV朴六線) CB | FEEDER |  |  |  |  | CDC | 208 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD26_DS | JD26_DS (非取樣點) | FEEDER | [5 empty] | 209 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | E1 | JD26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD26_ES | JD26_ES (非取樣點) | FEEDER | [5 empty] | 210 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/JD27/T1 |  |  | 0122 |  | 0075 | 1-0E-07 |  | 1-4A | JD27 | CB ON/OFF | 朴七線 11KV |  | abbb | B2/S31_D1 | [8 empty] | 朴子SS.JD27_CB | JD27(11KV朴七線) CB | FEEDER |  |  |  |  | CDC | 211 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD27_DS | JD27_DS (非取樣點) | FEEDER | [5 empty] | 212 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | E1 | JD27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD27_ES | JD27_ES (非取樣點) | FEEDER | [5 empty] | 213 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/JD28/T1 |  |  | 0123 |  | 0076 | 1-0F-00 |  | 1-4B | JD28 | CB ON/OFF | 朴八線 11KV |  | abdb | B2/S31_D1 | [8 empty] | 朴子SS.JD28_CB | JD28(11KV朴八線) CB | FEEDER |  |  |  |  | CDC | 214 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD28_DS | JD28_DS (非取樣點) | FEEDER | [5 empty] | 215 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | E1 | JD28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD28_ES | JD28_ES (非取樣點) | FEEDER | [5 empty] | 216 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | L/JD29/T1 |  |  | 0124 |  | 0077 | 1-0F-01 |  | 1-4C | JD29 | CB ON/OFF | 朴九線 11KV |  | accb | B2/S31_D1 | [8 empty] | 朴子SS.JD29_CB | JD29(11KV朴九線) CB | FEEDER |  |  |  |  | CDC | 217 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD29_DS | JD29_DS (非取樣點) | FEEDER | [5 empty] | 218 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | E1 | JD29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD29_ES | JD29_ES (非取樣點) | FEEDER | [5 empty] | 219 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | L/JD30/T1 |  |  | 0125 |  | 0078 | 1-0F-02 |  | 1-4D | JD30 | CB ON/OFF | 朴十線 11KV |  | acdb | B2/S31_D1 | [8 empty] | 朴子SS.JD30_CB | JD30(11KV朴十線) CB | FEEDER |  |  |  |  | CDC | 220 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD30_DS | JD30_DS (非取樣點) | FEEDER | [5 empty] | 221 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | E1 | JD30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD30_ES | JD30_ES (非取樣點) | FEEDER | [5 empty] | 222 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/JD31/T1 |  |  | 0143 |  | 0093 | 1-11-04 |  | 1-5C | JD31 | CB ON/OFF | 朴十一線 11KV |  | aabb | B2/S31_D1 | [8 empty] | 朴子SS.JD31_CB | JD31(11KV朴十一線) CB | FEEDER |  |  |  |  | CDC | 223 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD31_DS | JD31_DS (非取樣點) | FEEDER | [5 empty] | 224 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | E1 | JD31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD31_ES | JD31_ES (非取樣點) | FEEDER | [5 empty] | 225 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/JD32/T1 |  |  | 0144 |  | 0094 | 1-11-05 |  | 1-5D | JD32 | CB ON/OFF | 朴十二線 11KV |  | aadb | B2/S31_D1 | [8 empty] | 朴子SS.JD32_CB | JD32(11KV朴十二線) CB | FEEDER |  |  |  |  | CDC | 226 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD32_DS | JD32_DS (非取樣點) | FEEDER | [5 empty] | 227 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | E1 | JD32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD32_ES | JD32_ES (非取樣點) | FEEDER | [5 empty] | 228 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/JD33/T1 |  |  | 0145 |  | 0095 | 1-11-06 |  | 1-5E | JD33 | CB ON/OFF | 朴十三線 11KV |  | aaeb | B2/S31_D1 | [8 empty] | 朴子SS.JD33_CB | JD33(11KV朴十三線) CB | FEEDER |  |  |  |  | CDC | 229 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD33_DS | JD33_DS (非取樣點) | FEEDER | [5 empty] | 230 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | E1 | JD33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD33_ES | JD33_ES (非取樣點) | FEEDER | [5 empty] | 231 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/JD34/T1 |  |  | 0146 |  | 0096 | 1-11-07 |  | 1-5F | JD34 | CB ON/OFF | 朴十四線 11KV |  | aafb | B2/S31_D1 | [8 empty] | 朴子SS.JD34_CB | JD34(11KV朴十四線) CB | FEEDER |  |  |  |  | CDC | 232 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD34_DS | JD34_DS (非取樣點) | FEEDER | [5 empty] | 233 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | E1 | JD34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD34_ES | JD34_ES (非取樣點) | FEEDER | [5 empty] | 234 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/JD35/T1 |  |  | 0147 |  | 0097 | 1-12-00 |  | 1-60 | JD35 | CB ON/OFF | 朴十五線 11KV |  | aagb | B2/S31_D1 | [8 empty] | 朴子SS.JD35_CB | JD35(11KV朴十五線) CB | FEEDER |  |  |  |  | CDC | 235 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD35_DS | JD35_DS (非取樣點) | FEEDER | [5 empty] | 236 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | E1 | JD35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD35_ES | JD35_ES (非取樣點) | FEEDER | [5 empty] | 237 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | CB | JD36 | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JD36/T1 |  |  | 0500 |  | 0134 | 2-02-01 |  | 2-05 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.JD36_CB | JD36(11KV朴十六線) CB | FEEDER |  |  |  |  | CDC | 238 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | DS | JD36_DS(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD36_DS | JD36_DS (非取樣點) | FEEDER | [5 empty] | 239 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | ES | JD36_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD36_ES | JD36_ES (非取樣點) | FEEDER | [5 empty] | 240 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | CB | JD37 | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JD37/T1 |  |  | 0501 |  | 0135 | 2-02-02 |  | 2-06 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.JD37_CB | JD37(11KV朴十七線) CB | FEEDER |  |  |  |  | CDC | 241 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | DS | JD37_DS(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD37_DS | JD37_DS (非取樣點) | FEEDER | [5 empty] | 242 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | ES | JD37_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD37_ES | JD37_ES (非取樣點) | FEEDER | [5 empty] | 243 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | CB | JD38 | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JD38/T1 |  |  | 0502 |  | 0136 | 2-02-03 |  | 2-07 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.JD38_CB | JD38(11KV朴十八線) CB | FEEDER |  |  |  |  | CDC | 244 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | DS | JD38_DS(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD38_DS | JD38_DS (非取樣點) | FEEDER | [5 empty] | 245 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | ES | JD38_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD38_ES | JD38_ES (非取樣點) | FEEDER | [5 empty] | 246 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | CB | JD39 | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JD39/T1 |  |  | 0503 |  | 0137 | 2-02-04 |  | 2-08 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.JD39_CB | JD39(11KV朴十九線) CB | FEEDER |  |  |  |  | CDC | 247 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | DS | JD39_DS(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD39_DS | JD39_DS (非取樣點) | FEEDER | [5 empty] | 248 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | ES | JD39_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD39_ES | JD39_ES (非取樣點) | FEEDER | [5 empty] | 249 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | CB | JD40 | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | L/JD40/T1 |  |  | 0504 |  | 0138 | 2-02-05 |  | 2-09 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.JD40_CB | JD40(11KV朴二十線) CB | FEEDER |  |  |  |  | CDC | 250 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | DS | JD40_DS(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD40_DS | JD40_DS (非取樣點) | FEEDER | [5 empty] | 251 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | ES | JD40_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.JD40_ES | JD40_ES (非取樣點) | FEEDER | [5 empty] | 252 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | ＃2 TIE | A1 | 二號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 253 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | ＃2 TIE | A2 | 二號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 254 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | ＃2 TIE | A3 | 二號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 255 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | ＃3 TIE | A1 | 三號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE |  |  |  |  | CDC | 256 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | ＃3 TIE | A2 | 三號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE |  |  |  |  | CDC | 257 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | ＃3 TIE | A3 | 三號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE |  |  |  |  | CDC | 258 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BBUS | B/1BUS |  |  | 0104 |  | 0051 | 1-0C-05 |  | 1-32 | ＃2 TIE | CB ON/OFF | 二號聯絡斷路器 11KV |  | zzzz | B2/S31_D1 | [8 empty] | 朴子SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 259 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | ＃2 TIE | 51A(PHA) | 二號聯絡斷路器 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 260 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-04 |  |  | ＃2 TIE | 51NA(GDA) | 二號聯絡斷路器 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 261 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/3BUS | B/2ABUS |  |  | 0126 |  | 0072 | 1-0F-03 |  | 1-47 | ＃3 TIE | CB ON/OFF | 三號聯絡斷路器 |  | zzzz | B2/S31_D1 | [8 empty] | 朴子SS.TIE3_CB | 11KV TIE3 CB | TIE |  |  |  |  | CDC | 262 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-01 |  |  | ＃3 TIE | 51A(PHA) | 三號聯絡斷路器 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.TIE3_51A | 11KV TIE3 51RY | TIE |  |  |  |  | CDC | 263 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-02 |  |  | ＃3 TIE | 51NA(GDA) | 三號聯絡斷路器 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.TIE3_51NA | 11KV TIE3 51N RY | TIE |  |  |  |  | CDC | 264 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 265 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 266 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | TIE2(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | Point Empty | [7 empty] | 267 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D2 | TIE3(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | Point Empty | [7 empty] | 268 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | ＃1 MTR | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 269 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | ＃1 MTR | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 270 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | ＃1 MTR | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 271 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | ＃1 MTR | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 272 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | ＃1 MTR | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 273 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2 MTR | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 274 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | ＃2 MTR | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 275 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | ＃2 MTR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 276 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | ＃2 MTR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 277 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | ＃2 MTR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 278 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | ＃3 MTR | MW | 三號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 279 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | ＃3 MTR | MVAR | 三號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 280 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | ＃3 MTR | A1 | 三號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 281 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | ＃3 MTR | A2 | 三號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 282 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | ＃3 MTR | A3 | 三號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 283 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | MW |  | DELETE | MvMoment | MW |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | SPARE |  |  | MW_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MTR_MW | #4MTR二次側 MW | DTR |  |  |  |  | CDC | 284 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | MVAR |  | DELETE | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | SPARE |  |  | MVAR_-36_36(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR |  |  |  |  | CDC | 285 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 286 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 287 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | SPARE |  |  | A_-2000_2000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 288 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | ＃1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 289 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 290 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0058 | 1-9B |  | 1-39 | ＃1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 291 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | ＃1 MTR | MWH(＋) | 一號主變瓦時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 292 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | ＃1 MTR | MVARH(＋) | 一號主變乏時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 293 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | ＃2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 294 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | SPARE | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 295 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0079 | 1-BF |  | 1-4E | ＃2 MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 296 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | ＃2 MTR | MWH(＋) | 二號主變瓦時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 297 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | ＃2 MTR | MVARH(＋) | 二號主變乏時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 298 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | ＃3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 299 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | ＃3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 300 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-61 | ＃3 MTR | TAP | 三號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 301 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | ＃3 MTR | MWH(＋) | 三號主變瓦時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 302 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | ＃3 MTR | MVARH(＋) | 三號主變乏時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 303 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | SPARE |  |  | OIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_OIL | #4MTR 油溫 | DTR |  |  |  |  | CDC | 304 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | SPARE |  |  | COIL_-120_120(-2000_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_COIL | #4MTR 線溫 | DTR |  |  |  |  | CDC | 305 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0166 |  | 0139 | 2-A6 |  | 2-0A | SPARE |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_TAP | #4MTR OLTC TAP | DTR |  |  |  |  | CDC | 306 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0043 |  |  | 2-4B |  |  | 620 | MVARH(－) | 朴子鹿草線乏時(負)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 307 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | MVARH_M |  | Element | [12 empty] | 0044 |  |  | 2-4C |  |  | 640 | MVARH(＋) | 北港朴子線乏時(正)計量值 |  |  | B1/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 308 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0004 |  | 0049 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aafb | B3/S31_D1 | [8 empty] | 朴子SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 309 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 310 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 311 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aadb | B3/S31_D1 | [8 empty] | 朴子SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 312 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 313 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 314 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0025 |  | 0089 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aaab | B3/S31_D1 | [8 empty] | 朴子SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 315 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 316 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 317 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/4MTR |  |  | 0485 |  | 0131 | 2-00-02 |  | 2-02 | SPARE |  |  |  | not found | B3/S31_D1 | [8 empty] | 朴子SS.780_CB | 780(#4MTR) CB | DTR |  |  |  |  | CDC | 318 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.780TE | 780TE (非取樣點) | DTR | [5 empty] | 319 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S31_D1 | [8 empty] | 朴子SS.780BE | 780BE (非取樣點) | DTR | [5 empty] | 320 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0005 |  | 0050 | 1-00-02 |  | 1-31 | ＃1 MCB | CB ON/OFF | 一號主變二次側 |  | adaa | B2/S31_D1 | [8 empty] | 朴子SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 321 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | CB | 2MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | T/2MTR |  |  | 0014 |  | 0070 | 1-01-03 |  | 1-45 | ＃2 MCB(A) | CB ON/OFF | 二號主變二次側 |  | abca | B2/S31_D1 | [8 empty] | 朴子SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 322 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | CB | 2MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | T/2MTR |  |  | 0015 |  | 0071 | 1-01-04 |  | 1-46 | ＃2 MCB(B) | CB ON/OFF | 二號主變二次側 |  | acaa | B2/S31_D1 | [8 empty] | 朴子SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 323 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0026 |  | 0090 | 1-02-07 |  | 1-59 | ＃3 MCB | CB ON/OFF | 三號主變二次側 |  | aaca | B2/S31_D1 | [8 empty] | 朴子SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 324 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | CB | 4M | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/4BUS | T/4MTR |  |  | 0486 |  | 0132 | 2-00-03 |  | 2-03 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.4M_CB | 4M(#4MTR) CB | DTR |  |  |  |  | CDC | 325 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750 | 51A(PHA) | 一號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 326 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | 750 | 51NA(GDA) | 一號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 327 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | ＃1 MCB | 51ZA | 一號主變 51Z RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 328 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | ＃1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 329 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  |  | 1-33-03 |  |  | ＃1 MTR | 187S U/L | 一號主變差動電驛(使用 / 閉鎖) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 330 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | 760 | 51A(PHA) | 二號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 331 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | 760 | 51NA(GDA) | 二號主變一次側(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 332 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | ＃2 MCB | 51ZA | 二號主變 51Z RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 333 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | ＃2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 334 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0326 |  |  | 1-34-03 |  |  | ＃2 MTR | 287S U/L | 二號主變差動電驛(使用 / 閉鎖) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 335 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | 770 | 51A | 三號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 336 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | 770 | 51NA | 三號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 337 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | ＃3 MCB | 51ZA | 三號主變 51Z RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 338 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-04 |  |  | ＃3 MTR | 87A | 三號主變差動電驛 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 339 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0342 |  |  | 1-35-03 |  |  | ＃3 MTR | 387S U/L | 三號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 340 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  | 0106 | 1-12-01 |  | 1-69 | ＃3 MCB | 81A | 三號低頻電驛(跳脫＃3 MCB) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR |  |  |  |  | CDC | 341 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0487 |  |  | 2-00-04 |  |  | SPARE |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#4MTR_51A | #4MTR 51RY | DTR |  |  |  |  | CDC | 342 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0488 |  |  | 2-00-05 |  |  | SPARE |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.#4MTR_51NA | #4MTR 51N RY | DTR |  |  |  |  | CDC | 343 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0493 |  |  | 2-01-02 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_51ZA | #4MTR 51Z RY | DTR |  |  |  |  | CDC | 344 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0490 |  |  | 2-00-07 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_87A | #4MTR 87RY | DTR |  |  |  |  | CDC | 345 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 2-30-03 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_87UL | #4MTR 87RY U/L | DTR |  |  |  |  | CDC | 346 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-00-07 |  |  | ＃1 MCB | 51A(PHA) | 一號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 347 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-00 |  |  | ＃1 MTR | 1TRA | 一號主變重故障警報 |  | a | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 348 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0308 |  |  | 1-33-01 |  |  | ＃1 MTR | 1TRF | 一號主變輕故障警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 349 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 1-33-04 |  |  | ＃1 MTR | OLTC R/L | 一號主變OLTC(中心 / 現場) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 350 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0059 | 1-33-05 |  | 1-3A | ＃1 MTR | OLTC A/M | 一號主變OLTC(自動 / 手動) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 351 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-01 |  |  | ＃2 MCB(A) | 51A(PHA) | 二號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 352 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-03 |  |  | ＃2 MCB(B) | 51A(PHA) | 二號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 353 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-00 |  |  | ＃2 MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 354 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0324 |  |  | 1-34-01 |  |  | ＃2 MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 355 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0327 |  |  | 1-34-04 |  |  | ＃2 MTR | OLTC R/L | 二號主變OLTC(中心 / 現場) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 356 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0080 | 1-34-05 |  | 1-4F | ＃2 MTR | OLTC A/M | 二號主變OLTC(自動 / 手動) |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 357 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-03-05 |  |  | ＃3 MCB | 51A(PHA) | 三號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 358 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-00 |  |  | ＃3 MTR | 3TRA | 三號主變重故障警報 |  | a | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 359 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0340 |  |  | 1-35-01 |  |  | ＃3 MTR | 3TRF | 三號主變輕故障警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 360 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0343 |  |  | 1-35-04 |  |  | ＃3 MTR | OLTC R/L | 三號主變OLTC(中心 / 現場)指示 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 361 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0099 | 1-35-05 |  | 1-62 | ＃3 MTR | OLTC A/M | 三號主變OLTC(自動 / 手動)指示 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 362 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51A | 51A1 | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0491 |  |  | 2-01-00 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.4M_51A | #4MTR二次側(4M) 51RY | DTR |  |  |  |  | CDC | 363 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 2-30-00 |  |  | SPARE |  |  |  | a | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_TRA | #4MTR 重故障 | DTR |  |  |  |  | CDC | 364 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0548 |  |  | 2-30-01 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_TRF | #4MTR 輕故障 | DTR |  |  |  |  | CDC | 365 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 2-30-04 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_S/L | #4MTR OLTC S/L | DTR |  |  |  |  | CDC | 366 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0140 | 2-30-05 |  | 2-0B | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_A/M | #4MTR OLTC A/M | DTR |  |  |  |  | CDC | 367 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0387 | 388 | 0043 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | ＃1 MTR 一號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 368 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0389 | 390 | 0044 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | ＃2 MTR 二號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 369 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0391 | 392 | 0045 | 1-38-04 | 1-38-05 | 1-2C | 771 | ABS ON | ＃3 MTR 三號主變一次側 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 370 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | DELETE | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0579 | 580 | 0129 | 2-38-00 | 2-38-01 | 2-00 | SPARE |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.781_ABS | 781(#4MTR) ABS | DTR |  |  |  |  | CDC | 371 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 372 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | M1_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 373 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | ＃1 MTR | 96PA | 一號主變 96P RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 374 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0309 |  |  | 1-33-02 |  |  | ＃1 MTR | 148T | 一號主變OLTC遲滯警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 375 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-12 |  |  | #1 MTR | 127C | 一 號主變AC電源欠壓 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 376 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | DS | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 377 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | E1 | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 378 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | ＃2 MTR | 96PA | 二號主變 96P RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 379 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0325 |  |  | 1-34-02 |  |  | ＃2 MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 380 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0335 |  |  | 1-34-12 |  |  | #2 MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 381 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | 3M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 382 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | E1 | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 383 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-03 |  |  | ＃3 MTR | 96PA | 三號主變 96P RY |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 384 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0341 |  |  | 1-35-02 |  |  | ＃3 MTR | 348T | 三號主變OLTC遲滯警報 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 385 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 1-35-12 |  |  | ＃3 MTR | 327C | 三號主變AC電源欠壓 |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 386 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | DS | 4M(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.4M_DS | 4M_DS (非取樣點) | DTR | [5 empty] | 387 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | ES | 4M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.4M_ES | 4M_ES (非取樣點) | DTR | [5 empty] | 388 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0489 |  |  | 2-00-06 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_96A | #4MTR 96P RY | DTR |  |  |  |  | CDC | 389 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 2-30-02 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 390 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 2-31-03 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR |  |  |  |  | CDC | 391 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0095 |  | 0009 | 1-0B-04 |  | 1-08 | 810 | CB | 69KV SC |  | aaha | B2/S31_A1 | [8 empty] | 朴子SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 392 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | ES | 810_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_A1 | [8 empty] | 朴子SS.810_ES | 810_ES (非取樣點) | SC | [5 empty] | 393 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0098 |  | 0052 | 1-0B-07 |  | 1-33 | ＃1 SC | CB | 一號 SC 11KV |  | adgb | B2/S31_D1 | [8 empty] | 朴子SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 394 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0060 | 1-33-06 |  | 1-3B | ＃1 SC | Q-CTL A/M | 一號SC乏控器(自動 / 手動) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 395 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 396 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | C/2SC |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | ＃2 SC | CB ON/OFF | 二號 SC 11KV |  | acbb | B2/S31_D1 | [8 empty] | 朴子SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 397 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0081 | 1-34-06 |  | 1-50 | ＃2 SC | Q-CTL A/M | 二號SC乏控器(自動 / 手動) |  |  | B2/S31_D1 | [8 empty] | 朴子SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 398 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 399 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | C/3SC |  |  | 0142 |  | 0092 | 1-11-03 |  | 1-5B | ＃3 SC | CB ON/OFF | 三號 SC 11KV |  | aaab | B2/S31_D1 | [8 empty] | 朴子SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 400 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0100 | 1-35-06 |  | 1-63 | ＃3SC | Q-CTL A/M | 三號SC乏控器(自動 / 手動)指示 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 401 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 402 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/4BUS | C/4SC |  |  | 0499 |  | 0133 | 2-02-00 |  | 2-04 | SPARE |  |  |  | not found | B2/S31_D1 | [8 empty] | 朴子SS.240_CB | 240(11KV #4SC) CB | SC |  |  |  |  | CDC | 403 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | Tap Chan |  | DELETE | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0141 | 2-30-06 |  | 2-0C | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.240_A/M | 11KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 404 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | ES | 240_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 405 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0393 | 394 | 0040 | 1-38-06 | 1-38-07 | 1-27 | 811 | ABS ON | 69KV SC一次側 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 406 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0096 |  |  | 1-0B-05 |  |  | 810 | SCA | 69KV SC(51、51N RY) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 407 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0097 |  |  | 1-0B-06 |  |  | 810 | UVA | 69KV SC(27、59 RY) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 408 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | ＃1 SC | SCA | 一號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 409 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-00 |  |  | ＃1 SC | UVA | 一號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 410 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | ＃2 SC | SCA | 二號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 411 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | ＃2 SC | UVA | 二號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 412 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | ＃3 SC | SCA | 三號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 413 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 1-12-03 |  |  | ＃3 SC | UVA | 三號 SC 11KV |  |  | B2/S31_D1 | [8 empty] | 朴子SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 414 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  | DELETE | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0523 |  |  | 2-09-00 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.240_SCA | 11KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 415 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  | DELETE | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 2-09-01 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 416 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 417 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 418 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 419 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 420 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.231DS | 231DS (非取樣點) | SC | [5 empty] | 421 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | D2 | 232DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.232DS | 232DS (非取樣點) | SC | [5 empty] | 422 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241DS(非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.241DS | 241DS (非取樣點) | SC | [5 empty] | 423 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | D2 | 242DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.242DS | 242DS (非取樣點) | SC | [5 empty] | 424 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪A I 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 425 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪A I 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 426 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 427 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 428 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 429 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 430 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCL4 |  | B2 | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [9 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  | DNP_Mon1_EMPTY,PointList_NULL |  |  | CDC | 431 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | ADCH4 |  | B2 | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [9 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  | DNP_Mon1_EMPTY,PointList_NULL |  |  | CDC | 432 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0259 |  | 0001 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 朴子SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(STATUS) |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | CHG1 | 變電所故障 |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0261 |  |  | 1-30-02 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | CHG2 | 變電所故障 |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0262 |  |  | 1-30-03 |  |  | 通訊充電機 | CHG2 | 通訊充電機故障(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | DCE | 警報 |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0263 |  |  | 1-30-04 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 437 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0265 |  | 0046 | 1-30-06 |  | 1-2D | 所內開關場 | FLA | 開關場照明 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 438 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0266 |  | 0047 | 1-30-07 |  | 1-2E | 所內配電盤 | FLB | 市區路燈照明 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 439 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | STUV | 警報 |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0267 |  |  | 1-30-08 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 440 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | OPA | 充油電纜低油壓警報 |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-09 |  |  | 充油電纜 | OPA | 油壓電力電纜警報(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 441 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Fire1 | [朴子]火警 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火災警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.火災警報(1) | [朴子]火警 | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-12 |  |  | 變電所內 | PSF | 所內其他輕故障警報(無接線) |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 443 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-30-13 |  |  | 變電所內 | PSA | 所內其他重故障警報(無接線) |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 444 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | DCA | 警報 |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-30-14 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-30-15 |  |  | 洩油池泵 | OWF | 洩油池泵警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁警報(1) |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0280 |  |  | 1-31-05 |  |  | 門禁警報(1) |  | 無人化門禁警報(1)(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁警報(2) |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-06 |  |  | 門禁警報(2) |  | 無人化門禁警報(2)(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Door3 | 門禁警報(3) |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0282 |  |  | 1-31-07 |  |  | 門禁警報(3) |  | 無人化門禁警報(3)(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0284 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 | 6CBF | 69KV CB 輕警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-10 |  |  | 69KV CB 重故障 | 6CBA | 69KV CB 重警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0286 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 | 1CBF | 11KV CB NFB跳脫警報 |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-12 |  |  | 11KV CB 重故障 | 1CBA | 11KV CB NFB跳脫警報 |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0290 |  |  | 1-31-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | CommACF | 故障 |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0371 |  |  | 1-37-00 |  |  | 通訊設備AC故障 |  | 通訊設備光纖主故障(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0372 |  |  | 1-37-01 |  |  | 通訊設備光纖主故障 | OLTMA | 通訊設備光纖次故障(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0373 |  |  | 1-37-02 |  |  | 通訊設備光纖次故障 | OLTNA | 博碼調變器故障(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 通訊PCM警報 |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0374 |  |  | 1-37-03 |  |  | 博碼調變器故障 | PCMA | (無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | ＃1 MCB | 51NA(GDA) | 一號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#1MAIN51NA | #1MAIN51NA | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | ＃2 MCB(A) | 51NA(GDA) | 二號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MAIN51NA | #2MAIN51NA | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-04 |  |  | ＃2 MCB(B) | 51NA(GDA) | 二號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#2MBIN51NA | #2MBIN51NA | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | ＃3 MCB | 51NA(GDA) | 三號主變二次側 |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#3MAIN51NA | #3MAIN51NA | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0492 |  |  | 2-01-01 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.#4MAIN51NA | #4MAIN51NA | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0264 |  |  | 1-30-05 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0270 |  |  | 1-30-11 |  |  | 安全監控 | SUPA | 所內安全監控(無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Fire2 | MCSG火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 1-31-00 |  |  | MCSG火警 |  | 無人化防火警報(1) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.MCSG火警 | MCSG火警 | OTHER |  |  |  |  | CDC | 466 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | MCSG_89A | MCSG系統故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-01 |  |  | MCSG系統故障 |  | 無人化防火警報(2) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.MCSG系統故障 | MCSG系統故障 | OTHER |  |  |  |  | CDC | 467 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0283 |  |  | 1-31-08 |  |  | 69KV SC |  | 69KV SC 警報(無接線) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 468 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2BUS | #2BUS |  | BUS_VUA | 69KVBUS#2VUA | B2,B3,Element | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 1-31-14 |  |  | 69KV＃2 BUS | 6VUA | 69KV BUS#2衡相監視警報 |  |  | B2/S31_A1 | [8 empty] | 朴子SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER |  |  |  |  | CDC | 469 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Fire | 主變火警 | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 1-31-02 |  |  | 主變火警 |  | 無人化防盜警報(1) |  |  | ELEM/S31_D1 | [8 empty] | 朴子SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 470 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-03 |  |  | 細水霧故障 |  | 無人化防盜警報(2) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-04 |  |  | 細水霧噴灑 |  | 無人化防盜警報(3) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 維護運轉警報 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0386 |  |  | 1-37-15 |  |  | 維護運轉 |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 數據機重置 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0354 |  | 0088 | 1-35-15 |  | 1-57 | SPARE |  |  |  |  | B3/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 474 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | DD_Light | 路燈電源監視 | Element | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 0378 |  |  | 1-37-07 |  |  | 路燈監視 |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.路燈電源監視 | 路燈操作線電源監視 | OTHER |  |  |  |  | CDC | 475 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室溫度異常 | Element | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0375 |  |  | 1-37-04 |  |  | 通訊室溫度異常 |  | (無接線) |  |  | B3/S31_D1 | [8 empty] | 朴子SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER |  |  |  |  | CDC | 476 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1 MTR | #1 MTR 96B1 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 477 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | #1 MTR | #1 MTR 96B2 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1 MTR | #1 MTR 96D |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 479 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1 MTR | #1 MTR 96P |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 480 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1 MTR | #1 MTR 63Q |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2 MTR | #2 MTR 96B1 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR96B1 | #2MTR6撲氣電驛警報 | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | #2 MTR | #2 MTR 96B2 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR96B2 | #2MTR6撲氣電驛動作 | OTHER |  |  |  |  | CDC | 483 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2 MTR | #2 MTR 96D |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR96D | #2MTR6放壓電驛動作 | OTHER |  |  |  |  | CDC | 484 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2 MTR | #2 MTR 96P |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR96P | #2MTR6突壓電驛動作 | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 2MTR | #2MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2 MTR | #2 MTR 63Q |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#2MTR63Q | #2MTR6 ULTC電驛動作 | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 96B1 |  | B2,B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-02 |  |  | #3 MTR | #3 MTR 96B1 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 96B2 |  | B2,B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-03 |  |  | #3 MTR | #3 MTR 96B2 |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 488 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 96D |  | B2,B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-04 |  |  | #3 MTR | #3 MTR 96D |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 489 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 96P |  | B2,B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-19-05 |  |  | #3 MTR | #3 MTR 96P |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 490 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | 63Q |  | B2,B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-19-06 |  |  | #3 MTR | #3 MTR 63Q |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 491 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | JD21 | VAR | 朴一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線KVAR | 11KV朴一線 KVAR | FEEDER |  |  |  |  | CDC | 492 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | JD21 | A1 | 朴一線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線A1 | 11KV朴一線 R相AMP | FEEDER |  |  |  |  | CDC | 493 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | JD21 | A2 | 朴一線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線A2 | 11KV朴一線 S相AMP | FEEDER |  |  |  |  | CDC | 494 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | JD21 | A3 | 朴一線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線A3 | 11KV朴一線 T相AMP | FEEDER |  |  |  |  | CDC | 495 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | JD21 | NA | 朴一線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線A0 | 11KV朴一線 N相AMP | FEEDER |  |  |  |  | CDC | 496 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JD27 | VAR | 朴七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線KVAR | 11KV朴七線 KVAR | FEEDER |  |  |  |  | CDC | 497 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JD27 | A1 | 朴七線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線A1 | 11KV朴七線 R相AMP | FEEDER |  |  |  |  | CDC | 498 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JD27 | A2 | 朴七線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線A2 | 11KV朴七線 S相AMP | FEEDER |  |  |  |  | CDC | 499 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JD27 | A3 | 朴七線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線A3 | 11KV朴七線 T相AMP | FEEDER |  |  |  |  | CDC | 500 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JD27 | NA | 朴七線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線A0 | 11KV朴七線 N相AMP | FEEDER |  |  |  |  | CDC | 501 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JD29 | VAR | 朴九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線KVAR | 11KV朴九線 KVAR | FEEDER |  |  |  |  | CDC | 502 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JD29 | A1 | 朴九線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線A1 | 11KV朴九線 R相AMP | FEEDER |  |  |  |  | CDC | 503 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JD29 | A2 | 朴九線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線A2 | 11KV朴九線 S相AMP | FEEDER |  |  |  |  | CDC | 504 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JD29 | A3 | 朴九線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線A3 | 11KV朴九線 T相AMP | FEEDER |  |  |  |  | CDC | 505 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JD29 | NA | 朴九線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線A0 | 11KV朴九線 N相AMP | FEEDER |  |  |  |  | CDC | 506 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | JD22 | VAR | 朴二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線KVAR | 11KV朴二線 KVAR | FEEDER |  |  |  |  | CDC | 507 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | JD22 | A1 | 朴二線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線A1 | 11KV朴二線 R相AMP | FEEDER |  |  |  |  | CDC | 508 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | JD22 | A2 | 朴二線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線A2 | 11KV朴二線 S相AMP | FEEDER |  |  |  |  | CDC | 509 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | JD22 | A3 | 朴二線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線A3 | 11KV朴二線 T相AMP | FEEDER |  |  |  |  | CDC | 510 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | JD22 | NA | 朴二線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線A0 | 11KV朴二線 N相AMP | FEEDER |  |  |  |  | CDC | 511 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JD28 | VAR | 朴八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線KVAR | 11KV朴八線 KVAR | FEEDER |  |  |  |  | CDC | 512 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JD28 | A1 | 朴八線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線A1 | 11KV朴八線 R相AMP | FEEDER |  |  |  |  | CDC | 513 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JD28 | A2 | 朴八線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線A2 | 11KV朴八線 S相AMP | FEEDER |  |  |  |  | CDC | 514 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JD28 | A3 | 朴八線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線A3 | 11KV朴八線 T相AMP | FEEDER |  |  |  |  | CDC | 515 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | JD28 | NA | 朴八線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線A0 | 11KV朴八線 N相AMP | FEEDER |  |  |  |  | CDC | 516 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JD30 | VAR | 朴十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線KVAR | 11KV朴十線 KVAR | FEEDER |  |  |  |  | CDC | 517 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JD30 | A1 | 朴十線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線A1 | 11KV朴十線 R相AMP | FEEDER |  |  |  |  | CDC | 518 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JD30 | A2 | 朴十線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線A2 | 11KV朴十線 S相AMP | FEEDER |  |  |  |  | CDC | 519 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JD30 | A3 | 朴十線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線A3 | 11KV朴十線 T相AMP | FEEDER |  |  |  |  | CDC | 520 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JD30 | NA | 朴十線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線A0 | 11KV朴十線 N相AMP | FEEDER |  |  |  |  | CDC | 521 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | JD23 | VAR | 朴三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線KVAR | 11KV朴三線 KVAR | FEEDER |  |  |  |  | CDC | 522 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | JD23 | A1 | 朴三線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線A1 | 11KV朴三線 R相AMP | FEEDER |  |  |  |  | CDC | 523 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | JD23 | A2 | 朴三線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線A2 | 11KV朴三線 S相AMP | FEEDER |  |  |  |  | CDC | 524 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | JD23 | A3 | 朴三線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線A3 | 11KV朴三線 T相AMP | FEEDER |  |  |  |  | CDC | 525 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | JD23 | NA | 朴三線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線A0 | 11KV朴三線 N相AMP | FEEDER |  |  |  |  | CDC | 526 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | JD25 | VAR | 朴五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線KVAR | 11KV朴五線 KVAR | FEEDER |  |  |  |  | CDC | 527 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | JD25 | A1 | 朴五線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線A1 | 11KV朴五線 R相AMP | FEEDER |  |  |  |  | CDC | 528 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | JD25 | A2 | 朴五線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線A2 | 11KV朴五線 S相AMP | FEEDER |  |  |  |  | CDC | 529 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JD25 | A3 | 朴五線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線A3 | 11KV朴五線 T相AMP | FEEDER |  |  |  |  | CDC | 530 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | JD25 | NA | 朴五線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線A0 | 11KV朴五線 N相AMP | FEEDER |  |  |  |  | CDC | 531 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | JD26 | VAR | 朴六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線KVAR | 11KV朴六線 KVAR | FEEDER |  |  |  |  | CDC | 532 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JD26 | A1 | 朴六線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線A1 | 11KV朴六線 R相AMP | FEEDER |  |  |  |  | CDC | 533 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JD26 | A2 | 朴六線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線A2 | 11KV朴六線 S相AMP | FEEDER |  |  |  |  | CDC | 534 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JD26 | A3 | 朴六線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線A3 | 11KV朴六線 T相AMP | FEEDER |  |  |  |  | CDC | 535 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | JD26 | NA | 朴六線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線A0 | 11KV朴六線 N相AMP | FEEDER |  |  |  |  | CDC | 536 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | JD24 | VAR | 朴四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線KVAR | 11KV朴四線 KVAR | FEEDER |  |  |  |  | CDC | 537 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | JD24 | A1 | 朴四線R相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線A1 | 11KV朴四線 R相AMP | FEEDER |  |  |  |  | CDC | 538 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | JD24 | A2 | 朴四線S相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線A2 | 11KV朴四線 S相AMP | FEEDER |  |  |  |  | CDC | 539 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | JD24 | A3 | 朴四線T相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線A3 | 11KV朴四線 T相AMP | FEEDER |  |  |  |  | CDC | 540 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | JD24 | NA | 朴四線零相電流 | A_-500_500(-2000_2000) |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線A0 | 11KV朴四線 N相AMP | FEEDER |  |  |  |  | CDC | 541 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 充電機 | DC-V | 配電盤 "MAIN"NFB電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S31_D1 | [8 empty] | 朴子SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 542 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0522 |  | 0147 | 2-08-07 |  | 2-12 | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR_81A/S | #4MTR 81RY A/S | DTR |  |  |  |  | CDC | 543 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S31 | 朴子SS |  |  | 5MTR | #5MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-03 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#5MTR63Q | #5MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 544 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 5MTR | #5MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-19-07 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#5MTR96B1 | #5MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 545 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 5MTR | #5MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-00 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#5MTR96B2 | #5MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 546 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 5MTR | #5MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-01 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#5MTR96D | #5MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 547 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 5MTR | #5MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-02 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#5MTR96P | #5MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 548 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-00 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR63Q | ULTC電驛動作 | OTHER |  |  |  |  | CDC | 549 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-04 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR96B1 | 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 550 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1A-05 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR96B2 | 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 551 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1A-06 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR96D | 放壓電驛動作 | OTHER |  |  |  |  | CDC | 552 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1A-07 |  |  | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#4MTR96P | 突壓電驛動作 | OTHER |  |  |  |  | CDC | 553 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | ComPoint |  |  | FDR_CBA | IED警報 | INSERT | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-01 |  |  | 11KV IED | IEDA RYFA | 11KV IED故障警報 |  |  | B3/S31_D1 | [8 empty] | 朴子SS.IED警報 | 11/23KV重故障(IED警報) | OTHER | [5 empty] | 554 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0587 |  |  | 2-38-08 |  |  | JD21 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴一線LOA | 朴一線LOA | OTHER | [5 empty] | 555 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0593 |  |  | 2-38-14 |  |  | JD27 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴七線LOA | 朴七線LOA | OTHER | [5 empty] | 556 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0595 |  |  | 2-39-00 |  |  | JD29 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴九線LOA | 朴九線LOA | OTHER | [5 empty] | 557 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0606 |  |  | 2-39-11 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二十線LOA | 朴二十線LOA | OTHER | [5 empty] | 558 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0588 |  |  | 2-38-09 |  |  | JD22 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴二線LOA | 朴二線LOA | OTHER | [5 empty] | 559 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0594 |  |  | 2-38-15 |  |  | JD28 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴八線LOA | 朴八線LOA | OTHER | [5 empty] | 560 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0597 |  |  | 2-39-02 |  |  | JD31 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十一線LOA | 朴十一線LOA | OTHER | [5 empty] | 561 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0603 |  |  | 2-39-08 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十七線LOA | 朴十七線LOA | OTHER | [5 empty] | 562 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0605 |  |  | 2-39-10 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十九線LOA | 朴十九線LOA | OTHER | [5 empty] | 563 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0598 |  |  | 2-39-03 |  |  | JD32 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十二線LOA | 朴十二線LOA | OTHER | [5 empty] | 564 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0604 |  |  | 2-39-09 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十八線LOA | 朴十八線LOA | OTHER | [5 empty] | 565 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0599 |  |  | 2-39-04 |  |  | JD33 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十三線LOA | 朴十三線LOA | OTHER | [5 empty] | 566 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0601 |  |  | 2-39-06 |  |  | JD35 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十五線LOA | 朴十五線LOA | OTHER | [5 empty] | 567 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0602 |  |  | 2-39-07 |  |  | SPARE |  |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十六線LOA | 朴十六線LOA | OTHER | [5 empty] | 568 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0600 |  |  | 2-39-05 |  |  | JD34 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十四線LOA | 朴十四線LOA | OTHER | [5 empty] | 569 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0596 |  |  | 2-39-01 |  |  | JD30 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴十線LOA | 朴十線LOA | OTHER | [5 empty] | 570 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0589 |  |  | 2-38-10 |  |  | JD23 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴三線LOA | 朴三線LOA | OTHER | [5 empty] | 571 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0591 |  |  | 2-38-12 |  |  | JD25 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴五線LOA | 朴五線LOA | OTHER | [5 empty] | 572 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0592 |  |  | 2-38-13 |  |  | JD26 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴六線LOA | 朴六線LOA | OTHER | [5 empty] | 573 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0590 |  |  | 2-38-11 |  |  | JD24 | 79 LOA |  |  |  | B2/S31_D1 | [8 empty] | 朴子SS.朴四線LOA | 朴四線LOA | OTHER | [5 empty] | 574 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Water1 | 開關場水位警報 | INSERT | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0385 |  |  | 1-37-14 |  |  | 所內水位警報 |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 575 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-01 |  |  | 630 | 87A | 東石朴子線(630) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_87A | 東石線(630) 87RY | LINE69 | [5 empty] | 576 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-09 |  |  | 630 | CFA | 東石朴子線 CFA (#630 CFA ) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_CFA | 東石線(630) 通訊故障 | LINE69 | [5 empty] | 577 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0299 |  | 0014 | 1-32-08 |  | 1-0D | 630 | 587S U/L | 東石朴子線 69KV(#630 87A) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_87UL | 東石線(630) 87RY U/L | LINE69 | [5 empty] | 578 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-09-05 |  |  | 640 | 87A | 北港朴子線(640) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_87A | 北港線(640) 87RY | LINE69 | [5 empty] | 579 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-32-07 |  |  | 640 | CFA | 北港朴子線 CFA (#640 CFA ) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_CFA | 北港線(640) 通訊故障 | LINE69 | [5 empty] | 580 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0297 |  | 0013 | 1-32-06 |  | 1-0C | 640 | 487S U/L | 北港朴子線 69KV(#640 87A) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_87UL | 北港線(640) 87RY U/L | LINE69 | [5 empty] | 581 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0383 |  |  | 1-37-12 |  |  | 630 | IEDA | 東石朴子線 RYFA |  |  | B2/S31_A1 | [8 empty] | 朴子SS.630_RYFA | 630 東石線IED警報 | OTHER | [5 empty] | 582 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0382 |  |  | 1-37-11 |  |  | 640 | IEDA | 北港朴子線 RYFA |  |  | B2/S31_A1 | [8 empty] | 朴子SS.640_RYFA | 640 北港線IED警報 | OTHER | [5 empty] | 583 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | 610 | 87A | 嘉太朴子線(610) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_87A | 嘉太線(610) 87RY | LINE69 | [5 empty] | 584 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-32-03 |  |  | 610 | CFA | 嘉太朴子線 CFA (#610 CFA) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_CFA | 嘉太線(610) 通訊故障 | LINE69 | [5 empty] | 585 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0293 |  | 0011 | 1-32-02 |  | 1-0A | 610 | 287S U/L | 嘉太朴子線 69KV(#610 87A) |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_87UL | 嘉太線(610) 87 U/L | LINE69 | [5 empty] | 586 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0380 |  |  | 1-37-09 |  |  | 610 | IEDA | 嘉太朴子線 RYFA |  |  | B2/S31_A1 | [8 empty] | 朴子SS.610_RYFA | 610 嘉太線IED警報 | OTHER | [5 empty] | 587 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | StaDev | 所內設施 |  | Water2 | 開關場水位二段 | INSERT | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0384 |  |  | 1-37-13 |  |  | 開關場水位二段警報 |  |  |  |  | B3/S31_D1 | [8 empty] | 朴子SS.開關場水位二段 | 開關場水位二段警報檔 | OTHER | [5 empty] | 588 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3F-14 |  |  | Ladder 14,1 | PMA | POWER METER |  |  | B3/S31_D1 | [8 empty] | 朴子SS.PMA | POWER METER警報 | OTHER | [5 empty] | 589 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | JD21 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JD21 | KWH(＋) | 朴一線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 590 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD22 | JD22 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JD22 | KWH(＋) | 朴二線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 591 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD23 | JD23 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JD23 | KWH(＋) | 朴三線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 592 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD24 | JD24 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JD24 | KWH(＋) | 朴四線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 593 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD25 | JD25 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JD25 | KWH(＋) | 朴五線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 594 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD26 | JD26 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | JD26 | KWH(＋) | 朴六線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 595 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD27 | JD27 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | JD27 | KWH(＋) | 朴七線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 596 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD28 | JD28 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | JD28 | KWH(＋) | 朴八線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 597 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD29 | JD29 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | JD29 | KWH(＋) | 朴九線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 598 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | JD30 | JD30 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | JD30 | KWH(＋) | 朴十線瓦時(正)計量值 |  |  | B2/S31_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 599 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S31 | 朴子SS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0130 |  |  | 2-82 |  |  | #2 MCB | KV | 二號主變二次側11KV BUS(A) | kV_-9_9(-2000_2000) | aaa | B2/S31_D1 | [8 empty] | 朴子SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | BUS |  |  |  |  | 600 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  | 0066 | 1-0C-06 |  | 1-41 | SPARE |  |  |  |  | B1/S31_D1 | [8 empty] | 朴子SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | DTR |  |  |  |  | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S31 | 朴子SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | DS | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 377 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | E1 | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S31_D1 | [8 empty] | 朴子SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 378 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S31 | 朴子SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S31_D1 | [12 empty] | 朴子SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S31/69/1BUS/V
S31 | 朴子SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S31_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S31/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S31 | 朴子SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S31_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_7 | OPRD1: S31/11/M1/MW; OPRD2: S31/11/M3/MW; OPRD3: S31/11/M4/MW; OPRD4: S31/69/610/MW; OPRD5: S31/69/620/MW; OPRD6: S31/69/630/MW; OPRD7: S31/69/640/MW
S31 | 朴子SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S31_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S31/0/CalcPoint/OPRN2_MW
S31 | 朴子SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S31_D1 | [17 empty] | none
S31 | 朴子SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S31_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S31/0/CalcPoint/OPRN1; OPRD2: S31/0/CalcPoint/OPRN2; OPRD3: S31/0/CalcPoint/PRFL_UL
S31 | 朴子SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S31_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S31/11/M1/MW; OPRD2: S31/11/M1/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S31_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S31/11/M3/MW; OPRD2: S31/11/M3/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S31_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S31/11/M4/MW; OPRD2: S31/11/M4/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太～朴子線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S31_A1 | [12 empty] | 朴子SS.610_AMP | 嘉太線 AMP | LINE69 | AMP_CAL | C10R0879 | amp_cal | OPRD1: S31/69/610/MW; OPRD2: S31/69/610/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS | 69 | 69kV | 620 | 朴子～鹿草線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S31_A1 | [12 empty] | 朴子SS.620_AMP | 朴子鹿草線 AMP | LINE69 | AMP_CAL | C04R0400 | amp_cal | OPRD1: S31/69/620/MW; OPRD2: S31/69/620/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S31_A1 | [12 empty] | 朴子SS.630_AMP | 東石線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: S31/69/630/MW; OPRD2: S31/69/630/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS | 69 | 69kV | 640 | 北港～朴子線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S31_A1 | [12 empty] | 朴子SS.640_AMP | 北港線 AMP | LINE69 | AMP_CAL | C10R1000 | amp_cal | OPRD1: S31/69/640/MW; OPRD2: S31/69/640/MVAR; OPRD3: S31/0/CalcPoint/Vbs1
S31 | 朴子SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S31_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S31/11/1BUS/V
S31 | 朴子SS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S31_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S31/11/2ABUS/V
S31 | 朴子SS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S31_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S31/11/2BBUS/V
S31 | 朴子SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S31_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S31/11/3BUS/V
S31 | 朴子SS | 11 | 11kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S31_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S31/11/4BUS/V
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S31_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 朴子SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S31/11/M1/MW; OPRD2: S31/11/M1/MVAR
S31 | 朴子SS |  |  | 2MTR(A) | #2MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S31_D1 | LG_15 | 14.25 | 16.5 | 18.75 | 30 |  | -14.25 | -16.5 | -18.75 | -30 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S31/11/M2A/MW; OPRD2: S31/11/M2A/MVAR
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S31_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 朴子SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S31/11/M3/MW; OPRD2: S31/11/M3/MVAR
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S31_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 朴子SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S31/11/M4/MW; OPRD2: S31/11/M4/MVAR
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S31_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S31//1MTR/MVA; OPRD2: 0
S31 | 朴子SS |  |  | 2MTR(A) | #2MTR(A) |  | LOAD | [9 empty] | B1/S31_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S31//2MTR(A)/MVA; OPRD2: 0
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S31_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S31//3MTR/MVA; OPRD2: 0
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/S31_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S31//4MTR/MVA; OPRD2: 0
S31 | 朴子SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S31_D1 | [12 empty] | 朴子SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S31/11/M1/MW; OPRD2: S31/11/M1/MVAR
S31 | 朴子SS |  |  | 2MTR(A) | #2MTR(A) |  | PF | [9 empty] | B1/S31_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S31/11/M2A/MW; OPRD2: S31/11/M2A/MVAR
S31 | 朴子SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S31_D1 | [12 empty] | 朴子SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S31/11/M3/MW; OPRD2: S31/11/M3/MVAR
S31 | 朴子SS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/S31_D1 | [12 empty] | 朴子SS.#4MTR_PF | #4MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S31/11/M4/MW; OPRD2: S31/11/M4/MVAR
S31 | 朴子SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S31_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S31//1MTR/SupLocal; OPRD2: S31//1MTR/Tap Chan; OPRD3: NULL
S31 | 朴子SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S31_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S31//2MTR/SupLocal; OPRD2: S31//2MTR/Tap Chan; OPRD3: NULL
S31 | 朴子SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S31_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S31//3MTR/SupLocal; OPRD2: S31//3MTR/Tap Chan; OPRD3: NULL
S31 | 朴子SS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/S31_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S31//4MTR/SupLocal; OPRD2: S31//4MTR/Tap Chan; OPRD3: NULL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/1BUS/V; OPRD2: S31/11/JD21/I_R; OPRD3: S31/11/JD21/I_S; OPRD4: S31/11/JD21/I_T
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/1BUS/V; OPRD2: S31/11/JD22/I_R; OPRD3: S31/11/JD22/I_S; OPRD4: S31/11/JD22/I_T
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/1BUS/V; OPRD2: S31/11/JD23/I_R; OPRD3: S31/11/JD23/I_S; OPRD4: S31/11/JD23/I_T
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/1BUS/V; OPRD2: S31/11/JD24/I_R; OPRD3: S31/11/JD24/I_S; OPRD4: S31/11/JD24/I_T
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/1BUS/V; OPRD2: S31/11/JD25/I_R; OPRD3: S31/11/JD25/I_S; OPRD4: S31/11/JD25/I_T
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/2ABUS/V; OPRD2: S31/11/JD26/I_R; OPRD3: S31/11/JD26/I_S; OPRD4: S31/11/JD26/I_T
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/2ABUS/V; OPRD2: S31/11/JD27/I_R; OPRD3: S31/11/JD27/I_S; OPRD4: S31/11/JD27/I_T
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/2ABUS/V; OPRD2: S31/11/JD28/I_R; OPRD3: S31/11/JD28/I_S; OPRD4: S31/11/JD28/I_T
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/2BBUS/V; OPRD2: S31/11/JD29/I_R; OPRD3: S31/11/JD29/I_S; OPRD4: S31/11/JD29/I_T
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/2BBUS/V; OPRD2: S31/11/JD30/I_R; OPRD3: S31/11/JD30/I_S; OPRD4: S31/11/JD30/I_T
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/3BUS/V; OPRD2: S31/11/JD31/I_R; OPRD3: S31/11/JD31/I_S; OPRD4: S31/11/JD31/I_T
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/3BUS/V; OPRD2: S31/11/JD32/I_R; OPRD3: S31/11/JD32/I_S; OPRD4: S31/11/JD32/I_T
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/3BUS/V; OPRD2: S31/11/JD33/I_R; OPRD3: S31/11/JD33/I_S; OPRD4: S31/11/JD33/I_T
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/3BUS/V; OPRD2: S31/11/JD34/I_R; OPRD3: S31/11/JD34/I_S; OPRD4: S31/11/JD34/I_T
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/3BUS/V; OPRD2: S31/11/JD35/I_R; OPRD3: S31/11/JD35/I_S; OPRD4: S31/11/JD35/I_T
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/4BUS/V; OPRD2: S31/11/JD36/I_R; OPRD3: S31/11/JD36/I_S; OPRD4: S31/11/JD36/I_T
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/4BUS/V; OPRD2: S31/11/JD37/I_R; OPRD3: S31/11/JD37/I_S; OPRD4: S31/11/JD37/I_T
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/4BUS/V; OPRD2: S31/11/JD38/I_R; OPRD3: S31/11/JD38/I_S; OPRD4: S31/11/JD38/I_T
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/4BUS/V; OPRD2: S31/11/JD39/I_R; OPRD3: S31/11/JD39/I_S; OPRD4: S31/11/JD39/I_T
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S31/11/4BUS/V; OPRD2: S31/11/JD40/I_R; OPRD3: S31/11/JD40/I_S; OPRD4: S31/11/JD40/I_T
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD21/kVA; OPRD2: S31/11/JD21/KVAR
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD22/kVA; OPRD2: S31/11/JD22/KVAR
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD23/kVA; OPRD2: S31/11/JD23/KVAR
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD24/kVA; OPRD2: S31/11/JD24/KVAR
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD25/kVA; OPRD2: S31/11/JD25/KVAR
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD26/kVA; OPRD2: S31/11/JD26/KVAR
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD27/kVA; OPRD2: S31/11/JD27/KVAR
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD28/kVA; OPRD2: S31/11/JD28/KVAR
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD29/kVA; OPRD2: S31/11/JD29/KVAR
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD30/kVA; OPRD2: S31/11/JD30/KVAR
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD31/kVA; OPRD2: S31/11/JD31/KVAR
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD32/kVA; OPRD2: S31/11/JD32/KVAR
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD33/kVA; OPRD2: S31/11/JD33/KVAR
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD34/kVA; OPRD2: S31/11/JD34/KVAR
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD35/kVA; OPRD2: S31/11/JD35/KVAR
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD36/kVA; OPRD2: S31/11/JD36/KVAR
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD37/kVA; OPRD2: S31/11/JD37/KVAR
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD38/kVA; OPRD2: S31/11/JD38/KVAR
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD39/kVA; OPRD2: S31/11/JD39/KVAR
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S31_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S31/11/JD40/kVA; OPRD2: S31/11/JD40/KVAR
S31 | 朴子SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S31_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S31/11/M1/MW; OPRD2: S31/11/M3/MW; OPRD3: S31/11/M4/MW
S31 | 朴子SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S31_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S31/11/M1/MVAR; OPRD2: S31/11/M3/MVAR; OPRD3: S31/11/M4/MVAR
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S31_D1 | [12 empty] | 朴子SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S31/11/210/CB; OPRD2: 6.9; OPRD3: 0
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S31_D1 | [12 empty] | 朴子SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S31/11/220/CB; OPRD2: 6.9; OPRD3: 0
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S31_D1 | [12 empty] | 朴子SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S31/11/230/CB; OPRD2: 6.9; OPRD3: 0
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S31_D1 | [12 empty] | 朴子SS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S31/11/240/CB; OPRD2: 6.9; OPRD3: 0
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S31_A1 | [12 empty] | 朴子SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S31/69/810/CB; OPRD2: 69; OPRD3: 0
S31 | 朴子SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S31_D1 | [12 empty] | 朴子SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_16 |  | com_alarm_36 | S31//1MTR/96B1 | S31//1MTR/96PA | S31//1MTR/TRA | S31//1MTR/63Q | S31//1MTR/96D | S31//1MTR/96B2 | S31//1MTR/87A | S31//1MTR/51ZA | S31//2MTR/87A | S31//2MTR/51ZA | S31//2MTR/96D | S31//2MTR/63Q | S31//2MTR/96B1 | S31//2MTR/96B2 | S31//2MTR/96PA | S31//2MTR/TRA | S31//3MTR/96B1 | S31//3MTR/87A | S31//3MTR/63Q | S31//3MTR/96D | S31//3MTR/96B2 | S31//3MTR/51ZA | S31//3MTR/96PA | S31//3MTR/TRA | S31//4MTR/96D | S31//4MTR/63Q | S31//4MTR/96B1 | S31//4MTR/96B2 | S31//4MTR/51ZA | S31//4MTR/87A | S31//4MTR/96PA | S31//4MTR/TRA | S31//5MTR/96B1 | S31//5MTR/63Q | S31//5MTR/96D | S31//5MTR/96B2
S31 | 朴子SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S31_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: S31//1MTR/TRF; OPRD2: S31//2MTR/TRF; OPRD3: S31//3MTR/TRF; OPRD4: S31//4MTR/TRF
S31 | 朴子SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/RTU/RTU_R_L
S31 | 朴子SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE | 直流電源接地故障警報 |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/StaDev/DCE
S31 | 朴子SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 變電所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/StaDev/PSF
S31 | 朴子SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 變電所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/StaDev/PSA
S31 | 朴子SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA | 直流電源故障警報 |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/StaDev/DCA
S31 | 朴子SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S31_D1 | [17 empty] | lamp2CC | OPRD1: S31/69/ComPoint/CBF
S31 | 朴子SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S31_D1 | [17 empty] | lamp2CC | OPRD1: S31/69/ComPoint/CBA
S31 | 朴子SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S31_D1 | [17 empty] | lamp2CC | OPRD1: S31/69/ComPoint/ABS_89A
S31 | 朴子SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 主變火警 |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S31_A1 | [17 empty] | lamp2CC | OPRD1: S31/0/StaDev/Fire

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S31 | 朴子SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 朴子SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S31/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 朴子SS.610_AMP | 嘉太線 AMP | LINE69 | S31/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C10R0879 | 791.099976 | 791.099976 | 879.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 朴子SS.620_AMP | 朴子鹿草線 AMP | LINE69 | S31/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 朴子SS.630_AMP | 東石線 AMP | LINE69 | S31/69/630/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 朴子SS.640_AMP | 北港線 AMP | LINE69 | S31/69/640/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C10R1000 | 900.000000 | 900.000000 | 1000.000000 | 1000.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴一線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴一線KVA | 11KV朴一線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴一線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴一線KW | 11KV朴一線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴七線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴七線KVA | 11KV朴七線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴七線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴七線KW | 11KV朴七線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴九線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴九線KVA | 11KV朴九線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴九線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴九線KW | 11KV朴九線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴二十線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二十線KVA | 11KV朴二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴二十線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二十線KW | 11KV朴二十線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴二線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二線KVA | 11KV朴二線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴二線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二線KW | 11KV朴二線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴八線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴八線KVA | 11KV朴八線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴八線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴八線KW | 11KV朴八線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十一線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十一線KVA | 11KV朴十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十一線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十一線KW | 11KV朴十一線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十七線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十七線KVA | 11KV朴十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十七線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十七線KW | 11KV朴十七線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十九線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十九線KVA | 11KV朴十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十九線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十九線KW | 11KV朴十九線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十二線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十二線KVA | 11KV朴十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十二線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十二線KW | 11KV朴十二線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十八線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十八線KVA | 11KV朴十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十八線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十八線KW | 11KV朴十八線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十三線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十三線KVA | 11KV朴十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十三線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十三線KW | 11KV朴十三線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十五線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十五線KVA | 11KV朴十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十五線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十五線KW | 11KV朴十五線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十六線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十六線KVA | 11KV朴十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十六線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十六線KW | 11KV朴十六線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十四線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十四線KVA | 11KV朴十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十四線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十四線KW | 11KV朴十四線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十線KVA | 11KV朴十線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴十線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十線KW | 11KV朴十線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴三線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴三線KVA | 11KV朴三線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴三線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴三線KW | 11KV朴三線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴五線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴五線KVA | 11KV朴五線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴五線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴五線KW | 11KV朴五線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴六線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴六線KVA | 11KV朴六線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴六線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴六線KW | 11KV朴六線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴四線KVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴四線KVA | 11KV朴四線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  |  |  |  | 朴四線KW | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴四線KW | 11KV朴四線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S31//1MTR/MVA |  | MVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_PF | #1MTR 功率因素 | DTR | S31//1MTR/PF |  | RPDC_PF_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S31//3MTR/MVA |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_PF | #3MTR 功率因素 | DTR | S31//3MTR/PF |  | RPDC_PF_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | S31//4MTR/MVA |  | MVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_PF | #4MTR 功率因素 | DTR | S31//4MTR/PF |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S31 | 朴子SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S31/11/210/MVAR |  | SC_CAL_11 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S31/11/220/MVAR |  | SC_CAL_11 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S31/11/230/MVAR |  | SC_CAL_11 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_SC_MVAR | 11KV#4SC MVAR | SC | S31/11/240/MVAR |  | SC_CAL_11 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 69 | 69kV | 810_SC | #1SC | 21.6 | MVAR | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S31/69/810/MVAR |  | SC_CAL_69 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 69 | 69kV | 610_CB | 嘉太線(610_CB) | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.610_CB_2 | 610(嘉太線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 60 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 620_CB | 朴子鹿草線(620_CB) | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.620_CB_2 | 620(朴子鹿草線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 61 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 630_CB | 東石線(630_CB) | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.630_CB_2 | 630(東石線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 62 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 640_CB | 北港線(640_CB) | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.640_CB_2 | 640(北港線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 63 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 810_CB | #1SC(810_CB) | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.810_CB_2 | 810(69KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 64 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 朴子SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 65 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 朴子SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 66 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 朴子SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 67 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 朴子SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 68 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S31 | 朴子SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 69 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | BUS2VUA | BUS#2VUA | [27 empty] | ADCS_N | [8 empty] | 朴子SS.69KVBUS#2VUA_A | 69KVBUS#2VUA (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 70 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 71 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 朴子SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S31/0/CalcPoint/SUBA |  | STATION_FAULT_16 |  |  | 72 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 73 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_4 |  |  | 74 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610_AMP | 嘉太線 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.610_AMP_A | 嘉太線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 610_AMP | 嘉太線 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.610_AMP_2 | 嘉太線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 76 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 620_AMP | 朴子鹿草線 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.620_AMP_A | 朴子鹿草線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 620_AMP | 朴子鹿草線 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.620_AMP_2 | 朴子鹿草線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 78 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 630_AMP | 東石線 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.630_AMP_A | 東石線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 630_AMP | 東石線 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.630_AMP_2 | 東石線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 80 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 640_AMP | 北港線 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.640_AMP_A | 北港線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 69 | 69kV | 640_AMP | 北港線 | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.640_AMP_2 | 北港線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 82 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_MVA_2 | #3MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 4MTR_MVA | #4MTR | [27 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_MVA_2 | #4MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S31 | 朴子SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.630_RYFA_A | 630 東石線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 640_RYFA | 640 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.640_RYFA_A | 640 北港線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 610_RYFA | 610 | [27 empty] | ADCS_N | [8 empty] | 朴子SS.610_RYFA_A | 610 嘉太線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S31/0/RTU/ADCH1 |  |  |  | CDC | 94 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S31/0/RTU/ADCH2 |  |  |  | CDC | 95 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S31/0/RTU/ADCH3 |  |  |  | CDC | 96 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | S31/0/RTU/ADCH4 |  |  |  | CDC | 97 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S31/0/RTU/ADCL1 |  |  |  | CDC | 98 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S31/0/RTU/ADCL2 |  |  |  | CDC | 99 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S31/0/RTU/ADCL3 |  |  |  | CDC | 100 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | S31/0/RTU/ADCL4 |  |  |  | CDC | 101 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S31/69/1BUS/V |  |  |  | CDC | 102 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S31 | 朴子SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S31/11/1BUS/V |  |  |  | CDC | 103 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | S31/11/2ABUS/V |  |  |  | CDC | 104 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-82 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | S31/11/2BBUS/V |  |  |  | CDC | 105 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S31/11/3BUS/V |  |  |  | CDC | 106 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 11 | 11kV | 4BUS | #4BUS |  | V | [17 empty] | 2-A3 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS | S31/11/4BUS/V |  |  |  | CDC | 107 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.610_MW | 嘉太線 MW | LINE69 | S31/69/610/MW |  |  |  | CDC | 108 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.610_MVAR | 嘉太線 MVAR | LINE69 | S31/69/610/MVAR |  |  |  | CDC | 109 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.620_MW | 朴子鹿草線 MW | LINE69 | S31/69/620/MW |  |  |  | CDC | 110 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.620_MVAR | 朴子鹿草線 MVAR | LINE69 | S31/69/620/MVAR |  |  |  | CDC | 111 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.630_MW | 東石線 MW | LINE69 | S31/69/630/MW |  |  |  | CDC | 112 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.630_MVAR | 東石線 MVAR | LINE69 | S31/69/630/MVAR |  |  |  | CDC | 113 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.640_MW | 北港線 MW | LINE69 | S31/69/640/MW |  |  |  | CDC | 114 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 朴子SS.640_MVAR | 北港線 MVAR | LINE69 | S31/69/640/MVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴一線 | 朴一線 |  | 朴一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴一線KVAR | 11KV朴一線 KVAR | FEEDER | S31/11/JD21/KVAR |  |  |  | CDC | 116 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴一線 | 朴一線 |  | 朴一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴一線A1 | 11KV朴一線 R相AMP | FEEDER | S31/11/JD21/I_R |  |  |  | CDC | 117 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴一線 | 朴一線 |  | 朴一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴一線A2 | 11KV朴一線 S相AMP | FEEDER | S31/11/JD21/I_S |  |  |  | CDC | 118 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴一線 | 朴一線 |  | 朴一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴一線A3 | 11KV朴一線 T相AMP | FEEDER | S31/11/JD21/I_T |  |  |  | CDC | 119 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴一線 | 朴一線 |  | 朴一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴一線A0 | 11KV朴一線 N相AMP | FEEDER | S31/11/JD21/I_N |  |  |  | CDC | 120 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴七線 | 朴七線 |  | 朴七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴七線KVAR | 11KV朴七線 KVAR | FEEDER | S31/11/JD27/KVAR |  |  |  | CDC | 121 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴七線 | 朴七線 |  | 朴七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴七線A1 | 11KV朴七線 R相AMP | FEEDER | S31/11/JD27/I_R |  |  |  | CDC | 122 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴七線 | 朴七線 |  | 朴七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴七線A2 | 11KV朴七線 S相AMP | FEEDER | S31/11/JD27/I_S |  |  |  | CDC | 123 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴七線 | 朴七線 |  | 朴七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴七線A3 | 11KV朴七線 T相AMP | FEEDER | S31/11/JD27/I_T |  |  |  | CDC | 124 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴七線 | 朴七線 |  | 朴七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴七線A0 | 11KV朴七線 N相AMP | FEEDER | S31/11/JD27/I_N |  |  |  | CDC | 125 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴九線 | 朴九線 |  | 朴九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴九線KVAR | 11KV朴九線 KVAR | FEEDER | S31/11/JD29/KVAR |  |  |  | CDC | 126 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴九線 | 朴九線 |  | 朴九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴九線A1 | 11KV朴九線 R相AMP | FEEDER | S31/11/JD29/I_R |  |  |  | CDC | 127 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴九線 | 朴九線 |  | 朴九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴九線A2 | 11KV朴九線 S相AMP | FEEDER | S31/11/JD29/I_S |  |  |  | CDC | 128 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴九線 | 朴九線 |  | 朴九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴九線A3 | 11KV朴九線 T相AMP | FEEDER | S31/11/JD29/I_T |  |  |  | CDC | 129 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴九線 | 朴九線 |  | 朴九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴九線A0 | 11KV朴九線 N相AMP | FEEDER | S31/11/JD29/I_N |  |  |  | CDC | 130 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二十線 | 朴二十線 |  | 朴二十線KVAR | [17 empty] | 2-BC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二十線KVAR | 11KV朴二十線 KVAR | FEEDER | S31/11/JD40/KVAR |  |  |  | CDC | 131 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二十線 | 朴二十線 |  | 朴二十線A1 | [17 empty] | 2-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二十線A1 | 11KV朴二十線 R相AMP | FEEDER | S31/11/JD40/I_R |  |  |  | CDC | 132 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二十線 | 朴二十線 |  | 朴二十線A2 | [17 empty] | 2-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二十線A2 | 11KV朴二十線 S相AMP | FEEDER | S31/11/JD40/I_S |  |  |  | CDC | 133 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二十線 | 朴二十線 |  | 朴二十線A3 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二十線A3 | 11KV朴二十線 T相AMP | FEEDER | S31/11/JD40/I_T |  |  |  | CDC | 134 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二十線 | 朴二十線 |  | 朴二十線A0 | [17 empty] | 2-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二十線A0 | 11KV朴二十線 N相AMP | FEEDER | S31/11/JD40/I_N |  |  |  | CDC | 135 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二線 | 朴二線 |  | 朴二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二線KVAR | 11KV朴二線 KVAR | FEEDER | S31/11/JD22/KVAR |  |  |  | CDC | 136 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二線 | 朴二線 |  | 朴二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二線A1 | 11KV朴二線 R相AMP | FEEDER | S31/11/JD22/I_R |  |  |  | CDC | 137 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二線 | 朴二線 |  | 朴二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二線A2 | 11KV朴二線 S相AMP | FEEDER | S31/11/JD22/I_S |  |  |  | CDC | 138 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二線 | 朴二線 |  | 朴二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二線A3 | 11KV朴二線 T相AMP | FEEDER | S31/11/JD22/I_T |  |  |  | CDC | 139 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴二線 | 朴二線 |  | 朴二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴二線A0 | 11KV朴二線 N相AMP | FEEDER | S31/11/JD22/I_N |  |  |  | CDC | 140 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴八線 | 朴八線 |  | 朴八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴八線KVAR | 11KV朴八線 KVAR | FEEDER | S31/11/JD28/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴八線 | 朴八線 |  | 朴八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴八線A1 | 11KV朴八線 R相AMP | FEEDER | S31/11/JD28/I_R |  |  |  | CDC | 142 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴八線 | 朴八線 |  | 朴八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴八線A2 | 11KV朴八線 S相AMP | FEEDER | S31/11/JD28/I_S |  |  |  | CDC | 143 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴八線 | 朴八線 |  | 朴八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴八線A3 | 11KV朴八線 T相AMP | FEEDER | S31/11/JD28/I_T |  |  |  | CDC | 144 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴八線 | 朴八線 |  | 朴八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴八線A0 | 11KV朴八線 N相AMP | FEEDER | S31/11/JD28/I_N |  |  |  | CDC | 145 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十一線 | 朴十一線 |  | 朴十一線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十一線KVAR | 11KV朴十一線 KVAR | FEEDER | S31/11/JD31/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十一線 | 朴十一線 |  | 朴十一線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十一線A1 | 11KV朴十一線 R相AMP | FEEDER | S31/11/JD31/I_R |  |  |  | CDC | 147 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十一線 | 朴十一線 |  | 朴十一線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十一線A2 | 11KV朴十一線 S相AMP | FEEDER | S31/11/JD31/I_S |  |  |  | CDC | 148 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十一線 | 朴十一線 |  | 朴十一線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十一線A3 | 11KV朴十一線 T相AMP | FEEDER | S31/11/JD31/I_T |  |  |  | CDC | 149 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十一線 | 朴十一線 |  | 朴十一線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十一線A0 | 11KV朴十一線 N相AMP | FEEDER | S31/11/JD31/I_N |  |  |  | CDC | 150 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十七線 | 朴十七線 |  | 朴十七線KVAR | [17 empty] | 2-B0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十七線KVAR | 11KV朴十七線 KVAR | FEEDER | S31/11/JD37/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十七線 | 朴十七線 |  | 朴十七線A1 | [17 empty] | 2-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十七線A1 | 11KV朴十七線 R相AMP | FEEDER | S31/11/JD37/I_R |  |  |  | CDC | 152 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十七線 | 朴十七線 |  | 朴十七線A2 | [17 empty] | 2-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十七線A2 | 11KV朴十七線 S相AMP | FEEDER | S31/11/JD37/I_S |  |  |  | CDC | 153 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十七線 | 朴十七線 |  | 朴十七線A3 | [17 empty] | 2-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十七線A3 | 11KV朴十七線 T相AMP | FEEDER | S31/11/JD37/I_T |  |  |  | CDC | 154 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十七線 | 朴十七線 |  | 朴十七線A0 | [17 empty] | 2-9F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十七線A0 | 11KV朴十七線 N相AMP | FEEDER | S31/11/JD37/I_N |  |  |  | CDC | 155 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十九線 | 朴十九線 |  | 朴十九線KVAR | [17 empty] | 2-B8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十九線KVAR | 11KV朴十九線 KVAR | FEEDER | S31/11/JD39/KVAR |  |  |  | CDC | 156 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十九線 | 朴十九線 |  | 朴十九線A1 | [17 empty] | 2-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十九線A1 | 11KV朴十九線 R相AMP | FEEDER | S31/11/JD39/I_R |  |  |  | CDC | 157 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十九線 | 朴十九線 |  | 朴十九線A2 | [17 empty] | 2-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十九線A2 | 11KV朴十九線 S相AMP | FEEDER | S31/11/JD39/I_S |  |  |  | CDC | 158 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十九線 | 朴十九線 |  | 朴十九線A3 | [17 empty] | 2-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十九線A3 | 11KV朴十九線 T相AMP | FEEDER | S31/11/JD39/I_T |  |  |  | CDC | 159 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十九線 | 朴十九線 |  | 朴十九線A0 | [17 empty] | 2-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十九線A0 | 11KV朴十九線 N相AMP | FEEDER | S31/11/JD39/I_N |  |  |  | CDC | 160 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十二線 | 朴十二線 |  | 朴十二線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十二線KVAR | 11KV朴十二線 KVAR | FEEDER | S31/11/JD32/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十二線 | 朴十二線 |  | 朴十二線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十二線A1 | 11KV朴十二線 R相AMP | FEEDER | S31/11/JD32/I_R |  |  |  | CDC | 162 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十二線 | 朴十二線 |  | 朴十二線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十二線A2 | 11KV朴十二線 S相AMP | FEEDER | S31/11/JD32/I_S |  |  |  | CDC | 163 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十二線 | 朴十二線 |  | 朴十二線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十二線A3 | 11KV朴十二線 T相AMP | FEEDER | S31/11/JD32/I_T |  |  |  | CDC | 164 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十二線 | 朴十二線 |  | 朴十二線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十二線A0 | 11KV朴十二線 N相AMP | FEEDER | S31/11/JD32/I_N |  |  |  | CDC | 165 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十八線 | 朴十八線 |  | 朴十八線KVAR | [17 empty] | 2-B4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十八線KVAR | 11KV朴十八線 KVAR | FEEDER | S31/11/JD38/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十八線 | 朴十八線 |  | 朴十八線A1 | [17 empty] | 2-B5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十八線A1 | 11KV朴十八線 R相AMP | FEEDER | S31/11/JD38/I_R |  |  |  | CDC | 167 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十八線 | 朴十八線 |  | 朴十八線A2 | [17 empty] | 2-B6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十八線A2 | 11KV朴十八線 S相AMP | FEEDER | S31/11/JD38/I_S |  |  |  | CDC | 168 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十八線 | 朴十八線 |  | 朴十八線A3 | [17 empty] | 2-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十八線A3 | 11KV朴十八線 T相AMP | FEEDER | S31/11/JD38/I_T |  |  |  | CDC | 169 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十八線 | 朴十八線 |  | 朴十八線A0 | [17 empty] | 2-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十八線A0 | 11KV朴十八線 N相AMP | FEEDER | S31/11/JD38/I_N |  |  |  | CDC | 170 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十三線 | 朴十三線 |  | 朴十三線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十三線KVAR | 11KV朴十三線 KVAR | FEEDER | S31/11/JD33/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十三線 | 朴十三線 |  | 朴十三線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十三線A1 | 11KV朴十三線 R相AMP | FEEDER | S31/11/JD33/I_R |  |  |  | CDC | 172 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十三線 | 朴十三線 |  | 朴十三線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十三線A2 | 11KV朴十三線 S相AMP | FEEDER | S31/11/JD33/I_S |  |  |  | CDC | 173 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十三線 | 朴十三線 |  | 朴十三線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十三線A3 | 11KV朴十三線 T相AMP | FEEDER | S31/11/JD33/I_T |  |  |  | CDC | 174 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十三線 | 朴十三線 |  | 朴十三線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十三線A0 | 11KV朴十三線 N相AMP | FEEDER | S31/11/JD33/I_N |  |  |  | CDC | 175 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十五線 | 朴十五線 |  | 朴十五線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十五線KVAR | 11KV朴十五線 KVAR | FEEDER | S31/11/JD35/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十五線 | 朴十五線 |  | 朴十五線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十五線A1 | 11KV朴十五線 R相AMP | FEEDER | S31/11/JD35/I_R |  |  |  | CDC | 177 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十五線 | 朴十五線 |  | 朴十五線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十五線A2 | 11KV朴十五線 S相AMP | FEEDER | S31/11/JD35/I_S |  |  |  | CDC | 178 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十五線 | 朴十五線 |  | 朴十五線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十五線A3 | 11KV朴十五線 T相AMP | FEEDER | S31/11/JD35/I_T |  |  |  | CDC | 179 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十五線 | 朴十五線 |  | 朴十五線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十五線A0 | 11KV朴十五線 N相AMP | FEEDER | S31/11/JD35/I_N |  |  |  | CDC | 180 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十六線 | 朴十六線 |  | 朴十六線KVAR | [17 empty] | 2-AC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十六線KVAR | 11KV朴十六線 KVAR | FEEDER | S31/11/JD36/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十六線 | 朴十六線 |  | 朴十六線A1 | [17 empty] | 2-AD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十六線A1 | 11KV朴十六線 R相AMP | FEEDER | S31/11/JD36/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十六線 | 朴十六線 |  | 朴十六線A2 | [17 empty] | 2-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十六線A2 | 11KV朴十六線 S相AMP | FEEDER | S31/11/JD36/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十六線 | 朴十六線 |  | 朴十六線A3 | [17 empty] | 2-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十六線A3 | 11KV朴十六線 T相AMP | FEEDER | S31/11/JD36/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十六線 | 朴十六線 |  | 朴十六線A0 | [17 empty] | 2-9E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十六線A0 | 11KV朴十六線 N相AMP | FEEDER | S31/11/JD36/I_N |  |  |  | CDC | 185 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十四線 | 朴十四線 |  | 朴十四線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十四線KVAR | 11KV朴十四線 KVAR | FEEDER | S31/11/JD34/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十四線 | 朴十四線 |  | 朴十四線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十四線A1 | 11KV朴十四線 R相AMP | FEEDER | S31/11/JD34/I_R |  |  |  | CDC | 187 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十四線 | 朴十四線 |  | 朴十四線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十四線A2 | 11KV朴十四線 S相AMP | FEEDER | S31/11/JD34/I_S |  |  |  | CDC | 188 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十四線 | 朴十四線 |  | 朴十四線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十四線A3 | 11KV朴十四線 T相AMP | FEEDER | S31/11/JD34/I_T |  |  |  | CDC | 189 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十四線 | 朴十四線 |  | 朴十四線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十四線A0 | 11KV朴十四線 N相AMP | FEEDER | S31/11/JD34/I_N |  |  |  | CDC | 190 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十線 | 朴十線 |  | 朴十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十線KVAR | 11KV朴十線 KVAR | FEEDER | S31/11/JD30/KVAR |  |  |  | CDC | 191 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十線 | 朴十線 |  | 朴十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十線A1 | 11KV朴十線 R相AMP | FEEDER | S31/11/JD30/I_R |  |  |  | CDC | 192 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十線 | 朴十線 |  | 朴十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十線A2 | 11KV朴十線 S相AMP | FEEDER | S31/11/JD30/I_S |  |  |  | CDC | 193 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十線 | 朴十線 |  | 朴十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十線A3 | 11KV朴十線 T相AMP | FEEDER | S31/11/JD30/I_T |  |  |  | CDC | 194 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴十線 | 朴十線 |  | 朴十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴十線A0 | 11KV朴十線 N相AMP | FEEDER | S31/11/JD30/I_N |  |  |  | CDC | 195 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴三線 | 朴三線 |  | 朴三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴三線KVAR | 11KV朴三線 KVAR | FEEDER | S31/11/JD23/KVAR |  |  |  | CDC | 196 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴三線 | 朴三線 |  | 朴三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴三線A1 | 11KV朴三線 R相AMP | FEEDER | S31/11/JD23/I_R |  |  |  | CDC | 197 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴三線 | 朴三線 |  | 朴三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴三線A2 | 11KV朴三線 S相AMP | FEEDER | S31/11/JD23/I_S |  |  |  | CDC | 198 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴三線 | 朴三線 |  | 朴三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴三線A3 | 11KV朴三線 T相AMP | FEEDER | S31/11/JD23/I_T |  |  |  | CDC | 199 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴三線 | 朴三線 |  | 朴三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴三線A0 | 11KV朴三線 N相AMP | FEEDER | S31/11/JD23/I_N |  |  |  | CDC | 200 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴五線 | 朴五線 |  | 朴五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴五線KVAR | 11KV朴五線 KVAR | FEEDER | S31/11/JD25/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴五線 | 朴五線 |  | 朴五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴五線A1 | 11KV朴五線 R相AMP | FEEDER | S31/11/JD25/I_R |  |  |  | CDC | 202 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴五線 | 朴五線 |  | 朴五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴五線A2 | 11KV朴五線 S相AMP | FEEDER | S31/11/JD25/I_S |  |  |  | CDC | 203 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴五線 | 朴五線 |  | 朴五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴五線A3 | 11KV朴五線 T相AMP | FEEDER | S31/11/JD25/I_T |  |  |  | CDC | 204 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴五線 | 朴五線 |  | 朴五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴五線A0 | 11KV朴五線 N相AMP | FEEDER | S31/11/JD25/I_N |  |  |  | CDC | 205 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴六線 | 朴六線 |  | 朴六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴六線KVAR | 11KV朴六線 KVAR | FEEDER | S31/11/JD26/KVAR |  |  |  | CDC | 206 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴六線 | 朴六線 |  | 朴六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴六線A1 | 11KV朴六線 R相AMP | FEEDER | S31/11/JD26/I_R |  |  |  | CDC | 207 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴六線 | 朴六線 |  | 朴六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴六線A2 | 11KV朴六線 S相AMP | FEEDER | S31/11/JD26/I_S |  |  |  | CDC | 208 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴六線 | 朴六線 |  | 朴六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴六線A3 | 11KV朴六線 T相AMP | FEEDER | S31/11/JD26/I_T |  |  |  | CDC | 209 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴六線 | 朴六線 |  | 朴六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴六線A0 | 11KV朴六線 N相AMP | FEEDER | S31/11/JD26/I_N |  |  |  | CDC | 210 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴四線 | 朴四線 |  | 朴四線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴四線KVAR | 11KV朴四線 KVAR | FEEDER | S31/11/JD24/KVAR |  |  |  | CDC | 211 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴四線 | 朴四線 |  | 朴四線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴四線A1 | 11KV朴四線 R相AMP | FEEDER | S31/11/JD24/I_R |  |  |  | CDC | 212 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴四線 | 朴四線 |  | 朴四線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴四線A2 | 11KV朴四線 S相AMP | FEEDER | S31/11/JD24/I_S |  |  |  | CDC | 213 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴四線 | 朴四線 |  | 朴四線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴四線A3 | 11KV朴四線 T相AMP | FEEDER | S31/11/JD24/I_T |  |  |  | CDC | 214 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | 朴四線 | 朴四線 |  | 朴四線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.朴四線A0 | 11KV朴四線 N相AMP | FEEDER | S31/11/JD24/I_N |  |  |  | CDC | 215 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S31/11/TIE2/I_R |  |  |  | CDC | 216 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S31/11/TIE2/I_S |  |  |  | CDC | 217 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S31/11/TIE2/I_T |  |  |  | CDC | 218 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE | S31/11/TIE3/I_R |  |  |  | CDC | 219 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE | S31/11/TIE3/I_S |  |  |  | CDC | 220 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 11 | 11kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE | S31/11/TIE3/I_T |  |  |  | CDC | 221 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_MW | #1MTR二次側 MW | DTR | S31/11/M1/MW |  |  |  | CDC | 222 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S31/11/M1/MVAR |  |  |  | CDC | 223 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S31/11/M1/I_R |  |  |  | CDC | 224 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S31/11/M1/I_S |  |  |  | CDC | 225 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S31/11/M1/I_T |  |  |  | CDC | 226 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_OIL | #1MTR 油溫 | DTR | S31//1MTR/OilTemp |  |  |  | CDC | 227 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_COIL | #1MTR 線溫 | DTR | S31//1MTR/CoilTemp |  |  |  | CDC | 228 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S31//1MTR/TapPosMv |  |  |  | CDC | 229 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_MW | #2MTR二次側 MW | DTR | S31/11/M2A/MW |  |  |  | CDC | 230 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S31/11/M2A/MVAR |  |  |  | CDC | 231 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S31/11/M2A/I_R |  |  |  | CDC | 232 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S31/11/M2A/I_S |  |  |  | CDC | 233 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S31/11/M2A/I_T |  |  |  | CDC | 234 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_OIL | #2MTR 油溫 | DTR | S31//2MTR/OilTemp |  |  |  | CDC | 235 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_COIL | #2MTR 線溫 | DTR | S31//2MTR/CoilTemp |  |  |  | CDC | 236 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S31//2MTR/TapPosMv |  |  |  | CDC | 237 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_MW | #3MTR二次側 MW | DTR | S31/11/M3/MW |  |  |  | CDC | 238 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S31/11/M3/MVAR |  |  |  | CDC | 239 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S31/11/M3/I_R |  |  |  | CDC | 240 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S31/11/M3/I_S |  |  |  | CDC | 241 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S31/11/M3/I_T |  |  |  | CDC | 242 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_OIL | #3MTR 油溫 | DTR | S31//3MTR/OilTemp |  |  |  | CDC | 243 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_COIL | #3MTR 線溫 | DTR | S31//3MTR/CoilTemp |  |  |  | CDC | 244 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S31//3MTR/TapPosMv |  |  |  | CDC | 245 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 2-A7 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_MW | #4MTR二次側 MW | DTR | S31/11/M4/MW |  |  |  | CDC | 246 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 2-A8 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR | S31/11/M4/MVAR |  |  |  | CDC | 247 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | I_R | [17 empty] | 2-A9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR | S31/11/M4/I_R |  |  |  | CDC | 248 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | I_S | [17 empty] | 2-AA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR | S31/11/M4/I_S |  |  |  | CDC | 249 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR二次側 |  | I_T | [17 empty] | 2-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR | S31/11/M4/I_T |  |  |  | CDC | 250 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 2-A5 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_OIL | #4MTR 油溫 | DTR | S31//4MTR/OilTemp |  |  |  | CDC | 251 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 2-A4 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_COIL | #4MTR 線溫 | DTR | S31//4MTR/CoilTemp |  |  |  | CDC | 252 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 2-A6 |  | 2-0A |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_TAP | #4MTR OLTC TAP | DTR | S31//4MTR/TapPosMv |  |  |  | CDC | 253 | GENERICAIPoint | SS212_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S31 | 朴子SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS2_1 | [8 empty] | 朴子SS.直流電源電壓 | 直流電源電壓 | OTHER | S31/0/StaDev/DCV |  |  |  | CDC | 254 | GENERICAIPoint | SS212_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.610_PHA | 嘉太線(610) 相間RY | LINE69 | S31/69/610/PHA |  |  |  | CDC | 255 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.610_GDA | 嘉太線(610) 接地RY | LINE69 | S31/69/610/GDA |  |  |  | CDC | 256 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 朴子SS.610_CB | 610(嘉太線) CB | LINE69 | S31/69/610/CB |  |  |  | CDC | 257 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | ABS1 | 611 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.611_ABS | 611(嘉太線) ABS | LINE69 | S31/69/610/ABS1 |  |  |  | CDC | 258 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | ABS2 | 612 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.612_ABS | 612(嘉太線) ABS | LINE69 | S31/69/610/ABS2 |  |  |  | CDC | 259 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | E2 | 612E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.612E_ES | 612E(嘉太線) ES | LINE69 | S31/69/610/ES2 |  |  |  | CDC | 260 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.620_PHA | 朴子鹿草線(620) 相間RY | LINE69 | S31/69/620/PHA |  |  |  | CDC | 261 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.620_GDA | 朴子鹿草線(620) 接地RY | LINE69 | S31/69/620/GDA |  |  |  | CDC | 262 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 朴子SS.620_CB | 620(朴子鹿草線) CB | LINE69 | S31/69/620/CB |  |  |  | CDC | 263 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | ABS1 | 621 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.621_ABS | 621(朴子鹿草線) ABS | LINE69 | S31/69/620/ABS1 |  |  |  | CDC | 264 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | ABS2 | 622 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.622_ABS | 622(朴子鹿草線) ABS | LINE69 | S31/69/620/ABS2 |  |  |  | CDC | 265 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | E2 | 622E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 朴子SS.622E_ES | 622E(朴子鹿草線) ES | LINE69 | S31/69/620/ES2 |  |  |  | CDC | 266 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.630_PHA | 東石線(630) 相間RY | LINE69 | S31/69/630/PHA |  |  |  | CDC | 267 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.630_GDA | 東石線(630) 接地RY | LINE69 | S31/69/630/GDA |  |  |  | CDC | 268 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | CB | [17 empty] | 1-0A-00 |  | 1-05 | [5 empty] | 69KV_N | [8 empty] | 朴子SS.630_CB | 630(東石線) CB | LINE69 | S31/69/630/CB |  |  |  | CDC | 269 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | ABS1 | 631 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 朴子SS.631_ABS | 631(東石線) ABS | LINE69 | S31/69/630/ABS1 |  |  |  | CDC | 270 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | ABS2 | 632 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 朴子SS.632_ABS | 632(東石線) ABS | LINE69 | S31/69/630/ABS2 |  |  |  | CDC | 271 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | E2 | 632E | [16 empty] | 1-3A-04 | 1-3A-05 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.632E_ES | 632E(東石線) ES | LINE69 | S31/69/630/ES2 |  |  |  | CDC | 272 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.640_PHA | 北港線(640) 相間RY | LINE69 | S31/69/640/PHA |  |  |  | CDC | 273 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.640_GDA | 北港線(640) 接地RY | LINE69 | S31/69/640/GDA |  |  |  | CDC | 274 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 朴子SS.640_CB | 640(北港線) CB | LINE69 | S31/69/640/CB |  |  |  | CDC | 275 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | ABS1 | 641 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 朴子SS.641_ABS | 641(北港線) ABS | LINE69 | S31/69/640/ABS1 |  |  |  | CDC | 276 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | ABS2 | 642 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 朴子SS.642_ABS | 642(北港線) ABS | LINE69 | S31/69/640/ABS2 |  |  |  | CDC | 277 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | E2 | 642E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 朴子SS.642E_ES | 642E(北港線) ES | LINE69 | S31/69/640/ES2 |  |  |  | CDC | 278 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_PHA | 11KV朴一線(JD21) 相間RY | FEEDER | S31/11/JD21/PHA |  |  |  | CDC | 279 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_GDA | 11KV朴一線(JD21) 接地RY | FEEDER | S31/11/JD21/GDA |  |  |  | CDC | 280 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_79UL | 11KV朴一線(JD21) 79RY U/L | FEEDER | S31/11/JD21/79UL |  |  |  | CDC | 281 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD21 | 朴一線(JD21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_ADJ | 11KV朴一線(JD21) LCO分流器 U/L | FEEDER | S31/11/JD21/ADJ |  |  |  | CDC | 282 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD21 | JD21(11KV朴一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_CB | JD21(11KV朴一線) CB | FEEDER | S31/11/JD21/CB |  |  |  | CDC | 283 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_PHA | 11KV朴二線(JD22) 相間RY | FEEDER | S31/11/JD22/PHA |  |  |  | CDC | 284 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_GDA | 11KV朴二線(JD22) 接地RY | FEEDER | S31/11/JD22/GDA |  |  |  | CDC | 285 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_79UL | 11KV朴二線(JD22) 79RY U/L | FEEDER | S31/11/JD22/79UL |  |  |  | CDC | 286 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD22 | 朴二線(JD22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_ADJ | 11KV朴二線(JD22) LCO分流器 U/L | FEEDER | S31/11/JD22/ADJ |  |  |  | CDC | 287 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD22 | JD22(11KV朴二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_CB | JD22(11KV朴二線) CB | FEEDER | S31/11/JD22/CB |  |  |  | CDC | 288 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_PHA | 11KV朴三線(JD23) 相間RY | FEEDER | S31/11/JD23/PHA |  |  |  | CDC | 289 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_GDA | 11KV朴三線(JD23) 接地RY | FEEDER | S31/11/JD23/GDA |  |  |  | CDC | 290 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_79UL | 11KV朴三線(JD23) 79RY U/L | FEEDER | S31/11/JD23/79UL |  |  |  | CDC | 291 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD23 | 朴三線(JD23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_ADJ | 11KV朴三線(JD23) LCO分流器 U/L | FEEDER | S31/11/JD23/ADJ |  |  |  | CDC | 292 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD23 | JD23(11KV朴三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_CB | JD23(11KV朴三線) CB | FEEDER | S31/11/JD23/CB |  |  |  | CDC | 293 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_PHA | 11KV朴四線(JD24) 相間RY | FEEDER | S31/11/JD24/PHA |  |  |  | CDC | 294 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_GDA | 11KV朴四線(JD24) 接地RY | FEEDER | S31/11/JD24/GDA |  |  |  | CDC | 295 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_79UL | 11KV朴四線(JD24) 79RY U/L | FEEDER | S31/11/JD24/79UL |  |  |  | CDC | 296 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD24 | 朴四線(JD24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_ADJ | 11KV朴四線(JD24) LCO分流器 U/L | FEEDER | S31/11/JD24/ADJ |  |  |  | CDC | 297 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD24 | JD24(11KV朴四線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_CB | JD24(11KV朴四線) CB | FEEDER | S31/11/JD24/CB |  |  |  | CDC | 298 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_PHA | 11KV朴五線(JD25) 相間RY | FEEDER | S31/11/JD25/PHA |  |  |  | CDC | 299 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_GDA | 11KV朴五線(JD25) 接地RY | FEEDER | S31/11/JD25/GDA |  |  |  | CDC | 300 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_79UL | 11KV朴五線(JD25) 79RY U/L | FEEDER | S31/11/JD25/79UL |  |  |  | CDC | 301 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD25 | 朴五線(JD25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_ADJ | 11KV朴五線(JD25) LCO分流器 U/L | FEEDER | S31/11/JD25/ADJ |  |  |  | CDC | 302 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD25 | JD25(11KV朴五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_CB | JD25(11KV朴五線) CB | FEEDER | S31/11/JD25/CB |  |  |  | CDC | 303 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_PHA | 11KV朴六線(JD26) 相間RY | FEEDER | S31/11/JD26/PHA |  |  |  | CDC | 304 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_GDA | 11KV朴六線(JD26) 接地RY | FEEDER | S31/11/JD26/GDA |  |  |  | CDC | 305 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_79UL | 11KV朴六線(JD26) 79RY U/L | FEEDER | S31/11/JD26/79UL |  |  |  | CDC | 306 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD26 | 朴六線(JD26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_ADJ | 11KV朴六線(JD26) LCO分流器 U/L | FEEDER | S31/11/JD26/ADJ |  |  |  | CDC | 307 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD26 | JD26(11KV朴六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_CB | JD26(11KV朴六線) CB | FEEDER | S31/11/JD26/CB |  |  |  | CDC | 308 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_PHA | 11KV朴七線(JD27) 相間RY | FEEDER | S31/11/JD27/PHA |  |  |  | CDC | 309 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_GDA | 11KV朴七線(JD27) 接地RY | FEEDER | S31/11/JD27/GDA |  |  |  | CDC | 310 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_79UL | 11KV朴七線(JD27) 79RY U/L | FEEDER | S31/11/JD27/79UL |  |  |  | CDC | 311 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD27 | 朴七線(JD27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_ADJ | 11KV朴七線(JD27) LCO分流器 U/L | FEEDER | S31/11/JD27/ADJ |  |  |  | CDC | 312 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD27 | JD27(11KV朴七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_CB | JD27(11KV朴七線) CB | FEEDER | S31/11/JD27/CB |  |  |  | CDC | 313 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_PHA | 11KV朴八線(JD28) 相間RY | FEEDER | S31/11/JD28/PHA |  |  |  | CDC | 314 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_GDA | 11KV朴八線(JD28) 接地RY | FEEDER | S31/11/JD28/GDA |  |  |  | CDC | 315 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_79UL | 11KV朴八線(JD28) 79RY U/L | FEEDER | S31/11/JD28/79UL |  |  |  | CDC | 316 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD28 | 朴八線(JD28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_ADJ | 11KV朴八線(JD28) LCO分流器 U/L | FEEDER | S31/11/JD28/ADJ |  |  |  | CDC | 317 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD28 | JD28(11KV朴八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_CB | JD28(11KV朴八線) CB | FEEDER | S31/11/JD28/CB |  |  |  | CDC | 318 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_PHA | 11KV朴九線(JD29) 相間RY | FEEDER | S31/11/JD29/PHA |  |  |  | CDC | 319 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_GDA | 11KV朴九線(JD29) 接地RY | FEEDER | S31/11/JD29/GDA |  |  |  | CDC | 320 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_79UL | 11KV朴九線(JD29) 79RY U/L | FEEDER | S31/11/JD29/79UL |  |  |  | CDC | 321 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD29 | 朴九線(JD29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_ADJ | 11KV朴九線(JD29) LCO分流器 U/L | FEEDER | S31/11/JD29/ADJ |  |  |  | CDC | 322 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD29 | JD29(11KV朴九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_CB | JD29(11KV朴九線) CB | FEEDER | S31/11/JD29/CB |  |  |  | CDC | 323 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_PHA | 11KV朴十線(JD30) 相間RY | FEEDER | S31/11/JD30/PHA |  |  |  | CDC | 324 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_GDA | 11KV朴十線(JD30) 接地RY | FEEDER | S31/11/JD30/GDA |  |  |  | CDC | 325 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_79UL | 11KV朴十線(JD30) 79RY U/L | FEEDER | S31/11/JD30/79UL |  |  |  | CDC | 326 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD30 | 朴十線(JD30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_ADJ | 11KV朴十線(JD30) LCO分流器 U/L | FEEDER | S31/11/JD30/ADJ |  |  |  | CDC | 327 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD30 | JD30(11KV朴十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_CB | JD30(11KV朴十線) CB | FEEDER | S31/11/JD30/CB |  |  |  | CDC | 328 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_PHA | 11KV朴十一線(JD31) 相間RY | FEEDER | S31/11/JD31/PHA |  |  |  | CDC | 329 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_GDA | 11KV朴十一線(JD31) 接地RY | FEEDER | S31/11/JD31/GDA |  |  |  | CDC | 330 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_79UL | 11KV朴十一線(JD31) 79RY U/L | FEEDER | S31/11/JD31/79UL |  |  |  | CDC | 331 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD31 | 朴十一線(JD31) |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_ADJ | 11KV朴十一線(JD31) LCO分流器 | FEEDER | S31/11/JD31/ADJ |  |  |  | CDC | 332 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD31 | JD31(11KV朴十一線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_CB | JD31(11KV朴十一線) CB | FEEDER | S31/11/JD31/CB |  |  |  | CDC | 333 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_PHA | 11KV朴十二線(JD32) 相間RY | FEEDER | S31/11/JD32/PHA |  |  |  | CDC | 334 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_GDA | 11KV朴十二線(JD32) 接地RY | FEEDER | S31/11/JD32/GDA |  |  |  | CDC | 335 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_79UL | 11KV朴十二線(JD32) 79RY U/L | FEEDER | S31/11/JD32/79UL |  |  |  | CDC | 336 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD32 | 朴十二線(JD32) |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_ADJ | 11KV朴十二線(JD32) LCO分流器 | FEEDER | S31/11/JD32/ADJ |  |  |  | CDC | 337 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD32 | JD32(11KV朴十二線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_CB | JD32(11KV朴十二線) CB | FEEDER | S31/11/JD32/CB |  |  |  | CDC | 338 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_PHA | 11KV朴十三線(JD33) 相間RY | FEEDER | S31/11/JD33/PHA |  |  |  | CDC | 339 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_GDA | 11KV朴十三線(JD33) 接地RY | FEEDER | S31/11/JD33/GDA |  |  |  | CDC | 340 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_79UL | 11KV朴十三線(JD33) 79RY U/L | FEEDER | S31/11/JD33/79UL |  |  |  | CDC | 341 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD33 | 朴十三線(JD33) |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_ADJ | 11KV朴十三線(JD33) LCO分流器 | FEEDER | S31/11/JD33/ADJ |  |  |  | CDC | 342 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD33 | JD33(11KV朴十三線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_CB | JD33(11KV朴十三線) CB | FEEDER | S31/11/JD33/CB |  |  |  | CDC | 343 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_PHA | 11KV朴十四線(JD34) 相間RY | FEEDER | S31/11/JD34/PHA |  |  |  | CDC | 344 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_GDA | 11KV朴十四線(JD34) 接地RY | FEEDER | S31/11/JD34/GDA |  |  |  | CDC | 345 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_79UL | 11KV朴十四線(JD34) 79RY U/L | FEEDER | S31/11/JD34/79UL |  |  |  | CDC | 346 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD34 | 朴十四線(JD34) |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_ADJ | 11KV朴十四線(JD34) LCO分流器 | FEEDER | S31/11/JD34/ADJ |  |  |  | CDC | 347 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD34 | JD34(11KV朴十四線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_CB | JD34(11KV朴十四線) CB | FEEDER | S31/11/JD34/CB |  |  |  | CDC | 348 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_PHA | 11KV朴十五線(JD35) 相間RY | FEEDER | S31/11/JD35/PHA |  |  |  | CDC | 349 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_GDA | 11KV朴十五線(JD35) 接地RY | FEEDER | S31/11/JD35/GDA |  |  |  | CDC | 350 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_79UL | 11KV朴十五線(JD35) 79RY U/L | FEEDER | S31/11/JD35/79UL |  |  |  | CDC | 351 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD35 | 朴十五線(JD35) |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_ADJ | 11KV朴十五線(JD35) LCO分流器 | FEEDER | S31/11/JD35/ADJ |  |  |  | CDC | 352 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD35 | JD35(11KV朴十五線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_CB | JD35(11KV朴十五線) CB | FEEDER | S31/11/JD35/CB |  |  |  | CDC | 353 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | PHA | [17 empty] | 2-09-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_PHA | 11KV朴十六線(JD36) 相間RY | FEEDER | S31/11/JD36/PHA |  |  |  | CDC | 354 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | GDA | [17 empty] | 2-09-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_GDA | 11KV朴十六線(JD36) 接地RY | FEEDER | S31/11/JD36/GDA |  |  |  | CDC | 355 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) 79RY |  | 79UL | [17 empty] | 2-30-07 |  | 2-0D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_79UL | 11KV朴十六線(JD36) 79RY U/L | FEEDER | S31/11/JD36/79UL |  |  |  | CDC | 356 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD36 | 朴十六線(JD36) |  | ADJ | [17 empty] | 2-30-12 |  | 2-13 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_ADJ | 11KV朴十六線(JD36) LCO分流器 | FEEDER | S31/11/JD36/ADJ |  |  |  | CDC | 357 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD36 | JD36(11KV朴十六線) |  | CB | [17 empty] | 2-02-01 |  | 2-05 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_CB | JD36(11KV朴十六線) CB | FEEDER | S31/11/JD36/CB |  |  |  | CDC | 358 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_PHA | 11KV朴十七線(JD37) 相間RY | FEEDER | S31/11/JD37/PHA |  |  |  | CDC | 359 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_GDA | 11KV朴十七線(JD37) 接地RY | FEEDER | S31/11/JD37/GDA |  |  |  | CDC | 360 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-0E | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_79UL | 11KV朴十七線(JD37) 79RY U/L | FEEDER | S31/11/JD37/79UL |  |  |  | CDC | 361 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD37 | 朴十七線(JD37) |  | ADJ | [17 empty] | 2-30-13 |  | 2-14 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_ADJ | 11KV朴十七線(JD37) LCO分流器 | FEEDER | S31/11/JD37/ADJ |  |  |  | CDC | 362 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD37 | JD37(11KV朴十七線) |  | CB | [17 empty] | 2-02-02 |  | 2-06 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_CB | JD37(11KV朴十七線) CB | FEEDER | S31/11/JD37/CB |  |  |  | CDC | 363 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | PHA | [17 empty] | 2-09-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_PHA | 11KV朴十八線(JD38) 相間RY | FEEDER | S31/11/JD38/PHA |  |  |  | CDC | 364 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | GDA | [17 empty] | 2-09-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_GDA | 11KV朴十八線(JD38) 接地RY | FEEDER | S31/11/JD38/GDA |  |  |  | CDC | 365 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) 79RY |  | 79UL | [17 empty] | 2-30-09 |  | 2-0F | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_79UL | 11KV朴十八線(JD38) 79RY U/L | FEEDER | S31/11/JD38/79UL |  |  |  | CDC | 366 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD38 | 朴十八線(JD38) |  | ADJ | [17 empty] | 2-30-14 |  | 2-15 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_ADJ | 11KV朴十八線(JD38) LCO分流器 | FEEDER | S31/11/JD38/ADJ |  |  |  | CDC | 367 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD38 | JD38(11KV朴十八線) |  | CB | [17 empty] | 2-02-03 |  | 2-07 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_CB | JD38(11KV朴十八線) CB | FEEDER | S31/11/JD38/CB |  |  |  | CDC | 368 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | PHA | [17 empty] | 2-0A-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_PHA | 11KV朴十九線(JD39) 相間RY | FEEDER | S31/11/JD39/PHA |  |  |  | CDC | 369 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | GDA | [17 empty] | 2-0A-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_GDA | 11KV朴十九線(JD39) 接地RY | FEEDER | S31/11/JD39/GDA |  |  |  | CDC | 370 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-10 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_79UL | 11KV朴十九線(JD39) 79RY U/L | FEEDER | S31/11/JD39/79UL |  |  |  | CDC | 371 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD39 | 朴十九線(JD39) |  | ADJ | [17 empty] | 2-30-15 |  | 2-16 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_ADJ | 11KV朴十九線(JD39) LCO分流器 | FEEDER | S31/11/JD39/ADJ |  |  |  | CDC | 372 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD39 | JD39(11KV朴十九線) |  | CB | [17 empty] | 2-02-04 |  | 2-08 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_CB | JD39(11KV朴十九線) CB | FEEDER | S31/11/JD39/CB |  |  |  | CDC | 373 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_PHA | 11KV朴二十線(JD40) 相間RY | FEEDER | S31/11/JD40/PHA |  |  |  | CDC | 374 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_GDA | 11KV朴二十線(JD40) 接地RY | FEEDER | S31/11/JD40/GDA |  |  |  | CDC | 375 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-11 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_79UL | 11KV朴二十線(JD40) 79RY U/L | FEEDER | S31/11/JD40/79UL |  |  |  | CDC | 376 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 11 | 11kV | JD40 | 朴二十線(JD40) |  | ADJ | [17 empty] | 2-31-00 |  | 2-17 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_ADJ | 11KV朴二十線(JD40) LCO分流器 | FEEDER | S31/11/JD40/ADJ |  |  |  | CDC | 377 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S31 | 朴子SS | 11 | 11kV | JD40 | JD40(11KV朴二十線) |  | CB | [17 empty] | 2-02-05 |  | 2-09 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_CB | JD40(11KV朴二十線) CB | FEEDER | S31/11/JD40/CB |  |  |  | CDC | 378 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE2_CB | 11KV TIE2 CB | TIE | S31/11/TIE2/CB |  |  |  | CDC | 379 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE2_51A | 11KV TIE2 51RY | TIE | S31/11/TIE2/51A |  |  |  | CDC | 380 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S31/11/TIE2/51NA |  |  |  | CDC | 381 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE3_CB | 11KV TIE3 CB | TIE | S31/11/TIE3/CB |  |  |  | CDC | 382 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE3_51A | 11KV TIE3 51RY | TIE | S31/11/TIE3/51A |  |  |  | CDC | 383 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE3_51NA | 11KV TIE3 51N RY | TIE | S31/11/TIE3/51NA |  |  |  | CDC | 384 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.750_CB | 750(#1MTR) CB | DTR | S31/69/750/CB |  |  |  | CDC | 385 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.1M_CB | 1M(#1MTR) CB | DTR | S31/11/M1/CB |  |  |  | CDC | 386 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_51A | #1MTR 51RY | DTR | S31/69/750/51A |  |  |  | CDC | 387 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_51NA | #1MTR 51N RY | DTR | S31/69/750/51NA |  |  |  | CDC | 388 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S31//1MTR/51ZA |  |  |  | CDC | 389 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_87A | #1MTR 87RY | DTR | S31//1MTR/87A |  |  |  | CDC | 390 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S31//1MTR/87UL |  |  |  | CDC | 391 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S31/11/M1/51A |  |  |  | CDC | 392 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_TRA | #1MTR 重故障 | DTR | S31//1MTR/TRA |  |  |  | CDC | 393 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S31//1MTR/TRF |  |  |  | CDC | 394 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S31//1MTR/SupLocal |  |  |  | CDC | 395 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S31//1MTR/Tap Chan |  |  |  | CDC | 396 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.751_ABS | 751(#1MTR) ABS | DTR | S31/69/750/ABS1 |  |  |  | CDC | 397 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_96A | #1MTR 96P RY | DTR | S31//1MTR/96PA |  |  |  | CDC | 398 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S31//1MTR/OLTC_DLY |  |  |  | CDC | 399 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S31//1MTR/AC_Fault |  |  |  | CDC | 400 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.760_CB | 760(#2MTR) CB | DTR | S31/69/760/CB |  |  |  | CDC | 401 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.2MA_CB | 2MA(#2MTR) CB | DTR | S31/11/M2A/CB |  |  |  | CDC | 402 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-46 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.2MB_CB | 2MB(#2MTR) CB | DTR | S31/11/M2B/CB |  |  |  | CDC | 403 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_51A | #2MTR 51RY | DTR | S31/69/760/51A |  |  |  | CDC | 404 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_51NA | #2MTR 51N RY | DTR | S31/69/760/51NA |  |  |  | CDC | 405 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S31//2MTR/51ZA |  |  |  | CDC | 406 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_87A | #2MTR 87RY | DTR | S31//2MTR/87A |  |  |  | CDC | 407 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S31//2MTR/87UL |  |  |  | CDC | 408 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S31/11/M2A/51A |  |  |  | CDC | 409 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S31/11/M2B/51A |  |  |  | CDC | 410 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_TRA | #2MTR 重故障 | DTR | S31//2MTR/TRA |  |  |  | CDC | 411 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S31//2MTR/TRF |  |  |  | CDC | 412 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S31//2MTR/SupLocal |  |  |  | CDC | 413 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S31//2MTR/Tap Chan |  |  |  | CDC | 414 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.761_ABS | 761(#2MTR) ABS | DTR | S31/69/760/ABS1 |  |  |  | CDC | 415 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_96A | #2MTR 96P RY | DTR | S31//2MTR/96PA |  |  |  | CDC | 416 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S31//2MTR/OLTC_DLY |  |  |  | CDC | 417 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S31//2MTR/AC_Fault |  |  |  | CDC | 418 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.770_CB | 770(#3MTR) CB | DTR | S31/69/770/CB |  |  |  | CDC | 419 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.3M_CB | 3M(#3MTR) CB | DTR | S31/11/M3/CB |  |  |  | CDC | 420 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_51A | #3MTR 51RY | DTR | S31/69/770/51A |  |  |  | CDC | 421 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_51NA | #3MTR 51N RY | DTR | S31/69/770/51NA |  |  |  | CDC | 422 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S31//3MTR/51ZA |  |  |  | CDC | 423 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_87A | #3MTR 87RY | DTR | S31//3MTR/87A |  |  |  | CDC | 424 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S31//3MTR/87UL |  |  |  | CDC | 425 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-12-01 |  | 1-69 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S31/11/M3/81AS |  |  |  | CDC | 426 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S31 | 朴子SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S31/11/M3/51A |  |  |  | CDC | 427 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_TRA | #3MTR 重故障 | DTR | S31//3MTR/TRA |  |  |  | CDC | 428 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S31//3MTR/TRF |  |  |  | CDC | 429 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S31//3MTR/SupLocal |  |  |  | CDC | 430 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S31//3MTR/Tap Chan |  |  |  | CDC | 431 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.771_ABS | 771(#3MTR) ABS | DTR | S31/69/770/ABS1 |  |  |  | CDC | 432 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_96A | #3MTR 96P RY | DTR | S31//3MTR/96PA |  |  |  | CDC | 433 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S31//3MTR/OLTC_DLY |  |  |  | CDC | 434 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S31//3MTR/AC_Fault |  |  |  | CDC | 435 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 2-00-02 |  | 2-02 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.780_CB | 780(#4MTR) CB | DTR | S31/69/780/CB |  |  |  | CDC | 436 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 4M | #4MTR |  | CB | [17 empty] | 2-00-03 |  | 2-03 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.4M_CB | 4M(#4MTR) CB | DTR | S31/11/M4/CB |  |  |  | CDC | 437 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 51A | [17 empty] | 2-00-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_51A | #4MTR 51RY | DTR | S31/69/780/51A |  |  |  | CDC | 438 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 51NA | [17 empty] | 2-00-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_51NA | #4MTR 51N RY | DTR | S31/69/780/51NA |  |  |  | CDC | 439 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 2-01-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_51ZA | #4MTR 51Z RY | DTR | S31//4MTR/51ZA |  |  |  | CDC | 440 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 2-00-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_87A | #4MTR 87RY | DTR | S31//4MTR/87A |  |  |  | CDC | 441 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 87UL | [17 empty] | 2-30-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_87UL | #4MTR 87RY U/L | DTR | S31//4MTR/87UL |  |  |  | CDC | 442 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 81AS | [17 empty] | 2-08-07 |  | 2-12 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_81A/S | #4MTR 81RY A/S | DTR | S31//4MTR/81AS |  |  |  | CDC | 443 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S31 | 朴子SS | 0 |  | 4M | #4MTR二次側(4M) |  | 51A | [17 empty] | 2-01-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.4M_51A | #4MTR二次側(4M) 51RY | DTR | S31/11/M4/51A |  |  |  | CDC | 444 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 2-30-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_TRA | #4MTR 重故障 | DTR | S31//4MTR/TRA |  |  |  | CDC | 445 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 2-30-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_TRF | #4MTR 輕故障 | DTR | S31//4MTR/TRF |  |  |  | CDC | 446 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 2-30-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_S/L | #4MTR OLTC S/L | DTR | S31//4MTR/SupLocal |  |  |  | CDC | 447 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 2-30-05 |  | 2-0B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_A/M | #4MTR OLTC A/M | DTR | S31//4MTR/Tap Chan |  |  |  | CDC | 448 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | [16 empty] | 2-38-00 | 2-38-01 | 2-00 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.781_ABS | 781(#4MTR) ABS | DTR | S31/69/780/ABS1 |  |  |  | CDC | 449 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 2-00-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_96A | #4MTR 96P RY | DTR | S31//4MTR/96PA |  |  |  | CDC | 450 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR | #4MTR |  | OLTC_DLY | [17 empty] | 2-30-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR | S31//4MTR/OLTC_DLY |  |  |  | CDC | 451 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 4MTR_AC | #4MTR |  | FAULT | [17 empty] | 2-31-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR | S31//4MTR/AC_Fault |  |  |  | CDC | 452 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_CB | 210(11KV #1SC) CB | SC | S31/11/210/CB |  |  |  | CDC | 453 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S31/11/210/Tap Chan |  |  |  | CDC | 454 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_SCA | 11KV #1SC 51,51N RY | SC | S31/11/210/SCA |  |  |  | CDC | 455 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S31/11/210/UVA |  |  |  | CDC | 456 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_CB | 220(11KV #2SC) CB | SC | S31/11/220/CB |  |  |  | CDC | 457 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S31/11/220/Tap Chan |  |  |  | CDC | 458 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_SCA | 11KV #2SC 51,51N RY | SC | S31/11/220/SCA |  |  |  | CDC | 459 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S31/11/220/UVA |  |  |  | CDC | 460 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_CB | 230(11KV #3SC) CB | SC | S31/11/230/CB |  |  |  | CDC | 461 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S31/11/230/Tap Chan |  |  |  | CDC | 462 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_SCA | 11KV #3SC 51,51N RY | SC | S31/11/230/SCA |  |  |  | CDC | 463 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S31/11/230/UVA |  |  |  | CDC | 464 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-02-00 |  | 2-04 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_CB | 240(11KV #4SC) CB | SC | S31/11/240/CB |  |  |  | CDC | 465 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-30-06 |  | 2-0C | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_A/M | 11KV #4SC 乏控器 A/M | SC | S31/11/240/Tap Chan |  |  |  | CDC | 466 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-09-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_SCA | 11KV #4SC 51,51N RY | SC | S31/11/240/SCA |  |  |  | CDC | 467 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-09-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | S31/11/240/UVA |  |  |  | CDC | 468 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 朴子SS.810_CB | 810(69KV #1SC) CB | SC | S31/69/810/CB |  |  |  | CDC | 469 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 朴子SS.811_ABS | 811(69KV #1SC) ABS | SC | S31/69/810/ABS1 |  |  |  | CDC | 470 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.810_SCA | 69KV #1SC 51,51N RY | SC | S31/69/810/SCA |  |  |  | CDC | 471 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.810_OUVA | 69KV #1SC 27,59RY | SC | S31/69/810/UVA |  |  |  | CDC | 472 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 朴子SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S31/69/1BUS/BUS_VUA |  |  |  | CDC | 473 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S31/11/ComPoint/CBA |  |  |  | CDC | 474 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S31/11/ComPoint/CBF |  |  |  | CDC | 475 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S31/69/ComPoint/ABS_89A |  |  |  | CDC | 476 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S31/69/ComPoint/CBA |  |  |  | CDC | 477 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S31/69/ComPoint/CBF |  |  |  | CDC | 478 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S31/0/RTU/RTU_R_L |  |  |  | CDC | 479 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S31 | 朴子SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.TEST_CB | TEST CB | OTHER | S31/0/RTU/Test_CB |  |  |  | CDC | 480 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.火災警報(1) | [朴子]火警 | OTHER | S31/0/StaDev/Fire1 |  |  |  | CDC | 481 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S31/0/StaDev/OPA |  |  |  | CDC | 482 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.其他重故障 | 變電所內其他重故障 | OTHER | S31/0/StaDev/PSA |  |  |  | CDC | 483 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S31/0/StaDev/PSF |  |  |  | CDC | 484 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S31/0/StaDev/STUV |  |  |  | CDC | 485 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S31/0/StaDev/CHG1 |  |  |  | CDC | 486 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.直流電源DCA | 直流電源故障警報 | OTHER | S31/0/StaDev/DCA |  |  |  | CDC | 487 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S31/0/StaDev/DCE |  |  |  | CDC | 488 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S31/0/StaDev/OilLeak |  |  |  | CDC | 489 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S31/0/StaDev/6A5Other |  |  |  | CDC | 490 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S31/0/StaDev/7A5Other |  |  |  | CDC | 491 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S31/0/StaDev/8A5Other |  |  |  | CDC | 492 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S31/0/StaDev/CHG2 |  |  |  | CDC | 493 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S31/0/StaDev/CommACF |  |  |  | CDC | 494 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S31/0/StaDev/Door1 |  |  |  | CDC | 495 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S31/0/StaDev/Door2 |  |  |  | CDC | 496 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S31/0/StaDev/Door3 |  |  |  | CDC | 497 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S31 | 朴子SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.開關場照明(A) | 所內開關場照明 | OTHER | S31/0/StaDev/Lights1 |  |  |  | CDC | 498 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S31 | 朴子SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.開關場照明(B) | 路燈照明 | OTHER | S31/0/StaDev/Lights2 |  |  |  | CDC | 499 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S31 | 朴子SS | 0 |  |  |  |  | #1MAIN51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MAIN51NA | #1MAIN51NA | OTHER | S31/11/M1/51NA |  |  |  | CDC | 500 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MAIN51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MAIN51NA | #2MAIN51NA | OTHER | S31/11/M2A/51NA |  |  |  | CDC | 501 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MBIN51NA | [17 empty] | 1-02-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MBIN51NA | #2MBIN51NA | OTHER | S31/11/M2B/51NA |  |  |  | CDC | 502 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #3MAIN51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MAIN51NA | #3MAIN51NA | OTHER | S31/11/M3/51NA |  |  |  | CDC | 503 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MAIN51NA | [17 empty] | 2-01-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MAIN51NA | #4MAIN51NA | OTHER | S31/11/M4/51NA |  |  |  | CDC | 504 | GENERICDIPoint | SS212_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 69KVBUS#2VUA | [17 empty] | 1-31-14 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.69KVBUS#2VUA | 69KVBUS#2VUA | OTHER | S31/69/2BUS/BUS_VUA |  |  |  | CDC | 505 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.69KVSC警報 | 69KVSC警報 | OTHER | S31/69/810/60A |  |  |  | CDC | 506 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | MCSG火警 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.MCSG火警 | MCSG火警 | OTHER | S31/0/StaDev/Fire2 |  |  |  | CDC | 507 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | MCSG系統故障 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.MCSG系統故障 | MCSG系統故障 | OTHER | S31/0/StaDev/1A5Other |  |  |  | CDC | 508 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.主變火警 | 主變火警 | OTHER | S31/0/StaDev/Fire |  |  |  | CDC | 509 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.安全監控 | 安全監控 | OTHER | S31/0/StaDev/Burglar |  |  |  | CDC | 510 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.門禁 | 大門側門 | OTHER | S31/0/StaDev/Door |  |  |  | CDC | 511 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.細水霧故障 | 細水霧故障 | OTHER | S31/0/StaDev/2A5Other |  |  |  | CDC | 512 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S31/0/StaDev/3A5Other |  |  |  | CDC | 513 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.維護運轉警報 | 維護運轉警報 | OTHER | S31/0/StaDev/4A5Other |  |  |  | CDC | 514 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S31//1MTR/63Q |  |  |  | CDC | 515 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S31//1MTR/96B1 |  |  |  | CDC | 516 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S31//1MTR/96B2 |  |  |  | CDC | 517 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S31//1MTR/96D |  |  |  | CDC | 518 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S31//1MTR/96P |  |  |  | CDC | 519 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 2MTR6 | #2MTR6 |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR63Q | #2MTR6 ULTC電驛動作 | OTHER | S31//2MTR/63Q |  |  |  | CDC | 520 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR96B1 | #2MTR6撲氣電驛警報 | OTHER | S31//2MTR/96B1 |  |  |  | CDC | 521 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR96B2 | #2MTR6撲氣電驛動作 | OTHER | S31//2MTR/96B2 |  |  |  | CDC | 522 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR96D | #2MTR6放壓電驛動作 | OTHER | S31//2MTR/96D |  |  |  | CDC | 523 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#2MTR96P | #2MTR6突壓電驛動作 | OTHER | S31//2MTR/96P |  |  |  | CDC | 524 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 3MTR | #3MTR |  | #3MTR63Q | [17 empty] | 1-19-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR63Q | #3MTR ULTC電驛動作 | OTHER | S31//3MTR/63Q |  |  |  | CDC | 525 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #3MTR96B1 | [17 empty] | 1-19-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR96B1 | #3MTR撲氣電驛警報 | OTHER | S31//3MTR/96B1 |  |  |  | CDC | 526 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #3MTR96B2 | [17 empty] | 1-19-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR96B2 | #3MTR撲氣電驛動作 | OTHER | S31//3MTR/96B2 |  |  |  | CDC | 527 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #3MTR96D | [17 empty] | 1-19-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR96D | #3MTR放壓電驛動作 | OTHER | S31//3MTR/96D |  |  |  | CDC | 528 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #3MTR96P | [17 empty] | 1-19-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#3MTR96P | #3MTR突壓電驛動作 | OTHER | S31//3MTR/96P |  |  |  | CDC | 529 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 5MTR | #5MTR |  | #5MTR63Q | [17 empty] | 1-1A-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#5MTR63Q | #5MTR ULTC電驛動作 | OTHER | S31//5MTR/63Q |  |  |  | CDC | 530 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #5MTR96B1 | [17 empty] | 1-19-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#5MTR96B1 | #5MTR撲氣電驛警報 | OTHER | S31//5MTR/96B1 |  |  |  | CDC | 531 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #5MTR96B2 | [17 empty] | 1-1A-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#5MTR96B2 | #5MTR撲氣電驛動作 | OTHER | S31//5MTR/96B2 |  |  |  | CDC | 532 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #5MTR96D | [17 empty] | 1-1A-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#5MTR96D | #5MTR放壓電驛動作 | OTHER | S31//5MTR/96D |  |  |  | CDC | 533 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #5MTR96P | [17 empty] | 1-1A-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#5MTR96P | #5MTR突壓電驛動作 | OTHER | S31//5MTR/96P |  |  |  | CDC | 534 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MTR63Q | [17 empty] | 1-1B-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR63Q | ULTC電驛動作 | OTHER | S31//4MTR/63Q |  |  |  | CDC | 535 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MTR96B1 | [17 empty] | 1-1A-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR96B1 | 撲氣電驛警報 | OTHER | S31//4MTR/96B1 |  |  |  | CDC | 536 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MTR96B2 | [17 empty] | 1-1A-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR96B2 | 撲氣電驛動作 | OTHER | S31//4MTR/96B2 |  |  |  | CDC | 537 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MTR96D | [17 empty] | 1-1A-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR96D | 放壓電驛動作 | OTHER | S31//4MTR/96D |  |  |  | CDC | 538 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | #4MTR96P | [17 empty] | 1-1A-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.#4MTR96P | 突壓電驛動作 | OTHER | S31//4MTR/96P |  |  |  | CDC | 539 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S31/0/StaDev/DD_Light |  |  |  | CDC | 540 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-37-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S31/0/StaDev/R_Temp |  |  |  | CDC | 541 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS2_1 | [8 empty] | 朴子SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S31//1MTR/81AS |  |  |  | CDC | 542 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S31 | 朴子SS | 0 |  |  |  |  | IED警報 | [17 empty] | 1-1B-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.IED警報 | 11/23KV重故障(IED警報) | OTHER | S31/0/ComPoint/FDR_CBA |  |  |  | CDC | 543 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴一線LOA | [17 empty] | 2-38-08 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴一線LOA | 朴一線LOA | OTHER | S31/11/JD21/LOA |  |  |  | CDC | 544 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴七線LOA | [17 empty] | 2-38-14 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴七線LOA | 朴七線LOA | OTHER | S31/11/JD27/LOA |  |  |  | CDC | 545 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴九線LOA | [17 empty] | 2-39-00 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴九線LOA | 朴九線LOA | OTHER | S31/11/JD29/LOA |  |  |  | CDC | 546 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴二十線LOA | [17 empty] | 2-39-11 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二十線LOA | 朴二十線LOA | OTHER | S31/11/JD40/LOA |  |  |  | CDC | 547 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴二線LOA | [17 empty] | 2-38-09 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴二線LOA | 朴二線LOA | OTHER | S31/11/JD22/LOA |  |  |  | CDC | 548 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴八線LOA | [17 empty] | 2-38-15 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴八線LOA | 朴八線LOA | OTHER | S31/11/JD28/LOA |  |  |  | CDC | 549 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十一線LOA | [17 empty] | 2-39-02 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十一線LOA | 朴十一線LOA | OTHER | S31/11/JD31/LOA |  |  |  | CDC | 550 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十七線LOA | [17 empty] | 2-39-08 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十七線LOA | 朴十七線LOA | OTHER | S31/11/JD37/LOA |  |  |  | CDC | 551 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十九線LOA | [17 empty] | 2-39-10 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十九線LOA | 朴十九線LOA | OTHER | S31/11/JD39/LOA |  |  |  | CDC | 552 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十二線LOA | [17 empty] | 2-39-03 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十二線LOA | 朴十二線LOA | OTHER | S31/11/JD32/LOA |  |  |  | CDC | 553 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十八線LOA | [17 empty] | 2-39-09 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十八線LOA | 朴十八線LOA | OTHER | S31/11/JD38/LOA |  |  |  | CDC | 554 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十三線LOA | [17 empty] | 2-39-04 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十三線LOA | 朴十三線LOA | OTHER | S31/11/JD33/LOA |  |  |  | CDC | 555 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十五線LOA | [17 empty] | 2-39-06 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十五線LOA | 朴十五線LOA | OTHER | S31/11/JD35/LOA |  |  |  | CDC | 556 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十六線LOA | [17 empty] | 2-39-07 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十六線LOA | 朴十六線LOA | OTHER | S31/11/JD36/LOA |  |  |  | CDC | 557 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十四線LOA | [17 empty] | 2-39-05 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十四線LOA | 朴十四線LOA | OTHER | S31/11/JD34/LOA |  |  |  | CDC | 558 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴十線LOA | [17 empty] | 2-39-01 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴十線LOA | 朴十線LOA | OTHER | S31/11/JD30/LOA |  |  |  | CDC | 559 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴三線LOA | [17 empty] | 2-38-10 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴三線LOA | 朴三線LOA | OTHER | S31/11/JD23/LOA |  |  |  | CDC | 560 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴五線LOA | [17 empty] | 2-38-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴五線LOA | 朴五線LOA | OTHER | S31/11/JD25/LOA |  |  |  | CDC | 561 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴六線LOA | [17 empty] | 2-38-13 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴六線LOA | 朴六線LOA | OTHER | S31/11/JD26/LOA |  |  |  | CDC | 562 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 朴四線LOA | [17 empty] | 2-38-11 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.朴四線LOA | 朴四線LOA | OTHER | S31/11/JD24/LOA |  |  |  | CDC | 563 | GENERICDIPoint | SS212_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-14 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.開關場水位警報 | 開關場水位警報 | OTHER | S31/0/StaDev/Water1 |  |  |  | CDC | 564 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.630_87A | 東石線(630) 87RY | LINE69 | S31/69/630/87A |  |  |  | CDC | 565 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | CFA | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 朴子SS.630_CFA | 東石線(630) 通訊故障 | LINE69 | S31/69/630/87CFA |  |  |  | CDC | 566 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 朴子SS.630_87UL | 東石線(630) 87RY U/L | LINE69 | S31/69/630/87UL |  |  |  | CDC | 567 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.640_87A | 北港線(640) 87RY | LINE69 | S31/69/640/87A |  |  |  | CDC | 568 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | CFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 朴子SS.640_CFA | 北港線(640) 通訊故障 | LINE69 | S31/69/640/87CFA |  |  |  | CDC | 569 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 朴子SS.640_87UL | 北港線(640) 87RY U/L | LINE69 | S31/69/640/87UL |  |  |  | CDC | 570 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 630 | 東石線(630) |  | RYFA | [17 empty] | 1-37-12 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.630_RYFA | 630 東石線IED警報 | OTHER | S31/69/630/RYFA |  |  |  | CDC | 571 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | 640 | 北港線(640) |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.640_RYFA | 640 北港線IED警報 | OTHER | S31/69/640/RYFA |  |  |  | CDC | 572 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 朴子SS.610_87A | 嘉太線(610) 87RY | LINE69 | S31/69/610/87A |  |  |  | CDC | 573 | GENERICDIPoint | SS212_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | CFA | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 朴子SS.610_CFA | 嘉太線(610) 通訊故障 | LINE69 | S31/69/610/87CFA |  |  |  | CDC | 574 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 朴子SS.610_87UL | 嘉太線(610) 87 U/L | LINE69 | S31/69/610/87UL |  |  |  | CDC | 575 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S31 | 朴子SS | 0 |  | 610 | 嘉太線(610) |  | RYFA | [17 empty] | 1-37-09 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.610_RYFA | 610 嘉太線IED警報 | OTHER | S31/69/610/RYFA |  |  |  | CDC | 576 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.開關場水位二段 | 開關場水位二段警報檔 | OTHER | S31/0/StaDev/Water2 |  |  |  | CDC | 577 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_1 | [8 empty] | 朴子SS.PMA | POWER METER警報 | OTHER | S31/0/ComPoint/PMA |  |  |  | CDC | 578 | GENERICDIPoint | SS212_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S31 | 朴子SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 579 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 580 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 581 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 582 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 69 | 69kV | 810_SC | #1SC | 21.6 | CAP | [25 empty] | DDCS2_1 | [8 empty] | 朴子SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 583 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.610LE | 610LE (非取樣點) | LINE69 | S31/69/610/LE0 |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 610 | 嘉太線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.610BE | 610BE (非取樣點) | LINE69 | S31/69/610/BE0 |  |  |  |  | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.620LE | 620LE (非取樣點) | LINE69 | S31/69/620/LE0 |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 620 | 朴子鹿草線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.620BE | 620BE (非取樣點) | LINE69 | S31/69/620/BE0 |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.630LE | 630LE (非取樣點) | LINE69 | S31/69/630/LE0 |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 630 | 東石線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.630BE | 630BE (非取樣點) | LINE69 | S31/69/630/BE0 |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.640LE | 640LE (非取樣點) | LINE69 | S31/69/640/LE0 |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 640 | 北港線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 朴子SS.640BE | 640BE (非取樣點) | LINE69 | S31/69/640/BE0 |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD21 | JD21_DS |  | DS1 | JD21_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_DS | JD21_DS (非取樣點) | FEEDER | S31/11/JD21/DS |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD21 | JD21_ES |  | LE0 | JD21_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD21_ES | JD21_ES (非取樣點) | FEEDER | S31/11/JD21/ES |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD22 | JD22_DS |  | DS1 | JD22_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_DS | JD22_DS (非取樣點) | FEEDER | S31/11/JD22/DS |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD22 | JD22_ES |  | LE0 | JD22_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD22_ES | JD22_ES (非取樣點) | FEEDER | S31/11/JD22/ES |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD23 | JD23_DS |  | DS1 | JD23_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_DS | JD23_DS (非取樣點) | FEEDER | S31/11/JD23/DS |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD23 | JD23_ES |  | LE0 | JD23_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD23_ES | JD23_ES (非取樣點) | FEEDER | S31/11/JD23/ES |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD24 | JD24_DS |  | DS1 | JD24_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_DS | JD24_DS (非取樣點) | FEEDER | S31/11/JD24/DS |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD24 | JD24_ES |  | LE0 | JD24_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD24_ES | JD24_ES (非取樣點) | FEEDER | S31/11/JD24/ES |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD25 | JD25_DS |  | DS1 | JD25_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_DS | JD25_DS (非取樣點) | FEEDER | S31/11/JD25/DS |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD25 | JD25_ES |  | LE0 | JD25_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD25_ES | JD25_ES (非取樣點) | FEEDER | S31/11/JD25/ES |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD26 | JD26_DS |  | DS1 | JD26_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_DS | JD26_DS (非取樣點) | FEEDER | S31/11/JD26/DS |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD26 | JD26_ES |  | LE0 | JD26_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD26_ES | JD26_ES (非取樣點) | FEEDER | S31/11/JD26/ES |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD27 | JD27_DS |  | DS1 | JD27_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_DS | JD27_DS (非取樣點) | FEEDER | S31/11/JD27/DS |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD27 | JD27_ES |  | LE0 | JD27_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD27_ES | JD27_ES (非取樣點) | FEEDER | S31/11/JD27/ES |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD28 | JD28_DS |  | DS1 | JD28_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_DS | JD28_DS (非取樣點) | FEEDER | S31/11/JD28/DS |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD28 | JD28_ES |  | LE0 | JD28_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD28_ES | JD28_ES (非取樣點) | FEEDER | S31/11/JD28/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD29 | JD29_DS |  | DS1 | JD29_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_DS | JD29_DS (非取樣點) | FEEDER | S31/11/JD29/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD29 | JD29_ES |  | LE0 | JD29_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD29_ES | JD29_ES (非取樣點) | FEEDER | S31/11/JD29/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD30 | JD30_DS |  | DS1 | JD30_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_DS | JD30_DS (非取樣點) | FEEDER | S31/11/JD30/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD30 | JD30_ES |  | LE0 | JD30_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD30_ES | JD30_ES (非取樣點) | FEEDER | S31/11/JD30/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD31 | JD31_DS |  | DS1 | JD31_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_DS | JD31_DS (非取樣點) | FEEDER | S31/11/JD31/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD31 | JD31_ES |  | LE0 | JD31_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD31_ES | JD31_ES (非取樣點) | FEEDER | S31/11/JD31/ES |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD32 | JD32_DS |  | DS1 | JD32_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_DS | JD32_DS (非取樣點) | FEEDER | S31/11/JD32/DS |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD32 | JD32_ES |  | LE0 | JD32_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD32_ES | JD32_ES (非取樣點) | FEEDER | S31/11/JD32/ES |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD33 | JD33_DS |  | DS1 | JD33_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_DS | JD33_DS (非取樣點) | FEEDER | S31/11/JD33/DS |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD33 | JD33_ES |  | LE0 | JD33_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD33_ES | JD33_ES (非取樣點) | FEEDER | S31/11/JD33/ES |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD34 | JD34_DS |  | DS1 | JD34_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_DS | JD34_DS (非取樣點) | FEEDER | S31/11/JD34/DS |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD34 | JD34_ES |  | LE0 | JD34_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD34_ES | JD34_ES (非取樣點) | FEEDER | S31/11/JD34/ES |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD35 | JD35_DS |  | DS1 | JD35_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_DS | JD35_DS (非取樣點) | FEEDER | S31/11/JD35/DS |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD35 | JD35_ES |  | LE0 | JD35_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD35_ES | JD35_ES (非取樣點) | FEEDER | S31/11/JD35/ES |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD36 | JD36_DS |  | DS1 | JD36_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_DS | JD36_DS (非取樣點) | FEEDER | S31/11/JD36/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD36 | JD36_ES |  | LE0 | JD36_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD36_ES | JD36_ES (非取樣點) | FEEDER | S31/11/JD36/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD37 | JD37_DS |  | DS1 | JD37_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_DS | JD37_DS (非取樣點) | FEEDER | S31/11/JD37/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD37 | JD37_ES |  | LE0 | JD37_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD37_ES | JD37_ES (非取樣點) | FEEDER | S31/11/JD37/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD38 | JD38_DS |  | DS1 | JD38_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_DS | JD38_DS (非取樣點) | FEEDER | S31/11/JD38/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD38 | JD38_ES |  | LE0 | JD38_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD38_ES | JD38_ES (非取樣點) | FEEDER | S31/11/JD38/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD39 | JD39_DS |  | DS1 | JD39_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_DS | JD39_DS (非取樣點) | FEEDER | S31/11/JD39/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD39 | JD39_ES |  | LE0 | JD39_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD39_ES | JD39_ES (非取樣點) | FEEDER | S31/11/JD39/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | JD40 | JD40_DS |  | DS1 | JD40_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_DS | JD40_DS (非取樣點) | FEEDER | S31/11/JD40/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | JD40 | JD40_ES |  | LE0 | JD40_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.JD40_ES | JD40_ES (非取樣點) | FEEDER | S31/11/JD40/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S31/11/TIE2/D1 |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S31/11/TIE3/D1 |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.750TE | 750TE (非取樣點) | DTR | S31/69/750/TE0 |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.750BE | 750BE (非取樣點) | DTR | S31/69/750/BE0 |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.1M_DS | 1M_DS (非取樣點) | DTR | S31/11/M1/DS |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.1M_ES | 1M_ES (非取樣點) | DTR | S31/11/M1/ES |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.760TE | 760TE (非取樣點) | DTR | S31/69/760/TE0 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.760BE | 760BE (非取樣點) | DTR | S31/69/760/BE0 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.2M_DS | 2M_DS (非取樣點) | DTR | S31/11/M2A/DS |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.2M_ES | 2M_ES (非取樣點) | DTR | S31/11/M2A/ES |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.770TE | 770TE (非取樣點) | DTR | S31/69/770/TE0 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.770BE | 770BE (非取樣點) | DTR | S31/69/770/BE0 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.3M_DS | 3M_DS (非取樣點) | DTR | S31/11/M3/DS |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.3M_ES | 3M_ES (非取樣點) | DTR | S31/11/M3/ES |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.780TE | 780TE (非取樣點) | DTR | S31/69/780/TE0 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.780BE | 780BE (非取樣點) | DTR | S31/69/780/BE0 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 4M | 4M_DS |  | DS1 | 4M_DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.4M_DS | 4M_DS (非取樣點) | DTR | S31/11/M4/DS |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 4M | 4M_ES |  | M0 | 4M_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.4M_ES | 4M_ES (非取樣點) | DTR | S31/11/M4/ES |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.210_ES | 210_ES (非取樣點) | SC | S31/11/210/ES |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.211DS | 211DS (非取樣點) | SC | S31/11/210/D1 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.212DS | 212DS (非取樣點) | SC | S31/11/210/D2 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.220_ES | 220_ES (非取樣點) | SC | S31/11/220/ES |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.221DS | 221DS (非取樣點) | SC | S31/11/220/D1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.222DS | 222DS (非取樣點) | SC | S31/11/220/D2 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.230_ES | 230_ES (非取樣點) | SC | S31/11/230/ES |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 231DS | 231DS |  | 231DS | 231DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.231DS | 231DS (非取樣點) | SC | S31/11/230/D1 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 232DS | 232DS |  | 232DS | 232DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.232DS | 232DS (非取樣點) | SC | S31/11/230/D2 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.240_ES | 240_ES (非取樣點) | SC | S31/11/240/ES |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 241DS | 241DS |  | 241DS | 241DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.241DS | 241DS (非取樣點) | SC | S31/11/240/D1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 0 |  | 242DS | 242DS |  | 242DS | 242DS | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.242DS | 242DS (非取樣點) | SC | S31/11/240/D2 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S31 | 朴子SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810_ES | [24 empty] | ADCS_N | [8 empty] | 朴子SS.810_ES | 810_ES (非取樣點) | SC | S31/69/810/ES |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 朴子SS.69B1E | 69B1E (非取樣點) | BUS | S31/69/1BUS/BE1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S31 | 朴子SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_1 | [8 empty] | 朴子SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 664 | NotelDIPoint | [38 empty] | START/STOP | STOP

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo