## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 69KV 一號 BUS PT R相 | kV_-90_90(-2000_2000) | aaa | B2/S32_A1 | [8 empty] | 新塭SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV＃2BUS | KV | 69KV 二號 BUS PT R相 | kV_-90_90(-2000_2000) | aab | B2/S32_A1 | [8 empty] | 新塭SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S32 | 新塭SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0017 |  |  | 1-91 |  |  | ＃1 MTR | KV | 一號主變二次側BUS11KV | kV_-9_9(-2000_2000) | aaa | B2/S32_D1 | [8 empty] | 新塭SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S32 | 新塭SS | 11 | 11kV | 2BUS | #2BUS |  | V |  | SPARE | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0094 |  |  | 1-DE |  |  | SPARE |  |  | kV_-9_9(-2000_2000) | aba | B2/S32_D1 | [8 empty] | 新塭SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S32 | 新塭SS | 69 | 69kV | 69B1E | 69B1E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aaaz | B2/S32_A1 | [8 empty] | 新塭SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0256 |  |  | 1-31-13 |  |  | 69KV BUS#1 衡相監視警報 |  |  |  |  | B2/S32_A1 | [15 empty] | CDC | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-04-05 |  |  | 69KV ＃1BUS 87 B1A |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0273 |  | 0012 | 1-32-14 |  | 1-0B | 87 B1S (#1 匯流排 87S) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 69 | 69kV | 69B2E | 69B2E |  | BE2 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BUS | [13 empty] | aaaz | B2/S32_A1 | [8 empty] | 新塭SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-31-14 |  |  | 69KV BUS#2 衡相監視警報 |  |  |  |  | B2/S32_A1 | [15 empty] | CDC | 11 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-04-06 |  |  | 69KV ＃2BUS 87 B2A |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0274 |  | 0013 | 1-32-15 |  | 1-0C | 87 B2S (#2 匯流排 87S) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 630 | MW | 大寮新塭線有效電力 | MW_-96_96(-2000_2000) |  | B2/S32_A1 | [8 empty] | 新塭SS.630_MW | 大寮新塭線 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 630 | MVAR | 大寮新塭線無效電力 | MVAR_-96_96(-2000_2000) |  | B2/S32_A1 | [8 empty] | 新塭SS.630_MVAR | 大寮新塭線 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | #3 MTR MVARH(-) |  |  |  |  | B2/S32_A1 | [15 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 640 | MW | 新塭永華線有效電力 | MW_-144_144(-2000_2000) |  | B2/S32_A1 | [8 empty] | 新塭SS.640_MW | 新塭永華線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 640 | MVAR | 新塭永華線無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S32_A1 | [8 empty] | 新塭SS.640_MVAR | 新塭永華線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 69KV LINE 1(630) MWH(-) |  |  |  |  | B2/S32_A1 | [15 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 大寮新塭線(630) PHA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_PHA | 大寮新塭線(630) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 大寮新塭線(630) GDA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_GDA | 大寮新塭線(630) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 大寮新塭線(630) 87A |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_87A | 大寮新塭線(630) 87RY | LINE161 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 1-32-01 |  |  | LINE 1(630) CFA (SP) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_CFA | 630 CFA | OTHER |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 新塭永華線(640) PHA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_PHA | 新塭永華線(640) 相間RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 新塭永華線(640) GDA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_GDA | 新塭永華線(640) 接地RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | 新塭永華線(640) 87A |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_87A | 新塭永華線(640) 87RY | LINE161 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 1-32-03 |  |  | LINE 2(640) CFA (SP) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_CFA | 640 CFA | OTHER |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0259 |  | 0010 | 1-32-00 |  | 1-09 | LINE 1(630) 87S U/L |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_87UL | 大寮新塭線(630) 87RY U/L | LINE161 |  |  |  |  | CDC | 28 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0261 |  | 0011 | 1-32-02 |  | 1-0A | LINE 2(640) 87S U/L |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_87UL | 新塭永華線(640) 87RY U/L | LINE161 |  |  |  |  | CDC | 29 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S21S32/T2 |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 大寮新塭線(630) CB ON/OFF (52AS) |  |  |  | aaba | B2/S32_A1 | [8 empty] | 新塭SS.630_CB | 630(大寮新塭線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S32S47/T1 |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 新塭永華線(640) CB ON/OFF (52AS) |  |  |  | aaea | B2/S32_A1 | [8 empty] | 新塭SS.640_CB | 640(新塭永華線) CB | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | D1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0355 | 356 | 0017 | 1-38-00 | 1-38-01 | 1-10 | LINE-1 1AS (631) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.631_DS | 631(大寮新塭線) DS | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | D2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0357 | 358 | 0018 | 1-38-02 | 1-38-03 | 1-11 | LINE-1 2AS (632) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.632_DS | 632(大寮新塭線) DS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | D1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0363 | 364 | 0021 | 1-38-08 | 1-38-09 | 1-14 | LINE-2 1AS (641) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.641_DS | 641(新塭永華線) DS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | D2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0365 | 366 | 0022 | 1-38-10 | 1-38-11 | 1-15 | LINE-2 2AS (642) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.642_DS | 642(新塭永華線) DS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | D3 | 633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0359 | 360 | 0019 | 1-38-04 | 1-38-05 | 1-12 | LINE-1 3AS (633) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.633_DS | 633(大寮新塭線) DS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | E3 | 633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0361 | 362 | 0020 | 1-38-06 | 1-38-07 | 1-13 | LINE-1 3EAS (633E) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.633E_ES | 633E(大寮新塭線) ES | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 38 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 39 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | D3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0367 | 368 | 0023 | 1-38-12 | 1-38-13 | 1-16 | LINE-2 3AS (643) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.643_DS | 643(新塭永華線) DS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | E3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0369 | 370 | 0024 | 1-38-14 | 1-38-15 | 1-17 | LINE-2 3EAS (643E) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.643E_ES | 643E(新塭永華線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-00 |  |  | F1 CB PHA (JZ21) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_PHA | 11KV塭一線(JZ21) 相間RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-01 |  |  | F1 CB GDA (JZ21) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_GDA | 11KV塭一線(JZ21) 接地RY | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0281 |  | 0063 | 1-33-06 |  | 1-3E | F1 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_79UL | 11KV塭一線(JZ21) 79RY U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0323 |  | 0113 | 1-36-00 |  | 1-70 | F1 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_ADJ | 11KV塭一線(JZ21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-03 |  |  | F2 CB PHA (JZ22) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_PHA | 11KV塭二線(JZ22) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-04 |  |  | F2 CB GDA (JZ22) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_GDA | 11KV塭二線(JZ22) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0282 |  | 0064 | 1-33-07 |  | 1-3F | F2 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_79UL | 11KV塭二線(JZ22) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0324 |  | 0114 | 1-36-01 |  | 1-71 | F2 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_ADJ | 11KV塭二線(JZ22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0C-06 |  |  | F3 CB PHA (JZ23) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_PHA | 11KV塭三線(JZ23) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | F3 CB GDA (JZ23) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_GDA | 11KV塭三線(JZ23) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0283 |  | 0065 | 1-33-08 |  | 1-40 | F3 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_79UL | 11KV塭三線(JZ23) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0325 |  | 0115 | 1-36-02 |  | 1-72 | F3 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_ADJ | 11KV塭三線(JZ23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | F4 CB PHA (JZ24) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_PHA | 11KV塭四線(JZ24) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | F4 CB GDA (JZ24) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_GDA | 11KV塭四線(JZ24) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0284 |  | 0066 | 1-33-09 |  | 1-41 | F4 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_79UL | 11KV塭四線(JZ24) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0326 |  | 0116 | 1-36-03 |  | 1-73 | F4 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_ADJ | 11KV塭四線(JZ24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | F5 CB PHA (JZ25) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_PHA | 11KV塭五線(JZ25) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | F5 CB GDA (JZ25) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_GDA | 11KV塭五線(JZ25) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0285 |  | 0067 | 1-33-10 |  | 1-42 | F5 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_79UL | 11KV塭五線(JZ25) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0327 |  | 0117 | 1-36-04 |  | 1-74 | F5 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_ADJ | 11KV塭五線(JZ25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-04 |  |  | F14 CB 52AS (JZ52) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_CB | JZ52(23KV塭52線) CB | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-11-05 |  |  | F14 CB PHA (JZ52) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_PHA | 23KV塭52線(JZ52) 相間RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | B2,B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0101 | 1-35-06 |  | 1-64 | #3 MTR 51ZS |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_51ZS | #3MTR 51ZS | OTHER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | ADJ | ADJ_LCO | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0333 |  | 0123 | 1-36-10 |  | 1-7A | F13 LCO ADJ U/L (F13 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_ADJ | 23KV塭51線(JZ51) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-11-07 |  |  | F14 CB 81A (JZ52) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線81A | JZ52線81A | OTHER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-00 |  |  | F15 CB 52AS (JZ53) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_CB | JZ53(23KV塭53線) CB | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0102 | 1-35-07 |  | 1-65 | #3 MTR 81S |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_81S | #3MTR 81S | OTHER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | ADJ | ADJ_LCO | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0334 |  | 0124 | 1-36-11 |  | 1-7B | F14 LCO ADJ U/L (F14 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_ADJ | 23KV塭52線(JZ52) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | F15 CB GDA (JZ53) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_GDA | 23KV塭53線(JZ53) 接地RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-03 |  |  | F15 CB 81A (JZ53) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線81A | JZ53線81A | OTHER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | 81UL |  | DELETE | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0103 | 1-35-08 |  | 1-66 | #3MCB(A) 81S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#M3A_81S | #M3A 81S | OTHER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | ADJ | ADJ_LCO | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0335 |  | 0125 | 1-36-12 |  | 1-7C | F15 LCO ADJ U/L (F15 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_ADJ | 23KV塭53線(JZ53) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-12-05 |  |  | F16 CB PHA (JZ54) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_PHA | 23KV塭54線(JZ54) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-12-06 |  |  | F16 CB GDA (JZ54) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_GDA | 23KV塭54線(JZ54) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | 81UL |  | DELETE | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0316 |  | 0104 | 1-35-09 |  | 1-67 | #3MCB(A) 81S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#M3B_81S | #M3B 81S | OTHER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | ADJ | ADJ_LCO | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0336 |  | 0126 | 1-36-13 |  | 1-7D | F16 LCO ADJ U/L (F16 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_ADJ | 23KV塭54線(JZ54) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | F17 CB 52AS (JZ55) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_CB | JZ55(23KV塭55線) CB | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | F17 CB PHA (JZ55) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_PHA | 23KV塭55線(JZ55) 相間RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0105 | 1-35-10 |  | 1-68 | F13 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_79UL | 23KV塭51線(JZ51) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | ADJ | ADJ_LCO | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0337 |  | 0127 | 1-36-14 |  | 1-7E | F17 LCO ADJ U/L (F17 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_ADJ | 23KV塭55線(JZ55) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JZ21/T1 |  |  | 0098 |  | 0054 | 1-0B-07 |  | 1-35 | F1 CB 52AS (JZ21) |  |  |  | aabb | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_CB | JZ21(11KV塭一線) CB | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_DS | JZ21_DS (非取樣點) | FEEDER | [5 empty] | 85 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | ES | JZ21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ21_ES | JZ21_ES (非取樣點) | FEEDER | [5 empty] | 86 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JZ22/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | F2 CB 52AS (JZ22) |  |  |  | aacb | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_CB | JZ22(11KV塭二線) CB | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_DS | JZ22_DS (非取樣點) | FEEDER | [5 empty] | 88 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | ES | JZ22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ22_ES | JZ22_ES (非取樣點) | FEEDER | [5 empty] | 89 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JZ23/T1 |  |  | 0104 |  | 0056 | 1-0C-05 |  | 1-37 | F3 CB 52AS (JZ23) |  |  |  | aaeb | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_CB | JZ23(11KV塭三線) CB | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_DS | JZ23_DS (非取樣點) | FEEDER | [5 empty] | 91 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | ES | JZ23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ23_ES | JZ23_ES (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JZ24/T1 |  |  | 0107 |  | 0057 | 1-0D-00 |  | 1-38 | F4 CB 52AS (JZ24) |  |  |  | aafb | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_CB | JZ24(11KV塭四線) CB | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_DS | JZ24_DS (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | ES | JZ24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ24_ES | JZ24_ES (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JZ25/T1 |  |  | 0110 |  | 0058 | 1-0D-03 |  | 1-39 | F5 CB 52AS (JZ25) |  |  |  | aagb | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_CB | JZ25(11KV塭五線) CB | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_DS | JZ25_DS (非取樣點) | FEEDER | [5 empty] | 97 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | ES | JZ25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ25_ES | JZ25_ES (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JZ26/T1 |  |  | 0142 |  |  | 1-11-03 |  |  | F13 CB 81A (JZ51) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線81A | JZ51線81A | OTHER |  |  |  |  | CDC | 99 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_DS | JZ26_DS (非取樣點) | FEEDER | [5 empty] | 100 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | ES | JZ26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_ES | JZ26_ES (非取樣點) | FEEDER | [5 empty] | 101 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JZ27/T1 |  |  | 0145 |  | 0094 | 1-11-06 |  | 1-5D | F14 CB GDA (JZ52) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_GDA | 23KV塭52線(JZ52) 接地RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_DS | JZ27_DS (非取樣點) | FEEDER | [5 empty] | 103 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | ES | JZ27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_ES | JZ27_ES (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JZ28/T1 |  |  | 0148 |  | 0095 | 1-12-01 |  | 1-5E | F15 CB PHA (JZ53) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_PHA | 23KV塭53線(JZ53) 相間RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_DS | JZ28_DS (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | ES | JZ28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_ES | JZ28_ES (非取樣點) | FEEDER | [5 empty] | 107 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JZ29/T1 |  |  | 0151 |  | 0096 | 1-12-04 |  | 1-5F | F16 CB 52AS (JZ54) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_CB | JZ54(23KV塭54線) CB | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_DS | JZ29_DS (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | ES | JZ29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_ES | JZ29_ES (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | BayFdrA | B/2BUS | L/JZ30/T1 |  |  | 0154 |  | 0097 | 1-12-07 |  | 1-60 | F16 CB 81A (JZ54) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線81A | JZ54線81A | OTHER |  |  |  |  | CDC | 111 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_DS | JZ30_DS (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | ES | JZ30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_ES | JZ30_ES (非取樣點) | FEEDER | [5 empty] | 113 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 600 TIE | A | TIE 600 R 相電流 | A_-1200_1200(-2000_2000) |  | B2/S32_A1 | [8 empty] | 新塭SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 114 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | ＃1 TIE | A1 | 一號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 115 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | ＃1 TIE | A2 | 一號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 116 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | ＃1 TIE | A3 | 一號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 117 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0037 |  | 0008 | 1-04-02 |  | 1-07 | TIE (600) CB ON/OFF(52AS) |  |  |  | aafz | B2/S32_A1 | [8 empty] | 新塭SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 118 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-03 |  |  | TIE (600) CB PHA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600_51A | 69KV TIE(600) 51RY | TIE |  |  |  |  | CDC | 119 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-04 |  |  | TIE (600) CB GDA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600_51NA | 69KV TIE(600) 51N RY | TIE |  |  |  |  | CDC | 120 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2BUS |  |  | 0116 |  | 0059 | 1-0E-01 |  | 1-3A | #1 TIE CB 52AS |  |  |  | zzzz | B2/S32_D1 | [8 empty] | 新塭SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 121 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | #1 TIE CB PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 122 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | #1 TIE CB GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 123 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0403 | 404 | 0043 | 1-3B-00 | 1-3B-01 | 1-2A | 600 TIE 1AS (611) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 124 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0405 | 406 | 0044 | 1-3B-02 | 1-3B-03 | 1-2B | 600 TIE 2AS (612) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 125 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.601E | 601E (非取樣點) | TIE | [5 empty] | 126 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_A1 | [8 empty] | 新塭SS.602E | 602E (非取樣點) | TIE | [5 empty] | 127 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 128 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | ＃1 MTR | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 129 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | ＃1 MTR | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 130 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | ＃1 MCB | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 131 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | ＃1 MCB | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 132 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1 MCB | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 133 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | OilTemp |  | B2,B3,Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | ＃3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 134 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | TapPosMv |  | B2,B3,Element | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | ＃3 MTR | TAP | 三號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 135 | AI_DTR(1) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | MW |  | DELETE | MvMoment | MW |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | ＃3 MTR | MW | 三號主變二次側有效電力 | MW_-72_72(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 136 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | MVAR |  | DELETE | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | ＃3 MTR | MVAR | 三號主變二次側無效電力 | MVAR_-72_72(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 137 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | ＃3 MTR | A1 | 三號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 138 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | ＃1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 139 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | ＃1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 140 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0020 |  | 0060 | 1-94 |  | 1-3B | ＃1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 141 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | JZ56 KWH(+) |  |  |  |  | B1/S32_D1 | [15 empty] | CDC | 142 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1 MTR MWH(+) |  |  |  |  | B1/S32_D1 | [15 empty] | CDC | 143 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | ＃2MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 144 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0056 |  |  | 1-B8 |  |  | ＃2 MTR | KV | 二號主變二次側BUS11KV | kV_-9_9(-2000_2000) | aba | B2/S32_D1 | [8 empty] | 新塭SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 145 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0058 |  | 0079 | 1-BA |  | 1-4E | ＃2MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 146 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #2 MTR MVARH(-) |  |  |  |  | B1/S32_D1 | [15 empty] | CDC | 147 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3 MTR MWH(+) |  |  |  |  | B1/S32_D1 | [15 empty] | CDC | 148 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0004 |  | 0051 | 1-00-01 |  | 1-32 | 750CB ON/OFF(52AS) |  |  |  | aacb | B3/S32_D1 | [8 empty] | 新塭SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 149 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S32_D1 | [8 empty] | 新塭SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 150 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S32_D1 | [8 empty] | 新塭SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 151 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760CB ON/OFF(52AS) |  |  |  | aadb | B3/S32_D1 | [8 empty] | 新塭SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 152 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S32_D1 | [8 empty] | 新塭SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 153 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S32_D1 | [8 empty] | 新塭SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 154 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0010 |  | 0052 | 1-00-07 |  | 1-33 | #1 MCB ON/OFF(52AS) |  |  |  | aada | B2/S32_D1 | [8 empty] | 新塭SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 155 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/2BUS | T/2MTR |  |  | 0031 |  | 0090 | 1-03-04 |  | 1-59 | #3 MCB(A) ON/OFF(52AS) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.M3A_CB | M3A(#3MTR) CB | DTR |  |  |  |  | CDC | 156 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-02 |  |  | 750CB PHA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 157 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750CB GDA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 158 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | #1 MTR 51ZA |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 159 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | DI-SP | [6 empty] | 8 |  |  | 1-00-05 |  | #1 MTR 87A |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_87A | #1MTR 87RY | DTR | DTR | CDC_Mon1_NULL,DNP_Mon1_NULL |  |  |  | 160 | 160 | DI_DTR(3) |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 1-33-03 |  |  | #1 MTR 87 LS U/L |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 161 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  | 0068 | 1-0E-04 |  | 1-43 | #1 81A |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 162 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-03 |  |  | 760CB PHA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 163 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-04 |  |  | 760CB GDA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 164 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | #2 MTR 51ZA |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 165 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | #2 MTR 87A |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 166 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-34-03 |  |  | #2 MTR 87 LS U/L |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 167 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-13-05 |  |  | F18 CB PHA (JZ56) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_PHA | 23KV塭56線(JZ56) 相間RY | FEEDER |  |  |  |  | CDC | 168 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | #1 MCB PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 169 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0275 |  |  | 1-33-00 |  |  | #1 MTR 重故障(1TRA) |  |  |  | a | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 170 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-33-01 |  |  | #1 MTR 輕故障(1TRF) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 171 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-33-04 |  |  | #1 MTR OLTC S/L(中心/現場) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 172 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0280 |  | 0061 | 1-33-05 |  | 1-3C | #1 MTR OLTC A/M(手動/自動) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 173 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | 51A | 51A1 | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | #3 MCB(A) PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.M3A_51A | #3MTR二次側(M3A) 51RY | DTR |  |  |  |  | CDC | 174 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0291 |  |  | 1-34-00 |  |  | #2 MTR 重故障(2TRA) |  |  |  | a | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 175 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0292 |  |  | 1-34-01 |  |  | #2 MTR 輕故障(2TRF) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 176 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-34-04 |  |  | #2 MTR OLTC S/L(中心/現場) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 177 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0080 | 1-34-05 |  | 1-4F | #2 MTR OLTC A/M(手動/自動) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 178 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0339 | 340 | 0045 | 1-37-00 | 1-37-01 | 1-2C | #1MTR(751) 1AS |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 179 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0341 | 342 | 0046 | 1-37-02 | 1-37-03 | 1-2D | #1MTR(752) 2AS |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 180 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0343 | 344 | 0047 | 1-37-04 | 1-37-05 | 1-2E | #2MTR(761) 1AS |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 181 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0345 | 346 | 0048 | 1-37-06 | 1-37-07 | 1-2F | #2MTR(762) 2AS |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 182 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | 1M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 183 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 184 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | #1 MTR 96PA |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 1-33-02 |  |  | #1 MTR OLTC遲滯警報(148T) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 186 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0290 |  |  | 1-33-15 |  |  | #1 MTR AC電源失效 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 187 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 188 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 189 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | #2 MTR 96PA |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 190 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-34-02 |  |  | #2 MTR OLTC遲滯警報(248T) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 191 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 1-34-12 |  |  | #2 MTR AC電源失效 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 192 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0113 |  | 0053 | 1-0D-06 |  | 1-34 | #1 11KV SC CB 52AS |  |  |  | aaab | B2/S32_D1 | [8 empty] | 新塭SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 193 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0286 |  | 0062 | 1-33-11 |  | 1-3D | #1 SC Q-CTL A/M(手動/自動) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 194 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 195 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP |  | BayFdrB | B/2BUS | C/2SC |  |  | 0157 |  |  | 1-13-02 |  |  | F17 CB GDA (JZ55) |  |  |  | not found | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_GDA | 23KV塭55線(JZ55) 接地RY | FEEDER |  |  |  |  | CDC | 196 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0318 |  | 0100 | 1-35-11 |  | 1-63 | F14 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_79UL | 23KV塭52線(JZ52) 79RY U/L | FEEDER |  |  |  |  | CDC | 197 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 198 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | #1 11KV SC CB SCA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 199 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | #1 11KV SC CB UVA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 200 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | F17 CB 81A (JZ55) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線81A | JZ55線81A | OTHER |  |  |  |  | CDC | 201 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | F18 CB 52AS (JZ56) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_CB | JZ56(23KV塭56線) CB | FEEDER |  |  |  |  | CDC | 202 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 203 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 204 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 205 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 206 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 207 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS(For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 208 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 209 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS(For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 210 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 211 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS(For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 212 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0227 |  | 0001 | 1-30-00 |  | 1-00 | TEST_CB |  |  |  |  | ELEM/ALL | [8 empty] | 新塭SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 213 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0228 |  |  | 1-30-01 |  |  | LOCAL/REMOTE (STATUS) |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 214 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-30-02 |  |  | 直流充電機故障(變電設備用) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 215 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0230 |  |  | 1-30-03 |  |  | 通訊充電機故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 216 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0231 |  |  | 1-30-04 |  |  | DC接地故障(DCE) |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 217 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0233 |  | 0110 | 1-30-06 |  | 1-6D | 所內照明 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 218 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0234 |  | 0111 | 1-30-07 |  | 1-6E | 路燈照明 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 219 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-30-08 |  |  | 所內用電警報(STUV) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 220 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0236 |  |  | 1-30-09 |  |  | 油壓電力電纜警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 221 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-31-08 |  |  | 所內電源警報(ACBA) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 222 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0241 |  |  | 1-30-14 |  |  | 配電盤DC-NFB跳脫警報 |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 223 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0242 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 224 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0248 |  |  | 1-31-05 |  |  | 保全總機(DOOR) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.無人化門禁(1) | 保全(DOOR) | OTHER |  |  |  |  | CDC | 225 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Door2 | 開關場水位二段警報 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0249 |  |  | 1-31-06 |  |  | 開關場水位警報第二段 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.開關場水位二段 | 開關場水位二段警報 | OTHER |  |  |  |  | CDC | 226 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0250 |  |  | 1-31-07 |  |  | 無人化門禁警報(3) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 227 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S32 | 新塭SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0252 |  |  | 1-31-09 |  |  | 69KV CB 輕故障警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 228 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 1-31-10 |  |  | 69KV CB 重故障警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 229 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0254 |  |  | 1-31-11 |  |  | 11KV CB 輕故障警報(MCSG) |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 230 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-31-12 |  |  | 11KV CB 重故障警報(MCSG) |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 231 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-31-15 |  |  | 69KV ABS NFB跳脫警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 232 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-35-13 |  |  | F16 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_79UL | 23KV塭54線(JZ54) 79RY U/L | FEEDER |  |  |  |  | CDC | 233 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 1-35-14 |  |  | F17 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_79UL | 23KV塭55線(JZ55) 79RY U/L | FEEDER |  |  |  |  | CDC | 234 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-35-15 |  |  | F18 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_79UL | 23KV塭56線(JZ56) 79RY U/L | FEEDER |  |  |  |  | CDC | 235 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | #1 MCB GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER |  |  |  |  | CDC | 236 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | 51NA | #M3A 51NA | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-03-07 |  |  | #3 MCB(A) GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#M3A_51NA | #M3A 51NA | OTHER |  |  |  |  | CDC | 237 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0232 |  |  | 1-30-05 |  |  | 門禁 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 238 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0238 |  |  | 1-30-11 |  |  | 所內安全監控 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 239 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | PSF | 所內其他輕故障 | Element | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0239 |  |  | 1-30-12 |  |  | 所內其他輕故障警報 |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.所內其他輕故障 | 所內其他輕故障 | OTHER |  |  |  |  | CDC | 240 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | PSA | 所內其他重故障 | Element | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0240 |  |  | 1-30-13 |  |  | 所內其他重故障警報 |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.所內其他重故障 | 所內其他重故障 | OTHER |  |  |  |  | CDC | 241 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | CO2 |  | Element | Status | CO2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0243 |  |  | 1-31-00 |  |  | CO2系統故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.CO2故障 | CO2故障 | OTHER |  |  |  |  | CDC | 242 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Fire2 | CO2火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0244 |  |  | 1-31-01 |  |  | CO2系統火警 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.CO2火警 | CO2火警 | OTHER |  |  |  |  | CDC | 243 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報(2) | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-34-14 |  |  | 水位警報 2 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.水位警報(2) | 水位警報(2) | OTHER |  |  |  |  | CDC | 244 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | TRA |  | B2,B3,Element | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-34-15 |  |  | #3 MTR 重故障(3TRA) |  |  |  | not found | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 245 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  | Element | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0271 |  |  | 1-32-12 |  |  | ACB 1S (#1 所內電源) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.所內電源ACB1 | 所內電源ACB1S | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  | Element | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-32-13 |  |  | ACB 2S (#2 所內電源) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.所內電源ACB2 | 所內電源ACB2S | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Fire1 | 主變火警 | Element | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0245 |  |  | 1-31-02 |  |  | 主變火警 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.主變火警 | 主變火警 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 細水霧故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0246 |  |  | 1-31-03 |  |  | 細水霧故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.細水霧故障 | 細水霧故障 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Burglar3 | 細水霧噴灑 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0247 |  |  | 1-31-04 |  |  | 細水霧噴灑 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.細水霧噴灑 | 細水霧噴灑 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 維護運轉警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0354 |  |  | 1-37-15 |  |  | 維護運轉警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-13-07 |  |  | F18 CB 81A (JZ56) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線81A | JZ56線81A | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-33-12 |  |  | SC 60A |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.11KV_SC_60A | 60RY | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | #1 MTR 196B1 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | #1 MTR 196B2 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | #1 MTR 196D |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | #1 MTR 196P |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | #1 MTR 163Q |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | #2 MTR 296B1 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | #2 MTR 296B2 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | #2 MTR 296D |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | #2 MTR 296P |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | #2 MTR 263Q |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | TIE (600) CB 67(1A) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600PHA(1) | 600(TIE) 67A(B1) | TIE |  |  |  |  | CDC | 264 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | TIE (600) CB 67N(1A) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE |  |  |  |  | CDC | 265 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-02 |  |  | TIE (600) CB 67(2A) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600PHA(2) | 600(TIE) 67A(B2) | TIE |  |  |  |  | CDC | 266 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-03 |  |  | TIE (600) CB 67N(2A) |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE |  |  |  |  | CDC | 267 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 塭一線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線KVAR | 11KV塭一線 KVAR | FEEDER |  |  |  |  | CDC | 268 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 塭一線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線A1 | 11KV塭一線 R相AMP | FEEDER |  |  |  |  | CDC | 269 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 塭一線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線A2 | 11KV塭一線 S相AMP | FEEDER |  |  |  |  | CDC | 270 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 塭一線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線A3 | 11KV塭一線 T相AMP | FEEDER |  |  |  |  | CDC | 271 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 塭一線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線A0 | 11KV塭一線 N相AMP | FEEDER |  |  |  |  | CDC | 272 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 塭51線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線A3 | 23KVJZ51線 T相AMP | FEEDER |  |  |  |  | CDC | 273 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 塭51線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線A0 | 23KVJZ51線 N相AMP | FEEDER |  |  |  |  | CDC | 274 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 塭52線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線KVAR | 23KVJZ52線 KVAR | FEEDER |  |  |  |  | CDC | 275 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 塭52線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線A1 | 23KVJZ52線 R相AMP | FEEDER |  |  |  |  | CDC | 276 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 塭52線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線A2 | 23KVJZ52線 S相AMP | FEEDER |  |  |  |  | CDC | 277 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 塭53線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線A3 | 23KVJZ53線 T相AMP | FEEDER |  |  |  |  | CDC | 278 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 塭53線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線A0 | 23KVJZ53線 N相AMP | FEEDER |  |  |  |  | CDC | 279 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 塭54線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線KVAR | 23KVJZ54線 KVAR | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 塭54線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線A1 | 23KVJZ54線 R相AMP | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 塭54線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線A2 | 23KVJZ54線 S相AMP | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 塭二線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線KVAR | 11KV塭二線 KVAR | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 塭二線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線A1 | 11KV塭二線 R相AMP | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 塭二線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線A2 | 11KV塭二線 S相AMP | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 塭二線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線A3 | 11KV塭二線 T相AMP | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 塭二線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線A0 | 11KV塭二線 N相AMP | FEEDER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 塭52線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線A3 | 23KVJZ52線 T相AMP | FEEDER |  |  |  |  | CDC | 288 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 塭52線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線A0 | 23KVJZ52線 N相AMP | FEEDER |  |  |  |  | CDC | 289 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 塭53線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線KVAR | 23KVJZ53線 KVAR | FEEDER |  |  |  |  | CDC | 290 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 塭53線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線A1 | 23KVJZ53線 R相AMP | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 塭53線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線A2 | 23KVJZ53線 S相AMP | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 塭54線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線A3 | 23KVJZ54線 T相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 塭54線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線A0 | 23KVJZ54線 N相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 塭55線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線KVAR | 23KVJZ55線 KVAR | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 塭55線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線A1 | 23KVJZ55線 R相AMP | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 塭55線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線A2 | 23KVJZ55線 S相AMP | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 塭三線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線KVAR | 11KV塭三線 KVAR | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 塭三線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線A1 | 11KV塭三線 R相AMP | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 塭三線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線A2 | 11KV塭三線 S相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 塭三線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線A3 | 11KV塭三線 T相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 塭三線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線A0 | 11KV塭三線 N相AMP | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 塭五線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線KVAR | 11KV塭五線 KVAR | FEEDER |  |  |  |  | CDC | 303 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 塭五線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線A1 | 11KV塭五線 R相AMP | FEEDER |  |  |  |  | CDC | 304 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 塭五線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線A2 | 11KV塭五線 S相AMP | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 塭五線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線A3 | 11KV塭五線 T相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 塭五線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線A0 | 11KV塭五線 N相AMP | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | ＃3 MTR | A2 | 三號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 308 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | ＃3 MTR | A3 | 三號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 309 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 塭51線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線KVAR | 23KVJZ51線 KVAR | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 塭51線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線A1 | 23KVJZ51線 R相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 塭51線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線A2 | 23KVJZ51線 S相AMP | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 塭四線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線KVAR | 11KV塭四線 KVAR | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 塭四線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線A1 | 11KV塭四線 R相AMP | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 塭四線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線A2 | 11KV塭四線 S相AMP | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 塭四線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線A3 | 11KV塭四線 T相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 塭四線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線A0 | 11KV塭四線 N相AMP | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 塭55線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線A3 | 23KVJZ55線 T相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 路燈電源監視 | INSERT | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0289 |  |  | 1-33-14 |  |  | 路燈電源監視 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 319 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | ADJ |  | DELETE | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0338 |  |  | 1-36-15 |  |  | F18 LCO ADJ U/L (F18 51NS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_ADJ | 23KV塭56線(JZ56) LCO分流器 U/L | FEEDER | [5 empty] | 320 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Water3 | 開關場水位警報 | INSERT | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0288 |  |  | 1-33-13 |  |  | 開關場水位警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 321 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 1-3F-15 |  |  | 11KV IED重警報 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 322 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0419 |  |  | 1-3E-00 |  |  | JZ21 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭一線79LOA | 塭一線79LOA | OTHER | [5 empty] | 323 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0425 |  |  | 1-3E-06 |  |  | JZ27 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線79LOA | 塭七線79LOA | OTHER | [5 empty] | 324 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0427 |  |  | 1-3E-08 |  |  | JZ29 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線79LOA | 塭九線79LOA | OTHER | [5 empty] | 325 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0420 |  |  | 1-3E-01 |  |  | JZ22 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭二線79LOA | 塭二線79LOA | OTHER | [5 empty] | 326 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0426 |  |  | 1-3E-07 |  |  | JZ28 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線79LOA | 塭八線79LOA | OTHER | [5 empty] | 327 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0428 |  |  | 1-3E-09 |  |  | JZ30 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線79LOA | 塭十線79LOA | OTHER | [5 empty] | 328 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0421 |  |  | 1-3E-02 |  |  | JZ23 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭三線79LOA | 塭三線79LOA | OTHER | [5 empty] | 329 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0423 |  |  | 1-3E-04 |  |  | JZ25 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭五線79LOA | 塭五線79LOA | OTHER | [5 empty] | 330 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0424 |  |  | 1-3E-05 |  |  | JZ26 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線79LOA | 塭六線79LOA | OTHER | [5 empty] | 331 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0422 |  |  | 1-3E-03 |  |  | JZ24 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.塭四線79LOA | 塭四線79LOA | OTHER | [5 empty] | 332 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0418 |  |  | 1-3B-15 |  |  | 600TIE RYFA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.600_RYFA | 600 RYFA | OTHER | [5 empty] | 333 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0417 |  |  | 1-3B-14 |  |  | 大寮新塭線(630) RYFA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.630_RYFA | 630 RYFA | OTHER | [5 empty] | 334 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0416 |  |  | 1-3B-13 |  |  | 新塭永華線(640) RYFA |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.640_RYFA | 640 RYFA | OTHER | [5 empty] | 335 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 1-34-06 |  |  | F6 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_79UL | 11KV塭六線(JZ26) 79RY U/L | FEEDER | [5 empty] | 336 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-34-07 |  |  | F7 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_79UL | 11KV塭七線(JZ27) 79RY U/L | FEEDER | [5 empty] | 337 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-34-08 |  |  | F8 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_79UL | 11KV塭八線(JZ28) 79RY U/L | FEEDER | [5 empty] | 338 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-34-09 |  |  | F9 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_79UL | 11KV塭九線(JZ29) 79RY U/L | FEEDER | [5 empty] | 339 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0449 |  |  | 1-3F-14 |  |  | PMA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.PMA | POWER METER警報 | OTHER | [5 empty] | 340 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JZ21 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 341 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JZ22 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 342 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JZ23 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 343 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JZ24 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 344 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JZ25 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 345 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | JZ51 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 346 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | JZ52 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 347 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | JZ53 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 348 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | JZ54 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 349 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | JZ55 KWH(+) |  |  |  |  | B2/S32_D1 | [15 empty] | CDC | 350 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 塭七線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線KVAR | 11KV塭七線 KVAR | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 塭七線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線A1 | 11KV塭七線 R相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 塭七線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線A2 | 11KV塭七線 S相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 塭七線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線A3 | 11KV塭七線 T相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 塭七線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭七線A0 | 11KV塭七線 N相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 塭九線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線KVAR | 11KV塭九線 KVAR | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 塭九線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線A1 | 11KV塭九線 R相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 塭九線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線A2 | 11KV塭九線 S相AMP | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 塭九線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線A3 | 11KV塭九線 T相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 塭九線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭九線A0 | 11KV塭九線 N相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 塭八線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線KVAR | 11KV塭八線 KVAR | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 塭八線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線A1 | 11KV塭八線 R相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 塭八線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線A2 | 11KV塭八線 S相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 塭八線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線A3 | 11KV塭八線 T相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 塭八線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭八線A0 | 11KV塭八線 N相AMP | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 塭十線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線KVAR | 11KV塭十線 KVAR | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 塭十線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線A1 | 11KV塭十線 R相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 塭十線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線A2 | 11KV塭十線 S相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 塭十線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線A3 | 11KV塭十線 T相AMP | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 塭十線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭十線A0 | 11KV塭十線 N相AMP | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 塭六線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線KVAR | 11KV塭六線 KVAR | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 塭六線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線A1 | 11KV塭六線 R相AMP | FEEDER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 塭六線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線A2 | 11KV塭六線 S相AMP | FEEDER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 塭六線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線A3 | 11KV塭六線 T相AMP | FEEDER | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 塭六線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.塭六線A0 | 11KV塭六線 N相AMP | FEEDER | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | ＃2 MTR | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#2MTR_MW | #2MTR二次側 MW | DTR | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | ＃2 MTR | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | ＃2 MTR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | ＃2 MTR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2 MTR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0059 |  | 0078 | 1-BB |  | 1-4D | ＃2MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | DCV |  |  | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 充電機 | DC-V | 配電盤"MAIN"NFB電壓 | DCVolt_-150_150(-2000_2000) |  | B3/S32_D1 | [8 empty] | 新塭SS.直流電源電壓 | 直流電源電壓 | OTHER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S32 | 新塭SS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  | DELETE | MvMoment | kV |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | ＃3 MCB(A) | KV | 三號主變二次側BUS(MA) 11KV (PT-3A) | kV_-18_18(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S32 | 新塭SS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  | DELETE | MvMoment | kV |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | ＃3 MCB(B) | KV | 三號主變二次側BUS(MB) 11KV (PT-3B) | kV_-18_18(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭56線(JZ56) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 塭55線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線A0 | 23KVJZ55線 N相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 塭56線 | VAR | KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線KVAR | 23KVJZ56線 KVAR | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 塭56線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線A1 | 23KVJZ56線 R相AMP | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 塭56線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線A2 | 23KVJZ56線 S相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 塭56線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線A3 | 23KVJZ56線 T相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | I_N |  | DELETE | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 塭56線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線A0 | 23KVJZ56線 N相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | ＃3 TIE | A1 | 三號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV_TIE3_A1 | 23KV TIE3 R相AMP | TIE | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | ＃3 TIE | A2 | 三號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV_TIE3_A2 | 23KV TIE3 S相AMP | TIE | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | ＃3 TIE | A3 | 三號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV_TIE3_A3 | 23KV TIE3 T相AMP | TIE | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | ＃3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_COIL | #3MTR 線溫 | DTR | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0E-06 |  |  | F6 CB PHA (JZ26) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_PHA | 11KV塭六線(JZ26) 相間RY | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0122 |  |  | 1-0E-07 |  |  | F6 CB GDA (JZ26) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_GDA | 11KV塭六線(JZ26) 接地RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0328 |  | 0118 | 1-36-05 |  | 1-75 | F6 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_ADJ | 11KV塭六線(JZ26) LCO分流器 U/L | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JZ26/T1 |  |  | 0120 |  | 0073 | 1-0E-05 |  | 1-48 | F6 CB 52AS (JZ26) |  |  |  | abab | B2/S32_D1 | [8 empty] | 新塭SS.JZ26_CB | JZ26(11KV塭六線) CB | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-01 |  |  | F7 CB PHA (JZ27) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_PHA | 11KV塭七線(JZ27) 相間RY | FEEDER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-02 |  |  | F7 CB GDA (JZ27) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_GDA | 11KV塭七線(JZ27) 接地RY | FEEDER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0329 |  | 0119 | 1-36-06 |  | 1-76 | F7 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_ADJ | 11KV塭七線(JZ27) LCO分流器 U/L | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JZ27/T1 |  |  | 0123 |  | 0074 | 1-0F-00 |  | 1-49 | F7 CB 52AS (JZ27) |  |  |  | abcb | B2/S32_D1 | [8 empty] | 新塭SS.JZ27_CB | JZ27(11KV塭七線) CB | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-04 |  |  | F8 CB PHA (JZ28) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_PHA | 11KV塭八線(JZ28) 相間RY | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | F8 CB GDA (JZ28) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_GDA | 11KV塭八線(JZ28) 接地RY | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0330 |  | 0120 | 1-36-07 |  | 1-77 | F8 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_ADJ | 11KV塭八線(JZ28) LCO分流器 U/L | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JZ28/T1 |  |  | 0126 |  | 0075 | 1-0F-03 |  | 1-4A | F8 CB 52AS (JZ28) |  |  |  | abdb | B2/S32_D1 | [8 empty] | 新塭SS.JZ28_CB | JZ28(11KV塭八線) CB | FEEDER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | F9 CB PHA (JZ29) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_PHA | 11KV塭九線(JZ29) 相間RY | FEEDER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | F9 CB GDA (JZ29) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_GDA | 11KV塭九線(JZ29) 接地RY | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0331 |  | 0121 | 1-36-08 |  | 1-78 | F9 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_ADJ | 11KV塭九線(JZ29) LCO分流器 U/L | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JZ29/T1 |  |  | 0129 |  | 0076 | 1-0F-06 |  | 1-4B | F9 CB 52AS (JZ29) |  |  |  | abeb | B2/S32_D1 | [8 empty] | 新塭SS.JZ29_CB | JZ29(11KV塭九線) CB | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | F10 CB PHA (JZ30) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_PHA | 11KV塭十線(JZ30) 相間RY | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | F10 CB GDA (JZ30) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_GDA | 11KV塭十線(JZ30) 接地RY | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0301 |  | 0085 | 1-34-10 |  | 1-54 | F10 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_79UL | 11KV塭十線(JZ30) 79RY U/L | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0332 |  | 0122 | 1-36-09 |  | 1-79 | F10 LCO ADJ U/L |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_ADJ | 11KV塭十線(JZ30) LCO分流器 U/L | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JZ30/T1 |  |  | 0132 |  | 0077 | 1-10-01 |  | 1-4C | F10 CB 52AS (JZ30) |  |  |  | abfb | B2/S32_D1 | [8 empty] | 新塭SS.JZ30_CB | JZ30(11KV塭十線) CB | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | T/2MTR |  |  | 0019 |  | 0071 | 1-02-00 |  | 1-46 | #2 MCB ON/OFF(52AS) |  |  |  | abba | B2/S32_D1 | [8 empty] | 新塭SS.2M_CB | 2M(#2MTR) CB | DTR | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | #2 MCB PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | C/2SC |  |  | 0135 |  | 0072 | 1-10-04 |  | 1-47 | #2 11KV SC CB 52AS |  |  |  | abgb | B2/S32_D1 | [8 empty] | 新塭SS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-34-11 |  |  | #2 SC Q-CTL A/M(手動/自動) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | #2 11KV SC CB SCA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | #2 11KV SC CB UVA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0237 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.火災警報(1) | [新塭]火警 | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | OLTE | [14 empty] | 0373 |  |  | 1-39-02 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | PCM | [14 empty] | 0374 |  |  | 1-39-03 |  |  | 博碼調變器故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | AC_Fault | 通訊設備AC故障 |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0371 |  |  | 1-39-00 |  |  | 通訊設備AC故障 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-03 |  |  | #2 MCB GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報(1) |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0304 |  |  | 1-34-13 |  |  | 水位警報 1 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.水位警報(1) | 水位警報(1) | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  | 0086 | 1-10-07 |  | 1-55 | #2 81A |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室溫度異常 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0375 |  |  | 1-39-04 |  |  | 通訊室溫度異常 |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | 27A |  |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-32-08 |  |  | 69KV #1BPT 27B1 |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | 27A |  |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-32-09 |  |  | 69KV #2BPT 27B2 |  |  |  |  | B2/S32_A1 | [8 empty] | 新塭SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | ComPoint |  |  | 87A | BUSRY BF |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 1-32-10 |  |  | 69KV BUS RY 87BF (RYFA) | [13 empty] | 新塭SS.BUSRY_BF | BUSRY BF | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | ComPoint |  |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-32-11 |  |  | 69KV BUS RY CTFA (CTFA) | [13 empty] | 新塭SS.BUSRY_CTFA | BUSRY CTFA | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 數據機重置 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0174 |  | 0087 | 1-15-03 |  | 1-56 | Modem Reset |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.數據機重置 | 數據機重置 | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-01 |  |  | F13 CB PHA (JZ51) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_PHA | 23KV塭51線(JZ51) 相間RY | FEEDER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-02 |  |  | F13 CB GDA (JZ51) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_GDA | 23KV塭51線(JZ51) 接地RY | FEEDER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0139 |  | 0093 | 1-11-00 |  | 1-5C | F13 CB 52AS (JZ51) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_CB | JZ51(23KV塭51線) CB | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | 79UL |  | DELETE | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0319 |  | 0106 | 1-35-12 |  | 1-69 | F15 79S |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_79UL | 23KV塭53線(JZ53) 79RY U/L | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-13-06 |  |  | F18 CB GDA (JZ56) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_GDA | 23KV塭56線(JZ56) 接地RY | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0169 |  | 0099 | 1-14-06 |  | 1-62 | #3TIE CB 52AS |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.TIE3_CB | 23KV TIE3 CB | TIE | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-14-07 |  |  | #3TIE CB PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.TIE3_51A | 23KV TIE3 51RY | TIE | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-00 |  |  | #3TIE CB GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.TIE3_51NA | 23KV TIE3 51N RY | TIE | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0023 |  | 0088 | 1-02-04 |  | 1-57 | 770CB ON/OFF(52AS) |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.770_CB | 770(#3MTR) CB | DTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-03-05 |  |  | #3 MCB(B) ON/OFF(52AS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.M3B_CB | M3B(#3MTR) CB | DTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | 770CB PHA |  |  |  |  | B3/S32_D1 | [8 empty] | 新塭SS.#3MTR_51A | #3MTR 51RY | DTR | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | M3 | #3MTR(M3) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-02-06 |  |  | 770CB GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_51NA | #3MTR 51N RY | DTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | M3 | #3MTR(M3) |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | #3 MTR 51ZA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | M3 | #3MTR(M3) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-00 |  |  | #3 MTR 87A |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_87A | #3MTR 87RY | DTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | M3 | #3MTR(M3) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  |  | 1-35-03 |  |  | #3 MTR 96 LS U/L (96PS) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS |  |  | M3 | #3MTR(M3) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-03 |  |  | #3 MTR 81A |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-00 |  |  | #3 MCB(B) PHA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.M3B_51A | #3MTR二次側(M3B) 51RY | DTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0307 |  |  | 1-35-00 |  |  | #3 MTR 輕故障(3TRF) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_TRF | #3MTR 輕故障 | DTR | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-35-01 |  |  | #3 MTR OLTC S/L(中心/現場) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  |  | 1-35-02 |  |  | #3 MTR OLTC A/M(手動/自動) |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S32 | 新塭SS | 22 | 22kV | 770 | #3MTR(770) |  | DS1 |  | DELETE | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0347 | 348 | 0049 | 1-37-08 | 1-37-09 | 1-30 | #3MTR(771) 1AS |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.771_DS | 771(#3MTR) DS | DTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 22 | 22kV | 770 | #3MTR(770) |  | DS2 |  | DELETE | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0349 | 350 | 0050 | 1-37-10 | 1-37-11 | 1-31 | #3MTR(772) 2AS |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.772_DS | 772(#3MTR) DS | DTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-02-07 |  |  | #3 MTR 96PA |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_96A | #3MTR 96P RY | DTR | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0163 |  | 0091 | 1-14-00 |  | 1-5A | #3A 23KV SC CB 52AS |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.410_CB | 410(23KV #3SC) CB | SC | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | SCA |  | DELETE | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0164 |  |  | 1-14-01 |  |  | #3A 23KV SC CB SCA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.410_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | UVA |  | DELETE | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0165 |  |  | 1-14-02 |  |  | #3A 23KV SC CB UVA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.410_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0166 |  | 0092 | 1-14-03 |  | 1-5B | #3B 23KV SC CB 52AS |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.420_CB | 420(23KV #4SC) CB | SC | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | SCA |  | DELETE | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0167 |  |  | 1-14-04 |  |  | #3B 23KV SC CB SCA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.420_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | UVA |  | DELETE | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-14-05 |  |  | #3B 23KV SC CB UVA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.420_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | CGIS | CGIS |  | CBA |  | DELETE | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0436 |  |  | 1-3F-01 |  |  | #3 23KVGIS CBA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV_CBA | 23KV CGIS重故障 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | CGIS | CGIS |  | CBF |  | DELETE | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0437 |  |  | 1-3F-02 |  |  | #3 23KVGIS CBF |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.23KV_CBF | 23KV CGIS輕故障 | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-19-06 |  |  | #3 MTR 363Q |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR63Q | ULTC電驛動作 | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-02 |  |  | #3 MTR 396B1 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR96B1 | 撲氣電驛警報 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-03 |  |  | #3 MTR 396B2 |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR96B2 | 撲氣電驛動作 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-04 |  |  | #3 MTR 396D |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR96D | 放壓電驛動作 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-19-05 |  |  | #3 MTR 396P |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR96P | 突壓電驛動作 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 86A |  |  | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | #3 MTR 86A |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_86A | #3MTR 86A | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 1-35-04 |  |  | #3 MTR 87T1S |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_87T1S | #3MTR 87T1S | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  |  | 1-35-05 |  |  | #3 MTR 87T2S |  |  |  |  | B1/S32_D1 | [8 empty] | 新塭SS.#3MTR_87T2S | #3MTR 87T2S | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-01 |  |  | #M3A 81A |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.#M3A_81A | #M3A 81A | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | #3 MCB(B) GDA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.#M3B_51NA | #M3B 51NA | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-02 |  |  | #M3B 81A |  |  |  |  | ELEM/S32_D1 | [8 empty] | 新塭SS.#M3B_81A | #M3B 81A | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S32 | 新塭SS | 22 | 22kV | CGIS | CGIS |  | IRFA |  | DELETE | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0435 |  |  | 1-3F-00 |  |  | #3 23KVGIS IRFA (IED AL) |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.23KVIED重警報 | 23KV CGIS IRFA | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0429 |  |  | 1-3E-10 |  |  | JZ51 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ51線79LOA | JZ51線79LOA | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0430 |  |  | 1-3E-11 |  |  | JZ52 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ52線79LOA | JZ52線79LOA | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0431 |  |  | 1-3E-12 |  |  | JZ53 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ53線79LOA | JZ53線79LOA | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0432 |  |  | 1-3E-13 |  |  | JZ54 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ54線79LOA | JZ54線79LOA | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0433 |  |  | 1-3E-14 |  |  | JZ55 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ55線79LOA | JZ55線79LOA | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | LOA |  | DELETE | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0434 |  |  | 1-3E-15 |  |  | JZ56 79LOA |  |  |  |  | B2/S32_D1 | [8 empty] | 新塭SS.JZ56線79LOA | JZ56線79LOA | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | DS | JZ51_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_DS | JZ51_DS (非取樣點) | FEEDER | [5 empty] | 484 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | ES | JZ51_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ51_ES | JZ51_ES (非取樣點) | FEEDER | [5 empty] | 485 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | DS | JZ52_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_DS | JZ52_DS (非取樣點) | FEEDER | [5 empty] | 486 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | ES | JZ52_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ52_ES | JZ52_ES (非取樣點) | FEEDER | [5 empty] | 487 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | DS | JZ53_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_DS | JZ53_DS (非取樣點) | FEEDER | [5 empty] | 488 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | ES | JZ53_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ53_ES | JZ53_ES (非取樣點) | FEEDER | [5 empty] | 489 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | DS | JZ54_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_DS | JZ54_DS (非取樣點) | FEEDER | [5 empty] | 490 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | ES | JZ54_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ54_ES | JZ54_ES (非取樣點) | FEEDER | [5 empty] | 491 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | DS | JZ55_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_DS | JZ55_DS (非取樣點) | FEEDER | [5 empty] | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | ES | JZ55_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ55_ES | JZ55_ES (非取樣點) | FEEDER | [5 empty] | 493 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | DS | JZ56_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_DS | JZ56_DS (非取樣點) | FEEDER | [5 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | ES | JZ56_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.JZ56_ES | JZ56_ES (非取樣點) | FEEDER | [5 empty] | 495 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | DS | TIE3_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 770 | #3MTR(770) |  | TE0 | 770TE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 497 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | 770 | #3MTR(770) |  | BE0 | 770BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 498 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | DS | M3A_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.M3A_DS | M3A_DS (非取樣點) | DTR | [5 empty] | 499 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | DS | M3B_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.M3B_DS | M3B_DS (非取樣點) | DTR | [5 empty] | 500 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | M3A | #3MTR(M3A) |  | ES | M3A_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.M3A_ES | M3A_ES (非取樣點) | DTR | [5 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | M3B | #3MTR(M3B) |  | ES | M3B_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.M3B_ES | M3B_ES (非取樣點) | DTR | [5 empty] | 502 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | ES | 410_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.410_ES | 410_ES (非取樣點) | SC | [5 empty] | 503 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | D1 | 411DS (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.411DS | 411DS (非取樣點) | SC | [5 empty] | 504 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | D2 | 412DS (非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.412DS | 412DS (非取樣點) | SC | [5 empty] | 505 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | ES | 420_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.420_ES | 420_ES (非取樣點) | SC | [5 empty] | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | D1 | 421DS (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.421DS | 421DS (非取樣點) | SC | [5 empty] | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | D2 | 422DS (非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.422DS | 422DS (非取樣點) | SC | [5 empty] | 508 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE(TIE3) |  | ES | TIE3_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.TIE3_ES | TIE3_ES (非取樣點) | TIE | [5 empty] | 509 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 3ABUS | #3ABUS |  | ES | #3ABUS_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.#3ABUS_ES | #3ABUS_ES (非取樣點) | OTHER | [5 empty] | 510 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | 3BBUS | #3BBUS |  | ES | #3BBUS_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.#3BBUS_ES | #3BBUS_ES (非取樣點) | OTHER | [5 empty] | 511 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | BR3 | BR3 |  | DS | BR-3_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.BR-3_DS | BR-3_DS (非取樣點) | OTHER | [5 empty] | 512 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | BR3 | BR3 |  | ES | BR-3_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S32_D1 | [8 empty] | 新塭SS.BR-3_ES | BR-3_ES (非取樣點) | OTHER | [5 empty] | 513 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S32 | 新塭SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S32_D1 | [12 empty] | 新塭SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S32/69/1BUS/V; OPRD2: S32/69/2BUS/V
S32 | 新塭SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S32_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S32/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S32 | 新塭SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S32_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_5 | OPRD1: S32/11/M1/MW; OPRD2: S32/11/M2/MW; OPRD3: S32/22/M3A/MW; OPRD4: S32/69/630/MW; OPRD5: S32/69/640/MW
S32 | 新塭SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S32_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S32/0/CalcPoint/OPRN2_MW
S32 | 新塭SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S32_D1 | [17 empty] | none
S32 | 新塭SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S32_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S32/0/CalcPoint/OPRN1; OPRD2: S32/0/CalcPoint/OPRN2; OPRD3: S32/0/CalcPoint/PRFL_UL
S32 | 新塭SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S32_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S32/11/M1/MW; OPRD2: S32/11/M1/MVAR; OPRD3: S32/0/CalcPoint/Vbs2
S32 | 新塭SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S32_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S32/11/M2/MW; OPRD2: S32/11/M2/MVAR; OPRD3: S32/0/CalcPoint/Vbs2
S32 | 新塭SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S32_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S32/22/M3A/MW; OPRD2: S32/22/M3A/MVAR; OPRD3: NULL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮～新塭線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S32_A1 | [12 empty] | 新塭SS.630_AMP | 大寮新塭線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S32/69/630/MW; OPRD2: S32/69/630/MVAR; OPRD3: S32/0/CalcPoint/Vbs2
S32 | 新塭SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S32_A1 | [12 empty] | 新塭SS.640_AMP | 新塭永華線 AMP | LINE69 | AMP_CAL | C12R0831 | amp_cal | OPRD1: S32/69/640/MW; OPRD2: S32/69/640/MVAR; OPRD3: S32/0/CalcPoint/Vbs2
S32 | 新塭SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S32_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S32/11/1BUS/V
S32 | 新塭SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S32_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S32/11/2BUS/V
S32 | 新塭SS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S32_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S32/22/3ABUS/V
S32 | 新塭SS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S32_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S32/22/3BBUS/V
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S32_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新塭SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S32/11/M1/MW; OPRD2: S32/11/M1/MVAR
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S32_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新塭SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S32/11/M2/MW; OPRD2: S32/11/M2/MVAR
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S32_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新塭SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S32/22/M3A/MW; OPRD2: S32/22/M3A/MVAR
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S32_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S32//1MTR/MVA; OPRD2: 0
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S32_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S32//2MTR/MVA; OPRD2: 0
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S32_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S32//3MTR/MVA; OPRD2: 0
S32 | 新塭SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S32_D1 | [12 empty] | 新塭SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S32/11/M1/MW; OPRD2: S32/11/M1/MVAR
S32 | 新塭SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S32_D1 | [12 empty] | 新塭SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S32/11/M2/MW; OPRD2: S32/11/M2/MVAR
S32 | 新塭SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S32_D1 | [12 empty] | 新塭SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S32/22/M3A/MW; OPRD2: S32/22/M3A/MVAR
S32 | 新塭SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S32_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S32//1MTR/SupLocal; OPRD2: S32//1MTR/Tap Chan; OPRD3: NULL
S32 | 新塭SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S32_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S32//2MTR/SupLocal; OPRD2: S32//2MTR/Tap Chan; OPRD3: NULL
S32 | 新塭SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S32_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S32//3MTR/SupLocal; OPRD2: S32//3MTR/Tap Chan; OPRD3: NULL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S32/11/1BUS/V; OPRD2: S32/11/JZ21/I_R; OPRD3: S32/11/JZ21/I_S; OPRD4: S32/11/JZ21/I_T
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S32/11/1BUS/V; OPRD2: S32/11/JZ22/I_R; OPRD3: S32/11/JZ22/I_S; OPRD4: S32/11/JZ22/I_T
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S32/11/1BUS/V; OPRD2: S32/11/JZ23/I_R; OPRD3: S32/11/JZ23/I_S; OPRD4: S32/11/JZ23/I_T
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S32/11/1BUS/V; OPRD2: S32/11/JZ24/I_R; OPRD3: S32/11/JZ24/I_S; OPRD4: S32/11/JZ24/I_T
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S32/11/1BUS/V; OPRD2: S32/11/JZ25/I_R; OPRD3: S32/11/JZ25/I_S; OPRD4: S32/11/JZ25/I_T
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/11/JZ26/I_R; OPRD3: S32/11/JZ26/I_S; OPRD4: S32/11/JZ26/I_T
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/11/JZ27/I_R; OPRD3: S32/11/JZ27/I_S; OPRD4: S32/11/JZ27/I_T
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/11/JZ28/I_R; OPRD3: S32/11/JZ28/I_S; OPRD4: S32/11/JZ28/I_T
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/11/JZ29/I_R; OPRD3: S32/11/JZ29/I_S; OPRD4: S32/11/JZ29/I_T
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/11/JZ30/I_R; OPRD3: S32/11/JZ30/I_S; OPRD4: S32/11/JZ30/I_T
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ51/I_R; OPRD3: S32/22/JZ51/I_S; OPRD4: S32/22/JZ51/I_T
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ52/I_R; OPRD3: S32/22/JZ52/I_S; OPRD4: S32/22/JZ52/I_T
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ53/I_R; OPRD3: S32/22/JZ53/I_S; OPRD4: S32/22/JZ53/I_T
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ54/I_R; OPRD3: S32/22/JZ54/I_S; OPRD4: S32/22/JZ54/I_T
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ55/I_R; OPRD3: S32/22/JZ55/I_S; OPRD4: S32/22/JZ55/I_T
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S32/22/JZ56/I_R; OPRD3: S32/22/JZ56/I_S; OPRD4: S32/22/JZ56/I_T
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ21/kVA; OPRD2: S32/11/JZ21/KVAR
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ22/kVA; OPRD2: S32/11/JZ22/KVAR
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ23/kVA; OPRD2: S32/11/JZ23/KVAR
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ24/kVA; OPRD2: S32/11/JZ24/KVAR
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ25/kVA; OPRD2: S32/11/JZ25/KVAR
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ26/kVA; OPRD2: S32/11/JZ26/KVAR
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ27/kVA; OPRD2: S32/11/JZ27/KVAR
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ28/kVA; OPRD2: S32/11/JZ28/KVAR
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ29/kVA; OPRD2: S32/11/JZ29/KVAR
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/11/JZ30/kVA; OPRD2: S32/11/JZ30/KVAR
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ51/kVA; OPRD2: S32/22/JZ51/KVAR
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ52/kVA; OPRD2: S32/22/JZ52/KVAR
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ53/kVA; OPRD2: S32/22/JZ53/KVAR
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ54/kVA; OPRD2: S32/22/JZ54/KVAR
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ55/kVA; OPRD2: S32/22/JZ55/KVAR
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S32_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S32/22/JZ56/kVA; OPRD2: S32/22/JZ56/KVAR
S32 | 新塭SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S32_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S32/11/M1/MW; OPRD2: S32/11/M2/MW; OPRD3: S32/22/M3A/MW
S32 | 新塭SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S32_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S32/11/M1/MVAR; OPRD2: S32/11/M2/MVAR; OPRD3: S32/22/M3A/MVAR
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S32_D1 | [12 empty] | 新塭SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S32/11/210/CB; OPRD2: 6.9; OPRD3: 0
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S32_D1 | [12 empty] | 新塭SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S32/11/220/CB; OPRD2: 6.9; OPRD3: 0
S32 | 新塭SS | 22 | 22kV | 410 | #3ASC(410) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S32_D1 | [12 empty] | 新塭SS.410_SC_MVAR | 23KV#3ASC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: S32/22/410/CB; OPRD2: 13.8; OPRD3: 0
S32 | 新塭SS | 22 | 22kV | 420 | #3BSC(420) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S32_D1 | [12 empty] | 新塭SS.420_SC_MVAR | 23KV#3BSC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: S32/22/420/CB; OPRD2: 13.8; OPRD3: 0
S32 | 新塭SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S32_D1 | [12 empty] | 新塭SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_26 | OPRD1: S32//1MTR/96B1; OPRD2: S32//1MTR/96PA; OPRD3: S32//1MTR/TRA; OPRD4: S32//1MTR/63Q; OPRD5: S32//1MTR/96D; OPRD6: S32//1MTR/96B2; OPRD7: S32//1MTR/51ZA; OPRD8: S32//1MTR/87A/DI-SP; OPRD9: S32//2MTR/96B1; OPRD10: S32//2MTR/63Q; OPRD11: S32//2MTR/96D; OPRD12: S32//2MTR/96B2; OPRD13: S32//2MTR/51ZA; OPRD14: S32//2MTR/TRA; OPRD15: S32//2MTR/87A; OPRD16: S32//2MTR/96PA; OPRD17: S32//3MTR/96B1; OPRD18: S32//3MTR/63Q; OPRD19: S32//3MTR/96PA; OPRD20: S32//3MTR/96D; OPRD21: S32//3MTR/96B2; OPRD22: S32//3MTR/TRA; OPRD23: S32/22/M3/51ZA; OPRD24: S32/22/M3/87A; OPRD25: S32/69/1BUS/87A; OPRD26: S32/69/2BUS/87A
S32 | 新塭SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S32_D1 | [12 empty] | 新塭SS.變電所輕故障 | 變電所輕故障(AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: S32//1MTR/TRF; OPRD2: S32//2MTR/TRF; OPRD3: S32//3MTR/TRF
S32 | 新塭SS | 11 | 11kV | M1_A1 | #1MTR(M1) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/11/M1/81A
S32 | 新塭SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/RTU/RTU_R_L
S32 | 新塭SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/StaDev/DCE
S32 | 新塭SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/StaDev/DCA
S32 | 新塭SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S32_D1 | [17 empty] | lamp2CC | OPRD1: S32/69/ComPoint/CBF
S32 | 新塭SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S32_D1 | [17 empty] | lamp2CC | OPRD1: S32/69/ComPoint/CBA
S32 | 新塭SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S32_D1 | [17 empty] | lamp2CC | OPRD1: S32/69/ComPoint/ABS_89A
S32 | 新塭SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/StaDev/PSF
S32 | 新塭SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/StaDev/PSA
S32 | 新塭SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/0/StaDev/Fire
S32 | 新塭SS | 22 | 22kV | M3A_A1 | #3MTR(M3A) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/22/M3A/81A
S32 | 新塭SS | 22 | 22kV | M3B_A1 | #3MTR(M3B) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S32_A1 | [17 empty] | lamp2CC | OPRD1: S32/22/M3B/81A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S32 | 新塭SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 新塭SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S32/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 新塭SS.630_AMP | 大寮新塭線 AMP | LINE69 | S32/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 新塭SS.640_AMP | 新塭永華線 AMP | LINE69 | S32/69/640/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0831 | 747.900024 | 747.900024 | 831.000000 | 1200.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭一線KVA | 11KV塭一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭一線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭一線KW | 11KV塭一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭七線KVA | 11KV塭七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭七線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭七線KW | 11KV塭七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭九線KVA | 11KV塭九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭九線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭九線KW | 11KV塭九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭二線KVA | 11KV塭二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭二線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭二線KW | 11KV塭二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭八線KVA | 11KV塭八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭八線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭八線KW | 11KV塭八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭十線KVA | 11KV塭十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭十線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭十線KW | 11KV塭十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭三線KVA | 11KV塭三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭三線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭三線KW | 11KV塭三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭五線KVA | 11KV塭五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭五線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭五線KW | 11KV塭五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭六線KVA | 11KV塭六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭六線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭六線KW | 11KV塭六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭四線KVA | 11KV塭四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | 塭四線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭四線KW | 11KV塭四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S32//1MTR/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_PF | #1MTR 功率因素 | DTR | S32//1MTR/PF |  | RPDC_PF_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S32//2MTR/MVA |  | MVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_PF | #2MTR 功率因素 | DTR | S32//2MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S32 | 新塭SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S32/11/210/MVAR |  | SC_CAL_11 |  |  | 29 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S32/11/220/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ51線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51線KVA | 23KVJZ51線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ51線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51線KW | 23KVJZ51線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ52線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52線KVA | 23KVJZ52線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ52線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52線KW | 23KVJZ52線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ53線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53線KVA | 23KVJZ53線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ53線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53線KW | 23KVJZ53線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ54線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54線KVA | 23KVJZ54線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ54線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54線KW | 23KVJZ54線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ55線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55線KVA | 23KVJZ55線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ55線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55線KW | 23KVJZ55線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ56線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56線KVA | 23KVJZ56線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  |  |  |  | JZ56線KW | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56線KW | 23KVJZ56線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S32//3MTR/MVA |  | MVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_PF | #3MTR 功率因素 | DTR | S32//3MTR/PF |  | RPDC_PF_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S32 | 新塭SS | 22 | 22kV | 410_SC | #3ASC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_SC_MVAR | 23KV#3ASC MVAR | SC | S32/22/410/MVAR |  | SC_CAL_23 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 22 | 22kV | 420_SC | #3BSC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_SC_MVAR | 23KV#3BSC MVAR | SC | S32/22/420/MVAR |  | SC_CAL_23 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 69 | 69kV | 630_CB | 大寮新塭線(630_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.630_CB_2 | 630(大寮新塭線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 640_CB | 新塭永華線(640_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.640_CB_2 | 640(新塭永華線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 48 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 600_CB | 600(600_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.600_CB_2 | 600 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 49 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 新塭SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 50 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 新塭SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 51 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 新塭SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 52 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S32 | 新塭SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 53 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 新塭SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S32/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 新塭SS.變電所輕故障 | 變電所輕故障(AD) | OTHER | S32/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 57 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630_AMP | 大寮新塭線 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.630_AMP_A | 大寮新塭線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 69 | 69kV | 630_AMP | 大寮新塭線 | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.630_AMP_2 | 大寮新塭線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 59 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 69 | 69kV | 640_AMP | 新塭永華線 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.640_AMP_A | 新塭永華線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 69 | 69kV | 640_AMP | 新塭永華線 | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.640_AMP_2 | 新塭永華線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | 600_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.600_RYFA_A | 600 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 66 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 630_CFA | 630 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.630_CFA_A | 630 CFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 67 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.630_RYFA_A | 630 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 68 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 640_CFA | 640 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.640_CFA_A | 640 CFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 69 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 640_RYFA | 640 | [27 empty] | ADCS_N | [8 empty] | 新塭SS.640_RYFA_A | 640 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 70 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 691BUS_27BA | 69#1BUS | [27 empty] | ADCS_N | [8 empty] | 新塭SS.69#1BUS_27BA_A | 69#1BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 71 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 692BUS_27BA | 69#2BUS | [27 empty] | ADCS_N | [8 empty] | 新塭SS.69#2BUS_27BA_A | 69#2BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 72 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | BUSRY_BF | BUSRY | [27 empty] | ADCS_N | [8 empty] | 新塭SS.BUSRY_BF_A | BUSRY BF (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 73 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | BUSRY_CTFA | BUSRY | [27 empty] | ADCS_N | [8 empty] | 新塭SS.BUSRY_CTFA_A | BUSRY CTFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 74 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S32 | 新塭SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S32/0/RTU/ADCH1 |  |  |  | CDC | 76 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S32/0/RTU/ADCH2 |  |  |  | CDC | 77 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S32/0/RTU/ADCH3 |  |  |  | CDC | 78 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S32/0/RTU/ADCL1 |  |  |  | CDC | 79 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S32/0/RTU/ADCL2 |  |  |  | CDC | 80 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S32/0/RTU/ADCL3 |  |  |  | CDC | 81 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S32/69/1BUS/V |  |  |  | CDC | 82 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S32 | 新塭SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S32/69/2BUS/V |  |  |  | CDC | 83 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S32 | 新塭SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-91 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S32/11/1BUS/V |  |  |  | CDC | 84 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S32 | 新塭SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-B8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S32/11/2BUS/V |  |  |  | CDC | 85 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.630_MW | 大寮新塭線 MW | LINE69 | S32/69/630/MW |  |  |  | CDC | 86 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.630_MVAR | 大寮新塭線 MVAR | LINE69 | S32/69/630/MVAR |  |  |  | CDC | 87 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.640_MW | 新塭永華線 MW | LINE69 | S32/69/640/MW |  |  |  | CDC | 88 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.640_MVAR | 新塭永華線 MVAR | LINE69 | S32/69/640/MVAR |  |  |  | CDC | 89 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭一線 | 塭一線 |  | 塭一線KVAR | [17 empty] | 1-9A | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭一線KVAR | 11KV塭一線 KVAR | FEEDER | S32/11/JZ21/KVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭一線 | 塭一線 |  | 塭一線A1 | [17 empty] | 1-9B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭一線A1 | 11KV塭一線 R相AMP | FEEDER | S32/11/JZ21/I_R |  |  |  | CDC | 91 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭一線 | 塭一線 |  | 塭一線A2 | [17 empty] | 1-9C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭一線A2 | 11KV塭一線 S相AMP | FEEDER | S32/11/JZ21/I_S |  |  |  | CDC | 92 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭一線 | 塭一線 |  | 塭一線A3 | [17 empty] | 1-9D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭一線A3 | 11KV塭一線 T相AMP | FEEDER | S32/11/JZ21/I_T |  |  |  | CDC | 93 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭一線 | 塭一線 |  | 塭一線A0 | [17 empty] | 1-9E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭一線A0 | 11KV塭一線 N相AMP | FEEDER | S32/11/JZ21/I_N |  |  |  | CDC | 94 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭七線 | 塭七線 |  | 塭七線KVAR | [17 empty] | 1-C8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭七線KVAR | 11KV塭七線 KVAR | FEEDER | S32/11/JZ27/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭七線 | 塭七線 |  | 塭七線A1 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭七線A1 | 11KV塭七線 R相AMP | FEEDER | S32/11/JZ27/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭七線 | 塭七線 |  | 塭七線A2 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭七線A2 | 11KV塭七線 S相AMP | FEEDER | S32/11/JZ27/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭七線 | 塭七線 |  | 塭七線A3 | [17 empty] | 1-CB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭七線A3 | 11KV塭七線 T相AMP | FEEDER | S32/11/JZ27/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭七線 | 塭七線 |  | 塭七線A0 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭七線A0 | 11KV塭七線 N相AMP | FEEDER | S32/11/JZ27/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭九線 | 塭九線 |  | 塭九線KVAR | [17 empty] | 1-D2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭九線KVAR | 11KV塭九線 KVAR | FEEDER | S32/11/JZ29/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭九線 | 塭九線 |  | 塭九線A1 | [17 empty] | 1-D3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭九線A1 | 11KV塭九線 R相AMP | FEEDER | S32/11/JZ29/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭九線 | 塭九線 |  | 塭九線A2 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭九線A2 | 11KV塭九線 S相AMP | FEEDER | S32/11/JZ29/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭九線 | 塭九線 |  | 塭九線A3 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭九線A3 | 11KV塭九線 T相AMP | FEEDER | S32/11/JZ29/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭九線 | 塭九線 |  | 塭九線A0 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭九線A0 | 11KV塭九線 N相AMP | FEEDER | S32/11/JZ29/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭二線 | 塭二線 |  | 塭二線KVAR | [17 empty] | 1-9F | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭二線KVAR | 11KV塭二線 KVAR | FEEDER | S32/11/JZ22/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭二線 | 塭二線 |  | 塭二線A1 | [17 empty] | 1-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭二線A1 | 11KV塭二線 R相AMP | FEEDER | S32/11/JZ22/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭二線 | 塭二線 |  | 塭二線A2 | [17 empty] | 1-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭二線A2 | 11KV塭二線 S相AMP | FEEDER | S32/11/JZ22/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭二線 | 塭二線 |  | 塭二線A3 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭二線A3 | 11KV塭二線 T相AMP | FEEDER | S32/11/JZ22/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭二線 | 塭二線 |  | 塭二線A0 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭二線A0 | 11KV塭二線 N相AMP | FEEDER | S32/11/JZ22/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭八線 | 塭八線 |  | 塭八線KVAR | [17 empty] | 1-CD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭八線KVAR | 11KV塭八線 KVAR | FEEDER | S32/11/JZ28/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭八線 | 塭八線 |  | 塭八線A1 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭八線A1 | 11KV塭八線 R相AMP | FEEDER | S32/11/JZ28/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭八線 | 塭八線 |  | 塭八線A2 | [17 empty] | 1-CF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭八線A2 | 11KV塭八線 S相AMP | FEEDER | S32/11/JZ28/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭八線 | 塭八線 |  | 塭八線A3 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭八線A3 | 11KV塭八線 T相AMP | FEEDER | S32/11/JZ28/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭八線 | 塭八線 |  | 塭八線A0 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭八線A0 | 11KV塭八線 N相AMP | FEEDER | S32/11/JZ28/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭十線 | 塭十線 |  | 塭十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭十線KVAR | 11KV塭十線 KVAR | FEEDER | S32/11/JZ30/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭十線 | 塭十線 |  | 塭十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭十線A1 | 11KV塭十線 R相AMP | FEEDER | S32/11/JZ30/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭十線 | 塭十線 |  | 塭十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭十線A2 | 11KV塭十線 S相AMP | FEEDER | S32/11/JZ30/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭十線 | 塭十線 |  | 塭十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭十線A3 | 11KV塭十線 T相AMP | FEEDER | S32/11/JZ30/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭十線 | 塭十線 |  | 塭十線A0 | [17 empty] | 1-DB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭十線A0 | 11KV塭十線 N相AMP | FEEDER | S32/11/JZ30/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭三線 | 塭三線 |  | 塭三線KVAR | [17 empty] | 1-A4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭三線KVAR | 11KV塭三線 KVAR | FEEDER | S32/11/JZ23/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭三線 | 塭三線 |  | 塭三線A1 | [17 empty] | 1-A5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭三線A1 | 11KV塭三線 R相AMP | FEEDER | S32/11/JZ23/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭三線 | 塭三線 |  | 塭三線A2 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭三線A2 | 11KV塭三線 S相AMP | FEEDER | S32/11/JZ23/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭三線 | 塭三線 |  | 塭三線A3 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭三線A3 | 11KV塭三線 T相AMP | FEEDER | S32/11/JZ23/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭三線 | 塭三線 |  | 塭三線A0 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭三線A0 | 11KV塭三線 N相AMP | FEEDER | S32/11/JZ23/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭五線 | 塭五線 |  | 塭五線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭五線KVAR | 11KV塭五線 KVAR | FEEDER | S32/11/JZ25/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭五線 | 塭五線 |  | 塭五線A1 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭五線A1 | 11KV塭五線 R相AMP | FEEDER | S32/11/JZ25/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭五線 | 塭五線 |  | 塭五線A2 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭五線A2 | 11KV塭五線 S相AMP | FEEDER | S32/11/JZ25/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭五線 | 塭五線 |  | 塭五線A3 | [17 empty] | 1-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭五線A3 | 11KV塭五線 T相AMP | FEEDER | S32/11/JZ25/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭五線 | 塭五線 |  | 塭五線A0 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭五線A0 | 11KV塭五線 N相AMP | FEEDER | S32/11/JZ25/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭六線 | 塭六線 |  | 塭六線KVAR | [17 empty] | 1-C3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭六線KVAR | 11KV塭六線 KVAR | FEEDER | S32/11/JZ26/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭六線 | 塭六線 |  | 塭六線A1 | [17 empty] | 1-C4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭六線A1 | 11KV塭六線 R相AMP | FEEDER | S32/11/JZ26/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭六線 | 塭六線 |  | 塭六線A2 | [17 empty] | 1-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭六線A2 | 11KV塭六線 S相AMP | FEEDER | S32/11/JZ26/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭六線 | 塭六線 |  | 塭六線A3 | [17 empty] | 1-C6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭六線A3 | 11KV塭六線 T相AMP | FEEDER | S32/11/JZ26/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭六線 | 塭六線 |  | 塭六線A0 | [17 empty] | 1-C7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭六線A0 | 11KV塭六線 N相AMP | FEEDER | S32/11/JZ26/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭四線 | 塭四線 |  | 塭四線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭四線KVAR | 11KV塭四線 KVAR | FEEDER | S32/11/JZ24/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭四線 | 塭四線 |  | 塭四線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭四線A1 | 11KV塭四線 R相AMP | FEEDER | S32/11/JZ24/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭四線 | 塭四線 |  | 塭四線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭四線A2 | 11KV塭四線 S相AMP | FEEDER | S32/11/JZ24/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭四線 | 塭四線 |  | 塭四線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭四線A3 | 11KV塭四線 T相AMP | FEEDER | S32/11/JZ24/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | 塭四線 | 塭四線 |  | 塭四線A0 | [17 empty] | 1-AD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.塭四線A0 | 11KV塭四線 N相AMP | FEEDER | S32/11/JZ24/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-90 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 新塭SS.600TIE_AMP | 600TIE AMP | TIE | S32/69/600/I |  |  |  | CDC | 140 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S32/11/TIE1/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S32/11/TIE1/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S32/11/TIE1/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_MW | #1MTR二次側 MW | DTR | S32/11/M1/MW |  |  |  | CDC | 144 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S32/11/M1/MVAR |  |  |  | CDC | 145 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-97 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S32/11/M1/I_R |  |  |  | CDC | 146 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S32/11/M1/I_S |  |  |  | CDC | 147 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-99 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S32/11/M1/I_T |  |  |  | CDC | 148 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-93 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_OIL | #1MTR 油溫 | DTR | S32//1MTR/OilTemp |  |  |  | CDC | 149 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-92 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_COIL | #1MTR 線溫 | DTR | S32//1MTR/CoilTemp |  |  |  | CDC | 150 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-94 |  | 1-3B |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S32//1MTR/TapPosMv |  |  |  | CDC | 151 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-BC | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_MW | #2MTR二次側 MW | DTR | S32/11/M2/MW |  |  |  | CDC | 152 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-BD | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S32/11/M2/MVAR |  |  |  | CDC | 153 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-BE | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S32/11/M2/I_R |  |  |  | CDC | 154 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-BF | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S32/11/M2/I_S |  |  |  | CDC | 155 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C2 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S32/11/M2/I_T |  |  |  | CDC | 156 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BA | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_OIL | #2MTR 油溫 | DTR | S32//2MTR/OilTemp |  |  |  | CDC | 157 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-B9 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_COIL | #2MTR 線溫 | DTR | S32//2MTR/CoilTemp |  |  |  | CDC | 158 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BB |  | 1-4D |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S32//2MTR/TapPosMv |  |  |  | CDC | 159 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS | 0 |  |  |  |  | DCV | [17 empty] | 2-90 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.直流電源電壓 | 直流電源電壓 | OTHER | S32/0/StaDev/DCV |  |  |  | CDC | 160 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S32 | 新塭SS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [17 empty] | 1-E0 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | S32/22/3ABUS/V |  |  |  | CDC | 161 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S32 | 新塭SS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-8C | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | S32/22/3BBUS/V |  |  |  | CDC | 162 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S32 | 新塭SS | 22 | 22kV | JZ51線 | JZ51線 |  | JZ51線KVAR | [17 empty] | 1-E9 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ51線KVAR | 23KVJZ51線 KVAR | FEEDER | S32/22/JZ51/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51線 | JZ51線 |  | JZ51線A1 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ51線A1 | 23KVJZ51線 R相AMP | FEEDER | S32/22/JZ51/I_R |  |  |  | CDC | 164 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51線 | JZ51線 |  | JZ51線A2 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ51線A2 | 23KVJZ51線 S相AMP | FEEDER | S32/22/JZ51/I_S |  |  |  | CDC | 165 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51線 | JZ51線 |  | JZ51線A3 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ51線A3 | 23KVJZ51線 T相AMP | FEEDER | S32/22/JZ51/I_T |  |  |  | CDC | 166 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ51線 | JZ51線 |  | JZ51線A0 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ51線A0 | 23KVJZ51線 N相AMP | FEEDER | S32/22/JZ51/I_N |  |  |  | CDC | 167 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52線 | JZ52線 |  | JZ52線KVAR | [17 empty] | 1-EE | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ52線KVAR | 23KVJZ52線 KVAR | FEEDER | S32/22/JZ52/KVAR |  |  |  | CDC | 168 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52線 | JZ52線 |  | JZ52線A1 | [17 empty] | 1-EF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ52線A1 | 23KVJZ52線 R相AMP | FEEDER | S32/22/JZ52/I_R |  |  |  | CDC | 169 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52線 | JZ52線 |  | JZ52線A2 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ52線A2 | 23KVJZ52線 S相AMP | FEEDER | S32/22/JZ52/I_S |  |  |  | CDC | 170 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52線 | JZ52線 |  | JZ52線A3 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ52線A3 | 23KVJZ52線 T相AMP | FEEDER | S32/22/JZ52/I_T |  |  |  | CDC | 171 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ52線 | JZ52線 |  | JZ52線A0 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ52線A0 | 23KVJZ52線 N相AMP | FEEDER | S32/22/JZ52/I_N |  |  |  | CDC | 172 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53線 | JZ53線 |  | JZ53線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ53線KVAR | 23KVJZ53線 KVAR | FEEDER | S32/22/JZ53/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53線 | JZ53線 |  | JZ53線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ53線A1 | 23KVJZ53線 R相AMP | FEEDER | S32/22/JZ53/I_R |  |  |  | CDC | 174 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53線 | JZ53線 |  | JZ53線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ53線A2 | 23KVJZ53線 S相AMP | FEEDER | S32/22/JZ53/I_S |  |  |  | CDC | 175 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53線 | JZ53線 |  | JZ53線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ53線A3 | 23KVJZ53線 T相AMP | FEEDER | S32/22/JZ53/I_T |  |  |  | CDC | 176 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ53線 | JZ53線 |  | JZ53線A0 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ53線A0 | 23KVJZ53線 N相AMP | FEEDER | S32/22/JZ53/I_N |  |  |  | CDC | 177 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54線 | JZ54線 |  | JZ54線KVAR | [17 empty] | 1-F8 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ54線KVAR | 23KVJZ54線 KVAR | FEEDER | S32/22/JZ54/KVAR |  |  |  | CDC | 178 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54線 | JZ54線 |  | JZ54線A1 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ54線A1 | 23KVJZ54線 R相AMP | FEEDER | S32/22/JZ54/I_R |  |  |  | CDC | 179 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54線 | JZ54線 |  | JZ54線A2 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ54線A2 | 23KVJZ54線 S相AMP | FEEDER | S32/22/JZ54/I_S |  |  |  | CDC | 180 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54線 | JZ54線 |  | JZ54線A3 | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ54線A3 | 23KVJZ54線 T相AMP | FEEDER | S32/22/JZ54/I_T |  |  |  | CDC | 181 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ54線 | JZ54線 |  | JZ54線A0 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ54線A0 | 23KVJZ54線 N相AMP | FEEDER | S32/22/JZ54/I_N |  |  |  | CDC | 182 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55線 | JZ55線 |  | JZ55線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ55線KVAR | 23KVJZ55線 KVAR | FEEDER | S32/22/JZ55/KVAR |  |  |  | CDC | 183 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55線 | JZ55線 |  | JZ55線A1 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ55線A1 | 23KVJZ55線 R相AMP | FEEDER | S32/22/JZ55/I_R |  |  |  | CDC | 184 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55線 | JZ55線 |  | JZ55線A2 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ55線A2 | 23KVJZ55線 S相AMP | FEEDER | S32/22/JZ55/I_S |  |  |  | CDC | 185 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55線 | JZ55線 |  | JZ55線A3 | [17 empty] | 2-82 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ55線A3 | 23KVJZ55線 T相AMP | FEEDER | S32/22/JZ55/I_T |  |  |  | CDC | 186 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ55線 | JZ55線 |  | JZ55線A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ55線A0 | 23KVJZ55線 N相AMP | FEEDER | S32/22/JZ55/I_N |  |  |  | CDC | 187 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56線 | JZ56線 |  | JZ56線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ56線KVAR | 23KVJZ56線 KVAR | FEEDER | S32/22/JZ56/KVAR |  |  |  | CDC | 188 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56線 | JZ56線 |  | JZ56線A1 | [17 empty] | 2-85 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ56線A1 | 23KVJZ56線 R相AMP | FEEDER | S32/22/JZ56/I_R |  |  |  | CDC | 189 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56線 | JZ56線 |  | JZ56線A2 | [17 empty] | 2-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ56線A2 | 23KVJZ56線 S相AMP | FEEDER | S32/22/JZ56/I_S |  |  |  | CDC | 190 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56線 | JZ56線 |  | JZ56線A3 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ56線A3 | 23KVJZ56線 T相AMP | FEEDER | S32/22/JZ56/I_T |  |  |  | CDC | 191 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | JZ56線 | JZ56線 |  | JZ56線A0 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.JZ56線A0 | 23KVJZ56線 N相AMP | FEEDER | S32/22/JZ56/I_N |  |  |  | CDC | 192 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 2-89 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.23KV_TIE3_A1 | 23KV TIE3 R相AMP | TIE | S32/22/TIE3/I_R |  |  |  | CDC | 193 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 2-8A | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.23KV_TIE3_A2 | 23KV TIE3 S相AMP | TIE | S32/22/TIE3/I_S |  |  |  | CDC | 194 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 22 | 22kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 2-8B | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.23KV_TIE3_A3 | 23KV TIE3 T相AMP | TIE | S32/22/TIE3/I_T |  |  |  | CDC | 195 | GENERICAIPoint | SS213_L2 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E4 | [5 empty] | MW_-72_72(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_MW | #3MTR二次側 MW | DTR | S32/22/M3A/MW |  |  |  | CDC | 196 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E5 | [5 empty] | MVAR_-72_72(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S32/22/M3A/MVAR |  |  |  | CDC | 197 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S32/22/M3A/I_R |  |  |  | CDC | 198 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S32/22/M3A/I_S |  |  |  | CDC | 199 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S32/22/M3A/I_T |  |  |  | CDC | 200 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E2 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_OIL | #3MTR 油溫 | DTR | S32//3MTR/OilTemp |  |  |  | CDC | 201 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E1 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_COIL | #3MTR 線溫 | DTR | S32//3MTR/CoilTemp |  |  |  | CDC | 202 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E3 |  | 1-63 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S32//3MTR/TapPosMv |  |  |  | CDC | 203 | GENERICAIPoint | SS213_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.630_PHA | 大寮新塭線(630) 相間RY | LINE69 | S32/69/630/PHA |  |  |  | CDC | 204 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.630_GDA | 大寮新塭線(630) 接地RY | LINE69 | S32/69/630/GDA |  |  |  | CDC | 205 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 新塭SS.630_CB | 630(大寮新塭線) CB | LINE69 | S32/69/630/CB |  |  |  | CDC | 206 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | DS1 | 631 | [16 empty] | 1-38-00 | 1-38-01 | 1-10 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.631_DS | 631(大寮新塭線) DS | LINE69 | S32/69/630/DS1 |  |  |  | CDC | 207 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | DS2 | 632 | [16 empty] | 1-38-02 | 1-38-03 | 1-11 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.632_DS | 632(大寮新塭線) DS | LINE69 | S32/69/630/DS2 |  |  |  | CDC | 208 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | DS3 | 633 | [16 empty] | 1-38-04 | 1-38-05 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.633_DS | 633(大寮新塭線) DS | LINE69 | S32/69/630/DS3 |  |  |  | CDC | 209 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | E3 | 633E | [16 empty] | 1-38-06 | 1-38-07 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.633E_ES | 633E(大寮新塭線) ES | LINE69 | S32/69/630/ES3 |  |  |  | CDC | 210 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.640_PHA | 新塭永華線(640) 相間RY | LINE69 | S32/69/640/PHA |  |  |  | CDC | 211 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.640_GDA | 新塭永華線(640) 接地RY | LINE69 | S32/69/640/GDA |  |  |  | CDC | 212 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 新塭SS.640_CB | 640(新塭永華線) CB | LINE69 | S32/69/640/CB |  |  |  | CDC | 213 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | DS1 | 641 | [16 empty] | 1-38-08 | 1-38-09 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.641_DS | 641(新塭永華線) DS | LINE69 | S32/69/640/DS1 |  |  |  | CDC | 214 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | DS2 | 642 | [16 empty] | 1-38-10 | 1-38-11 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.642_DS | 642(新塭永華線) DS | LINE69 | S32/69/640/DS2 |  |  |  | CDC | 215 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | DS3 | 643 | [16 empty] | 1-38-12 | 1-38-13 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.643_DS | 643(新塭永華線) DS | LINE69 | S32/69/640/DS3 |  |  |  | CDC | 216 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | E3 | 643E | [16 empty] | 1-38-14 | 1-38-15 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.643E_ES | 643E(新塭永華線) ES | LINE69 | S32/69/640/ES3 |  |  |  | CDC | 217 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | PHA | [17 empty] | 1-0C-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_PHA | 11KV塭一線(JZ21) 相間RY | FEEDER | S32/11/JZ21/PHA |  |  |  | CDC | 218 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) |  | GDA | [17 empty] | 1-0C-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_GDA | 11KV塭一線(JZ21) 接地RY | FEEDER | S32/11/JZ21/GDA |  |  |  | CDC | 219 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) 79RY |  | 79UL | [17 empty] | 1-33-06 |  | 1-3E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_79UL | 11KV塭一線(JZ21) 79RY U/L | FEEDER | S32/11/JZ21/79UL |  |  |  | CDC | 220 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ21 | 塭一線(JZ21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_ADJ | 11KV塭一線(JZ21) LCO分流器 U/L | FEEDER | S32/11/JZ21/ADJ |  |  |  | CDC | 221 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ21 | JZ21(11KV塭一線) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_CB | JZ21(11KV塭一線) CB | FEEDER | S32/11/JZ21/CB |  |  |  | CDC | 222 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_PHA | 11KV塭二線(JZ22) 相間RY | FEEDER | S32/11/JZ22/PHA |  |  |  | CDC | 223 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_GDA | 11KV塭二線(JZ22) 接地RY | FEEDER | S32/11/JZ22/GDA |  |  |  | CDC | 224 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_79UL | 11KV塭二線(JZ22) 79RY U/L | FEEDER | S32/11/JZ22/79UL |  |  |  | CDC | 225 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ22 | 塭二線(JZ22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_ADJ | 11KV塭二線(JZ22) LCO分流器 U/L | FEEDER | S32/11/JZ22/ADJ |  |  |  | CDC | 226 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ22 | JZ22(11KV塭二線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_CB | JZ22(11KV塭二線) CB | FEEDER | S32/11/JZ22/CB |  |  |  | CDC | 227 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_PHA | 11KV塭三線(JZ23) 相間RY | FEEDER | S32/11/JZ23/PHA |  |  |  | CDC | 228 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_GDA | 11KV塭三線(JZ23) 接地RY | FEEDER | S32/11/JZ23/GDA |  |  |  | CDC | 229 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-40 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_79UL | 11KV塭三線(JZ23) 79RY U/L | FEEDER | S32/11/JZ23/79UL |  |  |  | CDC | 230 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ23 | 塭三線(JZ23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_ADJ | 11KV塭三線(JZ23) LCO分流器 U/L | FEEDER | S32/11/JZ23/ADJ |  |  |  | CDC | 231 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ23 | JZ23(11KV塭三線) |  | CB | [17 empty] | 1-0C-05 |  | 1-37 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_CB | JZ23(11KV塭三線) CB | FEEDER | S32/11/JZ23/CB |  |  |  | CDC | 232 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_PHA | 11KV塭四線(JZ24) 相間RY | FEEDER | S32/11/JZ24/PHA |  |  |  | CDC | 233 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_GDA | 11KV塭四線(JZ24) 接地RY | FEEDER | S32/11/JZ24/GDA |  |  |  | CDC | 234 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-41 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_79UL | 11KV塭四線(JZ24) 79RY U/L | FEEDER | S32/11/JZ24/79UL |  |  |  | CDC | 235 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ24 | 塭四線(JZ24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_ADJ | 11KV塭四線(JZ24) LCO分流器 U/L | FEEDER | S32/11/JZ24/ADJ |  |  |  | CDC | 236 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ24 | JZ24(11KV塭四線) |  | CB | [17 empty] | 1-0D-00 |  | 1-38 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_CB | JZ24(11KV塭四線) CB | FEEDER | S32/11/JZ24/CB |  |  |  | CDC | 237 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_PHA | 11KV塭五線(JZ25) 相間RY | FEEDER | S32/11/JZ25/PHA |  |  |  | CDC | 238 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_GDA | 11KV塭五線(JZ25) 接地RY | FEEDER | S32/11/JZ25/GDA |  |  |  | CDC | 239 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-42 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_79UL | 11KV塭五線(JZ25) 79RY U/L | FEEDER | S32/11/JZ25/79UL |  |  |  | CDC | 240 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ25 | 塭五線(JZ25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_ADJ | 11KV塭五線(JZ25) LCO分流器 U/L | FEEDER | S32/11/JZ25/ADJ |  |  |  | CDC | 241 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ25 | JZ25(11KV塭五線) |  | CB | [17 empty] | 1-0D-03 |  | 1-39 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_CB | JZ25(11KV塭五線) CB | FEEDER | S32/11/JZ25/CB |  |  |  | CDC | 242 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | PHA | [17 empty] | 1-0E-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_PHA | 11KV塭六線(JZ26) 相間RY | FEEDER | S32/11/JZ26/PHA |  |  |  | CDC | 243 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) |  | GDA | [17 empty] | 1-0E-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_GDA | 11KV塭六線(JZ26) 接地RY | FEEDER | S32/11/JZ26/GDA |  |  |  | CDC | 244 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) 79RY |  | 79UL | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_79UL | 11KV塭六線(JZ26) 79RY U/L | FEEDER | S32/11/JZ26/79UL |  |  |  | CDC | 245 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ26 | 塭六線(JZ26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_ADJ | 11KV塭六線(JZ26) LCO分流器 U/L | FEEDER | S32/11/JZ26/ADJ |  |  |  | CDC | 246 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ26 | JZ26(11KV塭六線) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_CB | JZ26(11KV塭六線) CB | FEEDER | S32/11/JZ26/CB |  |  |  | CDC | 247 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | PHA | [17 empty] | 1-0F-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_PHA | 11KV塭七線(JZ27) 相間RY | FEEDER | S32/11/JZ27/PHA |  |  |  | CDC | 248 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) |  | GDA | [17 empty] | 1-0F-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_GDA | 11KV塭七線(JZ27) 接地RY | FEEDER | S32/11/JZ27/GDA |  |  |  | CDC | 249 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_79UL | 11KV塭七線(JZ27) 79RY U/L | FEEDER | S32/11/JZ27/79UL |  |  |  | CDC | 250 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ27 | 塭七線(JZ27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_ADJ | 11KV塭七線(JZ27) LCO分流器 U/L | FEEDER | S32/11/JZ27/ADJ |  |  |  | CDC | 251 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ27 | JZ27(11KV塭七線) |  | CB | [17 empty] | 1-0F-00 |  | 1-49 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_CB | JZ27(11KV塭七線) CB | FEEDER | S32/11/JZ27/CB |  |  |  | CDC | 252 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | PHA | [17 empty] | 1-0F-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_PHA | 11KV塭八線(JZ28) 相間RY | FEEDER | S32/11/JZ28/PHA |  |  |  | CDC | 253 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) |  | GDA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_GDA | 11KV塭八線(JZ28) 接地RY | FEEDER | S32/11/JZ28/GDA |  |  |  | CDC | 254 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_79UL | 11KV塭八線(JZ28) 79RY U/L | FEEDER | S32/11/JZ28/79UL |  |  |  | CDC | 255 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ28 | 塭八線(JZ28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_ADJ | 11KV塭八線(JZ28) LCO分流器 U/L | FEEDER | S32/11/JZ28/ADJ |  |  |  | CDC | 256 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ28 | JZ28(11KV塭八線) |  | CB | [17 empty] | 1-0F-03 |  | 1-4A | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_CB | JZ28(11KV塭八線) CB | FEEDER | S32/11/JZ28/CB |  |  |  | CDC | 257 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_PHA | 11KV塭九線(JZ29) 相間RY | FEEDER | S32/11/JZ29/PHA |  |  |  | CDC | 258 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_GDA | 11KV塭九線(JZ29) 接地RY | FEEDER | S32/11/JZ29/GDA |  |  |  | CDC | 259 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_79UL | 11KV塭九線(JZ29) 79RY U/L | FEEDER | S32/11/JZ29/79UL |  |  |  | CDC | 260 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ29 | 塭九線(JZ29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_ADJ | 11KV塭九線(JZ29) LCO分流器 U/L | FEEDER | S32/11/JZ29/ADJ |  |  |  | CDC | 261 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ29 | JZ29(11KV塭九線) |  | CB | [17 empty] | 1-0F-06 |  | 1-4B | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_CB | JZ29(11KV塭九線) CB | FEEDER | S32/11/JZ29/CB |  |  |  | CDC | 262 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_PHA | 11KV塭十線(JZ30) 相間RY | FEEDER | S32/11/JZ30/PHA |  |  |  | CDC | 263 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_GDA | 11KV塭十線(JZ30) 接地RY | FEEDER | S32/11/JZ30/GDA |  |  |  | CDC | 264 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_79UL | 11KV塭十線(JZ30) 79RY U/L | FEEDER | S32/11/JZ30/79UL |  |  |  | CDC | 265 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV | JZ30 | 塭十線(JZ30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_ADJ | 11KV塭十線(JZ30) LCO分流器 U/L | FEEDER | S32/11/JZ30/ADJ |  |  |  | CDC | 266 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 11 | 11kV | JZ30 | JZ30(11KV塭十線) |  | CB | [17 empty] | 1-10-01 |  | 1-4C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_CB | JZ30(11KV塭十線) CB | FEEDER | S32/11/JZ30/CB |  |  |  | CDC | 267 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-02 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 新塭SS.600_CB | 600(TIE) CB | TIE | S32/69/600/CB |  |  |  | CDC | 268 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 600 | TIE(600) |  | 51A | [17 empty] | 1-04-03 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600_51A | 69KV TIE(600) 51RY | TIE | S32/69/600/51A |  |  |  | CDC | 269 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 600 | TIE(600) |  | 51NA | [17 empty] | 1-04-04 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600_51NA | 69KV TIE(600) 51N RY | TIE | S32/69/600/51NA |  |  |  | CDC | 270 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 新塭SS.601_DS | 601(TIE) DS | TIE | S32/69/600/DS1 |  |  |  | CDC | 271 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 新塭SS.602_DS | 602(TIE) DS | TIE | S32/69/600/DS2 |  |  |  | CDC | 272 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0E-01 |  | 1-3A | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE1_CB | 11KV TIE1 CB | TIE | S32/11/TIE1/CB |  |  |  | CDC | 273 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE1_51A | 11KV TIE1 51RY | TIE | S32/11/TIE1/51A |  |  |  | CDC | 274 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S32/11/TIE1/51NA |  |  |  | CDC | 275 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.750_CB | 750(#1MTR) CB | DTR | S32/69/750/CB |  |  |  | CDC | 276 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.1M_CB | 1M(#1MTR) CB | DTR | S32/11/M1/CB |  |  |  | CDC | 277 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_51A | #1MTR 51RY | DTR | S32/69/750/51A |  |  |  | CDC | 278 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_51NA | #1MTR 51N RY | DTR | S32/69/750/51NA |  |  |  | CDC | 279 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S32//1MTR/51ZA |  |  |  | CDC | 280 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_87A | #1MTR 87RY | DTR | S32//1MTR/87A/DI-SP |  |  |  | CDC | 281 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S32//1MTR/87UL |  |  |  | CDC | 282 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S32/11/M1/51A |  |  |  | CDC | 283 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_TRA | #1MTR 重故障 | DTR | S32//1MTR/TRA |  |  |  | CDC | 284 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S32//1MTR/TRF |  |  |  | CDC | 285 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S32//1MTR/SupLocal |  |  |  | CDC | 286 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S32//1MTR/Tap Chan |  |  |  | CDC | 287 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-37-00 | 1-37-01 | 1-2C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.751_DS | 751(#1MTR) DS | DTR | S32/69/750/DS1 |  |  |  | CDC | 288 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-37-02 | 1-37-03 | 1-2D | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.752_DS | 752(#1MTR) DS | DTR | S32/69/750/DS2 |  |  |  | CDC | 289 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_96A | #1MTR 96P RY | DTR | S32//1MTR/96PA |  |  |  | CDC | 290 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S32//1MTR/OLTC_DLY |  |  |  | CDC | 291 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S32//1MTR/AC_Fault |  |  |  | CDC | 292 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-45 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.760_CB | 760(#2MTR) CB | DTR | S32/69/760/CB |  |  |  | CDC | 293 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-02-00 |  | 1-46 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.2M_CB | 2M(#2MTR) CB | DTR | S32/11/M2/CB |  |  |  | CDC | 294 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_51A | #2MTR 51RY | DTR | S32/69/760/51A |  |  |  | CDC | 295 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_51NA | #2MTR 51N RY | DTR | S32/69/760/51NA |  |  |  | CDC | 296 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S32//2MTR/51ZA |  |  |  | CDC | 297 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_87A | #2MTR 87RY | DTR | S32//2MTR/87A |  |  |  | CDC | 298 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S32//2MTR/87UL |  |  |  | CDC | 299 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S32/11/M2/51A |  |  |  | CDC | 300 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_TRA | #2MTR 重故障 | DTR | S32//2MTR/TRA |  |  |  | CDC | 301 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S32//2MTR/TRF |  |  |  | CDC | 302 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S32//2MTR/SupLocal |  |  |  | CDC | 303 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S32//2MTR/Tap Chan |  |  |  | CDC | 304 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-37-04 | 1-37-05 | 1-2E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.761_DS | 761(#2MTR) DS | DTR | S32/69/760/DS1 |  |  |  | CDC | 305 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-37-06 | 1-37-07 | 1-2F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.762_DS | 762(#2MTR) DS | DTR | S32/69/760/DS2 |  |  |  | CDC | 306 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_96A | #2MTR 96P RY | DTR | S32//2MTR/96PA |  |  |  | CDC | 307 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S32//2MTR/OLTC_DLY |  |  |  | CDC | 308 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S32//2MTR/AC_Fault |  |  |  | CDC | 309 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0D-06 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_CB | 210(11KV #1SC) CB | SC | S32/11/210/CB |  |  |  | CDC | 310 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-11 |  | 1-3D | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S32/11/210/Tap Chan |  |  |  | CDC | 311 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_SCA | 11KV #1SC 51,51N RY | SC | S32/11/210/SCA |  |  |  | CDC | 312 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S32/11/210/UVA |  |  |  | CDC | 313 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-10-04 |  | 1-47 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_CB | 220(11KV #2SC) CB | SC | S32/11/220/CB |  |  |  | CDC | 314 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-11 |  | 1-4F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S32/11/220/Tap Chan |  |  |  | CDC | 315 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_SCA | 11KV #2SC 51,51N RY | SC | S32/11/220/SCA |  |  |  | CDC | 316 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S32/11/220/UVA |  |  |  | CDC | 317 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S32/69/1BUS/87A |  |  |  | CDC | 318 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-32-14 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 新塭SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER | S32/69/1BUS/87UL |  |  |  | CDC | 319 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S32/69/2BUS/87A |  |  |  | CDC | 320 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 692BUS | 69#2BUS |  | 87UL | [17 empty] | 1-32-15 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 新塭SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER | S32/69/2BUS/87UL |  |  |  | CDC | 321 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S32/11/ComPoint/CBA |  |  |  | CDC | 322 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S32/11/ComPoint/CBF |  |  |  | CDC | 323 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S32/69/ComPoint/ABS_89A |  |  |  | CDC | 324 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S32/69/ComPoint/CBA |  |  |  | CDC | 325 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S32/69/ComPoint/CBF |  |  |  | CDC | 326 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S32/0/RTU/RTU_R_L |  |  |  | CDC | 327 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S32 | 新塭SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.TEST_CB | TEST CB | OTHER | S32/0/RTU/Test_CB |  |  |  | CDC | 328 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.火災警報(1) | [新塭]火警 | OTHER | S32/0/StaDev/Fire |  |  |  | CDC | 329 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S32/0/StaDev/OPA |  |  |  | CDC | 330 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S32/0/StaDev/STUV |  |  |  | CDC | 331 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S32/0/StaDev/CHG1 |  |  |  | CDC | 332 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.直流電源DCA | 直流電源故障警報 | OTHER | S32/0/StaDev/DCA |  |  |  | CDC | 333 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S32/0/StaDev/DCE |  |  |  | CDC | 334 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S32/0/StaDev/OilLeak |  |  |  | CDC | 335 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-39-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S32/0/StaDev/OLTE |  |  |  | CDC | 336 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-39-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S32/0/StaDev/PCM |  |  |  | CDC | 337 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S32/0/StaDev/CHG2 |  |  |  | CDC | 338 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-39-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S32/0/StaDev/AC_Fault |  |  |  | CDC | 339 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.無人化門禁(1) | 保全(DOOR) | OTHER | S32/0/StaDev/Door1 |  |  |  | CDC | 340 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S32/0/StaDev/Door3 |  |  |  | CDC | 341 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S32 | 新塭SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-6E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.開關場照明(A) | 所內開關場照明 | OTHER | S32/0/StaDev/Lights1 |  |  |  | CDC | 342 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S32 | 新塭SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-6F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.開關場照明(B) | 路燈照明 | OTHER | S32/0/StaDev/Lights2 |  |  |  | CDC | 343 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S32 | 新塭SS | 0 |  | 1_MAIN | #1 |  | 51NA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER | S32/11/M1/51NA |  |  |  | CDC | 344 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2_MAIN | #2 |  | 51NA | [17 empty] | 1-02-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER | S32/11/M2/51NA |  |  |  | CDC | 345 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 主變火警 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.主變火警 | 主變火警 | OTHER | S32/0/StaDev/Fire1 |  |  |  | CDC | 346 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.安全監控 | 安全監控 | OTHER | S32/0/StaDev/Burglar |  |  |  | CDC | 347 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內其他重故障 | 所內其他重故障 | OTHER | S32/0/StaDev/PSA |  |  |  | CDC | 348 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內其他輕故障 | 所內其他輕故障 | OTHER | S32/0/StaDev/PSF |  |  |  | CDC | 349 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.門禁 | 大門側門 | OTHER | S32/0/StaDev/Door |  |  |  | CDC | 350 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  |  |  |  | 細水霧故障 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.細水霧故障 | 細水霧故障 | OTHER | S32/0/StaDev/1A5Other |  |  |  | CDC | 351 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 細水霧噴灑 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.細水霧噴灑 | 細水霧噴灑 | OTHER | S32/0/StaDev/2A5Other |  |  |  | CDC | 352 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.維護運轉警報 | 維護運轉警報 | OTHER | S32/0/StaDev/3A5Other |  |  |  | CDC | 353 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 11 | 11kV | _SC | _SC |  | 60A | [17 empty] | 1-33-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.11KV_SC_60A | 60RY | OTHER | S32/11/ComPoint/FDR_60A |  |  |  | CDC | 354 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | CO2火警 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.CO2火警 | CO2火警 | OTHER | S32/0/StaDev/Fire2 |  |  |  | CDC | 355 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | CO2故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.CO2故障 | CO2故障 | OTHER | S32/0/StaDev/CO2 |  |  |  | CDC | 356 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-34-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.水位警報(1) | 水位警報(1) | OTHER | S32/0/StaDev/Water1 |  |  |  | CDC | 357 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-34-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.水位警報(2) | 水位警報(2) | OTHER | S32/0/StaDev/Water2 |  |  |  | CDC | 358 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-31-08 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內電源ACBA | 所內電源故障警報 | OTHER | S32/0/StaDev/ACBA |  |  |  | CDC | 359 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S32//1MTR/63Q |  |  |  | CDC | 360 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S32//1MTR/96B1 |  |  |  | CDC | 361 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S32//1MTR/96B2 |  |  |  | CDC | 362 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S32//1MTR/96D |  |  |  | CDC | 363 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S32//1MTR/96P |  |  |  | CDC | 364 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S32//2MTR/63Q |  |  |  | CDC | 365 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S32//2MTR/96B1 |  |  |  | CDC | 366 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S32//2MTR/96B2 |  |  |  | CDC | 367 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S32//2MTR/96D |  |  |  | CDC | 368 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S32//2MTR/96P |  |  |  | CDC | 369 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內電源ACB1 | 所內電源ACB1S | OTHER | S32/0/StaDev/ACB1 |  |  |  | CDC | 370 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S32 | 新塭SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.所內電源ACB2 | 所內電源ACB2S | OTHER | S32/0/StaDev/ACB2 |  |  |  | CDC | 371 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S32 | 新塭SS | 0 |  | TIE | TIE |  | 600GDA(1) | [17 empty] | 1-05-01 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE | S32/69/600/GDA1 |  |  |  | CDC | 372 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | TIE | TIE |  | 600GDA(2) | [17 empty] | 1-05-03 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE | S32/69/600/GDA2 |  |  |  | CDC | 373 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | TIE | TIE |  | 600PHA(1) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600PHA(1) | 600(TIE) 67A(B1) | TIE | S32/69/600/PHA1 |  |  |  | CDC | 374 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | TIE | TIE |  | 600PHA(2) | [17 empty] | 1-05-02 | [7 empty] | 69KV_N | [8 empty] | 新塭SS.600PHA(2) | 600(TIE) 67A(B2) | TIE | S32/69/600/PHA2 |  |  |  | CDC | 375 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0E-04 |  | 1-43 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S32/11/M1/81A |  |  |  | CDC | 376 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-10-07 |  | 1-55 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S32//2MTR/81AS |  |  |  | CDC | 377 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-33-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S32/0/StaDev/4A5Other |  |  |  | CDC | 378 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-39-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S32/0/StaDev/R_Temp |  |  |  | CDC | 379 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-33-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.開關場水位警報 | 開關場水位警報 | OTHER | S32/0/StaDev/Water3 |  |  |  | CDC | 380 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S32/11/ComPoint/IRFA |  |  |  | CDC | 381 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭一線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭一線79LOA | 塭一線79LOA | OTHER | S32/11/JZ21/LOA |  |  |  | CDC | 382 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭七線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭七線79LOA | 塭七線79LOA | OTHER | S32/11/JZ27/LOA |  |  |  | CDC | 383 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭九線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭九線79LOA | 塭九線79LOA | OTHER | S32/11/JZ29/LOA |  |  |  | CDC | 384 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭二線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭二線79LOA | 塭二線79LOA | OTHER | S32/11/JZ22/LOA |  |  |  | CDC | 385 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭八線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭八線79LOA | 塭八線79LOA | OTHER | S32/11/JZ28/LOA |  |  |  | CDC | 386 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭十線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭十線79LOA | 塭十線79LOA | OTHER | S32/11/JZ30/LOA |  |  |  | CDC | 387 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭三線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭三線79LOA | 塭三線79LOA | OTHER | S32/11/JZ23/LOA |  |  |  | CDC | 388 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭五線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭五線79LOA | 塭五線79LOA | OTHER | S32/11/JZ25/LOA |  |  |  | CDC | 389 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭六線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭六線79LOA | 塭六線79LOA | OTHER | S32/11/JZ26/LOA |  |  |  | CDC | 390 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 塭四線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.塭四線79LOA | 塭四線79LOA | OTHER | S32/11/JZ24/LOA |  |  |  | CDC | 391 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S32/0/StaDev/Door2 |  |  |  | CDC | 392 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-3B-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.600_RYFA | 600 RYFA | OTHER | S32/69/600/RYFA |  |  |  | CDC | 393 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 161 | 161kV | 630 | 大寮新塭線(630) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 新塭SS.630_87A | 大寮新塭線(630) 87RY | LINE161 | S32/69/630/87A |  |  |  | CDC | 394 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 161 | 161kV | 630 | 大寮新塭線(630) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 新塭SS.630_87UL | 大寮新塭線(630) 87RY U/L | LINE161 | S32/69/630/87UL |  |  |  | CDC | 395 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 630 | 大寮新塭線(630) |  | CFA | [17 empty] | 1-32-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.630_CFA | 630 CFA | OTHER | S32/69/630/74A |  |  |  | CDC | 396 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 630 | 大寮新塭線(630) |  | RYFA | [17 empty] | 1-3B-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.630_RYFA | 630 RYFA | OTHER | S32/69/630/RYFA |  |  |  | CDC | 397 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 161 | 161kV | 640 | 新塭永華線(640) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 新塭SS.640_87A | 新塭永華線(640) 87RY | LINE161 | S32/69/640/87A |  |  |  | CDC | 398 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 161 | 161kV | 640 | 新塭永華線(640) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 新塭SS.640_87UL | 新塭永華線(640) 87RY U/L | LINE161 | S32/69/640/87UL |  |  |  | CDC | 399 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 640 | 新塭永華線(640) |  | CFA | [17 empty] | 1-32-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.640_CFA | 640 CFA | OTHER | S32/69/640/74A |  |  |  | CDC | 400 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 640 | 新塭永華線(640) |  | RYFA | [17 empty] | 1-3B-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.640_RYFA | 640 RYFA | OTHER | S32/69/640/RYFA |  |  |  | CDC | 401 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 691BUS | 69#1BUS |  | 27BA | [17 empty] | 1-32-08 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | S32/69/1BUS/5A5Other |  |  |  | CDC | 402 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 692BUS | 69#2BUS |  | 27BA | [17 empty] | 1-32-09 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER | S32/69/2BUS/5A5Other |  |  |  | CDC | 403 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | BUSRY | BUSRY |  | BF | [17 empty] | 1-32-10 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.BUSRY_BF | BUSRY BF | OTHER | S32//ComPoint/87A |  |  |  | CDC | 404 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | BUSRY | BUSRY |  | 87CTFA | [17 empty] | 1-32-11 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.BUSRY_CTFA | BUSRY CTFA | OTHER | S32//ComPoint/87CTFA |  |  |  | CDC | 405 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.PMA | POWER METER警報 | OTHER | S32/0/ComPoint/PMA |  |  |  | CDC | 406 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | 數據機重置 | [17 empty] | 1-15-03 |  | 1-56 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.數據機重置 | 數據機重置 | OTHER | S32/0/StaDev/6A5Other |  |  |  | CDC | 407 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | PHA | [17 empty] | 1-11-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_PHA | 23KV塭51線(JZ51) 相間RY | FEEDER | S32/22/JZ51/PHA |  |  |  | CDC | 408 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) |  | GDA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_GDA | 23KV塭51線(JZ51) 接地RY | FEEDER | S32/22/JZ51/GDA |  |  |  | CDC | 409 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_79UL | 23KV塭51線(JZ51) 79RY U/L | FEEDER | S32/22/JZ51/79UL |  |  |  | CDC | 410 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ51 | 塭51線(JZ51) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_ADJ | 23KV塭51線(JZ51) LCO分流器 U/L | FEEDER | S32/22/JZ51/ADJ |  |  |  | CDC | 411 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ51 | JZ51(23KV塭51線) |  | CB | [17 empty] | 1-11-00 |  | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_CB | JZ51(23KV塭51線) CB | FEEDER | S32/22/JZ51/CB |  |  |  | CDC | 412 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_PHA | 23KV塭52線(JZ52) 相間RY | FEEDER | S32/22/JZ52/PHA |  |  |  | CDC | 413 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_GDA | 23KV塭52線(JZ52) 接地RY | FEEDER | S32/22/JZ52/GDA |  |  |  | CDC | 414 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_79UL | 23KV塭52線(JZ52) 79RY U/L | FEEDER | S32/22/JZ52/79UL |  |  |  | CDC | 415 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ52 | 塭52線(JZ52) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_ADJ | 23KV塭52線(JZ52) LCO分流器 U/L | FEEDER | S32/22/JZ52/ADJ |  |  |  | CDC | 416 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ52 | JZ52(23KV塭52線) |  | CB | [17 empty] | 1-11-04 |  | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_CB | JZ52(23KV塭52線) CB | FEEDER | S32/22/JZ52/CB |  |  |  | CDC | 417 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | PHA | [17 empty] | 1-12-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_PHA | 23KV塭53線(JZ53) 相間RY | FEEDER | S32/22/JZ53/PHA |  |  |  | CDC | 418 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) |  | GDA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_GDA | 23KV塭53線(JZ53) 接地RY | FEEDER | S32/22/JZ53/GDA |  |  |  | CDC | 419 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) 79RY |  | 79UL | [17 empty] | 1-35-12 |  | 1-69 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_79UL | 23KV塭53線(JZ53) 79RY U/L | FEEDER | S32/22/JZ53/79UL |  |  |  | CDC | 420 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ53 | 塭53線(JZ53) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_ADJ | 23KV塭53線(JZ53) LCO分流器 U/L | FEEDER | S32/22/JZ53/ADJ |  |  |  | CDC | 421 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ53 | JZ53(23KV塭53線) |  | CB | [17 empty] | 1-12-00 |  | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_CB | JZ53(23KV塭53線) CB | FEEDER | S32/22/JZ53/CB |  |  |  | CDC | 422 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_PHA | 23KV塭54線(JZ54) 相間RY | FEEDER | S32/22/JZ54/PHA |  |  |  | CDC | 423 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_GDA | 23KV塭54線(JZ54) 接地RY | FEEDER | S32/22/JZ54/GDA |  |  |  | CDC | 424 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) 79RY |  | 79UL | [17 empty] | 1-35-13 |  | 1-6A | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_79UL | 23KV塭54線(JZ54) 79RY U/L | FEEDER | S32/22/JZ54/79UL |  |  |  | CDC | 425 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ54 | 塭54線(JZ54) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_ADJ | 23KV塭54線(JZ54) LCO分流器 U/L | FEEDER | S32/22/JZ54/ADJ |  |  |  | CDC | 426 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ54 | JZ54(23KV塭54線) |  | CB | [17 empty] | 1-12-04 |  | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_CB | JZ54(23KV塭54線) CB | FEEDER | S32/22/JZ54/CB |  |  |  | CDC | 427 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_PHA | 23KV塭55線(JZ55) 相間RY | FEEDER | S32/22/JZ55/PHA |  |  |  | CDC | 428 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_GDA | 23KV塭55線(JZ55) 接地RY | FEEDER | S32/22/JZ55/GDA |  |  |  | CDC | 429 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) 79RY |  | 79UL | [17 empty] | 1-35-14 |  | 1-6B | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_79UL | 23KV塭55線(JZ55) 79RY U/L | FEEDER | S32/22/JZ55/79UL |  |  |  | CDC | 430 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ55 | 塭55線(JZ55) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_ADJ | 23KV塭55線(JZ55) LCO分流器 U/L | FEEDER | S32/22/JZ55/ADJ |  |  |  | CDC | 431 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ55 | JZ55(23KV塭55線) |  | CB | [17 empty] | 1-13-00 |  | 1-60 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_CB | JZ55(23KV塭55線) CB | FEEDER | S32/22/JZ55/CB |  |  |  | CDC | 432 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | PHA | [17 empty] | 1-13-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_PHA | 23KV塭56線(JZ56) 相間RY | FEEDER | S32/22/JZ56/PHA |  |  |  | CDC | 433 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) |  | GDA | [17 empty] | 1-13-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_GDA | 23KV塭56線(JZ56) 接地RY | FEEDER | S32/22/JZ56/GDA |  |  |  | CDC | 434 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) 79RY |  | 79UL | [17 empty] | 1-35-15 |  | 1-6C | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_79UL | 23KV塭56線(JZ56) 79RY U/L | FEEDER | S32/22/JZ56/79UL |  |  |  | CDC | 435 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | JZ56 | 塭56線(JZ56) LCO分流器 |  | ADJ | [17 empty] | 1-36-15 |  | 1-7F | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_ADJ | 23KV塭56線(JZ56) LCO分流器 U/L | FEEDER | S32/22/JZ56/ADJ |  |  |  | CDC | 436 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S32 | 新塭SS | 22 | 22kV | JZ56 | JZ56(23KV塭56線) |  | CB | [17 empty] | 1-13-04 |  | 1-61 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_CB | JZ56(23KV塭56線) CB | FEEDER | S32/22/JZ56/CB |  |  |  | CDC | 437 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-14-06 |  | 1-62 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE3_CB | 23KV TIE3 CB | TIE | S32/22/TIE3/CB |  |  |  | CDC | 438 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-14-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE3_51A | 23KV TIE3 51RY | TIE | S32/22/TIE3/51A |  |  |  | CDC | 439 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-15-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE3_51NA | 23KV TIE3 51N RY | TIE | S32/22/TIE3/51NA |  |  |  | CDC | 440 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-04 |  | 1-57 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.770_CB | 770(#3MTR) CB | DTR | S32/69/770/CB |  |  |  | CDC | 441 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | M3A | M3A(#3MTR) |  | CB | [17 empty] | 1-03-04 |  | 1-58 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3A_CB | M3A(#3MTR) CB | DTR | S32/22/M3A/CB |  |  |  | CDC | 442 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | M3B | M3B(#3MTR) |  | CB | [17 empty] | 1-03-05 |  | 1-59 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3B_CB | M3B(#3MTR) CB | DTR | S32/22/M3B/CB |  |  |  | CDC | 443 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-02-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_51A | #3MTR 51RY | DTR | S32/69/770/51A |  |  |  | CDC | 444 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-02-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_51NA | #3MTR 51N RY | DTR | S32/22/M3/51NA |  |  |  | CDC | 445 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S32/22/M3/51ZA |  |  |  | CDC | 446 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_87A | #3MTR 87RY | DTR | S32/22/M3/87A |  |  |  | CDC | 447 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S32/22/M3/87UL |  |  |  | CDC | 448 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-03-03 |  | 1-6D | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S32/22/M3/81AS |  |  |  | CDC | 449 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  | M3A | #3MTR二次側(M3A) |  | 51A | [17 empty] | 1-03-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3A_51A | #3MTR二次側(M3A) 51RY | DTR | S32/22/M3A/51A |  |  |  | CDC | 450 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | M3B | #3MTR二次側(M3B) |  | 51A | [17 empty] | 1-04-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3B_51A | #3MTR二次側(M3B) 51RY | DTR | S32/22/M3B/51A |  |  |  | CDC | 451 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-34-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_TRA | #3MTR 重故障 | DTR | S32//3MTR/TRA |  |  |  | CDC | 452 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S32//3MTR/TRF |  |  |  | CDC | 453 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S32//3MTR/SupLocal |  |  |  | CDC | 454 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-02 |  | 1-64 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S32//3MTR/Tap Chan |  |  |  | CDC | 455 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-37-08 | 1-37-09 | 1-30 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.771_DS | 771(#3MTR) DS | DTR | S32/22/770/DS1 |  |  |  | CDC | 456 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-37-10 | 1-37-11 | 1-31 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.772_DS | 772(#3MTR) DS | DTR | S32/22/770/DS2 |  |  |  | CDC | 457 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-02-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_96A | #3MTR 96P RY | DTR | S32//3MTR/96PA |  |  |  | CDC | 458 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 410 | #3SC(410) |  | CB | [17 empty] | 1-14-00 |  | 1-5A | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_CB | 410(23KV #3SC) CB | SC | S32/22/410/CB |  |  |  | CDC | 459 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 410 | #3SC(410) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_SCA | 23KV #3SC 51,51N RY | SC | S32/22/410/SCA |  |  |  | CDC | 460 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 410 | #3SC(410) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_UVA | 23KV #3SC 27RY(欠壓) | SC | S32/22/410/UVA |  |  |  | CDC | 461 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 420 | #4SC(420) |  | CB | [17 empty] | 1-14-03 |  | 1-5B | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_CB | 420(23KV #4SC) CB | SC | S32/22/420/CB |  |  |  | CDC | 462 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 22 | 22kV | 420 | #4SC(420) |  | SCA | [17 empty] | 1-14-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_SCA | 23KV #4SC 51,51N RY | SC | S32/22/420/SCA |  |  |  | CDC | 463 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV | 420 | #4SC(420) |  | UVA | [17 empty] | 1-14-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_UVA | 23KV #4SC 27RY(欠壓) | SC | S32/22/420/UVA |  |  |  | CDC | 464 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV |  |  |  | CBA | [17 empty] | 1-3F-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.23KV_CBA | 23KV CGIS重故障 | OTHER | S32/22/CGIS/CBA |  |  |  | CDC | 465 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 22 | 22kV |  |  |  | CBF | [17 empty] | 1-3F-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.23KV_CBF | 23KV CGIS輕故障 | OTHER | S32/22/CGIS/CBF |  |  |  | CDC | 466 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #3MTR63Q | [17 empty] | 1-19-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR63Q | ULTC電驛動作 | OTHER | S32//3MTR/63Q |  |  |  | CDC | 467 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #3MTR96B1 | [17 empty] | 1-19-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR96B1 | 撲氣電驛警報 | OTHER | S32//3MTR/96B1 |  |  |  | CDC | 468 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #3MTR96B2 | [17 empty] | 1-19-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR96B2 | 撲氣電驛動作 | OTHER | S32//3MTR/96B2 |  |  |  | CDC | 469 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #3MTR96D | [17 empty] | 1-19-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR96D | 放壓電驛動作 | OTHER | S32//3MTR/96D |  |  |  | CDC | 470 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | #3MTR96P | [17 empty] | 1-19-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR96P | 突壓電驛動作 | OTHER | S32//3MTR/96P |  |  |  | CDC | 471 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-35-06 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_51ZS | #3MTR 51ZS | OTHER | S32//3MTR/51Z_UL |  |  |  | CDC | 472 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 81UL | [17 empty] | 1-35-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_81S | #3MTR 81S | OTHER | S32//3MTR/81UL |  |  |  | CDC | 473 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-03-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_86A | #3MTR 86A | OTHER | S32//3MTR/86A |  |  |  | CDC | 474 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 87UL1 | [17 empty] | 1-35-04 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_87T1S | #3MTR 87T1S | OTHER | S32//3MTR/87UL1 |  |  |  | CDC | 475 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | 3MTR | #3MTR |  | 87UL2 | [17 empty] | 1-35-05 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3MTR_87T2S | #3MTR 87T2S | OTHER | S32//3MTR/87UL2 |  |  |  | CDC | 476 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | M3A | #M3A |  | 51NA | [17 empty] | 1-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3A_51NA | #M3A 51NA | OTHER | S32/22/M3A/51NA |  |  |  | CDC | 477 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | M3A | #M3A |  | 81A | [17 empty] | 1-15-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3A_81A | #M3A 81A | OTHER | S32/22/M3A/81A |  |  |  | CDC | 478 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  | M3A | #M3A |  | 81UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3A_81S | #M3A 81S | OTHER | S32/22/M3A/81UL |  |  |  | CDC | 479 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 0 |  | M3B | #M3B |  | 51NA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3B_51NA | #M3B 51NA | OTHER | S32/22/M3B/51NA |  |  |  | CDC | 480 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  | M3B | #M3B |  | 81A | [17 empty] | 1-15-02 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3B_81A | #M3B 81A | OTHER | S32/22/M3B/81A |  |  |  | CDC | 481 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  | M3B | #M3B |  | 81UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS2_2 | [8 empty] | 新塭SS.#M3B_81S | #M3B 81S | OTHER | S32/22/M3B/81UL |  |  |  | CDC | 482 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S32 | 新塭SS | 22 | 22kV | CGIS | CGIS |  | 23KVIED重警報 | [17 empty] | 1-3F-00 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.23KVIED重警報 | 23KV CGIS IRFA | OTHER | S32/22/CGIS/IRFA |  |  |  | CDC | 483 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ51線79LOA | [17 empty] | 1-3E-10 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51線79LOA | JZ51線79LOA | OTHER | S32/22/JZ51/LOA |  |  |  | CDC | 484 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ51線81A | [17 empty] | 1-11-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51線81A | JZ51線81A | OTHER | S32/22/JZ51/81A |  |  |  | CDC | 485 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | JZ52線79LOA | [17 empty] | 1-3E-11 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52線79LOA | JZ52線79LOA | OTHER | S32/22/JZ52/LOA |  |  |  | CDC | 486 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ52線81A | [17 empty] | 1-11-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52線81A | JZ52線81A | OTHER | S32/22/JZ52/81A |  |  |  | CDC | 487 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | JZ53線79LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53線79LOA | JZ53線79LOA | OTHER | S32/22/JZ53/LOA |  |  |  | CDC | 488 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ53線81A | [17 empty] | 1-12-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53線81A | JZ53線81A | OTHER | S32/22/JZ53/81A |  |  |  | CDC | 489 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | JZ54線79LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54線79LOA | JZ54線79LOA | OTHER | S32/22/JZ54/LOA |  |  |  | CDC | 490 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ54線81A | [17 empty] | 1-12-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54線81A | JZ54線81A | OTHER | S32/22/JZ54/81A |  |  |  | CDC | 491 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | JZ55線79LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55線79LOA | JZ55線79LOA | OTHER | S32/22/JZ55/LOA |  |  |  | CDC | 492 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ55線81A | [17 empty] | 1-13-03 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55線81A | JZ55線81A | OTHER | S32/22/JZ55/81A |  |  |  | CDC | 493 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 0 |  |  |  |  | JZ56線79LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56線79LOA | JZ56線79LOA | OTHER | S32/22/JZ56/LOA |  |  |  | CDC | 494 | GENERICDIPoint | SS213_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S32 | 新塭SS | 0 |  |  |  |  | JZ56線81A | [17 empty] | 1-13-07 | [7 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56線81A | JZ56線81A | OTHER | S32/22/JZ56/81A |  |  |  | CDC | 495 | GENERICDIPoint | SS213_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S32 | 新塭SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 496 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 497 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 22 | 22kV | 410_SC | #3ASC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_SC_CAP | 23KV#3ASC 容量 | SC | [5 empty] | 498 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 22 | 22kV | 420_SC | #3BSC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_SC_CAP | 23KV#3BSC 容量 | SC | [5 empty] | 499 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 新塭SS.630LE | 630LE (非取樣點) | LINE69 | S32/69/630/LE0 |  |  |  |  | 500 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 630 | 大寮新塭線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 新塭SS.630BE | 630BE (非取樣點) | LINE69 | S32/69/630/BE0 |  |  |  |  | 501 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 新塭SS.640LE | 640LE (非取樣點) | LINE69 | S32/69/640/LE0 |  |  |  |  | 502 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 640 | 新塭永華線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 新塭SS.640BE | 640BE (非取樣點) | LINE69 | S32/69/640/BE0 |  |  |  |  | 503 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ21 | JZ21_DS |  | DS1 | JZ21_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_DS | JZ21_DS (非取樣點) | FEEDER | S32/11/JZ21/DS |  |  |  |  | 504 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ21 | JZ21_ES |  | LE0 | JZ21_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ21_ES | JZ21_ES (非取樣點) | FEEDER | S32/11/JZ21/ES |  |  |  |  | 505 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ22 | JZ22_DS |  | DS1 | JZ22_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_DS | JZ22_DS (非取樣點) | FEEDER | S32/11/JZ22/DS |  |  |  |  | 506 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ22 | JZ22_ES |  | LE0 | JZ22_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ22_ES | JZ22_ES (非取樣點) | FEEDER | S32/11/JZ22/ES |  |  |  |  | 507 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ23 | JZ23_DS |  | DS1 | JZ23_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_DS | JZ23_DS (非取樣點) | FEEDER | S32/11/JZ23/DS |  |  |  |  | 508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ23 | JZ23_ES |  | LE0 | JZ23_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ23_ES | JZ23_ES (非取樣點) | FEEDER | S32/11/JZ23/ES |  |  |  |  | 509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ24 | JZ24_DS |  | DS1 | JZ24_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_DS | JZ24_DS (非取樣點) | FEEDER | S32/11/JZ24/DS |  |  |  |  | 510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ24 | JZ24_ES |  | LE0 | JZ24_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ24_ES | JZ24_ES (非取樣點) | FEEDER | S32/11/JZ24/ES |  |  |  |  | 511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ25 | JZ25_DS |  | DS1 | JZ25_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_DS | JZ25_DS (非取樣點) | FEEDER | S32/11/JZ25/DS |  |  |  |  | 512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ25 | JZ25_ES |  | LE0 | JZ25_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ25_ES | JZ25_ES (非取樣點) | FEEDER | S32/11/JZ25/ES |  |  |  |  | 513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ26 | JZ26_DS |  | DS1 | JZ26_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_DS | JZ26_DS (非取樣點) | FEEDER | S32/11/JZ26/DS |  |  |  |  | 514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ26 | JZ26_ES |  | LE0 | JZ26_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ26_ES | JZ26_ES (非取樣點) | FEEDER | S32/11/JZ26/ES |  |  |  |  | 515 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ27 | JZ27_DS |  | DS1 | JZ27_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_DS | JZ27_DS (非取樣點) | FEEDER | S32/11/JZ27/DS |  |  |  |  | 516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ27 | JZ27_ES |  | LE0 | JZ27_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ27_ES | JZ27_ES (非取樣點) | FEEDER | S32/11/JZ27/ES |  |  |  |  | 517 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ28 | JZ28_DS |  | DS1 | JZ28_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_DS | JZ28_DS (非取樣點) | FEEDER | S32/11/JZ28/DS |  |  |  |  | 518 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ28 | JZ28_ES |  | LE0 | JZ28_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ28_ES | JZ28_ES (非取樣點) | FEEDER | S32/11/JZ28/ES |  |  |  |  | 519 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ29 | JZ29_DS |  | DS1 | JZ29_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_DS | JZ29_DS (非取樣點) | FEEDER | S32/11/JZ29/DS |  |  |  |  | 520 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ29 | JZ29_ES |  | LE0 | JZ29_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ29_ES | JZ29_ES (非取樣點) | FEEDER | S32/11/JZ29/ES |  |  |  |  | 521 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ30 | JZ30_DS |  | DS1 | JZ30_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_DS | JZ30_DS (非取樣點) | FEEDER | S32/11/JZ30/DS |  |  |  |  | 522 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ30 | JZ30_ES |  | LE0 | JZ30_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ30_ES | JZ30_ES (非取樣點) | FEEDER | S32/11/JZ30/ES |  |  |  |  | 523 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 新塭SS.601E | 601E (非取樣點) | TIE | S32/69/600/E1 |  |  |  |  | 524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 新塭SS.602E | 602E (非取樣點) | TIE | S32/69/600/E2 |  |  |  |  | 525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S32/11/TIE1/DS |  |  |  |  | 526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.750TE | 750TE (非取樣點) | DTR | S32/69/750/TE0 |  |  |  |  | 527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.750BE | 750BE (非取樣點) | DTR | S32/69/750/BE0 |  |  |  |  | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.1M_DS | 1M_DS (非取樣點) | DTR | S32/11/M1/DS |  |  |  |  | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.1M_ES | 1M_ES (非取樣點) | DTR | S32/11/M1/ES |  |  |  |  | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.760TE | 760TE (非取樣點) | DTR | S32/69/760/TE0 |  |  |  |  | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.760BE | 760BE (非取樣點) | DTR | S32/69/760/BE0 |  |  |  |  | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.2M_DS | 2M_DS (非取樣點) | DTR | S32/11/M2/DS |  |  |  |  | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.2M_ES | 2M_ES (非取樣點) | DTR | S32/11/M2/ES |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.210_ES | 210_ES (非取樣點) | SC | S32/11/210/ES |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.211DS | 211DS (非取樣點) | SC | S32/11/210/D1 |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.212DS | 212DS (非取樣點) | SC | S32/11/210/D2 |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.220_ES | 220_ES (非取樣點) | SC | S32/11/220/ES |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.221DS | 221DS (非取樣點) | SC | S32/11/220/D1 |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.222DS | 222DS (非取樣點) | SC | S32/11/220/D2 |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 新塭SS.69B1E | 69B1E (非取樣點) | BUS | S32/69/1BUS/BE1 |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 新塭SS.69B2E | 69B2E (非取樣點) | BUS | S32/69/2BUS/BE2 |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 543 | NotelDIPoint | [38 empty] | START/STOP | STOP
S32 | 新塭SS | 0 |  | JZ51 | JZ51_DS |  | DS1 | JZ51_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_DS | JZ51_DS (非取樣點) | FEEDER | S32/22/JZ51/DS |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ51 | JZ51_ES |  | LE0 | JZ51_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ51_ES | JZ51_ES (非取樣點) | FEEDER | S32/22/JZ51/ES |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ52 | JZ52_DS |  | DS1 | JZ52_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_DS | JZ52_DS (非取樣點) | FEEDER | S32/22/JZ52/DS |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ52 | JZ52_ES |  | LE0 | JZ52_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ52_ES | JZ52_ES (非取樣點) | FEEDER | S32/22/JZ52/ES |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ53 | JZ53_DS |  | DS1 | JZ53_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_DS | JZ53_DS (非取樣點) | FEEDER | S32/22/JZ53/DS |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ53 | JZ53_ES |  | LE0 | JZ53_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ53_ES | JZ53_ES (非取樣點) | FEEDER | S32/22/JZ53/ES |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ54 | JZ54_DS |  | DS1 | JZ54_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_DS | JZ54_DS (非取樣點) | FEEDER | S32/22/JZ54/DS |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ54 | JZ54_ES |  | LE0 | JZ54_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ54_ES | JZ54_ES (非取樣點) | FEEDER | S32/22/JZ54/ES |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ55 | JZ55_DS |  | DS1 | JZ55_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_DS | JZ55_DS (非取樣點) | FEEDER | S32/22/JZ55/DS |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ55 | JZ55_ES |  | LE0 | JZ55_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ55_ES | JZ55_ES (非取樣點) | FEEDER | S32/22/JZ55/ES |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | JZ56 | JZ56_DS |  | DS1 | JZ56_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_DS | JZ56_DS (非取樣點) | FEEDER | S32/22/JZ56/DS |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | JZ56 | JZ56_ES |  | LE0 | JZ56_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.JZ56_ES | JZ56_ES (非取樣點) | FEEDER | S32/22/JZ56/ES |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S32/22/TIE3/DS |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.770TE | 770TE (非取樣點) | DTR | S32/22/770/TE0 |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.770BE | 770BE (非取樣點) | DTR | S32/22/770/BE0 |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | M3A | M3A_DS |  | DS1 | M3A_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3A_DS | M3A_DS (非取樣點) | DTR | S32/22/M3A/DS |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | M3B | M3B_DS |  | DS1 | M3B_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3B_DS | M3B_DS (非取樣點) | DTR | S32/22/M3B/DS |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | M3A | M3A_ES |  | LE0 | M3A_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3A_ES | M3A_ES (非取樣點) | DTR | S32/22/M3A/ES |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | M3B | M3B_ES |  | LE0 | M3B_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.M3B_ES | M3B_ES (非取樣點) | DTR | S32/22/M3B/ES |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 410 | #3SC(410) |  | LE0 | 410_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.410_ES | 410_ES (非取樣點) | SC | S32/22/410/ES |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 411DS | 411DS |  | 411DS | 411DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.411DS | 411DS (非取樣點) | SC | S32/22/410/D1 |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 412DS | 412DS |  | 412DS | 412DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.412DS | 412DS (非取樣點) | SC | S32/22/410/D2 |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 420 | #4SC(420) |  | LE0 | 420_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.420_ES | 420_ES (非取樣點) | SC | S32/22/420/ES |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 421DS | 421DS |  | 421DS | 421DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.421DS | 421DS (非取樣點) | SC | S32/22/420/D1 |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 422DS | 422DS |  | 422DS | 422DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.422DS | 422DS (非取樣點) | SC | S32/22/420/D2 |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | TIE3 | TIE3_ES |  | LE0 | TIE3_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.TIE3_ES | TIE3_ES (非取樣點) | TIE | S32/22/TIE3/ES |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | 3ABUS | #3ABUS_ES |  | ABUS0 | #3ABUS_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3ABUS_ES | #3ABUS_ES (非取樣點) | OTHER | S32/22/3ABUS/ES |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | 3BBUS | #3BBUS_ES |  | BBUS0 | #3BBUS_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.#3BBUS_ES | #3BBUS_ES (非取樣點) | OTHER | S32/22/3BBUS/ES |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S32 | 新塭SS | 0 |  | BR-3 | BR-3_DS |  | DS1 | BR-3_DS | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.BR-3_DS | BR-3_DS (非取樣點) | OTHER | S32/22/BR3/DS |  |  |  |  | 572 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S32 | 新塭SS | 0 |  | BR-3 | BR-3_ES |  | LE0 | BR-3_ES | [24 empty] | DDCS2_2 | [8 empty] | 新塭SS.BR-3_ES | BR-3_ES (非取樣點) | OTHER | S32/22/BR3/ES |  |  |  |  | 573 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo