## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S33 | 東石SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS | KV | 69KV 一號 BUS PT R相 | kV_-90_90(-2000_2000) | aaa | B2/S33_A1 | [8 empty] | 東石SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S33 | 東石SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV＃2BUS | KV | 69KV 二號 BUS PT R相 | kV_-90_90(-2000_2000) | aab | B2/S33_A1 | [8 empty] | 東石SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S33 | 東石SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0017 |  |  | 1-91 |  |  | ＃1 MCB | KV | 一號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aaa | B2/S33_D1 | [8 empty] | 東石SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S33 | 東石SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0094 |  |  | 1-DE |  |  | ＃2 MCB | KV | 二號主變二次側BUS 11KV | kV_-9_9(-2000_2000) | aba | B2/S33_D1 | [8 empty] | 東石SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S33 | 東石SS | 69 | 69kV | 69B1E | 69B1E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aaaz | B2/S33_A1 | [8 empty] | 東石SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0256 |  |  | 1-31-13 |  |  | 69KV BUS#1 衡相監視警報 | R11 PL-[3-2] |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-04-05 |  |  | 69KV ＃1BUS 87 B1A | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0497 |  | 0015 | 1-32-14 |  | 1-0E | 87 B1S (#1 匯流排 87S) | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#1BUS_87UL | 69#1BUS 87RY U/L | BUS |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 69B2E | 69B2E |  | BE2 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BUS | [13 empty] | aaaz | B2/S33_A1 | [8 empty] | 東石SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-31-14 |  |  | 69KV BUS#2 衡相監視警報 | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-04-06 |  |  | 69KV ＃2BUS 87 B2A | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0498 |  | 0016 | 1-32-15 |  | 1-0F | 87 B2S (#2 匯流排 87S) | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.69#2BUS_87UL | 69#2BUS 87RY U/L | BUS |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 630 | MW | 東石朴子線有效電力 | MW_-96_96(-2000_2000) |  | B2/S33_A1 | [8 empty] | 東石SS.630_MW | 東石朴子線 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 630 | MVAR | 東石朴子線無效電力 | MVAR_-96_96(-2000_2000) |  | B2/S33_A1 | [8 empty] | 東石SS.630_MVAR | 東石朴子線 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 東石朴子線 (630) MWH(+) |  |  |  |  | B2/S33_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 640 | MW | 水林東石線有效電力 | MW_-96_96(-2000_2000) |  | B2/S33_A1 | [8 empty] | 東石SS.640_MW | 水林東石線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 640 | MVAR | 水林東石線無效電力 | MVAR_-96_96(-2000_2000) |  | B2/S33_A1 | [8 empty] | 東石SS.640_MVAR | 水林東石線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 水林東石線 (640) MWH(+) |  |  |  |  | B2/S33_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | LINE 1(630) PHA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_PHA | 東石朴子線(630) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | LINE 1(630) GDA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_GDA | 東石朴子線(630) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | LINE1(630) 87A | R11 PL-[1-2] |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_87A | 東石朴子線(630) 87RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0484 |  |  | 1-32-01 |  |  | 東石朴子線(630) CFA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_CFA | 東石朴子線(630) 通訊故障 | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | LINE 2(640) PHA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_PHA | 水林東石線(640) 相間RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | LINE 2(640) GDA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_GDA | 水林東石線(640) 接地RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | LINE 2(640) 87A | R11 PL-[1-2] |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_87A | 水林東石線(640) 87RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0486 |  |  | 1-32-03 |  |  | 水林東石線(640) CFA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_CFA | 水林東石線(640) 通訊故障 | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  | 0010 | 1-32-00 |  | 1-09 | 東石朴子線(630) 87S U/L | R11 PL-[3-2] |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_87UL | 東石朴子線(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0485 |  | 0011 | 1-32-02 |  | 1-0A | 水林東石線(640) 87S U/L | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_87UL | 水林東石線(640) 87RY U/L | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S33S31/T1 |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | LINE1(630) CB ON/OFF (52AS) | LINE1 CB BOX |  |  | aaba | B2/S33_A1 | [8 empty] | 東石SS.630_CB | 630(東石朴子線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S13S33/T2 |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | LINE 2(640) CB ON/OFF (52AS) | LINE2 CB BOX |  |  | aaea | B2/S33_A1 | [8 empty] | 東石SS.640_CB | 640(水林東石線) CB | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | DS1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0579 | 580 | 0017 | 1-38-00 | 1-38-01 | 1-10 | 東石朴子線 631 ABS ON | LINE 1 CB BOX |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.631_DS | 631(東石朴子線) DS | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | DS2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0581 | 582 | 0018 | 1-38-02 | 1-38-03 | 1-11 | 東石朴子線 632 ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.632_DS | 632(東石朴子線) DS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0587 | 588 | 0021 | 1-38-08 | 1-38-09 | 1-14 | 水林東石線 641 ABS ON | LINE 1 CB BOX |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.641_DS | 641(水林東石線) DS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0589 | 590 | 0022 | 1-38-10 | 1-38-11 | 1-15 | 水林東石線 642 ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.642_DS | 642(水林東石線) DS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | DS3 | 633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0583 | 584 | 0019 | 1-38-04 | 1-38-05 | 1-12 | 東石朴子線 633 ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.633_DS | 633(東石朴子線) DS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | E3 | 633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0585 | 586 | 0020 | 1-38-06 | 1-38-07 | 1-13 | 東石朴子線 633E ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.633E_ES | 633E(東石朴子線) ES | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 38 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 39 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0591 | 592 | 0023 | 1-38-12 | 1-38-13 | 1-16 | 水林東石線 643 ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.643_DS | 643(水林東石線) DS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | E3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0593 | 594 | 0024 | 1-38-14 | 1-38-15 | 1-17 | 水林東石線 643E ABS ON | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.643E_ES | 643E(水林東石線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-00 |  |  | JL21 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL21_PHA | 11KV石一線(JL21) 相間RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-01 |  |  | JL21 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL21_GDA | 11KV石一線(JL21) 接地RY | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0505 |  | 0063 | 1-33-06 |  | 1-3E | JL21 79S (復閉電驛使用/閉鎖) | BR-3-[4-1] |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL21_79UL | 11KV石一線(JL21) 79RY U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0548 |  | 0114 | 1-36-01 |  | 1-71 | JL21 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL21_ADJ | 11KV石一線(JL21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-03 |  |  | JL22 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL22_PHA | 11KV石二線(JL22) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-04 |  |  | JL22 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL22_GDA | 11KV石二線(JL22) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0506 |  | 0064 | 1-33-07 |  | 1-3F | JL22 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL22_79UL | 11KV石二線(JL22) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0549 |  | 0115 | 1-36-02 |  | 1-72 | JL22 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL22_ADJ | 11KV石二線(JL22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0C-06 |  |  | JL23 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL23_PHA | 11KV石三線(JL23) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | JL23 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL23_GDA | 11KV石三線(JL23) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0507 |  | 0065 | 1-33-08 |  | 1-40 | JL23 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL23_79UL | 11KV石三線(JL23) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0550 |  | 0116 | 1-36-03 |  | 1-73 | JL23 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL23_ADJ | 11KV石三線(JL23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JL24 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL24_PHA | 11KV石四線(JL24) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JL24 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL24_GDA | 11KV石四線(JL24) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0508 |  | 0066 | 1-33-09 |  | 1-41 | JL24 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL24_79UL | 11KV石四線(JL24) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0551 |  | 0117 | 1-36-04 |  | 1-74 | JL24 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL24_ADJ | 11KV石四線(JL24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JL25 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL25_PHA | 11KV石五線(JL25) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JL25 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL25_GDA | 11KV石五線(JL25) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0509 |  | 0067 | 1-33-10 |  | 1-42 | JL25 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL25_79UL | 11KV石五線(JL25) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0552 |  | 0118 | 1-36-05 |  | 1-75 | JL25 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL25_ADJ | 11KV石五線(JL25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-04 |  |  | JL26 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL26_PHA | 11KV石六線(JL26) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-11-05 |  |  | JL26 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL26_GDA | 11KV石六線(JL26) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0537 |  | 0101 | 1-35-06 |  | 1-64 | JL26 79S (復閉電驛使用/閉鎖) | BR-3-[6-2] |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL26_79UL | 11KV石六線(JL26) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0558 |  | 0124 | 1-36-11 |  | 1-7B | JL26 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL26_ADJ | 11KV石六線(JL26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-11-07 |  |  | JL27 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL27_PHA | 11KV石七線(JL27) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-00 |  |  | JL27 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL27_GDA | 11KV石七線(JL27) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0102 | 1-35-07 |  | 1-65 | JL27 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL27_79UL | 11KV石七線(JL27) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0559 |  | 0125 | 1-36-12 |  | 1-7C | JL27 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL27_ADJ | 11KV石七線(JL27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | JL28 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL28_PHA | 11KV石八線(JL28) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-03 |  |  | JL28 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL28_GDA | 11KV石八線(JL28) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0103 | 1-35-08 |  | 1-66 | JL28 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL28_79UL | 11KV石八線(JL28) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0560 |  | 0126 | 1-36-13 |  | 1-7D | JL28 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL28_ADJ | 11KV石八線(JL28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-12-05 |  |  | JL29 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL29_PHA | 11KV石九線(JL29) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-12-06 |  |  | JL29 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL29_GDA | 11KV石九線(JL29) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0540 |  | 0104 | 1-35-09 |  | 1-67 | JL29 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL29_79UL | 11KV石九線(JL29) 79RY U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0561 |  | 0127 | 1-36-14 |  | 1-7E | JL29 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL29_ADJ | 11KV石九線(JL29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | JL30 FCB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL30_PHA | 11KV石十線(JL30) 相間RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | JL30 FCB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL30_GDA | 11KV石十線(JL30) 接地RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0541 |  | 0105 | 1-35-10 |  | 1-68 | JL30 79S (復閉電驛使用/閉鎖) | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL30_79UL | 11KV石十線(JL30) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0562 |  | 0128 | 1-36-15 |  | 1-7F | JL30 LCO ADJ U/L |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.JL30_ADJ | 11KV石十線(JL30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JL21/T1 |  |  | 0098 |  | 0054 | 1-0B-07 |  | 1-35 | JL21 FCB 52AS | BR-3-[4-3] |  |  | aabb | B2/S33_D1 | [8 empty] | 東石SS.JL21_CB | JL21(11KV石一線) CB | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL21_DS | JL21_DS (非取樣點) | FEEDER | [5 empty] | 85 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | ES | JL21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL21_ES | JL21_ES (非取樣點) | FEEDER | [5 empty] | 86 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JL22/T1 |  |  | 0101 |  | 0055 | 1-0C-02 |  | 1-36 | JL22 FCB 52AS | " |  |  | aacb | B2/S33_D1 | [8 empty] | 東石SS.JL22_CB | JL22(11KV石二線) CB | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL22_DS | JL22_DS (非取樣點) | FEEDER | [5 empty] | 88 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | ES | JL22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL22_ES | JL22_ES (非取樣點) | FEEDER | [5 empty] | 89 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JL23/T1 |  |  | 0104 |  | 0056 | 1-0C-05 |  | 1-37 | JL23 FCB 52AS | " |  |  | aadb | B2/S33_D1 | [8 empty] | 東石SS.JL23_CB | JL23(11KV石三線) CB | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL23_DS | JL23_DS (非取樣點) | FEEDER | [5 empty] | 91 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | ES | JL23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL23_ES | JL23_ES (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JL24/T1 |  |  | 0107 |  | 0057 | 1-0D-00 |  | 1-38 | JL24 FCB 52AS | " |  |  | aafb | B2/S33_D1 | [8 empty] | 東石SS.JL24_CB | JL24(11KV石四線) CB | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL24_DS | JL24_DS (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | ES | JL24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL24_ES | JL24_ES (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/JL25/T1 |  |  | 0110 |  | 0058 | 1-0D-03 |  | 1-39 | JL25 FCB 52AS | " |  |  | aagb | B2/S33_D1 | [8 empty] | 東石SS.JL25_CB | JL25(11KV石五線) CB | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL25_DS | JL25_DS (非取樣點) | FEEDER | [5 empty] | 97 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | ES | JL25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL25_ES | JL25_ES (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JL26/T1 |  |  | 0142 |  | 0093 | 1-11-03 |  | 1-5C | JL26 FCB 52AS | BR-3-[6-1] |  |  | aagb | B2/S33_D1 | [8 empty] | 東石SS.JL26_CB | JL26(11KV石六線) CB | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL26_DS | JL26_DS (非取樣點) | FEEDER | [5 empty] | 100 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | ES | JL26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL26_ES | JL26_ES (非取樣點) | FEEDER | [5 empty] | 101 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JL27/T1 |  |  | 0145 |  | 0094 | 1-11-06 |  | 1-5D | JL27 FCB 52AS | " |  |  | abcb | B2/S33_D1 | [8 empty] | 東石SS.JL27_CB | JL27(11KV石七線) CB | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL27_DS | JL27_DS (非取樣點) | FEEDER | [5 empty] | 103 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | ES | JL27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL27_ES | JL27_ES (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JL28/T1 |  |  | 0148 |  | 0095 | 1-12-01 |  | 1-5E | JL28 FCB 52AS | " |  |  | abdb | B2/S33_D1 | [8 empty] | 東石SS.JL28_CB | JL28(11KV石八線) CB | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL28_DS | JL28_DS (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | ES | JL28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL28_ES | JL28_ES (非取樣點) | FEEDER | [5 empty] | 107 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JL29/T1 |  |  | 0151 |  | 0096 | 1-12-04 |  | 1-5F | JL29 FCB 52AS | " |  |  | abeb | B2/S33_D1 | [8 empty] | 東石SS.JL29_CB | JL29(11KV石九線) CB | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL29_DS | JL29_DS (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | ES | JL29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL29_ES | JL29_ES (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/JL30/T1 |  |  | 0154 |  | 0097 | 1-12-07 |  | 1-60 | JL30 FCB 52AS | " |  |  | abfb | B2/S33_D1 | [8 empty] | 東石SS.JL30_CB | JL30(11KV石十線) CB | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL30_DS | JL30_DS (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | ES | JL30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.JL30_ES | JL30_ES (非取樣點) | FEEDER | [5 empty] | 113 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 600 | A | TIE 600 R 相電流 | A_-1200_1200(-2000_2000) |  | B2/S33_A1 | [8 empty] | 東石SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 114 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | ＃1 TIE | A1 | 一號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 115 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | ＃1 TIE | A2 | 一號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 116 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | ＃1 TIE | A3 | 一號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 117 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0037 |  | 0008 | 1-04-02 |  | 1-07 | TIE (600) CB ON/OFF(52AS) | 600 CB BOX |  |  | aafz | B2/S33_A1 | [8 empty] | 東石SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 118 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-03 |  |  | TIE (600) CB PHA | R11 PL-[1-3] |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600_51A | 69KV TIE(600) 51RY | TIE |  |  |  |  | CDC | 119 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-04 |  |  | TIE (600) CB GDA | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600_51NA | 69KV TIE(600) 51N RY | TIE |  |  |  |  | CDC | 120 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2BUS |  |  | 0116 |  | 0059 | 1-0E-01 |  | 1-3A | #1 TIE CB 52AS | " |  |  | zzzz | B2/S33_D1 | [8 empty] | 東石SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 121 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | #1 TIE CB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 122 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | #1 TIE CB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 123 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0627 | 628 | 0043 | 1-3B-00 | 1-3B-01 | 1-2A | 600 TIE 1AS (601) | 600 CB BOX |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 124 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0629 | 630 | 0044 | 1-3B-02 | 1-3B-03 | 1-2B | 600 TIE 2AS (602) | " |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 125 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.601E | 601E (非取樣點) | TIE | [5 empty] | 126 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_A1 | [8 empty] | 東石SS.602E | 602E (非取樣點) | TIE | [5 empty] | 127 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 128 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | ＃1 MTR | MW | 一號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 129 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | ＃1 MTR | MVAR | 一號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 130 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | ＃1 MTR | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 131 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | ＃1 MTR | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 132 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | ＃1 MTR | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 133 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | ＃2 MTR | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 134 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | ＃2 MTR | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 135 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | ＃2 MTR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 136 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | ＃2 MTR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 137 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | ＃2 MTR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 138 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | ＃1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 139 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | ＃1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 140 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0020 |  | 0060 | 1-94 |  | 1-3B | ＃1 MTR | TAP | 一號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 141 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S33 | 東石SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1MTR MWH(+) |  |  |  |  | B1/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 142 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1MTR MVARH(+) |  |  |  |  | B1/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 143 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | ＃2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 144 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | ＃2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 145 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0058 |  | 0079 | 1-BA |  | 1-4E | ＃2 MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 146 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S33 | 東石SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #2 MTR MWH(+) |  |  |  |  | B1/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 147 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #2 MTR MVARH(+) |  |  |  |  | B1/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 148 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0004 |  | 0051 | 1-00-01 |  | 1-32 | 750CB ON/OFF(52AS) | 750 CB BOX |  |  | aacb | B3/S33_D1 | [8 empty] | 東石SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 149 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S33_D1 | [8 empty] | 東石SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 150 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S33_D1 | [8 empty] | 東石SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 151 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0013 |  | 0069 | 1-01-02 |  | 1-44 | 760CB ON/OFF(52AS) | 760 CB BOX |  |  | aadb | B3/S33_D1 | [8 empty] | 東石SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 152 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S33_D1 | [8 empty] | 東石SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 153 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S33_D1 | [8 empty] | 東石SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 154 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0010 |  | 0052 | 1-00-07 |  | 1-33 | #1 MAIN CB ON/OFF(52AS) | BR-3-[4-3] |  |  | aaea | B2/S33_D1 | [8 empty] | 東石SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 155 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | T/2MTR |  |  | 0031 |  | 0090 | 1-03-04 |  | 1-59 | #2 MCB ON/OFF(52AS) | BR-3-[6-1] |  |  | abba | B2/S33_D1 | [8 empty] | 東石SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 156 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-02 |  |  | 750CB PHA | R11 PL-[1-1] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 157 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | 750CB GDA | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 158 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | #1 MTR 51ZA | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 159 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | #1 MTR 87A | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 160 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-33-03 |  |  | #1 MTR 87 LS U/L | R11 PL-[2-1] |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 161 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | M1 | #1MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  | 0068 | 1-0E-04 |  | 1-43 | #1 81A |  |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 162 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-03 |  |  | 760CB PHA | R11 PL-[1-1] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 163 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-04 |  |  | 760CB GDA | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 164 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | #2 MTR 51ZA | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 165 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | #2 MTR 87A | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 166 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-34-03 |  |  | #2 MTR 87 LS U/L | R11 PL-[2-1] |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 167 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | M2 | #2MTR |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  | 0087 | 1-11-02 |  | 1-56 | #2 81A |  |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR |  |  |  |  | CDC | 168 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | #1 MAIN CB PHA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 169 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0499 |  |  | 1-33-00 |  |  | #1 MTR 重故障(1TRA) | " |  |  | a | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 170 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-33-01 |  |  | #1 MTR 輕故障(1TRF) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 171 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0503 |  |  | 1-33-04 |  |  | #1 MTR OLTC S/L(中心/現場) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 172 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S33 | 東石SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0504 |  | 0061 | 1-33-05 |  | 1-3C | #1 MTR OLTC A/M(手動/自動) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 173 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | #2 MCB PHA | BR-3-[6-1] |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 174 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0515 |  |  | 1-34-00 |  |  | #2 MTR 重故障(2TRA) | R11 PL-[2-1] |  |  | a | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 175 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0516 |  |  | 1-34-01 |  |  | #2 MTR 輕故障(2TRF) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 176 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-34-04 |  |  | #2 MTR OLTC S/L(中心/現場) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 177 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S33 | 東石SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0080 | 1-34-05 |  | 1-4F | #2 MTR OLTC A/M(手動/自動) | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 178 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0563 | 564 | 0045 | 1-37-00 | 1-37-01 | 1-2C | #1MTR(751) 1AS | 750 CB BOX |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 179 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0565 | 566 | 0046 | 1-37-02 | 1-37-03 | 1-2D | #1MTR(752) 2AS | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 180 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0567 | 568 | 0047 | 1-37-04 | 1-37-05 | 1-2E | #2MTR(761) 1AS | 760 CB BOX |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 181 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0569 | 570 | 0048 | 1-37-06 | 1-37-07 | 1-2F | #2MTR(762) 2AS | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 182 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | 1M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 183 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 184 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | #1 MTR 96PA | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-33-02 |  |  | #1 MTR OLTC遲滯警報(148T) |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 186 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-33-15 |  |  | #1MTR AC電源欠壓 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 187 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 188 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 189 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | #2 MTR 96PA | " |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 190 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-34-02 |  |  | #2 MTR OLTC遲滯警報(248T) |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 191 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0527 |  |  | 1-34-12 |  |  | #2 MTR AC電源欠壓 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 192 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0113 |  | 0053 | 1-0D-06 |  | 1-34 | #1 11KV SC CB 52AS | BR-3-[4-4] |  |  | aaab | B2/S33_D1 | [8 empty] | 東石SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 193 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0510 |  | 0062 | 1-33-11 |  | 1-3D | #1 SC Q-CTL A/M | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 194 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 195 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | C/2SC |  |  | 0157 |  | 0092 | 1-13-02 |  | 1-5B | #2 11KV SC CB 52AS | " |  |  | abgb | B2/S33_D1 | [8 empty] | 東石SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 196 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0542 |  | 0100 | 1-35-11 |  | 1-63 | #2 SC Q-CTL A/M | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 197 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 198 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | #1 11KV SC CB SCA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 199 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | #1 11KV SC CB UVA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 200 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | #2 11KV SC CB SCA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 201 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | #2 11KV SC CB UVA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 202 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 203 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | D2 | 212DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.212DS | 212DS (非取樣點) | SC | [5 empty] | 204 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 205 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | D2 | 222DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S33_D1 | [8 empty] | 東石SS.222DS | 222DS (非取樣點) | SC | [5 empty] | 206 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 207 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 208 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 209 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 210 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪AI 轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 211 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪AI轉換卡檢查參考點1800 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 212 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0227 |  | 0001 | 1-30-00 |  | 1-00 | TEST_CB |  |  |  |  | ELEM/ALL | [8 empty] | 東石SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 213 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0228 |  |  | 1-30-01 |  |  | LOCAL/REMOTE (STATUS) |  |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 214 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-30-02 |  |  | 直流充電機故障(變電設備用) | R11 PL-[3-2] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 215 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-36-00 |  |  | 充電機-通信專用 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 216 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0231 |  |  | 1-30-04 |  |  | DC接地故障(DCE) | R11 PL-[3-2] |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 217 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-30-08 |  |  | 所內用電警報(STUV) | R11 PL-[2-1] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 218 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0236 |  |  | 1-30-09 |  |  | 油壓電力電纜警報 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 219 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0237 |  |  | 1-30-10 |  |  | 一般火警 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.火災警報(1) | [東石]火警 | OTHER |  |  |  |  | CDC | 220 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0241 |  |  | 1-30-14 |  |  | 配電盤DC-NFB跳脫警報 | R11 PL-[1-3] |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 221 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0242 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 222 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0245 |  |  | 1-31-02 |  |  | 無人化防盜警報(1) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 223 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0246 |  |  | 1-31-03 |  |  | 無人化防盜警報(2) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 224 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0247 |  |  | 1-31-04 |  |  | 無人化防盜警報(3) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化防盜(3) | 無人化防盜(3) | OTHER |  |  |  |  | CDC | 225 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0248 |  |  | 1-31-05 |  |  | 保全總機(DOOR) 無人化門禁(1) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化門禁(1) | 保全(DOOR) | OTHER |  |  |  |  | CDC | 226 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0249 |  |  | 1-31-06 |  |  | 開關場水位二段 無人化門禁(2) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化門禁(2) | 開關場水位二段警報 | OTHER |  |  |  |  | CDC | 227 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0250 |  |  | 1-31-07 |  |  | 無人化門禁警報(3) |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 228 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S33 | 東石SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0252 |  |  | 1-31-09 |  |  | 69KV CB 輕故障警報 CBF | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 229 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 1-31-10 |  |  | 69KV CB 重故障警報 CBA | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 230 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0254 |  |  | 1-31-11 |  |  | 11KV CB 輕故障警報 | BR-3-[4-1] |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 231 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-31-12 |  |  | 11KV CB 重故障警報 | " |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 232 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-31-15 |  |  | 69KV ABS NFB跳脫警報 89A |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 233 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-35-13 |  |  | 通訊設備AC故障 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 234 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0545 |  |  | 1-35-14 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 235 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊PCM警報 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0546 |  |  | 1-35-15 |  |  | 博碼調變器故障 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 236 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0233 |  | 0110 | 1-30-06 |  | 1-6D | 所內照明 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 237 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0234 |  | 0111 | 1-30-07 |  | 1-6E | 路燈照明 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 238 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | #1 MAIN CB GDA | " |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER |  |  |  |  | CDC | 239 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-03-07 |  |  | SPARE |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER |  |  |  |  | CDC | 240 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0232 |  |  | 1-30-05 |  |  | 門禁 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 241 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0238 |  |  | 1-30-11 |  |  | 所內安全監控 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 242 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | PSF | 所內其他輕故障 | Element | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0239 |  |  | 1-30-12 |  |  | 所內其他輕故障警報 |  |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.所內其他輕故障 | 所內其他輕故障 | OTHER |  |  |  |  | CDC | 243 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | PSA | 所內其他重故障 | Element | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0240 |  |  | 1-30-13 |  |  | 所內其他重故障警報 |  |  |  |  | ELEM/S33_D1 | [8 empty] | 東石SS.所內其他重故障 | 所內其他重故障 | OTHER |  |  |  |  | CDC | 244 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | CO2 |  | Element | Status | CO2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0243 |  |  | 1-31-00 |  |  | CO2系統火警(FIRE) | 火警授信總機 |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.CO2故障 | CO2故障 | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Fire2 | CO2火警 | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0244 |  |  | 1-31-01 |  |  | CO2系統故障 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.CO2火警 | CO2火警 | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-31-08 |  |  | 所內電源警報(ACBA) | R11 PL-[3-2] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  | Element | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0495 |  |  | 1-32-12 |  |  | ACB 1S (#1 所內電源) | R11 PL-[2-1] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.所內電源ACB1 | 所內電源ACB1S | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  | Element | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0496 |  |  | 1-32-13 |  |  | ACB 2S (#2 所內電源) | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.所內電源ACB2 | 所內電源ACB2S | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 維護運轉警報 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0578 |  |  | 1-37-15 |  |  | 維護運轉警報 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 數據機重置 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0162 |  | 0088 | 1-13-07 |  | 1-57 | Modem Reset |  |  |  |  | B3/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 251 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0511 |  |  | 1-33-12 |  |  | SC 60A | R11 PL-[1-3] |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.11KV_SC_60A | 60RY | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報(1) | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0529 |  |  | 1-34-14 |  |  | 水位警報 1 | 水位警示箱 |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.水位警報(1) | 水位警報(1) | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報(2) | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0530 |  |  | 1-34-15 |  |  | 水位警報 2 | " |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.水位警報(2) | 水位警報(2) | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-00 |  |  | 196B1 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-01 |  |  | 196B2 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-02 |  |  | 196D |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-03 |  |  | 196P |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-04 |  |  | 163Q |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-18-05 |  |  | 296B1 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-18-06 |  |  | 296B2 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-18-07 |  |  | 296D |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-00 |  |  | 296P |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-01 |  |  | 263Q |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 264 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | TIE (600) CB 67(1A) |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600PHA(1) | 600(TIE) 67A(B1) | TIE |  |  |  |  | CDC | 265 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | TIE (600) CB 67N(1A) |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE |  |  |  |  | CDC | 266 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-02 |  |  | TIE (600) CB 67(2A) |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600PHA(2) | 600(TIE) 67A(B2) | TIE |  |  |  |  | CDC | 267 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-03 |  |  | TIE (600) CB 67N(2A) |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE |  |  |  |  | CDC | 268 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 石一線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石一線KVAR | 11KV石一線 KVAR | FEEDER |  |  |  |  | CDC | 269 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 石一線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石一線A1 | 11KV石一線 R相AMP | FEEDER |  |  |  |  | CDC | 270 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 石一線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石一線A2 | 11KV石一線 S相AMP | FEEDER |  |  |  |  | CDC | 271 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 石一線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石一線A3 | 11KV石一線 T相AMP | FEEDER |  |  |  |  | CDC | 272 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 石一線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石一線A0 | 11KV石一線 N相AMP | FEEDER |  |  |  |  | CDC | 273 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 石七線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石七線KVAR | 11KV石七線 KVAR | FEEDER |  |  |  |  | CDC | 274 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 石七線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石七線A1 | 11KV石七線 R相AMP | FEEDER |  |  |  |  | CDC | 275 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 石七線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石七線A2 | 11KV石七線 S相AMP | FEEDER |  |  |  |  | CDC | 276 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 石七線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石七線A3 | 11KV石七線 T相AMP | FEEDER |  |  |  |  | CDC | 277 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 石七線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石七線A0 | 11KV石七線 N相AMP | FEEDER |  |  |  |  | CDC | 278 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 石九線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石九線KVAR | 11KV石九線 KVAR | FEEDER |  |  |  |  | CDC | 279 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 石九線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石九線A1 | 11KV石九線 R相AMP | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 石九線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石九線A2 | 11KV石九線 S相AMP | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 石九線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石九線A3 | 11KV石九線 T相AMP | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 石九線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石九線A0 | 11KV石九線 N相AMP | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 石二線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石二線KVAR | 11KV石二線 KVAR | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 石二線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石二線A1 | 11KV石二線 R相AMP | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 石二線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石二線A2 | 11KV石二線 S相AMP | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 石二線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石二線A3 | 11KV石二線 T相AMP | FEEDER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 石二線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石二線A0 | 11KV石二線 N相AMP | FEEDER |  |  |  |  | CDC | 288 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 石八線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石八線KVAR | 11KV石八線 KVAR | FEEDER |  |  |  |  | CDC | 289 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 石八線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石八線A1 | 11KV石八線 R相AMP | FEEDER |  |  |  |  | CDC | 290 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 石八線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石八線A2 | 11KV石八線 S相AMP | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 石八線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石八線A3 | 11KV石八線 T相AMP | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 石八線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石八線A0 | 11KV石八線 N相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 石十線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石十線KVAR | 11KV石十線 KVAR | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 石十線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石十線A1 | 11KV石十線 R相AMP | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 石十線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石十線A2 | 11KV石十線 S相AMP | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 石十線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石十線A3 | 11KV石十線 T相AMP | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 石十線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石十線A0 | 11KV石十線 N相AMP | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 石三線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石三線KVAR | 11KV石三線 KVAR | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 石三線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石三線A1 | 11KV石三線 R相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 石三線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石三線A2 | 11KV石三線 S相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 石三線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石三線A3 | 11KV石三線 T相AMP | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 石三線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石三線A0 | 11KV石三線 N相AMP | FEEDER |  |  |  |  | CDC | 303 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 石五線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石五線KVAR | 11KV石五線 KVAR | FEEDER |  |  |  |  | CDC | 304 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 石五線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石五線A1 | 11KV石五線 R相AMP | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 石五線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石五線A2 | 11KV石五線 S相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 石五線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石五線A3 | 11KV石五線 T相AMP | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 石五線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石五線A0 | 11KV石五線 N相AMP | FEEDER |  |  |  |  | CDC | 308 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 石六線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石六線KVAR | 11KV石六線 KVAR | FEEDER |  |  |  |  | CDC | 309 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 石六線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石六線A1 | 11KV石六線 R相AMP | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 石六線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石六線A2 | 11KV石六線 S相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 石六線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石六線A3 | 11KV石六線 T相AMP | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 石六線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石六線A0 | 11KV石六線 N相AMP | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 石四線 | VAR | KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石四線KVAR | 11KV石四線 KVAR | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 石四線 | A1 | R相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石四線A1 | 11KV石四線 R相AMP | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 石四線 | A2 | S相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石四線A2 | 11KV石四線 S相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 石四線 | A3 | T相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石四線A3 | 11KV石四線 T相AMP | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 石四線 | N | N相電流 | A_-500_500(-2000_2000) |  | B2/S33_D1 | [8 empty] | 東石SS.石四線A0 | 11KV石四線 N相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 充電機 | DC-V | 配電盤"MAIN"NFB電壓 | DCVolt_-150_150(-2000_2000) |  | B3/S33_D1 | [8 empty] | 東石SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 319 | GENERICAIPoint | SS214_L2 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 5AOther | 路燈電源監視 | INSERT | [12 empty] | 0513 |  |  | 1-33-14 |  |  | 路燈電源監視 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 320 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊室溫度異常 | INSERT | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0528 |  |  | 1-34-13 |  |  | 通訊溫度異常 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | [5 empty] | 321 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | StaDev | 所內設施 |  | Water3 | 開關場水位警報 | INSERT | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0512 |  |  | 1-33-13 |  |  | 開關場水位警報 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 322 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0051 |  |  | 1-06-00 |  |  | 630 RYFA L1 |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.630_RYFA | 630 東石朴子線IED警報 | OTHER | [5 empty] | 323 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0052 |  |  | 1-06-01 |  |  | 640 RYFA L2 |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.640_RYFA | 640 水林東石線IED警報 | OTHER | [5 empty] | 324 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KVIED重警報 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0674 |  |  | 1-3F-15 |  |  | 11KV IED 重警報 |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.11KVIED重警報 | 11KVIED重警報 | OTHER | [5 empty] | 325 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0643 |  |  | 1-3E-00 |  |  | JL21 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石一線79LOA | 石一線79LOA | OTHER | [5 empty] | 326 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0649 |  |  | 1-3E-06 |  |  | JL27 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石七線79LOA | 石七線79LOA | OTHER | [5 empty] | 327 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0651 |  |  | 1-3E-08 |  |  | JL29 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石九線79LOA | 石九線79LOA | OTHER | [5 empty] | 328 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0644 |  |  | 1-3E-01 |  |  | JL22 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石二線79LOA | 石二線79LOA | OTHER | [5 empty] | 329 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0650 |  |  | 1-3E-07 |  |  | JL28 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石八線79LOA | 石八線79LOA | OTHER | [5 empty] | 330 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0652 |  |  | 1-3E-09 |  |  | JL30 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石十線79LOA | 石十線79LOA | OTHER | [5 empty] | 331 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0645 |  |  | 1-3E-02 |  |  | JL23 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石三線79LOA | 石三線79LOA | OTHER | [5 empty] | 332 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0647 |  |  | 1-3E-04 |  |  | JL25 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石五線79LOA | 石五線79LOA | OTHER | [5 empty] | 333 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0648 |  |  | 1-3E-05 |  |  | JL26 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石六線79LOA | 石六線79LOA | OTHER | [5 empty] | 334 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0646 |  |  | 1-3E-03 |  |  | JL24 79LOA |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.石四線79LOA | 石四線79LOA | OTHER | [5 empty] | 335 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | 600 |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0058 |  |  | 1-06-07 |  |  | 600 RYFA |  |  |  |  | B2/S33_A1 | [8 empty] | 東石SS.600_RYFA | 600 RYFA | OTHER | [5 empty] | 336 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-00 |  |  | #1MTR 86A |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR-86A | #1MTR-86A | OTHER | [5 empty] | 337 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-3A-02 |  |  | #1MTR 51ZS |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_51ZS | #1MTR 51ZS | OTHER | [5 empty] | 338 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-3A-00 |  |  | #1MTR 87S2 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_87UL2 | #1MTR 87UL2 | OTHER | [5 empty] | 339 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS |  |  | 1MTR | #1MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-3A-01 |  |  | #1MTR RYFA |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#1MTR_RYFA | #1MTR IED警報 | OTHER | [5 empty] | 340 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-01 |  |  | #2MTR 86A |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR-86A | #2MTR-86A | OTHER | [5 empty] | 341 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-3A-06 |  |  | #2MTR 51ZS |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_51ZS | #2MTR 51ZS | OTHER | [5 empty] | 342 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-3A-04 |  |  | #2MTR 87S2 |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_87UL2 | #2MTR 87UL2 | OTHER | [5 empty] | 343 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS |  |  | 2MTR | #2MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-3A-05 |  |  | #2MTR RYFA |  |  |  |  | B1/S33_D1 | [8 empty] | 東石SS.#2MTR_RYFA | #2MTR IED警報 | OTHER | [5 empty] | 344 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0163 |  | 0107 | 1-14-00 |  | 1-6A | #1MTR 181S |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.#1M_81UL | #1M 81UL | OTHER | [5 empty] | 345 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | M2 | #2MTR(M2) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0164 |  | 0108 | 1-14-01 |  | 1-6B | #2MTR 281S |  |  |  |  | B2/S33_D1 | [8 empty] | 東石SS.#2M_81UL | #2M 81UL | OTHER | [5 empty] | 346 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S33 | 東石SS |  |  | BUSRY | BUSRY |  | BFA | 請TPC確認 | INSERT | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0493 |  |  | 1-32-10 |  |  | 69KV BUS RY 87BF | " | [12 empty] | 東石SS.BUSRY_BF | BUSRY BF | OTHER | [5 empty] | 347 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS |  |  | BUSRY | BUSRY |  | 87CTFA | 請TPC確認 | INSERT | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0494 |  |  | 1-32-11 |  |  | 69KV BUS RY CTFA | " | [12 empty] | 東石SS.BUSRY_CTFA | BUSRY CTFA | OTHER | [5 empty] | 348 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0673 |  |  | 1-3F-14 |  |  | PMA |  |  |  |  | B3/S33_D1 | [8 empty] | 東石SS.PMA | POWER METER警報 | OTHER | [5 empty] | 349 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | JL21 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | JL21 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 350 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL22 | JL22 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | JL22 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 351 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL23 | JL23 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | JL23 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 352 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL24 | JL24 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | JL24 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 353 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL25 | JL25 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | JL25 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 354 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL26 | JL26 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | JL26 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 355 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL27 | JL27 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | JL27 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 356 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL28 | JL28 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | JL28 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 357 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL29 | JL29 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | JL29 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 358 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S33 | 東石SS | 11 | 11kV | JL30 | JL30 |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | JL30 KWH(+) |  |  |  |  | B2/S33_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 359 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S33 | 東石SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S33_D1 | [12 empty] | 東石SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S33/69/1BUS/V; OPRD2: S33/69/2BUS/V
S33 | 東石SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S33_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S33/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S33 | 東石SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S33_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S33/11/M1/MW; OPRD2: S33/11/M2/MW; OPRD3: S33/69/630/MW; OPRD4: S33/69/640/MW
S33 | 東石SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S33_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S33/0/CalcPoint/OPRN2_MW
S33 | 東石SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S33_D1 | [17 empty] | none
S33 | 東石SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S33_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S33/0/CalcPoint/OPRN1; OPRD2: S33/0/CalcPoint/OPRN2; OPRD3: S33/0/CalcPoint/PRFL_UL
S33 | 東石SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S33_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S33/11/M1/MW; OPRD2: S33/11/M1/MVAR; OPRD3: S33/0/CalcPoint/Vbs2
S33 | 東石SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S33_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S33/11/M2/MW; OPRD2: S33/11/M2/MVAR; OPRD3: S33/0/CalcPoint/Vbs2
S33 | 東石SS | 69 | 69kV | 630 | 東石～朴子線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S33_A1 | [12 empty] | 東石SS.630_AMP | 東石朴子線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S33/69/630/MW; OPRD2: S33/69/630/MVAR; OPRD3: S33/0/CalcPoint/Vbs2
S33 | 東石SS | 69 | 69kV | 640 | 水林～東石線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S33_A1 | [12 empty] | 東石SS.640_AMP | 水林東石線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S33/69/640/MW; OPRD2: S33/69/640/MVAR; OPRD3: S33/0/CalcPoint/Vbs2
S33 | 東石SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S33_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S33/11/1BUS/V
S33 | 東石SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S33_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S33/11/2BUS/V
S33 | 東石SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S33_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 東石SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S33/11/M1/MW; OPRD2: S33/11/M1/MVAR
S33 | 東石SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S33_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 東石SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S33/11/M2/MW; OPRD2: S33/11/M2/MVAR
S33 | 東石SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S33_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S33//1MTR/MVA; OPRD2: 0
S33 | 東石SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S33_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S33//2MTR/MVA; OPRD2: 0
S33 | 東石SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S33_D1 | [12 empty] | 東石SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S33/11/M1/MW; OPRD2: S33/11/M1/MVAR
S33 | 東石SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S33_D1 | [12 empty] | 東石SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S33/11/M2/MW; OPRD2: S33/11/M2/MVAR
S33 | 東石SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S33_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S33//1MTR/SupLocal; OPRD2: S33//1MTR/Tap Chan; OPRD3: NULL
S33 | 東石SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S33_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S33//2MTR/SupLocal; OPRD2: S33//2MTR/Tap Chan; OPRD3: NULL
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/1BUS/V; OPRD2: S33/11/JL21/I_R; OPRD3: S33/11/JL21/I_S; OPRD4: S33/11/JL21/I_T
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/1BUS/V; OPRD2: S33/11/JL22/I_R; OPRD3: S33/11/JL22/I_S; OPRD4: S33/11/JL22/I_T
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/1BUS/V; OPRD2: S33/11/JL23/I_R; OPRD3: S33/11/JL23/I_S; OPRD4: S33/11/JL23/I_T
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/1BUS/V; OPRD2: S33/11/JL24/I_R; OPRD3: S33/11/JL24/I_S; OPRD4: S33/11/JL24/I_T
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/1BUS/V; OPRD2: S33/11/JL25/I_R; OPRD3: S33/11/JL25/I_S; OPRD4: S33/11/JL25/I_T
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/2BUS/V; OPRD2: S33/11/JL26/I_R; OPRD3: S33/11/JL26/I_S; OPRD4: S33/11/JL26/I_T
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/2BUS/V; OPRD2: S33/11/JL27/I_R; OPRD3: S33/11/JL27/I_S; OPRD4: S33/11/JL27/I_T
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/2BUS/V; OPRD2: S33/11/JL28/I_R; OPRD3: S33/11/JL28/I_S; OPRD4: S33/11/JL28/I_T
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/2BUS/V; OPRD2: S33/11/JL29/I_R; OPRD3: S33/11/JL29/I_S; OPRD4: S33/11/JL29/I_T
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S33/11/2BUS/V; OPRD2: S33/11/JL30/I_R; OPRD3: S33/11/JL30/I_S; OPRD4: S33/11/JL30/I_T
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL21/kVA; OPRD2: S33/11/JL21/KVAR
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL22/kVA; OPRD2: S33/11/JL22/KVAR
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL23/kVA; OPRD2: S33/11/JL23/KVAR
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL24/kVA; OPRD2: S33/11/JL24/KVAR
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL25/kVA; OPRD2: S33/11/JL25/KVAR
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL26/kVA; OPRD2: S33/11/JL26/KVAR
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL27/kVA; OPRD2: S33/11/JL27/KVAR
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL28/kVA; OPRD2: S33/11/JL28/KVAR
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL29/kVA; OPRD2: S33/11/JL29/KVAR
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S33_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S33/11/JL30/kVA; OPRD2: S33/11/JL30/KVAR
S33 | 東石SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S33_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S33/11/M1/MW; OPRD2: S33/11/M2/MW
S33 | 東石SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S33_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S33/11/M1/MVAR; OPRD2: S33/11/M2/MVAR
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S33_D1 | [12 empty] | 東石SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S33/11/210/CB; OPRD2: 6.9; OPRD3: 0
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S33_D1 | [12 empty] | 東石SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S33/11/220/CB; OPRD2: 6.9; OPRD3: 0
S33 | 東石SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S33_D1 | [12 empty] | 東石SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_18 | OPRD1: S33//1MTR/96B1; OPRD2: S33//1MTR/96PA; OPRD3: S33//1MTR/TRA; OPRD4: S33//1MTR/63Q; OPRD5: S33//1MTR/96D; OPRD6: S33//1MTR/96B2; OPRD7: S33//1MTR/87A; OPRD8: S33//1MTR/51ZA; OPRD9: S33//2MTR/96B1; OPRD10: S33//2MTR/63Q; OPRD11: S33//2MTR/96D; OPRD12: S33//2MTR/96B2; OPRD13: S33//2MTR/96PA; OPRD14: S33//2MTR/51ZA; OPRD15: S33//2MTR/TRA; OPRD16: S33//2MTR/87A; OPRD17: S33/69/1BUS/87A; OPRD18: S33/69/2BUS/87A
S33 | 東石SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S33_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S33//1MTR/TRF; OPRD2: S33//2MTR/TRF
S33 | 東石SS | 11 | 11kV | M1_A1 | #1MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/11/M1/81A
S33 | 東石SS | 11 | 11kV | M2_A1 | #2MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/11/M2/81A
S33 | 東石SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/0/RTU/RTU_R_L
S33 | 東石SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/0/StaDev/DCE
S33 | 東石SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/0/StaDev/DCA
S33 | 東石SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S33_D1 | [17 empty] | lamp2CC | OPRD1: S33/69/ComPoint/CBF
S33 | 東石SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S33_D1 | [17 empty] | lamp2CC | OPRD1: S33/69/ComPoint/CBA
S33 | 東石SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S33_D1 | [17 empty] | lamp2CC | OPRD1: S33/69/ComPoint/ABS_89A
S33 | 東石SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/0/StaDev/PSF
S33 | 東石SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S33_A1 | [17 empty] | lamp2CC | OPRD1: S33/0/StaDev/PSA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S33 | 東石SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 東石SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S33/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 東石SS.630_AMP | 東石朴子線 AMP | LINE69 | S33/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 東石SS.640_AMP | 水林東石線 AMP | LINE69 | S33/69/640/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S33 | 東石SS | 0 |  |  |  |  | 石一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石一線KVA | 11KV石一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石一線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石一線KW | 11KV石一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石七線KVA | 11KV石七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石七線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石七線KW | 11KV石七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石九線KVA | 11KV石九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石九線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石九線KW | 11KV石九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石二線KVA | 11KV石二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石二線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石二線KW | 11KV石二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石八線KVA | 11KV石八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石八線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石八線KW | 11KV石八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石十線KVA | 11KV石十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石十線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石十線KW | 11KV石十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石三線KVA | 11KV石三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石三線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石三線KW | 11KV石三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石五線KVA | 11KV石五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石五線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石五線KW | 11KV石五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石六線KVA | 11KV石六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石六線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石六線KW | 11KV石六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石四線KVA | 11KV石四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  |  |  |  | 石四線KW | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.石四線KW | 11KV石四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S33//1MTR/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_PF | #1MTR 功率因素 | DTR | S33//1MTR/PF |  | RPDC_PF_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S33//2MTR/MVA |  | MVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_PF | #2MTR 功率因素 | DTR | S33//2MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S33 | 東石SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S33/11/210/MVAR |  | SC_CAL_11 |  |  | 29 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S33/11/220/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 69 | 69kV | 630_CB | 東石朴子線(630_CB) | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.630_CB_2 | 630(東石朴子線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 31 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 640_CB | 水林東石線(640_CB) | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.640_CB_2 | 640(水林東石線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 32 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 600_CB | 600(600_CB) | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.600_CB_2 | 600 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 33 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 東石SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 34 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 東石SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 35 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 東石SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 36 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S33 | 東石SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 東石SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 37 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 東石SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S33/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 38 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 39 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 40 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630_AMP | 東石朴子線 | [27 empty] | ADCS_N | [8 empty] | 東石SS.630_AMP_A | 東石朴子線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 41 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 69 | 69kV | 630_AMP | 東石朴子線 | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.630_AMP_2 | 東石朴子線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 42 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 69 | 69kV | 640_AMP | 水林東石線 | [27 empty] | ADCS_N | [8 empty] | 東石SS.640_AMP_A | 水林東石線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 43 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 69 | 69kV | 640_AMP | 水林東石線 | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.640_AMP_2 | 水林東石線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 44 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 45 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S33 | 東石SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 東石SS.630_RYFA_A | 630 東石朴子線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 49 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 640_RYFA | 640 | [27 empty] | ADCS_N | [8 empty] | 東石SS.640_RYFA_A | 640 水林東石線IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 50 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 600_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 東石SS.600_RYFA_A | 600 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 51 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | BUSRY_BF | BUSRY | [27 empty] | ADCS_N | [8 empty] | 東石SS.BUSRY_BF_A | BUSRY BF (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 52 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | BUSRY_CTFA | BUSRY | [27 empty] | ADCS_N | [8 empty] | 東石SS.BUSRY_CTFA_A | BUSRY CTFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 53 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 691BUS_27BA | 69#1BUS | [27 empty] | ADCS_N | [8 empty] | 東石SS.69#1BUS_27BA_A | 69#1BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 692BUS_27BA | 69#2BUS | [27 empty] | ADCS_N | [8 empty] | 東石SS.69#2BUS_27BA_A | 69#2BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S33/0/RTU/ADCH1 |  |  |  | CDC | 56 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S33/0/RTU/ADCH2 |  |  |  | CDC | 57 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S33/0/RTU/ADCH3 |  |  |  | CDC | 58 | GENERICAIPoint | SS214_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S33/0/RTU/ADCL1 |  |  |  | CDC | 59 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S33/0/RTU/ADCL2 |  |  |  | CDC | 60 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S33/0/RTU/ADCL3 |  |  |  | CDC | 61 | GENERICAIPoint | SS214_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S33 | 東石SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S33/69/1BUS/V |  |  |  | CDC | 62 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S33 | 東石SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S33/69/2BUS/V |  |  |  | CDC | 63 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S33 | 東石SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-91 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S33/11/1BUS/V |  |  |  | CDC | 64 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S33 | 東石SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-DE | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S33/11/2BUS/V |  |  |  | CDC | 65 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.630_MW | 東石朴子線 MW | LINE69 | S33/69/630/MW |  |  |  | CDC | 66 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.630_MVAR | 東石朴子線 MVAR | LINE69 | S33/69/630/MVAR |  |  |  | CDC | 67 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.640_MW | 水林東石線 MW | LINE69 | S33/69/640/MW |  |  |  | CDC | 68 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.640_MVAR | 水林東石線 MVAR | LINE69 | S33/69/640/MVAR |  |  |  | CDC | 69 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石一線 | 石一線 |  | 石一線KVAR | [17 empty] | 1-9A | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石一線KVAR | 11KV石一線 KVAR | FEEDER | S33/11/JL21/KVAR |  |  |  | CDC | 70 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石一線 | 石一線 |  | 石一線A1 | [17 empty] | 1-9B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石一線A1 | 11KV石一線 R相AMP | FEEDER | S33/11/JL21/I_R |  |  |  | CDC | 71 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石一線 | 石一線 |  | 石一線A2 | [17 empty] | 1-9C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石一線A2 | 11KV石一線 S相AMP | FEEDER | S33/11/JL21/I_S |  |  |  | CDC | 72 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石一線 | 石一線 |  | 石一線A3 | [17 empty] | 1-9D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石一線A3 | 11KV石一線 T相AMP | FEEDER | S33/11/JL21/I_T |  |  |  | CDC | 73 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石一線 | 石一線 |  | 石一線A0 | [17 empty] | 1-9E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石一線A0 | 11KV石一線 N相AMP | FEEDER | S33/11/JL21/I_N |  |  |  | CDC | 74 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石七線 | 石七線 |  | 石七線KVAR | [17 empty] | 1-EC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石七線KVAR | 11KV石七線 KVAR | FEEDER | S33/11/JL27/KVAR |  |  |  | CDC | 75 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石七線 | 石七線 |  | 石七線A1 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石七線A1 | 11KV石七線 R相AMP | FEEDER | S33/11/JL27/I_R |  |  |  | CDC | 76 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石七線 | 石七線 |  | 石七線A2 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石七線A2 | 11KV石七線 S相AMP | FEEDER | S33/11/JL27/I_S |  |  |  | CDC | 77 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石七線 | 石七線 |  | 石七線A3 | [17 empty] | 1-EF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石七線A3 | 11KV石七線 T相AMP | FEEDER | S33/11/JL27/I_T |  |  |  | CDC | 78 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石七線 | 石七線 |  | 石七線A0 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石七線A0 | 11KV石七線 N相AMP | FEEDER | S33/11/JL27/I_N |  |  |  | CDC | 79 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石九線 | 石九線 |  | 石九線KVAR | [17 empty] | 1-F6 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石九線KVAR | 11KV石九線 KVAR | FEEDER | S33/11/JL29/KVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石九線 | 石九線 |  | 石九線A1 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石九線A1 | 11KV石九線 R相AMP | FEEDER | S33/11/JL29/I_R |  |  |  | CDC | 81 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石九線 | 石九線 |  | 石九線A2 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石九線A2 | 11KV石九線 S相AMP | FEEDER | S33/11/JL29/I_S |  |  |  | CDC | 82 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石九線 | 石九線 |  | 石九線A3 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石九線A3 | 11KV石九線 T相AMP | FEEDER | S33/11/JL29/I_T |  |  |  | CDC | 83 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石九線 | 石九線 |  | 石九線A0 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石九線A0 | 11KV石九線 N相AMP | FEEDER | S33/11/JL29/I_N |  |  |  | CDC | 84 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石二線 | 石二線 |  | 石二線KVAR | [17 empty] | 1-9F | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石二線KVAR | 11KV石二線 KVAR | FEEDER | S33/11/JL22/KVAR |  |  |  | CDC | 85 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石二線 | 石二線 |  | 石二線A1 | [17 empty] | 1-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石二線A1 | 11KV石二線 R相AMP | FEEDER | S33/11/JL22/I_R |  |  |  | CDC | 86 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石二線 | 石二線 |  | 石二線A2 | [17 empty] | 1-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石二線A2 | 11KV石二線 S相AMP | FEEDER | S33/11/JL22/I_S |  |  |  | CDC | 87 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石二線 | 石二線 |  | 石二線A3 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石二線A3 | 11KV石二線 T相AMP | FEEDER | S33/11/JL22/I_T |  |  |  | CDC | 88 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石二線 | 石二線 |  | 石二線A0 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石二線A0 | 11KV石二線 N相AMP | FEEDER | S33/11/JL22/I_N |  |  |  | CDC | 89 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石八線 | 石八線 |  | 石八線KVAR | [17 empty] | 1-F1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石八線KVAR | 11KV石八線 KVAR | FEEDER | S33/11/JL28/KVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石八線 | 石八線 |  | 石八線A1 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石八線A1 | 11KV石八線 R相AMP | FEEDER | S33/11/JL28/I_R |  |  |  | CDC | 91 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石八線 | 石八線 |  | 石八線A2 | [17 empty] | 1-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石八線A2 | 11KV石八線 S相AMP | FEEDER | S33/11/JL28/I_S |  |  |  | CDC | 92 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石八線 | 石八線 |  | 石八線A3 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石八線A3 | 11KV石八線 T相AMP | FEEDER | S33/11/JL28/I_T |  |  |  | CDC | 93 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石八線 | 石八線 |  | 石八線A0 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石八線A0 | 11KV石八線 N相AMP | FEEDER | S33/11/JL28/I_N |  |  |  | CDC | 94 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石十線 | 石十線 |  | 石十線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石十線KVAR | 11KV石十線 KVAR | FEEDER | S33/11/JL30/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石十線 | 石十線 |  | 石十線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石十線A1 | 11KV石十線 R相AMP | FEEDER | S33/11/JL30/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石十線 | 石十線 |  | 石十線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石十線A2 | 11KV石十線 S相AMP | FEEDER | S33/11/JL30/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石十線 | 石十線 |  | 石十線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石十線A3 | 11KV石十線 T相AMP | FEEDER | S33/11/JL30/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石十線 | 石十線 |  | 石十線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石十線A0 | 11KV石十線 N相AMP | FEEDER | S33/11/JL30/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石三線 | 石三線 |  | 石三線KVAR | [17 empty] | 1-A4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石三線KVAR | 11KV石三線 KVAR | FEEDER | S33/11/JL23/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石三線 | 石三線 |  | 石三線A1 | [17 empty] | 1-A5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石三線A1 | 11KV石三線 R相AMP | FEEDER | S33/11/JL23/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石三線 | 石三線 |  | 石三線A2 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石三線A2 | 11KV石三線 S相AMP | FEEDER | S33/11/JL23/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石三線 | 石三線 |  | 石三線A3 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石三線A3 | 11KV石三線 T相AMP | FEEDER | S33/11/JL23/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石三線 | 石三線 |  | 石三線A0 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石三線A0 | 11KV石三線 N相AMP | FEEDER | S33/11/JL23/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石五線 | 石五線 |  | 石五線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石五線KVAR | 11KV石五線 KVAR | FEEDER | S33/11/JL25/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石五線 | 石五線 |  | 石五線A1 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石五線A1 | 11KV石五線 R相AMP | FEEDER | S33/11/JL25/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石五線 | 石五線 |  | 石五線A2 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石五線A2 | 11KV石五線 S相AMP | FEEDER | S33/11/JL25/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石五線 | 石五線 |  | 石五線A3 | [17 empty] | 1-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石五線A3 | 11KV石五線 T相AMP | FEEDER | S33/11/JL25/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石五線 | 石五線 |  | 石五線A0 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石五線A0 | 11KV石五線 N相AMP | FEEDER | S33/11/JL25/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石六線 | 石六線 |  | 石六線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石六線KVAR | 11KV石六線 KVAR | FEEDER | S33/11/JL26/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石六線 | 石六線 |  | 石六線A1 | [17 empty] | 1-E8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石六線A1 | 11KV石六線 R相AMP | FEEDER | S33/11/JL26/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石六線 | 石六線 |  | 石六線A2 | [17 empty] | 1-E9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石六線A2 | 11KV石六線 S相AMP | FEEDER | S33/11/JL26/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石六線 | 石六線 |  | 石六線A3 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石六線A3 | 11KV石六線 T相AMP | FEEDER | S33/11/JL26/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石六線 | 石六線 |  | 石六線A0 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石六線A0 | 11KV石六線 N相AMP | FEEDER | S33/11/JL26/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石四線 | 石四線 |  | 石四線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石四線KVAR | 11KV石四線 KVAR | FEEDER | S33/11/JL24/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石四線 | 石四線 |  | 石四線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石四線A1 | 11KV石四線 R相AMP | FEEDER | S33/11/JL24/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石四線 | 石四線 |  | 石四線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石四線A2 | 11KV石四線 S相AMP | FEEDER | S33/11/JL24/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石四線 | 石四線 |  | 石四線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石四線A3 | 11KV石四線 T相AMP | FEEDER | S33/11/JL24/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | 石四線 | 石四線 |  | 石四線A0 | [17 empty] | 1-AD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.石四線A0 | 11KV石四線 N相AMP | FEEDER | S33/11/JL24/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-90 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 東石SS.600TIE_AMP | 600TIE AMP | TIE | S33/69/600/I |  |  |  | CDC | 120 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S33/11/TIE1/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S33/11/TIE1/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S33/11/TIE1/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_MW | #1MTR二次側 MW | DTR | S33/11/M1/MW |  |  |  | CDC | 124 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S33/11/M1/MVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-97 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S33/11/M1/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S33/11/M1/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-99 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S33/11/M1/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-93 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_OIL | #1MTR 油溫 | DTR | S33//1MTR/OilTemp |  |  |  | CDC | 129 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-92 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_COIL | #1MTR 線溫 | DTR | S33//1MTR/CoilTemp |  |  |  | CDC | 130 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-94 |  | 1-3B |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S33//1MTR/TapPosMv |  |  |  | CDC | 131 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-E2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_MW | #2MTR二次側 MW | DTR | S33/11/M2/MW |  |  |  | CDC | 132 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-E3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S33/11/M2/MVAR |  |  |  | CDC | 133 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S33/11/M2/I_R |  |  |  | CDC | 134 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S33/11/M2/I_S |  |  |  | CDC | 135 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S33/11/M2/I_T |  |  |  | CDC | 136 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-B9 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_OIL | #2MTR 油溫 | DTR | S33//2MTR/OilTemp |  |  |  | CDC | 137 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-B8 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_COIL | #2MTR 線溫 | DTR | S33//2MTR/CoilTemp |  |  |  | CDC | 138 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BA |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 東石SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S33//2MTR/TapPosMv |  |  |  | CDC | 139 | GENERICAIPoint | SS214_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S33 | 東石SS | 0 |  |  |  |  | DCV | [17 empty] | 2-82 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS2_2 | [8 empty] | 東石SS.直流電源電壓 | 直流電源電壓 | OTHER | S33/0/StaDev/DCV |  |  |  | CDC | 140 | GENERICAIPoint | SS214_L2 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 東石SS.630_PHA | 東石朴子線(630) 相間RY | LINE69 | S33/69/630/PHA |  |  |  | CDC | 141 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 東石SS.630_GDA | 東石朴子線(630) 接地RY | LINE69 | S33/69/630/GDA |  |  |  | CDC | 142 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 東石SS.630_CB | 630(東石朴子線) CB | LINE69 | S33/69/630/CB |  |  |  | CDC | 143 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | DS1 | 631 | [16 empty] | 1-38-00 | 1-38-01 | 1-10 | [5 empty] | ADCS_N | [8 empty] | 東石SS.631_DS | 631(東石朴子線) DS | LINE69 | S33/69/630/DS1 |  |  |  | CDC | 144 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | DS2 | 632 | [16 empty] | 1-38-02 | 1-38-03 | 1-11 | [5 empty] | ADCS_N | [8 empty] | 東石SS.632_DS | 632(東石朴子線) DS | LINE69 | S33/69/630/DS2 |  |  |  | CDC | 145 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | DS3 | 633 | [16 empty] | 1-38-04 | 1-38-05 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 東石SS.633_DS | 633(東石朴子線) DS | LINE69 | S33/69/630/DS3 |  |  |  | CDC | 146 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | E3 | 633E | [16 empty] | 1-38-06 | 1-38-07 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 東石SS.633E_ES | 633E(東石朴子線) ES | LINE69 | S33/69/630/ES3 |  |  |  | CDC | 147 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 東石SS.640_PHA | 水林東石線(640) 相間RY | LINE69 | S33/69/640/PHA |  |  |  | CDC | 148 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 東石SS.640_GDA | 水林東石線(640) 接地RY | LINE69 | S33/69/640/GDA |  |  |  | CDC | 149 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 東石SS.640_CB | 640(水林東石線) CB | LINE69 | S33/69/640/CB |  |  |  | CDC | 150 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | DS1 | 641 | [16 empty] | 1-38-08 | 1-38-09 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 東石SS.641_DS | 641(水林東石線) DS | LINE69 | S33/69/640/DS1 |  |  |  | CDC | 151 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | DS2 | 642 | [16 empty] | 1-38-10 | 1-38-11 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 東石SS.642_DS | 642(水林東石線) DS | LINE69 | S33/69/640/DS2 |  |  |  | CDC | 152 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | DS3 | 643 | [16 empty] | 1-38-12 | 1-38-13 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 東石SS.643_DS | 643(水林東石線) DS | LINE69 | S33/69/640/DS3 |  |  |  | CDC | 153 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | E3 | 643E | [16 empty] | 1-38-14 | 1-38-15 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 東石SS.643E_ES | 643E(水林東石線) ES | LINE69 | S33/69/640/ES3 |  |  |  | CDC | 154 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | PHA | [17 empty] | 1-0C-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_PHA | 11KV石一線(JL21) 相間RY | FEEDER | S33/11/JL21/PHA |  |  |  | CDC | 155 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) |  | GDA | [17 empty] | 1-0C-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_GDA | 11KV石一線(JL21) 接地RY | FEEDER | S33/11/JL21/GDA |  |  |  | CDC | 156 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) 79RY |  | 79UL | [17 empty] | 1-33-06 |  | 1-3E | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_79UL | 11KV石一線(JL21) 79RY U/L | FEEDER | S33/11/JL21/79UL |  |  |  | CDC | 157 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL21 | 石一線(JL21) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_ADJ | 11KV石一線(JL21) LCO分流器 U/L | FEEDER | S33/11/JL21/ADJ |  |  |  | CDC | 158 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL21 | JL21(11KV石一線) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_CB | JL21(11KV石一線) CB | FEEDER | S33/11/JL21/CB |  |  |  | CDC | 159 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_PHA | 11KV石二線(JL22) 相間RY | FEEDER | S33/11/JL22/PHA |  |  |  | CDC | 160 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_GDA | 11KV石二線(JL22) 接地RY | FEEDER | S33/11/JL22/GDA |  |  |  | CDC | 161 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3F | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_79UL | 11KV石二線(JL22) 79RY U/L | FEEDER | S33/11/JL22/79UL |  |  |  | CDC | 162 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL22 | 石二線(JL22) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_ADJ | 11KV石二線(JL22) LCO分流器 U/L | FEEDER | S33/11/JL22/ADJ |  |  |  | CDC | 163 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL22 | JL22(11KV石二線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_CB | JL22(11KV石二線) CB | FEEDER | S33/11/JL22/CB |  |  |  | CDC | 164 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_PHA | 11KV石三線(JL23) 相間RY | FEEDER | S33/11/JL23/PHA |  |  |  | CDC | 165 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_GDA | 11KV石三線(JL23) 接地RY | FEEDER | S33/11/JL23/GDA |  |  |  | CDC | 166 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-40 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_79UL | 11KV石三線(JL23) 79RY U/L | FEEDER | S33/11/JL23/79UL |  |  |  | CDC | 167 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL23 | 石三線(JL23) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_ADJ | 11KV石三線(JL23) LCO分流器 U/L | FEEDER | S33/11/JL23/ADJ |  |  |  | CDC | 168 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL23 | JL23(11KV石三線) |  | CB | [17 empty] | 1-0C-05 |  | 1-37 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_CB | JL23(11KV石三線) CB | FEEDER | S33/11/JL23/CB |  |  |  | CDC | 169 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_PHA | 11KV石四線(JL24) 相間RY | FEEDER | S33/11/JL24/PHA |  |  |  | CDC | 170 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_GDA | 11KV石四線(JL24) 接地RY | FEEDER | S33/11/JL24/GDA |  |  |  | CDC | 171 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-41 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_79UL | 11KV石四線(JL24) 79RY U/L | FEEDER | S33/11/JL24/79UL |  |  |  | CDC | 172 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL24 | 石四線(JL24) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_ADJ | 11KV石四線(JL24) LCO分流器 U/L | FEEDER | S33/11/JL24/ADJ |  |  |  | CDC | 173 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL24 | JL24(11KV石四線) |  | CB | [17 empty] | 1-0D-00 |  | 1-38 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_CB | JL24(11KV石四線) CB | FEEDER | S33/11/JL24/CB |  |  |  | CDC | 174 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_PHA | 11KV石五線(JL25) 相間RY | FEEDER | S33/11/JL25/PHA |  |  |  | CDC | 175 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_GDA | 11KV石五線(JL25) 接地RY | FEEDER | S33/11/JL25/GDA |  |  |  | CDC | 176 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-42 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_79UL | 11KV石五線(JL25) 79RY U/L | FEEDER | S33/11/JL25/79UL |  |  |  | CDC | 177 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL25 | 石五線(JL25) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_ADJ | 11KV石五線(JL25) LCO分流器 U/L | FEEDER | S33/11/JL25/ADJ |  |  |  | CDC | 178 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL25 | JL25(11KV石五線) |  | CB | [17 empty] | 1-0D-03 |  | 1-39 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_CB | JL25(11KV石五線) CB | FEEDER | S33/11/JL25/CB |  |  |  | CDC | 179 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | PHA | [17 empty] | 1-11-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_PHA | 11KV石六線(JL26) 相間RY | FEEDER | S33/11/JL26/PHA |  |  |  | CDC | 180 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) |  | GDA | [17 empty] | 1-11-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_GDA | 11KV石六線(JL26) 接地RY | FEEDER | S33/11/JL26/GDA |  |  |  | CDC | 181 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) 79RY |  | 79UL | [17 empty] | 1-35-06 |  | 1-64 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_79UL | 11KV石六線(JL26) 79RY U/L | FEEDER | S33/11/JL26/79UL |  |  |  | CDC | 182 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL26 | 石六線(JL26) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_ADJ | 11KV石六線(JL26) LCO分流器 U/L | FEEDER | S33/11/JL26/ADJ |  |  |  | CDC | 183 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL26 | JL26(11KV石六線) |  | CB | [17 empty] | 1-11-03 |  | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_CB | JL26(11KV石六線) CB | FEEDER | S33/11/JL26/CB |  |  |  | CDC | 184 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | PHA | [17 empty] | 1-11-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_PHA | 11KV石七線(JL27) 相間RY | FEEDER | S33/11/JL27/PHA |  |  |  | CDC | 185 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) |  | GDA | [17 empty] | 1-12-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_GDA | 11KV石七線(JL27) 接地RY | FEEDER | S33/11/JL27/GDA |  |  |  | CDC | 186 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-65 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_79UL | 11KV石七線(JL27) 79RY U/L | FEEDER | S33/11/JL27/79UL |  |  |  | CDC | 187 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL27 | 石七線(JL27) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_ADJ | 11KV石七線(JL27) LCO分流器 U/L | FEEDER | S33/11/JL27/ADJ |  |  |  | CDC | 188 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL27 | JL27(11KV石七線) |  | CB | [17 empty] | 1-11-06 |  | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_CB | JL27(11KV石七線) CB | FEEDER | S33/11/JL27/CB |  |  |  | CDC | 189 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | PHA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_PHA | 11KV石八線(JL28) 相間RY | FEEDER | S33/11/JL28/PHA |  |  |  | CDC | 190 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) |  | GDA | [17 empty] | 1-12-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_GDA | 11KV石八線(JL28) 接地RY | FEEDER | S33/11/JL28/GDA |  |  |  | CDC | 191 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-66 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_79UL | 11KV石八線(JL28) 79RY U/L | FEEDER | S33/11/JL28/79UL |  |  |  | CDC | 192 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL28 | 石八線(JL28) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_ADJ | 11KV石八線(JL28) LCO分流器 U/L | FEEDER | S33/11/JL28/ADJ |  |  |  | CDC | 193 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL28 | JL28(11KV石八線) |  | CB | [17 empty] | 1-12-01 |  | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_CB | JL28(11KV石八線) CB | FEEDER | S33/11/JL28/CB |  |  |  | CDC | 194 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_PHA | 11KV石九線(JL29) 相間RY | FEEDER | S33/11/JL29/PHA |  |  |  | CDC | 195 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_GDA | 11KV石九線(JL29) 接地RY | FEEDER | S33/11/JL29/GDA |  |  |  | CDC | 196 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-67 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_79UL | 11KV石九線(JL29) 79RY U/L | FEEDER | S33/11/JL29/79UL |  |  |  | CDC | 197 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL29 | 石九線(JL29) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_ADJ | 11KV石九線(JL29) LCO分流器 U/L | FEEDER | S33/11/JL29/ADJ |  |  |  | CDC | 198 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL29 | JL29(11KV石九線) |  | CB | [17 empty] | 1-12-04 |  | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_CB | JL29(11KV石九線) CB | FEEDER | S33/11/JL29/CB |  |  |  | CDC | 199 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_PHA | 11KV石十線(JL30) 相間RY | FEEDER | S33/11/JL30/PHA |  |  |  | CDC | 200 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_GDA | 11KV石十線(JL30) 接地RY | FEEDER | S33/11/JL30/GDA |  |  |  | CDC | 201 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-68 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_79UL | 11KV石十線(JL30) 79RY U/L | FEEDER | S33/11/JL30/79UL |  |  |  | CDC | 202 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV | JL30 | 石十線(JL30) LCO分流器 |  | ADJ | [17 empty] | 1-36-15 |  | 1-7F | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_ADJ | 11KV石十線(JL30) LCO分流器 U/L | FEEDER | S33/11/JL30/ADJ |  |  |  | CDC | 203 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S33 | 東石SS | 11 | 11kV | JL30 | JL30(11KV石十線) |  | CB | [17 empty] | 1-12-07 |  | 1-60 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_CB | JL30(11KV石十線) CB | FEEDER | S33/11/JL30/CB |  |  |  | CDC | 204 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-02 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 東石SS.600_CB | 600(TIE) CB | TIE | S33/69/600/CB |  |  |  | CDC | 205 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 600 | TIE(600) |  | 51A | [17 empty] | 1-04-03 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600_51A | 69KV TIE(600) 51RY | TIE | S33/69/600/51A |  |  |  | CDC | 206 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 600 | TIE(600) |  | 51NA | [17 empty] | 1-04-04 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600_51NA | 69KV TIE(600) 51N RY | TIE | S33/69/600/51NA |  |  |  | CDC | 207 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 東石SS.601_DS | 601(TIE) DS | TIE | S33/69/600/DS1 |  |  |  | CDC | 208 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 東石SS.602_DS | 602(TIE) DS | TIE | S33/69/600/DS2 |  |  |  | CDC | 209 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0E-01 |  | 1-3A | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.TIE1_CB | 11KV TIE1 CB | TIE | S33/11/TIE1/CB |  |  |  | CDC | 210 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.TIE1_51A | 11KV TIE1 51RY | TIE | S33/11/TIE1/51A |  |  |  | CDC | 211 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S33/11/TIE1/51NA |  |  |  | CDC | 212 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.750_CB | 750(#1MTR) CB | DTR | S33/69/750/CB |  |  |  | CDC | 213 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.1M_CB | 1M(#1MTR) CB | DTR | S33/11/M1/CB |  |  |  | CDC | 214 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_51A | #1MTR 51RY | DTR | S33/69/750/51A |  |  |  | CDC | 215 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_51NA | #1MTR 51N RY | DTR | S33/69/750/51NA |  |  |  | CDC | 216 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S33//1MTR/51ZA |  |  |  | CDC | 217 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_87A | #1MTR 87RY | DTR | S33//1MTR/87A |  |  |  | CDC | 218 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S33//1MTR/87UL |  |  |  | CDC | 219 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S33/11/M1/51A |  |  |  | CDC | 220 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_TRA | #1MTR 重故障 | DTR | S33//1MTR/TRA |  |  |  | CDC | 221 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S33//1MTR/TRF |  |  |  | CDC | 222 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S33//1MTR/SupLocal |  |  |  | CDC | 223 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3C | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S33//1MTR/Tap Chan |  |  |  | CDC | 224 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-37-00 | 1-37-01 | 1-2C | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.751_DS | 751(#1MTR) DS | DTR | S33/69/750/DS1 |  |  |  | CDC | 225 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-37-02 | 1-37-03 | 1-2D | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.752_DS | 752(#1MTR) DS | DTR | S33/69/750/DS2 |  |  |  | CDC | 226 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_96A | #1MTR 96P RY | DTR | S33//1MTR/96PA |  |  |  | CDC | 227 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S33//1MTR/OLTC_DLY |  |  |  | CDC | 228 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S33//1MTR/AC_Fault |  |  |  | CDC | 229 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.760_CB | 760(#2MTR) CB | DTR | S33/69/760/CB |  |  |  | CDC | 230 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-03-04 |  | 1-59 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.2M_CB | 2M(#2MTR) CB | DTR | S33/11/M2/CB |  |  |  | CDC | 231 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_51A | #2MTR 51RY | DTR | S33/69/760/51A |  |  |  | CDC | 232 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_51NA | #2MTR 51N RY | DTR | S33/69/760/51NA |  |  |  | CDC | 233 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S33//2MTR/51ZA |  |  |  | CDC | 234 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_87A | #2MTR 87RY | DTR | S33//2MTR/87A |  |  |  | CDC | 235 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S33//2MTR/87UL |  |  |  | CDC | 236 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-03-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S33/11/M2/51A |  |  |  | CDC | 237 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_TRA | #2MTR 重故障 | DTR | S33//2MTR/TRA |  |  |  | CDC | 238 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S33//2MTR/TRF |  |  |  | CDC | 239 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S33//2MTR/SupLocal |  |  |  | CDC | 240 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S33//2MTR/Tap Chan |  |  |  | CDC | 241 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-37-04 | 1-37-05 | 1-2E | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.761_DS | 761(#2MTR) DS | DTR | S33/69/760/DS1 |  |  |  | CDC | 242 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-37-06 | 1-37-07 | 1-2F | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.762_DS | 762(#2MTR) DS | DTR | S33/69/760/DS2 |  |  |  | CDC | 243 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_96A | #2MTR 96P RY | DTR | S33//2MTR/96PA |  |  |  | CDC | 244 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S33//2MTR/OLTC_DLY |  |  |  | CDC | 245 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S33//2MTR/AC_Fault |  |  |  | CDC | 246 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0D-06 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.210_CB | 210(11KV #1SC) CB | SC | S33/11/210/CB |  |  |  | CDC | 247 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-11 |  | 1-3D | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S33/11/210/Tap Chan |  |  |  | CDC | 248 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.210_SCA | 11KV #1SC 51,51N RY | SC | S33/11/210/SCA |  |  |  | CDC | 249 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S33/11/210/UVA |  |  |  | CDC | 250 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-13-02 |  | 1-5B | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.220_CB | 220(11KV #2SC) CB | SC | S33/11/220/CB |  |  |  | CDC | 251 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-35-11 |  | 1-63 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S33/11/220/Tap Chan |  |  |  | CDC | 252 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-13-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.220_SCA | 11KV #2SC 51,51N RY | SC | S33/11/220/SCA |  |  |  | CDC | 253 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S33/11/220/UVA |  |  |  | CDC | 254 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 東石SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S33/69/1BUS/87A |  |  |  | CDC | 255 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-32-14 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 東石SS.69#1BUS_87UL | 69#1BUS 87RY U/L | BUS | S33/69/1BUS/87UL |  |  |  | CDC | 256 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | 69KV_N | [8 empty] | 東石SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S33/69/2BUS/87A |  |  |  | CDC | 257 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 692BUS | 69#2BUS |  | 87UL | [17 empty] | 1-32-15 |  | 1-0F | [5 empty] | ADCS_N | [8 empty] | 東石SS.69#2BUS_87UL | 69#2BUS 87RY U/L | BUS | S33/69/2BUS/87UL |  |  |  | CDC | 258 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S33/11/ComPoint/CBA |  |  |  | CDC | 259 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S33/11/ComPoint/CBF |  |  |  | CDC | 260 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S33/69/ComPoint/ABS_89A |  |  |  | CDC | 261 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S33/69/ComPoint/CBA |  |  |  | CDC | 262 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S33/69/ComPoint/CBF |  |  |  | CDC | 263 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S33/0/RTU/RTU_R_L |  |  |  | CDC | 264 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S33 | 東石SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.TEST_CB | TEST CB | OTHER | S33/0/RTU/Test_CB |  |  |  | CDC | 265 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.火災警報(1) | [東石]火警 | OTHER | S33/0/StaDev/Fire1 |  |  |  | CDC | 266 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S33/0/StaDev/OPA |  |  |  | CDC | 267 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S33/0/StaDev/STUV |  |  |  | CDC | 268 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S33/0/StaDev/CHG1 |  |  |  | CDC | 269 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.直流電源DCA | 直流電源故障警報 | OTHER | S33/0/StaDev/DCA |  |  |  | CDC | 270 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S33/0/StaDev/DCE |  |  |  | CDC | 271 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S33/0/StaDev/OilLeak |  |  |  | CDC | 272 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-35-14 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S33/0/StaDev/3A5Other |  |  |  | CDC | 273 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-35-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S33/0/StaDev/4A5Other |  |  |  | CDC | 274 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S33/0/StaDev/CHG2 |  |  |  | CDC | 275 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-35-13 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S33/0/StaDev/CommACF |  |  |  | CDC | 276 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S33/0/StaDev/Burglar1 |  |  |  | CDC | 277 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S33/0/StaDev/Burglar2 |  |  |  | CDC | 278 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化防盜(3) | 無人化防盜(3) | OTHER | S33/0/StaDev/Burglar3 |  |  |  | CDC | 279 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化門禁(1) | 保全(DOOR) | OTHER | S33/0/StaDev/Door1 |  |  |  | CDC | 280 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S33 | 東石SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化門禁(2) | 開關場水位二段警報 | OTHER | S33/0/StaDev/Door2 |  |  |  | CDC | 281 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.無人化門禁(3) | 無人化門禁(3) | OTHER | S33/0/StaDev/Door3 |  |  |  | CDC | 282 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S33 | 東石SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-6D | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.開關場照明(A) | 所內開關場照明 | OTHER | S33/0/StaDev/Lights1 |  |  |  | CDC | 283 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S33 | 東石SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-6E | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.開關場照明(B) | 路燈照明 | OTHER | S33/0/StaDev/Lights2 |  |  |  | CDC | 284 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S33 | 東石SS | 0 |  | 1_MAIN | #1 |  | 51NA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER | S33/11/M1/51NA |  |  |  | CDC | 285 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2_MAIN | #2 |  | 51NA | [17 empty] | 1-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER | S33/11/M2/51NA |  |  |  | CDC | 286 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | _SC | _SC |  | 60A | [17 empty] | 1-33-12 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.11KV_SC_60A | 60RY | OTHER | S33/11/ComPoint/FDR_60A |  |  |  | CDC | 287 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | CO2火警 | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.CO2火警 | CO2火警 | OTHER | S33/0/StaDev/Fire2 |  |  |  | CDC | 288 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | CO2故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.CO2故障 | CO2故障 | OTHER | S33/0/StaDev/CO2 |  |  |  | CDC | 289 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.安全監控 | 安全監控 | OTHER | S33/0/StaDev/Burglar |  |  |  | CDC | 290 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內其他重故障 | 所內其他重故障 | OTHER | S33/0/StaDev/PSA |  |  |  | CDC | 291 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內其他輕故障 | 所內其他輕故障 | OTHER | S33/0/StaDev/PSF |  |  |  | CDC | 292 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.門禁 | 大門側門 | OTHER | S33/0/StaDev/Door |  |  |  | CDC | 293 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.維護運轉警報 | 維護運轉警報 | OTHER | S33/0/StaDev/1A5Other |  |  |  | CDC | 294 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-34-14 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.水位警報(1) | 水位警報(1) | OTHER | S33/0/StaDev/Water1 |  |  |  | CDC | 295 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-34-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.水位警報(2) | 水位警報(2) | OTHER | S33/0/StaDev/Water2 |  |  |  | CDC | 296 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #1MTR96B1 | [17 empty] | 1-18-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR96B1 | #1MTR撲氣電驛警報 | OTHER | S33//1MTR/96B1 |  |  |  | CDC | 297 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #1MTR96B2 | [17 empty] | 1-18-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR96B2 | #1MTR撲氣電驛動作 | OTHER | S33//1MTR/96B2 |  |  |  | CDC | 298 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #1MTR96D | [17 empty] | 1-18-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR96D | #1MTR放壓電驛動作 | OTHER | S33//1MTR/96D |  |  |  | CDC | 299 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #1MTR96P | [17 empty] | 1-18-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR96P | #1MTR突壓電驛動作 | OTHER | S33//1MTR/96P |  |  |  | CDC | 300 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | #2MTR63Q | [17 empty] | 1-19-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR63Q | #2MTR ULTC電驛動作 | OTHER | S33//2MTR/63Q |  |  |  | CDC | 301 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #2MTR96B1 | [17 empty] | 1-18-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR96B1 | #2MTR撲氣電驛警報 | OTHER | S33//2MTR/96B1 |  |  |  | CDC | 302 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #2MTR96B2 | [17 empty] | 1-18-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR96B2 | #2MTR撲氣電驛動作 | OTHER | S33//2MTR/96B2 |  |  |  | CDC | 303 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #2MTR96D | [17 empty] | 1-18-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR96D | #2MTR放壓電驛動作 | OTHER | S33//2MTR/96D |  |  |  | CDC | 304 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #2MTR96P | [17 empty] | 1-19-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR96P | #2MTR突壓電驛動作 | OTHER | S33//2MTR/96P |  |  |  | CDC | 305 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | #1MTR63Q | [17 empty] | 1-18-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR63Q | #1MTR ULTC電驛動作 | OTHER | S33//1MTR/63Q |  |  |  | CDC | 306 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0E-04 |  | 1-43 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S33/11/M1/81A |  |  |  | CDC | 307 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S33 | 東石SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內電源ACB1 | 所內電源ACB1S | OTHER | S33/0/StaDev/ACB1 |  |  |  | CDC | 308 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S33 | 東石SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內電源ACB2 | 所內電源ACB2S | OTHER | S33/0/StaDev/ACB2 |  |  |  | CDC | 309 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S33 | 東石SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-31-08 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.所內電源ACBA | 所內電源故障警報 | OTHER | S33/0/StaDev/ACBA |  |  |  | CDC | 310 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | TIE | TIE |  | 600GDA(1) | [17 empty] | 1-05-01 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE | S33/69/600/GDA1 |  |  |  | CDC | 311 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | TIE | TIE |  | 600GDA(2) | [17 empty] | 1-05-03 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE | S33/69/600/GDA2 |  |  |  | CDC | 312 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | TIE | TIE |  | 600PHA(1) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600PHA(1) | 600(TIE) 67A(B1) | TIE | S33/69/600/PHA1 |  |  |  | CDC | 313 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | TIE | TIE |  | 600PHA(2) | [17 empty] | 1-05-02 | [7 empty] | 69KV_N | [8 empty] | 東石SS.600PHA(2) | 600(TIE) 67A(B2) | TIE | S33/69/600/PHA2 |  |  |  | CDC | 314 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-11-02 |  | 1-56 | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S33/11/M2/81A |  |  |  | CDC | 315 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S33 | 東石SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-33-14 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S33/0/StaDev/5AOther |  |  |  | CDC | 316 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-34-13 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S33/0/StaDev/6A5Other |  |  |  | CDC | 317 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-33-13 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.開關場水位警報 | 開關場水位警報 | OTHER | S33/0/StaDev/Water3 |  |  |  | CDC | 318 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 東石SS.630_87A | 東石朴子線(630) 87RY | LINE69 | S33/69/630/87A |  |  |  | CDC | 319 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | CFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 東石SS.630_CFA | 東石朴子線(630) 通訊故障 | LINE69 | S33/69/630/74A |  |  |  | CDC | 320 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 東石SS.630_87UL | 東石朴子線(630) 87RY U/L | LINE69 | S33/69/630/87UL |  |  |  | CDC | 321 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 東石SS.640_87A | 水林東石線(640) 87RY | LINE69 | S33/69/640/87A |  |  |  | CDC | 322 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | CFA | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 東石SS.640_CFA | 水林東石線(640) 通訊故障 | LINE69 | S33/69/640/74A |  |  |  | CDC | 323 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 東石SS.640_87UL | 水林東石線(640) 87RY U/L | LINE69 | S33/69/640/87UL |  |  |  | CDC | 324 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 630 | 東石朴子線(630) |  | RYFA | [17 empty] | 1-06-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.630_RYFA | 630 東石朴子線IED警報 | OTHER | S33/69/630/RYFA |  |  |  | CDC | 325 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 640 | 水林東石線(640) |  | RYFA | [17 empty] | 1-06-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.640_RYFA | 640 水林東石線IED警報 | OTHER | S33/69/640/RYFA |  |  |  | CDC | 326 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 11KVIED重警報 | [17 empty] | 1-3F-15 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.11KVIED重警報 | 11KVIED重警報 | OTHER | S33/11/ComPoint/IRFA |  |  |  | CDC | 327 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石一線79LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石一線79LOA | 石一線79LOA | OTHER | S33/11/JL21/LOA |  |  |  | CDC | 328 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石七線79LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石七線79LOA | 石七線79LOA | OTHER | S33/11/JL27/LOA |  |  |  | CDC | 329 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石九線79LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石九線79LOA | 石九線79LOA | OTHER | S33/11/JL29/LOA |  |  |  | CDC | 330 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石二線79LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石二線79LOA | 石二線79LOA | OTHER | S33/11/JL22/LOA |  |  |  | CDC | 331 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石八線79LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石八線79LOA | 石八線79LOA | OTHER | S33/11/JL28/LOA |  |  |  | CDC | 332 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石十線79LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石十線79LOA | 石十線79LOA | OTHER | S33/11/JL30/LOA |  |  |  | CDC | 333 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石三線79LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石三線79LOA | 石三線79LOA | OTHER | S33/11/JL23/LOA |  |  |  | CDC | 334 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石五線79LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石五線79LOA | 石五線79LOA | OTHER | S33/11/JL25/LOA |  |  |  | CDC | 335 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石六線79LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石六線79LOA | 石六線79LOA | OTHER | S33/11/JL26/LOA |  |  |  | CDC | 336 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | 石四線79LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.石四線79LOA | 石四線79LOA | OTHER | S33/11/JL24/LOA |  |  |  | CDC | 337 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-06-07 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.600_RYFA | 600 RYFA | OTHER | S33/69/600/RYFA |  |  |  | CDC | 338 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #1MTR-86A | [17 empty] | 1-07-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR-86A | #1MTR-86A | OTHER | S33//1MTR/MTR_86A |  |  |  | CDC | 339 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3A-02 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_51ZS | #1MTR 51ZS | OTHER | S33//1MTR/51Z_UL |  |  |  | CDC | 340 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3A-00 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_87UL2 | #1MTR 87UL2 | OTHER | S33//1MTR/1_87UL2 |  |  |  | CDC | 341 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-3A-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#1MTR_RYFA | #1MTR IED警報 | OTHER | S33//1MTR/RYFA |  |  |  | CDC | 342 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  |  |  |  | #2MTR-86A | [17 empty] | 1-07-01 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR-86A | #2MTR-86A | OTHER | S33//2MTR/MTR_86A |  |  |  | CDC | 343 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3A-06 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_51ZS | #2MTR 51ZS | OTHER | S33//2MTR/51Z_UL |  |  |  | CDC | 344 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-3A-04 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_87UL2 | #2MTR 87UL2 | OTHER | S33//2MTR/1_87UL2 |  |  |  | CDC | 345 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-3A-05 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.#2MTR_RYFA | #2MTR IED警報 | OTHER | S33//2MTR/RYFA |  |  |  | CDC | 346 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 1M | #1M |  | 81UL | [17 empty] | 1-14-00 |  | 1-6A | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#1M_81UL | #1M 81UL | OTHER | S33/11/M1/81UL |  |  |  | CDC | 347 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | 2M | #2M |  | 81UL | [17 empty] | 1-14-01 |  | 1-6B | [5 empty] | DDCS2_2 | [8 empty] | 東石SS.#2M_81UL | #2M 81UL | OTHER | S33/11/M2/81UL |  |  |  | CDC | 348 | GENERICDIPoint | SS214_L1 | CDC2_CD2B |  | DI | [34 empty] | USE/LOCK | USE
S33 | 東石SS | 0 |  | BUSRY | BUSRY |  | BF | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 東石SS.BUSRY_BF | BUSRY BF | OTHER | S33//BUSRY/BFA |  |  |  | CDC | 349 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | BUSRY | BUSRY |  | 87CTFA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 東石SS.BUSRY_CTFA | BUSRY CTFA | OTHER | S33//BUSRY/87CTFA |  |  |  | CDC | 350 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 691BUS | 69#1BUS |  | 27BA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 東石SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | S33/69/1BUS/BUS_VUA |  |  |  | CDC | 351 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | 692BUS | 69#2BUS |  | 27BA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 東石SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER | S33/69/2BUS/BUS_VUA |  |  |  | CDC | 352 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_2 | [8 empty] | 東石SS.PMA | POWER METER警報 | OTHER | S33/0/ComPoint/PMA |  |  |  | CDC | 353 | GENERICDIPoint | SS214_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S33 | 東石SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 354 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 東石SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 355 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 東石SS.630LE | 630LE (非取樣點) | LINE69 | S33/69/630/LE0 |  |  |  |  | 356 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 630 | 東石朴子線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 東石SS.630BE | 630BE (非取樣點) | LINE69 | S33/69/630/BE0 |  |  |  |  | 357 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 東石SS.640LE | 640LE (非取樣點) | LINE69 | S33/69/640/LE0 |  |  |  |  | 358 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 640 | 水林東石線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 東石SS.640BE | 640BE (非取樣點) | LINE69 | S33/69/640/BE0 |  |  |  |  | 359 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL21 | JL21_DS |  | DS1 | JL21_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_DS | JL21_DS (非取樣點) | FEEDER | S33/11/JL21/DS |  |  |  |  | 360 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL21 | JL21_ES |  | LE0 | JL21_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL21_ES | JL21_ES (非取樣點) | FEEDER | S33/11/JL21/ES |  |  |  |  | 361 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL22 | JL22_DS |  | DS1 | JL22_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_DS | JL22_DS (非取樣點) | FEEDER | S33/11/JL22/DS |  |  |  |  | 362 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL22 | JL22_ES |  | LE0 | JL22_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL22_ES | JL22_ES (非取樣點) | FEEDER | S33/11/JL22/ES |  |  |  |  | 363 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL23 | JL23_DS |  | DS1 | JL23_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_DS | JL23_DS (非取樣點) | FEEDER | S33/11/JL23/DS |  |  |  |  | 364 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL23 | JL23_ES |  | LE0 | JL23_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL23_ES | JL23_ES (非取樣點) | FEEDER | S33/11/JL23/ES |  |  |  |  | 365 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL24 | JL24_DS |  | DS1 | JL24_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_DS | JL24_DS (非取樣點) | FEEDER | S33/11/JL24/DS |  |  |  |  | 366 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL24 | JL24_ES |  | LE0 | JL24_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL24_ES | JL24_ES (非取樣點) | FEEDER | S33/11/JL24/ES |  |  |  |  | 367 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL25 | JL25_DS |  | DS1 | JL25_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_DS | JL25_DS (非取樣點) | FEEDER | S33/11/JL25/DS |  |  |  |  | 368 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL25 | JL25_ES |  | LE0 | JL25_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL25_ES | JL25_ES (非取樣點) | FEEDER | S33/11/JL25/ES |  |  |  |  | 369 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL26 | JL26_DS |  | DS1 | JL26_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_DS | JL26_DS (非取樣點) | FEEDER | S33/11/JL26/DS |  |  |  |  | 370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL26 | JL26_ES |  | LE0 | JL26_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL26_ES | JL26_ES (非取樣點) | FEEDER | S33/11/JL26/ES |  |  |  |  | 371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL27 | JL27_DS |  | DS1 | JL27_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_DS | JL27_DS (非取樣點) | FEEDER | S33/11/JL27/DS |  |  |  |  | 372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL27 | JL27_ES |  | LE0 | JL27_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL27_ES | JL27_ES (非取樣點) | FEEDER | S33/11/JL27/ES |  |  |  |  | 373 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL28 | JL28_DS |  | DS1 | JL28_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_DS | JL28_DS (非取樣點) | FEEDER | S33/11/JL28/DS |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL28 | JL28_ES |  | LE0 | JL28_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL28_ES | JL28_ES (非取樣點) | FEEDER | S33/11/JL28/ES |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL29 | JL29_DS |  | DS1 | JL29_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_DS | JL29_DS (非取樣點) | FEEDER | S33/11/JL29/DS |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL29 | JL29_ES |  | LE0 | JL29_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL29_ES | JL29_ES (非取樣點) | FEEDER | S33/11/JL29/ES |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | JL30 | JL30_DS |  | DS1 | JL30_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_DS | JL30_DS (非取樣點) | FEEDER | S33/11/JL30/DS |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | JL30 | JL30_ES |  | LE0 | JL30_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.JL30_ES | JL30_ES (非取樣點) | FEEDER | S33/11/JL30/ES |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 東石SS.601E | 601E (非取樣點) | TIE | S33/69/600/E1 |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 東石SS.602E | 602E (非取樣點) | TIE | S33/69/600/E2 |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S33/11/TIE1/D1 |  |  |  |  | 382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.750TE | 750TE (非取樣點) | DTR | S33/69/750/TE0 |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.750BE | 750BE (非取樣點) | DTR | S33/69/750/BE0 |  |  |  |  | 384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.1M_DS | 1M_DS (非取樣點) | DTR | S33/11/M1/DS |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.1M_ES | 1M_ES (非取樣點) | DTR | S33/11/M1/ES |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.760TE | 760TE (非取樣點) | DTR | S33/69/760/TE0 |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.760BE | 760BE (非取樣點) | DTR | S33/69/760/BE0 |  |  |  |  | 388 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.2M_DS | 2M_DS (非取樣點) | DTR | S33/11/M2/DS |  |  |  |  | 389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.2M_ES | 2M_ES (非取樣點) | DTR | S33/11/M2/ES |  |  |  |  | 390 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.210_ES | 210_ES (非取樣點) | SC | S33/11/210/ES |  |  |  |  | 391 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.211DS | 211DS (非取樣點) | SC | S33/11/210/D1 |  |  |  |  | 392 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 212DS | 212DS |  | 212DS | 212DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.212DS | 212DS (非取樣點) | SC | S33/11/210/D2 |  |  |  |  | 393 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.220_ES | 220_ES (非取樣點) | SC | S33/11/220/ES |  |  |  |  | 394 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.221DS | 221DS (非取樣點) | SC | S33/11/220/D1 |  |  |  |  | 395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 222DS | 222DS |  | 222DS | 222DS | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.222DS | 222DS (非取樣點) | SC | S33/11/220/D2 |  |  |  |  | 396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S33 | 東石SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 東石SS.69B1E | 69B1E (非取樣點) | BUS | S33/69/1BUS/BE1 |  |  |  |  | 397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 東石SS.69B2E | 69B2E (非取樣點) | BUS | S33/69/2BUS/BE2 |  |  |  |  | 398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S33 | 東石SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 東石SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 399 | NotelDIPoint | [38 empty] | START/STOP | STOP

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo