## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S34 | 嘉埔SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV 1BUS | KV | 69KVBUS #1 PT R相 | kV_-90_90(-2000_2000) | aaa | B2/S34_A1 | [8 empty] | 嘉埔SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S34 | 嘉埔SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV 2BUS | KV | 69KVBUS #2 PT R相 | kV_-90_90(-2000_2000) | aab | B2/S34_A1 | [8 empty] | 嘉埔SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S34 | 嘉埔SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0055 |  |  | 1-B7 |  |  | PT-1 | KV | 一號 BUS 11KV | kV_-9_9(-2000_2000) | aaa | B2/S34_D1 | [8 empty] | 嘉埔SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S34 | 嘉埔SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0056 |  |  | 1-B8 |  |  | PT-2 | KV | 二號 BUS 11KV | kV_-9_9(-2000_2000) | aba | B2/S34_D1 | [8 empty] | 嘉埔SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S34 | 嘉埔SS | 69 | 69kV | 69B1E | 69B1E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aafz | B2/S34_A1 | [8 empty] | 嘉埔SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0606 |  |  | 1-36-10 |  |  | #1BUS RY | 27B1A | 69KV #1BUS 27B1欠壓電驛警報 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-02-07 |  |  | 69KV #1BUS | 87B1A | #1 BUS 差動電驛 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-13 |  |  | #1BUS RY | 87B1S | 69KV #1BUS 差動電驛 U/L |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | BUS |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 69B2E | 69B2E |  | BE2 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BUS | [13 empty] | aafz | B2/S34_A1 | [8 empty] | 嘉埔SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0607 |  |  | 1-36-11 |  |  | #2BUS RY | 27B2A | 69KV #2BUS 27B2欠壓電驛警報 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-00 |  |  | 69KV #2BUS | 87B2A | #2 BUS 差動電驛 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0546 |  |  | 1-32-14 |  |  | #2BUS RY | 87B2S | 69KV #2BUS 差動電驛 U/L |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | BUS |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | L3(730) | MW | 嘉義嘉埔線有效電力 | MW_-72_72(-2000_2000) |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_MW | 欣欣奮起嘉埔線 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | L3(730) | MVAR | 嘉義嘉埔線無效電力 | MVAR_-72_72(-2000_2000) |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_MVAR | 欣欣奮起嘉埔線 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 730 | 69KV Line3 MWH(+) | 嘉義嘉埔線 |  |  | B2/S34_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | L4(620) | MW | 嘉埔奮起線有效電力 | MW_-72_72(-2000_2000) |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_MW | 嘉埔奮起線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | L4(620) | MVAR | 嘉埔奮起線無效電力 | MVAR_-72_72(-2000_2000) |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_MVAR | 嘉埔奮起線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 620 | 69KV Line4 MWH(+) | 嘉埔奮起線 |  |  | B2/S34_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-09-05 |  |  | 730 | 3PHA | 欣欣嘉埔奮起線(L3) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_PHA | 欣欣奮起嘉埔線(730) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-09-06 |  |  | 730 | 3GDA | 欣欣嘉埔奮起線(L3) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_GDA | 欣欣奮起嘉埔線(730) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-04 |  |  | 730 | 87A | 欣欣嘉埔奮起線(L3) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_87A | 欣欣奮起嘉埔線(730) 87RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0633 |  |  | 1-38-05 |  |  | 730 74RY | CFA | 欣欣嘉埔奮起線 通訊故障 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_CFA | 欣欣奮起嘉埔線(730) CFA | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-01 |  |  | 620 | 4PHA | 嘉埔奮起線(L4) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_PHA | 嘉埔奮起線(620) 相間RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-02 |  |  | 620 | 4GDA | 嘉埔奮起線(L4) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_GDA | 嘉埔奮起線(620) 接地RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-00 |  |  | SPARE | 485A | 620嘉埔奮起線(L4) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_85A | 嘉埔奮起線(620) 85RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0635 |  |  | 1-38-07 |  |  | 620 74RY | 474A | 嘉埔奮起線 副線74A |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_74A | 嘉埔奮起線(620) 74RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0632 |  | 0069 | 1-38-04 |  | 1-44 | 730 87RY | 87S | 欣欣嘉埔奮起線87電驛(使用/閉鎖) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_87UL | 欣欣奮起嘉埔線(730) 87RY U/L | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0634 |  | 0070 | 1-38-06 |  | 1-45 | 620 85RY | 485S | 嘉埔奮起線 副線(使用/閉鎖) |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.620_85UL | 嘉埔奮起線(620) 85RY U/L | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/C49TN02/T1 |  | 0078 |  | 0006 | 1-09-03 |  | 1-05 | 730 | 52AS | 欣欣嘉埔奮起線(L3) |  | aaca | B2/S34_A1 | [8 empty] | 嘉埔SS.730_CB | 730(欣欣奮起嘉埔線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S34S29/T1 |  | 0082 |  | 0007 | 1-09-07 |  | 1-06 | 620 | 52AS | 嘉埔奮起線(L4) |  | aaea | B2/S34_A1 | [8 empty] | 嘉埔SS.620_CB | 620(嘉埔奮起線) CB | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | DS1 | 731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0085 | 1-3A-08 | 1-3A-09 | 1-54 | L3 DS (731) | AS | 欣欣嘉埔奮起線1BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.731_DS | 731(欣欣奮起嘉埔線) DS | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | DS2 | 732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0670 | 671 | 0086 | 1-3A-10 | 1-3A-11 | 1-55 | L3 DS (732) | AS | 欣欣嘉埔奮起線2BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.732_DS | 732(欣欣奮起嘉埔線) DS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS1 | 621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 | 0089 | 1-3B-00 | 1-3B-01 | 1-58 | L4 DS (621) | AS | 嘉埔奮起線1BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.621_DS | 621(嘉埔奮起線) DS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS2 | 622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 679 | 0090 | 1-3B-02 | 1-3B-03 | 1-59 | L4 DS (622) | AS | 嘉埔奮起線2BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.622_DS | 622(嘉埔奮起線) DS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | DS3 | 733 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 | 0087 | 1-3A-12 | 1-3A-13 | 1-56 | L3 DS (733) | AS | 欣欣嘉埔奮起線線路側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.733_DS | 733(欣欣奮起嘉埔線) DS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | E3 | 733E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0674 | 675 | 0088 | 1-3A-14 | 1-3A-15 | 1-57 | L3 DS (733E) | AS | 欣欣嘉埔奮起線線路側ES |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.733E_ES | 733E(欣欣奮起嘉埔線) ES | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.730LE | 730LE (非取樣點) | LINE69 | [5 empty] | 38 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.730BE | 730BE (非取樣點) | LINE69 | [5 empty] | 39 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS3 | 623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 | 0091 | 1-3B-04 | 1-3B-05 | 1-5A | L4 DS (623) | AS | 嘉埔奮起線線路側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.623_DS | 623(嘉埔奮起線) DS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | E3 | 623E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0682 | 683 | 0092 | 1-3B-06 | 1-3B-07 | 1-5B | L4 DS (623E) | AS | 嘉埔奮起線線路側ES |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.623E_ES | 623E(嘉埔奮起線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F11 | KVAR | 埔十一線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十一線KVAR | 11KV埔十一線 KVAR | FEEDER |  |  |  |  | CDC | 44 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F11 | A1 | 埔十一線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十一線A1 | 11KV埔十一線 R相AMP | FEEDER |  |  |  |  | CDC | 45 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F11 | A2 | 埔十一線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十一線A2 | 11KV埔十一線 S相AMP | FEEDER |  |  |  |  | CDC | 46 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F11 | A3 | 埔十一線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十一線A3 | 11KV埔十一線 T相AMP | FEEDER |  |  |  |  | CDC | 47 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F11 | A0 | 埔十一線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十一線A0 | 11KV埔十一線 N相AMP | FEEDER |  |  |  |  | CDC | 48 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | SPARE | F11 KWH(+) | 埔十一線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 49 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F12 | KVAR | 埔十二線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十二線KVAR | 11KV埔十二線 KVAR | FEEDER |  |  |  |  | CDC | 50 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F12 | A1 | 埔十二線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十二線A1 | 11KV埔十二線 R相AMP | FEEDER |  |  |  |  | CDC | 51 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F12 | A2 | 埔十二線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十二線A2 | 11KV埔十二線 S相AMP | FEEDER |  |  |  |  | CDC | 52 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F12 | A3 | 埔十二線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十二線A3 | 11KV埔十二線 T相AMP | FEEDER |  |  |  |  | CDC | 53 | AI_FEEDER |  |  |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F12 | A0 | 埔十二線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十二線A0 | 11KV埔十二線 N相AMP | FEEDER |  |  |  |  | CDC | 54 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0025 |  |  | 1-59 |  |  | SPARE | F12 KWH(+) | 埔十二線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 55 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-03 |  |  | JY21 RY | PHA | 埔一線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_PHA | 11KV埔一線(JY21) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-04 |  |  | JY21 RY | GDA | 埔一線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_GDA | 11KV埔一線(JY21) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0041 | 1-33-08 |  | 1-28 | F1 79 RY | 79S | 埔一線復79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_79UL | 11KV埔一線(JY21) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0557 |  | 0042 | 1-33-09 |  | 1-29 | F1 51N TAP | 51NS | 埔一線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_LCO_TAP | 11KV埔一線(JY21) LCO TAP | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0C-06 |  |  | JY22 RY | PHA | 埔二線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_PHA | 11KV埔二線(JY22) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0C-07 |  |  | JY22 RY | GDA | 埔二線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_GDA | 11KV埔二線(JY22) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0043 | 1-33-10 |  | 1-2A | F2 79 RY | 79S | 埔二線復79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_79UL | 11KV埔二線(JY22) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0559 |  | 0044 | 1-33-11 |  | 1-2B | F2 51N TAP | 51NS | 埔二線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_LCO_TAP | 11KV埔二線(JY22) LCO TAP | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-01 |  |  | JY23 RY | PHA | 埔三線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_PHA | 11KV埔三線(JY23) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-02 |  |  | JY23 RY | GDA | 埔三線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_GDA | 11KV埔三線(JY23) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0045 | 1-33-12 |  | 1-2C | F3 79 RY | 79S | 埔三線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_79UL | 11KV埔三線(JY23) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0561 |  | 0046 | 1-33-13 |  | 1-2D | F3 51N TAP | 51NS | 埔三線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_LCO_TAP | 11KV埔三線(JY23) LCO TAP | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-04 |  |  | JY24 RY | PHA | 埔四線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_PHA | 11KV埔四線(JY24) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0D-05 |  |  | JY24 RY | GDA | 埔四線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_GDA | 11KV埔四線(JY24) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0562 |  | 0047 | 1-33-14 |  | 1-2E | F4 79 RY | 79S | 埔四線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_79UL | 11KV埔四線(JY24) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0563 |  | 0048 | 1-33-15 |  | 1-2F | F4 51N TAP | 51NS | 埔四線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_LCO_TAP | 11KV埔四線(JY24) LCO TAP | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0D-07 |  |  | JY25 RY | PHA | 埔五線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_PHA | 11KV埔五線(JY25) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-00 |  |  | JY25 RY | GDA | 埔五線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_GDA | 11KV埔五線(JY25) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0564 |  | 0049 | 1-34-00 |  | 1-30 | F5 79 RY | 79S | 埔五線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_79UL | 11KV埔五線(JY25) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0565 |  | 0050 | 1-34-01 |  | 1-31 | F5 51N TAP | 51NS | 埔五線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_LCO_TAP | 11KV埔五線(JY25) LCO TAP | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-02 |  |  | JY26 RY | PHA | 埔六線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_PHA | 11KV埔六線(JY26) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-03 |  |  | JY26 RY | GDA | 埔六線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_GDA | 11KV埔六線(JY26) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0566 |  | 0051 | 1-34-02 |  | 1-32 | F6 79 RY | 79S | 埔六線復79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_79UL | 11KV埔六線(JY26) 79RY U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0567 |  | 0052 | 1-34-03 |  | 1-33 | F6 51N TAP | 51NS | 埔六線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_LCO_TAP | 11KV埔六線(JY26) LCO TAP | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-00 |  |  | JY27 RY | PHA | 埔七線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_PHA | 11KV埔七線(JY27) 相間RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-01 |  |  | JY27 RY | GDA | 埔七線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_GDA | 11KV埔七線(JY27) 接地RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  | 0053 | 1-34-04 |  | 1-34 | F7 79 RY | 79S | 埔七線復79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_79UL | 11KV埔七線(JY27) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0569 |  | 0054 | 1-34-05 |  | 1-35 | F7 51N TAP | 51NS | 埔七線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_LCO_TAP | 11KV埔七線(JY27) LCO TAP | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-03 |  |  | JY28 RY | PHA | 埔八線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_PHA | 11KV埔八線(JY28) 相間RY | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-04 |  |  | JY28 RY | GDA | 埔八線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_GDA | 11KV埔八線(JY28) 接地RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0055 | 1-34-06 |  | 1-36 | F8 79 RY | 79S | 埔八線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_79UL | 11KV埔八線(JY28) 79RY U/L | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0571 |  | 0056 | 1-34-07 |  | 1-37 | F8 51N TAP | 51NS | 埔八線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_LCO_TAP | 11KV埔八線(JY28) LCO TAP | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-0F-06 |  |  | JY29 RY | PHA | 埔九線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_PHA | 11KV埔九線(JY29) 相間RY | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JY29 RY | GDA | 埔九線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_GDA | 11KV埔九線(JY29) 接地RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0572 |  | 0057 | 1-34-08 |  | 1-38 | F9 79 RY | 79S | 埔九線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_79UL | 11KV埔九線(JY29) 79RY U/L | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0573 |  | 0058 | 1-34-09 |  | 1-39 | F9 51N TAP | 51NS | 埔九線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_LCO_TAP | 11KV埔九線(JY29) LCO TAP | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-01 |  |  | JY30 RY | PHA | 埔十線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_PHA | 11KV埔十線(JY30) 相間RY | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JY30 RY | GDA | 埔十線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_GDA | 11KV埔十線(JY30) 接地RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  | 0059 | 1-34-10 |  | 1-3A | F10 79 RY | 79S | 埔十線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_79UL | 11KV埔十線(JY30) 79RY U/L | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0575 |  | 0060 | 1-34-11 |  | 1-3B | F10 51N TAP | 51NS | 埔十線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_LCO_TAP | 11KV埔十線(JY30) LCO TAP | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-04 |  |  | JY31 RY | PHA | 埔十一線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_PHA | 11KV埔十一線(JY31) 相間RY | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JY31 RY | GDA | 埔十一線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_GDA | 11KV埔十一線(JY31) 接地RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0576 |  | 0061 | 1-34-12 |  | 1-3C | F11 79 RY | 79S | 埔十一線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_79UL | 11KV埔十一線(JY31) 79RY U/L | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0577 |  | 0062 | 1-34-13 |  | 1-3D | F11 51N TAP | 51NS | 埔十一線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_LCO_TAP | 11KV埔十一線(JY31) LCO TAP | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-10-07 |  |  | JY32 RY | PHA | 埔十二線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_PHA | 11KV埔十二線(JY32) 相間RY | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JY32 RY | GDA | 埔十二線 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_GDA | 11KV埔十二線(JY32) 接地RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0578 |  | 0063 | 1-34-14 |  | 1-3E | F12 79 RY | 79S | 埔十二線79(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_79UL | 11KV埔十二線(JY32) 79RY U/L | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0579 |  | 0064 | 1-34-15 |  | 1-3F | F12 51N TAP | 51NS | 埔十二線51N調整(使用/閉鎖) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_LCO_TAP | 11KV埔十二線(JY32) LCO TAP | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/JY21/T1 |  |  | 0101 |  | 0012 | 1-0C-02 |  | 1-0B | JY21 CB | 52AS | 埔一線 |  | aacb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_CB | JY21(11KV埔一線) CB | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_DS | JY21_DS (非取樣點) | FEEDER | [5 empty] | 105 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY21_ES | JY21_ES (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/JY22/T1 |  |  | 0104 |  | 0013 | 1-0C-05 |  | 1-0C | JY22 CB | 52AS | 埔二線 |  | aadb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_CB | JY22(11KV埔二線) CB | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_DS | JY22_DS (非取樣點) | FEEDER | [5 empty] | 108 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY22_ES | JY22_ES (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/JY23/T1 |  |  | 0107 |  | 0014 | 1-0D-00 |  | 1-0D | JY23 CB | 52AS | 埔三線 |  | aaeb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_CB | JY23(11KV埔三線) CB | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_DS | JY23_DS (非取樣點) | FEEDER | [5 empty] | 111 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY23_ES | JY23_ES (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/JY24/T1 |  |  | 0110 |  | 0015 | 1-0D-03 |  | 1-0E | JY24 CB | 52AS | 埔四線 |  | aagb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_CB | JY24(11KV埔四線) CB | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_DS | JY24_DS (非取樣點) | FEEDER | [5 empty] | 114 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY24_ES | JY24_ES (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/JY25/T1 |  |  | 0113 |  | 0016 | 1-0D-06 |  | 1-0F | JY25 CB | 52AS | 埔五線 |  | aahb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_CB | JY25(11KV埔五線) CB | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_DS | JY25_DS (非取樣點) | FEEDER | [5 empty] | 117 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY25_ES | JY25_ES (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY26/T1 |  |  | 0116 |  | 0017 | 1-0E-01 |  | 1-10 | JY26 CB | 52AS | 埔六線 |  | aaib | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_CB | JY26(11KV埔六線) CB | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_DS | JY26_DS (非取樣點) | FEEDER | [5 empty] | 120 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY26_ES | JY26_ES (非取樣點) | FEEDER | [5 empty] | 121 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY27/T1 |  |  | 0122 |  | 0024 | 1-0E-07 |  | 1-17 | JY27 CB | 52AS | 埔七線 |  | abab | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_CB | JY27(11KV埔七線) CB | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_DS | JY27_DS (非取樣點) | FEEDER | [5 empty] | 123 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY27_ES | JY27_ES (非取樣點) | FEEDER | [5 empty] | 124 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY28/T1 |  |  | 0125 |  | 0025 | 1-0F-02 |  | 1-18 | JY28 CB | 52AS | 埔八線 |  | abbb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_CB | JY28(11KV埔八線) CB | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_DS | JY28_DS (非取樣點) | FEEDER | [5 empty] | 126 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY28_ES | JY28_ES (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY29/T1 |  |  | 0128 |  | 0026 | 1-0F-05 |  | 1-19 | JY29 CB | 52AS | 埔九線 |  | abdb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_CB | JY29(11KV埔九線) CB | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_DS | JY29_DS (非取樣點) | FEEDER | [5 empty] | 129 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY29_ES | JY29_ES (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY30/T1 |  |  | 0131 |  | 0027 | 1-10-00 |  | 1-1A | JY30 CB | 52AS | 埔十線 |  | abeb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_CB | JY30(11KV埔十線) CB | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_DS | JY30_DS (非取樣點) | FEEDER | [5 empty] | 132 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY30_ES | JY30_ES (非取樣點) | FEEDER | [5 empty] | 133 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY31/T1 |  |  | 0134 |  | 0028 | 1-10-03 |  | 1-1B | JY31 CB | 52AS | 埔十一線 |  | abfb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_CB | JY31(11KV埔十一線) CB | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_DS | JY31_DS (非取樣點) | FEEDER | [5 empty] | 135 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY31_ES | JY31_ES (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JY32/T1 |  |  | 0137 |  | 0029 | 1-10-06 |  | 1-1C | JY32 CB | 52AS | 埔十二線 |  | abgb | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_CB | JY32(11KV埔十二線) CB | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_DS | JY32_DS (非取樣點) | FEEDER | [5 empty] | 138 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.JY32_ES | JY32_ES (非取樣點) | FEEDER | [5 empty] | 139 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | TIE(600) | A1 | 69KV TIE R相電流 | A_-1200_1200(-2000_2000) |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 140 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | TIE-2 | A1 | 23KV TIE-2 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 141 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | TIE-2 | A2 | 23KV TIE-2 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 142 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | TIE-2 | A3 | 23KV TIE-2 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 143 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0023 |  | 0005 | 1-02-04 |  | 1-04 | TIE(600) | 52AS | 69KV BUS聯絡斷路器 |  | aaaz | B2/S34_A1 | [8 empty] | 嘉埔SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 144 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | TIE(600) RY | 60PHA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600_51A | 69KV TIE(600) 51RY | TIE |  |  |  |  | CDC | 145 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-02-06 |  |  | TIE(600) RY | 60GDA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600_51NA | 69KV TIE(600) 51N RY | TIE |  |  |  |  | CDC | 146 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1BUS | B/2BUS |  |  | 0119 |  | 0023 | 1-0E-04 |  | 1-16 | TIE-2 CB | 52AS | 二號聯絡斷路器 11KV |  | zzzz | B2/S34_D1 | [8 empty] | 嘉埔SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 147 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0E-05 |  |  | TIE-2 RY | PHA | 二號聯絡斷路器 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 148 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0E-06 |  |  | TIE-2 RY | GDA | 二號聯絡斷路器 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 149 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 | 0083 | 1-3A-04 | 1-3A-05 | 1-52 | TIE DS (601) | AS | 69KV TIE一次BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 150 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0666 | 667 | 0084 | 1-3A-06 | 1-3A-07 | 1-53 | TIE DS (602) | AS | 69KV TIE二次BUS側DS |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 151 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.601E | 601E (非取樣點) | TIE | [5 empty] | 152 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_A1 | [8 empty] | 嘉埔SS.602E | 602E (非取樣點) | TIE | [5 empty] | 153 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | BR1DS(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.BR1DS | BR1DS (非取樣點) | TIE | [5 empty] | 154 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | BR1(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.BR1ES | BR1ES (非取樣點) | TIE | [5 empty] | 155 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 156 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | #1 TR | MW | 一號主變有效電力 | MW_-36_36(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 157 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | #1 TR | MVAR | 一號主變無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 158 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1 TR | A1 | 一號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 159 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1 TR | A2 | 一號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 160 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1 TR | A3 | 一號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 161 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR | MW | 二號主變有效電力 | MW_-36_36(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 162 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR | MVAR | 二號主變無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 163 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 164 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 165 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | #2 TR | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 166 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | #1 TR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 167 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | #1 TR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 168 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0015 |  | 0071 | 1-8F |  | 1-46 | #1 TR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 169 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | #1MTR | #1MTR MWH(+) | 一號主變 |  |  | B1/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 170 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0009 |  |  | 1-49 |  |  | #1MTR | #1MTR MVARH(+) | 一號主變 |  |  | B1/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 171 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | #2 TR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 172 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | #2 TR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 173 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0018 |  | 0072 | 1-92 |  | 1-47 | #2 TR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 174 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | #2MTR | #2MTR MWH(+) | 二號主變 |  |  | B1/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 175 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0012 |  |  | 1-4C |  |  | #2MTR | #2MTR MVARH(+) | 二號主變 |  |  | B1/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 176 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0003 |  | 0008 | 1-00-00 |  | 1-07 | 750 | 52AS | 一號主變一次側CB |  | aabb | B3/S34_D1 | [8 empty] | 嘉埔SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 177 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S34_D1 | [8 empty] | 嘉埔SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 178 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S34_D1 | [8 empty] | 嘉埔SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 179 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0013 |  | 0020 | 1-01-02 |  | 1-13 | 760 | 52AS | 二號主變一次側CB |  | aadb | B3/S34_D1 | [8 empty] | 嘉埔SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 180 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S34_D1 | [8 empty] | 嘉埔SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 181 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S34_D1 | [8 empty] | 嘉埔SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 182 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0010 |  | 0009 | 1-00-07 |  | 1-08 | #1MAIN | SEC(M1) 52AS | 一號主變二次側 CB |  | aafa | B2/S34_D1 | [8 empty] | 嘉埔SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 183 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2MTR |  |  | 0020 |  | 0021 | 1-02-01 |  | 1-14 | #2MAIN | SEC(M2) 52AS | 二號主變二次側 CB |  | abca | B2/S34_D1 | [8 empty] | 嘉埔SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 184 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-01 |  |  | 750 RY | 1PHA | 一號主變一次側 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-02 |  |  | 750 RY | 1GDA | 一號主變一次側 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 186 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-00-05 |  |  | #1TR | 151ZA | 一號主變51Z RY |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 187 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-04 |  |  | #1TR | 187A | 一號主變差動電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 188 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-32-03 |  |  | #1 TR | 187S | 一號主變87電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 189 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-03 |  |  | 760 RY | 2PHA | 二號主變一次側 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 190 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-04 |  |  | 760 RY | 2GDA | 二號主變一次側 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 191 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-01-07 |  |  | #2TR | 251ZA | 二號主變51Z RY |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 192 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-01-06 |  |  | #2TR | 287A | 二號主變差動電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 193 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-32-08 |  |  | #2 TR | 287S | 二號主變87電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 194 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-00 |  |  | #1MAIN RY | PHA | 一號主變二次側 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 195 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0536 |  |  | 1-32-04 |  |  | #1 TR | 1TRA | 一號主變重故障警報 |  | a | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 196 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0537 |  |  | 1-32-05 |  |  | #1 TR | 1TRF | 一號主變輕故障警報 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 197 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0538 |  |  | 1-32-06 |  |  | #1 TR S/L | 143RS2 | 一號主變OLTC(中心/現場)指示 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 198 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0034 | 1-32-07 |  | 1-21 | #1 TR A/M | 1AXS | 一號主變OLTC(自動/手動)指示 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 199 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | #2MAIN RY | 2PHA | 二號主變二次側 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 200 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0541 |  |  | 1-32-09 |  |  | #2 TR重故障 | 2TRA | 二號主變重故障警報 |  | a | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 201 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0542 |  |  | 1-32-10 |  |  | #2 TR輕故障 | 2TRF | 二號主變輕故障警報 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 202 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0543 |  |  | 1-32-11 |  |  | #2 TR S/L | 243RS2 | 二號主變OLTC(中心/現場)指示 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 203 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0544 |  | 0036 | 1-32-12 |  | 1-23 | #2 TR A/M | 2AXS | 二號主變OLTC(自動/手動)指示 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 204 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 | 0093 | 1-3C-00 | 1-3C-01 | 1-5C | #1 TR DS (751) | AS | 一號主變一次側1BUS側DS |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 205 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0694 | 695 | 0094 | 1-3C-02 | 1-3C-03 | 1-5D | #1 TR DS (752) | AS | 一號主變一次側2BUS側DS |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 206 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 | 0095 | 1-3C-04 | 1-3C-05 | 1-5E | #1 TR DS (761) | AS | 二號主變一次側1BUS側DS |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 207 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 699 | 0096 | 1-3C-06 | 1-3C-07 | 1-5F | #1 TR DS (762) | AS | 二號主變一次側2BUS側DS |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 208 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 209 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 210 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-03 |  |  | #1TR | 196PA | 一號主變96P RY |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 211 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-12 |  |  | #1 MTR | OLTC 48T | 一號主變OLTC遲滯警報 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 212 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-14 |  |  | #1 MTR | 27C | 一號主變AC電源欠壓 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 213 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 214 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | E1 | 2M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 215 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-01-05 |  |  | #2TR | 296PA | 二號主變96P RY |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 216 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-13 |  |  | #2 MTR | OLTC 48T | 二號主變OLTC遲滯警報 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 217 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-15 |  |  | #2 MTR | 27C | 二號主變AC電源欠壓 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 218 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1SSTR |  |  | 0095 |  | 0010 | 1-0B-04 |  | 1-09 | #1 SSTR CB | 52AS | 所內變壓器#1SSTR |  | aaaa | B2/S34_D1 | [8 empty] | 嘉埔SS.390_CB | 390(#1SSTR) CB | OTHER |  |  |  |  | CDC | 219 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B2,B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0B-05 |  |  | #1 SSTR RY | PHA | 所內變壓器#1SSTR |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 220 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B2,B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0B-06 |  |  | #1 SSTR RY | GDA | 所內變壓器#1SSTR |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  |  |  |  | CDC | 221 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 222 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 223 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2SSTR |  |  | 0143 |  | 0022 | 1-11-04 |  | 1-15 | #2 SSTR CB | 52AS | 所內變壓器#2SSTR |  | abha | B2/S34_D1 | [8 empty] | 嘉埔SS.490_CB | 490(#2SSTR) CB | OTHER |  |  |  |  | CDC | 224 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  | B2,B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-11-05 |  |  | #2 SSTR RY | PHA | 所內變壓器#2SSTR |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 225 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  | B2,B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-11-06 |  |  | #2 SSTR RY | GDA | 所內變壓器#2SSTR |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  |  |  |  | CDC | 226 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 227 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 228 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | A/LBS210^C/1SC(A) |  |  | 0098 |  | 0011 | 1-0B-07 |  | 1-0A | SC-1 CB | 52AS | 一號SC 11KV |  | aabb | B2/S34_D1 | [8 empty] | 嘉埔SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 229 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0037 | 1-33-06 |  | 1-24 | SPARE | SC-1 Q-CTL(1) AXS | 一號SC乏控器(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 230 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 231 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | A/LBS220^C/2SC(A) |  |  | 0140 |  | 0030 | 1-11-01 |  | 1-1D | SC-2 CB | 52AS | 二號SC 11KV |  | abib | B2/S34_D1 | [8 empty] | 嘉埔SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 232 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0580 |  | 0065 | 1-35-00 |  | 1-40 | SPARE | SC-2 Q-CTL(1) AXS | 二號SC乏控器(自動/手動) |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 233 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 234 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-00 |  |  | SC-1 RY | SCA | 一號SC 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 235 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-01 |  |  | SC-1 RY | UVA | 一號SC 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 236 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0141 |  |  | 1-11-02 |  |  | SC-2 RY | SCA | 二號SC 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 237 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0142 |  |  | 1-11-03 |  |  | SC-2 RY | UVA | 二號SC 11KV |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 238 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS | 210 | B3,Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0700 |  | 0018 | 1-3C-08 |  | 1-11 | 11KV SC-1 LBS. | AS | 一號SC LBS開關 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.210_LBS | 210(11KV #1SC) LBS | SC |  |  |  |  | CDC | 239 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS | 220 | B3,Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0702 |  | 0031 | 1-3C-10 |  | 1-1E | 11KV SC-2 LBS. | AS | 二號SC LBS開關 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.220_LBS | 220(11KV #2SC) LBS | SC |  |  |  |  | CDC | 240 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S34_D1 | [8 empty] | 嘉埔SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 241 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S34_D1 | [8 empty] | 嘉埔SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 242 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S34_D1 | [8 empty] | 嘉埔SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 243 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S34_D1 | [8 empty] | 嘉埔SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 244 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0500 |  | 0001 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 嘉埔SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(STATUS) |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0602 |  |  | 1-36-06 |  |  | DC充電機 | CHG1 | 直流充電機故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-37-00 |  |  | SPARE | CHG2 | 充電機故障(通信專用) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0603 |  |  | 1-36-07 |  |  | DC電源 | DCE | 直流接地故障 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-15 |  |  | 所內電源 | STUV | 所內電源欠壓 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0640 |  |  | 1-38-12 |  |  | SPARE | OPA | 油壓電力電纜 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-38-08 |  |  | 一般火警 | 火警警報(1) | 火警警報(1) |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.火災警報(1) | [嘉埔]火警 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-33-00 |  |  | 直流NFB | DCA | 直流NFB跳脫監視 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0620 |  |  | 1-37-08 |  |  | SPARE |  | 無人化防盜(1) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0621 |  |  | 1-37-09 |  |  | SPARE |  | 無人化防盜(2) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-37-10 |  |  | SPARE |  | 無人化防盜(3) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防盜(3) | 無人化防盜(3) | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0623 |  |  | 1-37-11 |  |  | 無人化門禁(1) |  | 保全門禁警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化門禁(1) | 保全(DOOR) | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0624 |  |  | 1-37-12 |  |  | 開關場水位二段 |  | 開關場水位二段警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.開關場水位二段 | 開關場水位二段警報 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0625 |  |  | 1-37-13 |  |  | 開關場水位一段 |  | 開關場水位一段警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.開關場水位警報 | 開關場水位警報 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0604 |  |  | 1-36-08 |  |  | 69KV CB | 69CBF | 69KV CB輕故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0605 |  |  | 1-36-09 |  |  | 69KV CB | 69CBA | 69KV CB重故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0551 |  |  | 1-33-03 |  |  | 11KV CB | CBF | 11KV CB 輕故障 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-33-04 |  |  | 11KV CB | CBA | 11KV CB 重故障 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0643 |  |  | 1-38-15 |  |  | 69KV ABS | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 264 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-37-01 |  |  | SPARE | ACFA | 通訊設備AC故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 265 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0614 |  |  | 1-37-02 |  |  | SPARE | OLTEA | 通訊設備光纖主故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 266 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-37-03 |  |  | SPARE | OLTEF | 通訊設備光纖次故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 267 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊PCM警報 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0616 |  |  | 1-37-04 |  |  | SPARE | PCMA | 博碼調變器故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 268 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0638 |  | 0110 | 1-38-10 |  | 1-6D | SPARE | FLA | 所內開關場照明 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 269 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0639 |  | 0111 | 1-38-11 |  | 1-6E | 路燈照明 | FLB | 路燈照明 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 270 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-01 |  |  | #1MAIN RY | GDA | 一號主變二次側 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER |  |  |  |  | CDC | 271 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-03 |  |  | #2MAIN RY | 2GDA | 二號主變二次側 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER |  |  |  |  | CDC | 272 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | M1 | #1MTR(M1) |  | 3P51A | #1M_三相51 | B2,B3,Element | Status | 3相 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-00-06 |  |  | #1TR PRI(SPAJ-140C) | 3Ø51 RY 12PHA | 一號主變一次側三相51 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#1M_三相51 | #1M 三相51 | OTHER |  |  |  |  | CDC | 273 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | M2 | #2MTR(M2) |  | 3P51A | #2M_三相51 | B2,B3,Element | Status | 3相 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-00 |  |  | #2TR PRI(SPAJ-140C) | 3Ø51 RY 22PHA | 一號主變一次側三相51 |  |  | B2/S34_D1 | [8 empty] | 嘉埔SS.#2M_三相51 | #2M 三相51 | OTHER |  |  |  |  | CDC | 274 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0637 |  |  | 1-38-09 |  |  | SAPRE |  | 一般門禁 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 275 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0641 |  |  | 1-38-13 |  |  | SPARE | SUPA | 安全監控 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 276 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | PSF | 所內其他輕故障 | Element | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0610 |  |  | 1-36-14 |  |  | SPARE | PSF | 所內其他輕故障 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.所內其他輕故障 | 所內其他輕故障 | OTHER |  |  |  |  | CDC | 277 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | PSA | 所內其他重故障 | Element | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-36-15 |  |  | SPARE | PSA | 所內其他重故障 |  |  | ELEM/S34_D1 | [8 empty] | 嘉埔SS.所內其他重故障 | 所內其他重故障 | OTHER |  |  |  |  | CDC | 278 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-36-05 |  |  | 所內電源 | ACBA | 所內電源警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.ACBA | ACBA | OTHER |  |  |  |  | CDC | 279 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  | Element | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 1-33-01 |  |  | 所內電源ACB-1 | ACB1S | 所內電源ACB-1運轉監視 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.所內電源ACB1 | 所內電源ACB1 | OTHER |  |  |  |  | CDC | 280 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  | Element | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-33-02 |  |  | 所內電源ACB-2 | ACB2S | 所內電源ACB-2運轉監視 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.所內電源ACB2 | 所內電源ACB2 | OTHER |  |  |  |  | CDC | 281 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 維護運轉警報 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-38-14 |  |  | 維護運轉警報 | 43 R/L | 維護運轉警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 282 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-36-04 |  |  | 11KV SC | 11KV_SC_60A | 11KV SC 電壓平衡電驛 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.11KV_SC_60A | 60RY | OTHER |  |  |  |  | CDC | 283 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報(1) | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0608 |  |  | 1-36-12 |  |  | 集油池水位 | OW1 | 集油池水位警報 1 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.水位警報(1) | 洩油池水位警報(1) | OTHER |  |  |  |  | CDC | 284 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報(2) | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0609 |  |  | 1-36-13 |  |  | 集油池水位 | OW2 | 集油池水位警報 2 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.水位警報(2) | 洩油池水位警報(2) | OTHER |  |  |  |  | CDC | 285 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-30-02 |  |  | #1MTR | 196B1 | #1MTR 樸氣電驛一段 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR96B1 | 1M 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 286 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0503 |  |  | 1-30-03 |  |  | #1MTR | 196B2 | #1MTR 樸氣電驛二段 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR96B2 | 1M 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 287 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0504 |  |  | 1-30-04 |  |  | #1MTR | 196D | #1MTR 放壓電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR96D | 1M 放壓電驛動作 | OTHER |  |  |  |  | CDC | 288 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0505 |  |  | 1-30-05 |  |  | #1MTR | 196P | #1MTR 突壓電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR96P | 1M 突壓電驛動作 | OTHER |  |  |  |  | CDC | 289 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0506 |  |  | 1-30-06 |  |  | #1MTR | 163Q | #1MTR 油流電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR63Q | 1M ULTC電驛動作 | OTHER |  |  |  |  | CDC | 290 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0507 |  |  | 1-30-07 |  |  | #2MTR | 296B1 | #2MTR 樸氣電驛一段 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR96B1 | 2M 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 291 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0508 |  |  | 1-30-08 |  |  | #2MTR | 296B2 | #2MTR 樸氣電驛二段 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR96B2 | 2M 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 292 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0509 |  |  | 1-30-09 |  |  | #2MTR | 296D | #2MTR 放壓電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR96D | 2M 放壓電驛動作 | OTHER |  |  |  |  | CDC | 293 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0510 |  |  | 1-30-10 |  |  | #2MTR | 296P | #2MTR 突壓電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR96P | 2M 突壓電驛動作 | OTHER |  |  |  |  | CDC | 294 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0511 |  |  | 1-30-11 |  |  | #2MTR | 263Q | #2MTR 油流電驛 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR63Q | 2M ULTC電驛動作 | OTHER |  |  |  |  | CDC | 295 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | 600TIE B1 | PHA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600PHA(1) | 600(TIE) 67A(B1) | TIE |  |  |  |  | CDC | 296 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | 600TIE B1 | GDA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE |  |  |  |  | CDC | 297 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-02 |  |  | 600TIE B2 | PHA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600PHA(2) | 600(TIE) 67A(B2) | TIE |  |  |  |  | CDC | 298 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-03 |  |  | 600TIE B2 | GDA | 69KV BUS聯絡斷路器 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE |  |  |  |  | CDC | 299 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | LOA |  | Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0553 |  |  | 1-33-05 |  |  | 11KV 79 RY | LOA | 11KV 79 Lockout警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.79RY_LOA | 79RY LOA | OTHER |  |  |  |  | CDC | 300 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Fire1 | 無人化防火(1) | Element | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-37-06 |  |  | 防火警報(2) | CO2 故障 | CO2系統故障 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防火(1) | CO2故障 | OTHER |  |  |  |  | CDC | 301 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Fire2 | 無人化防火(2) | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-37-05 |  |  | 防火警報(1) | CO2 FIRE | CO2系統火警 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防火(2) | CO2火警 | OTHER |  |  |  |  | CDC | 302 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Fire3 | 無人化防火(3) | Element | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-37-07 |  |  | SPARE |  | 無人化防火(3) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.無人化防火(3) | 無人化防火(3) | OTHER |  |  |  |  | CDC | 303 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | IRFA | IED警報 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-32-00 |  |  | 11KVIED | IEDA | 11KVIED重警報 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.IED警報 | 11/23KV CBA 重故障(IED故障) | OTHER |  |  |  |  | CDC | 304 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | F1 | KVAR | 埔一線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔一線KVAR | 11KV埔一線 KVAR | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | F1 | A1 | 埔一線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔一線A1 | 11KV埔一線 R相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | F1 | A2 | 埔一線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔一線A2 | 11KV埔一線 S相AMP | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | F1 | A3 | 埔一線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔一線A3 | 11KV埔一線 T相AMP | FEEDER |  |  |  |  | CDC | 308 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | F1 | A0 | 埔一線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔一線A0 | 11KV埔一線 N相AMP | FEEDER |  |  |  |  | CDC | 309 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F7 | KVAR | 埔七線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔七線KVAR | 11KV埔七線 KVAR | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F7 | A1 | 埔七線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔七線A1 | 11KV埔七線 R相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 | A2 | 埔七線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔七線A2 | 11KV埔七線 S相AMP | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 | A3 | 埔七線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔七線A3 | 11KV埔七線 T相AMP | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 | A0 | 埔七線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔七線A0 | 11KV埔七線 N相AMP | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 | KVAR | 埔九線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔九線KVAR | 11KV埔九線 KVAR | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 | A1 | 埔九線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔九線A1 | 11KV埔九線 R相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 | A2 | 埔九線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔九線A2 | 11KV埔九線 S相AMP | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 | A3 | 埔九線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔九線A3 | 11KV埔九線 T相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F9 | A0 | 埔九線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔九線A0 | 11KV埔九線 N相AMP | FEEDER |  |  |  |  | CDC | 319 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | F2 | KVAR | 埔二線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔二線KVAR | 11KV埔二線 KVAR | FEEDER |  |  |  |  | CDC | 320 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | F2 | A1 | 埔二線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔二線A1 | 11KV埔二線 R相AMP | FEEDER |  |  |  |  | CDC | 321 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | F2 | A2 | 埔二線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔二線A2 | 11KV埔二線 S相AMP | FEEDER |  |  |  |  | CDC | 322 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F2 | A3 | 埔二線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔二線A3 | 11KV埔二線 T相AMP | FEEDER |  |  |  |  | CDC | 323 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F2 | A0 | 埔二線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔二線A0 | 11KV埔二線 N相AMP | FEEDER |  |  |  |  | CDC | 324 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F8 | KVAR | 埔八線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔八線KVAR | 11KV埔八線 KVAR | FEEDER |  |  |  |  | CDC | 325 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 | A1 | 埔八線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔八線A1 | 11KV埔八線 R相AMP | FEEDER |  |  |  |  | CDC | 326 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 | A2 | 埔八線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔八線A2 | 11KV埔八線 S相AMP | FEEDER |  |  |  |  | CDC | 327 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 | A3 | 埔八線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔八線A3 | 11KV埔八線 T相AMP | FEEDER |  |  |  |  | CDC | 328 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 | A0 | 埔八線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔八線A0 | 11KV埔八線 N相AMP | FEEDER |  |  |  |  | CDC | 329 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 | KVAR | 埔十線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十線KVAR | 11KV埔十線 KVAR | FEEDER |  |  |  |  | CDC | 330 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 | A1 | 埔十線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十線A1 | 11KV埔十線 R相AMP | FEEDER |  |  |  |  | CDC | 331 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 | A2 | 埔十線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十線A2 | 11KV埔十線 S相AMP | FEEDER |  |  |  |  | CDC | 332 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F10 | A3 | 埔十線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十線A3 | 11KV埔十線 T相AMP | FEEDER |  |  |  |  | CDC | 333 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F10 | A0 | 埔十線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔十線A0 | 11KV埔十線 N相AMP | FEEDER |  |  |  |  | CDC | 334 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F3 | KVAR | 埔三線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔三線KVAR | 11KV埔三線 KVAR | FEEDER |  |  |  |  | CDC | 335 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F3 | A1 | 埔三線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔三線A1 | 11KV埔三線 R相AMP | FEEDER |  |  |  |  | CDC | 336 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F3 | A2 | 埔三線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔三線A2 | 11KV埔三線 S相AMP | FEEDER |  |  |  |  | CDC | 337 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F3 | A3 | 埔三線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔三線A3 | 11KV埔三線 T相AMP | FEEDER |  |  |  |  | CDC | 338 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F3 | A0 | 埔三線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔三線A0 | 11KV埔三線 N相AMP | FEEDER |  |  |  |  | CDC | 339 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F5 | KVAR | 埔五線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔五線KVAR | 11KV埔五線 KVAR | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F5 | A1 | 埔五線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔五線A1 | 11KV埔五線 R相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F5 | A2 | 埔五線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔五線A2 | 11KV埔五線 S相AMP | FEEDER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F5 | A3 | 埔五線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔五線A3 | 11KV埔五線 T相AMP | FEEDER |  |  |  |  | CDC | 343 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 | A0 | 埔五線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔五線A0 | 11KV埔五線 N相AMP | FEEDER |  |  |  |  | CDC | 344 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F6 | KVAR | 埔六線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔六線KVAR | 11KV埔六線 KVAR | FEEDER |  |  |  |  | CDC | 345 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F6 | A1 | 埔六線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔六線A1 | 11KV埔六線 R相AMP | FEEDER |  |  |  |  | CDC | 346 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F6 | A2 | 埔六線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔六線A2 | 11KV埔六線 S相AMP | FEEDER |  |  |  |  | CDC | 347 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F6 | A3 | 埔六線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔六線A3 | 11KV埔六線 T相AMP | FEEDER |  |  |  |  | CDC | 348 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F6 | A0 | 埔六線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔六線A0 | 11KV埔六線 N相AMP | FEEDER |  |  |  |  | CDC | 349 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F4 | KVAR | 埔四線無效電力 | KVAR_-7200_7200(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔四線KVAR | 11KV埔四線 KVAR | FEEDER |  |  |  |  | CDC | 350 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 7.2 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F4 | A1 | 埔四線R相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔四線A1 | 11KV埔四線 R相AMP | FEEDER |  |  |  |  | CDC | 351 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R400R | 360 | 361 | 400 | 401 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F4 | A2 | 埔四線S相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔四線A2 | 11KV埔四線 S相AMP | FEEDER |  |  |  |  | CDC | 352 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F4 | A3 | 埔四線T相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔四線A3 | 11KV埔四線 T相AMP | FEEDER |  |  |  |  | CDC | 353 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | C04R0400 | 380 | 400 | 401 | 402 | 0 | -380 | -400 | -401 | -402 | 1 | 0.01 | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F4 | A0 | 埔四線零相電流 | A_-400_400(-2000_2000) |  | B2/S34_D1 | [8 empty] | 嘉埔SS.埔四線A0 | 11KV埔四線 N相AMP | FEEDER |  |  |  |  | CDC | 354 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-150_150(-2000_2000) |  | B3/S34_D1 | [8 empty] | 嘉埔SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 355 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 路燈電源監視 | INSERT | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0533 |  |  | 1-32-01 |  |  | 路燈電源監視 |  | 路燈電源監視 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 356 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-36-00 |  |  | 730 RY | RYFA | 欣欣嘉埔奮起線 電驛故障 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.730_RYFA | 730 RYFA | OTHER | [5 empty] | 357 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | 600 |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-36-01 |  |  | 600 RY | RYFA | 嘉埔奮起線 電驛故障 |  |  | B2/S34_A1 | [8 empty] | 嘉埔SS.600_RYFA | 600 RYFA | OTHER | [5 empty] | 358 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | ＃1MTR | ＃1TR 86A | #1MTR(含87與96P之86RY) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR-86A | #1MTR-86A | OTHER | [5 empty] | 359 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-31-02 |  |  | #1MTR | 1 51ZS | 一號主變51Z電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_51ZS | #1MTR 51ZS | OTHER | [5 empty] | 360 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-31-00 |  |  | #1MTR | 1 87S2 | 一號主變87-2電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_87UL2 | #1MTR 87UL2 | OTHER | [5 empty] | 361 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-31-01 |  |  | #1MTR | #1TR RYFA | 一號主變電驛故障 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#1MTR_RYFA | #1MTR IED警報 | OTHER | [5 empty] | 362 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-02 |  |  | SPARE | ＃2TR 86A | #2MTR(含87與96P之86RY) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR-86A | #2MTR-86A | OTHER | [5 empty] | 363 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-31-06 |  |  | SPARE | 2 51ZS | 二號主變51Z電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_51ZS | #2MTR 51ZS | OTHER | [5 empty] | 364 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-31-04 |  |  | SPARE | 2 87S2 | 二號主變87電驛 (使用/閉鎖) |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_87UL2 | #2MTR 87UL2 | OTHER | [5 empty] | 365 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-31-05 |  |  | SPARE | #2TR RYFA | 二號主變電驛故障 |  |  | B1/S34_D1 | [8 empty] | 嘉埔SS.#2MTR_RYFA | #2MTR IED警報 | OTHER | [5 empty] | 366 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0754 |  |  | 1-3F-14 |  |  | Ladder 14,1 | PMA | POWER METER異常 |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.PMA | POWER METER警報 | OTHER | [5 empty] | 367 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | JY21 | F1 KWH(+) | 埔一線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 368 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | JY22 | F2 KWH(+) | 埔二線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 369 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0016 |  |  | 1-50 |  |  | JY23 | F3 KWH(+) | 埔三線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 370 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0017 |  |  | 1-51 |  |  | SPARE | F4 KWH(+) | 埔四線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 371 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | SPARE | F5 KWH(+) | 埔五線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 372 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0019 |  |  | 1-53 |  |  | SPARE | F6 KWH(+) | 埔六線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 373 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0020 |  |  | 1-54 |  |  | JY27 | F7 KWH(+) | 埔七線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 374 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | JY28 | F8 KWH(+) | 埔八線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 375 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0022 |  |  | 1-56 |  |  | JY29 | F9 KWH(+) | 埔九線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 376 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0023 |  |  | 1-57 |  |  | SPARE | F10 KWH(+) | 埔十線 |  |  | B2/S34_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 377 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Water3 | 地下室淹水(1) |  | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0626 |  |  | 1-37-14 |  |  | 地下室水位(1) |  | 地下室淹水(1) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.地下室淹水(1) | 地下室淹水(1) | OTHER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | StaDev | 所內設施 |  | Water4 | 地下室淹水(2) |  | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-15 |  |  | 地下室水位(2) |  | 地下室淹水(2) |  |  | B3/S34_D1 | [8 empty] | 嘉埔SS.地下室淹水(2) | 地下室淹水(2) | OTHER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.211DS | 211DS (非取樣點) | SC | [5 empty] | 380 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221DS (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.221DS | 221DS (非取樣點) | SC | [5 empty] | 381 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S34_D1 | [8 empty] | 嘉埔SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | [5 empty] | 382 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S34_D1 | [12 empty] | 嘉埔SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S34/69/1BUS/V; OPRD2: S34/69/2BUS/V
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S34_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S34/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S34_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S34/11/M1/MW; OPRD2: S34/11/M2/MW; OPRD3: S34/69/620/MW; OPRD4: S34/69/730/MW
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S34_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S34/0/CalcPoint/OPRN2_MW
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S34_D1 | [17 empty] | none
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S34_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S34/0/CalcPoint/OPRN1; OPRD2: S34/0/CalcPoint/OPRN2; OPRD3: S34/0/CalcPoint/PRFL_UL
S34 | 嘉埔SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S34_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S34/11/M1/MW; OPRD2: S34/11/M1/MVAR; OPRD3: S34/0/CalcPoint/Vbs2
S34 | 嘉埔SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S34_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S34/11/M2/MW; OPRD2: S34/11/M2/MVAR; OPRD3: S34/0/CalcPoint/Vbs2
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S34_A1 | [12 empty] | 嘉埔SS.620_AMP | 嘉埔奮起線 AMP | LINE69 | AMP_CAL | C06R0600 | amp_cal | OPRD1: S34/69/620/MW; OPRD2: S34/69/620/MVAR; OPRD3: S34/0/CalcPoint/Vbs2
S34 | 嘉埔SS | 69 | 69kV | 730 | 竹崎～欣欣、嘉埔、奮起線(730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S34_A1 | [12 empty] | 嘉埔SS.730_AMP | 欣欣奮起嘉埔線 AMP | LINE69 | AMP_CAL | C06R0600 | amp_cal | OPRD1: S34/69/730/MW; OPRD2: S34/69/730/MVAR; OPRD3: S34/0/CalcPoint/Vbs2
S34 | 嘉埔SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S34_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S34/11/1BUS/V
S34 | 嘉埔SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S34_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S34/11/2BUS/V
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S34_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 嘉埔SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S34/11/M1/MW; OPRD2: S34/11/M1/MVAR
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S34_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 嘉埔SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S34/11/M2/MW; OPRD2: S34/11/M2/MVAR
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S34_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S34//1MTR/MVA; OPRD2: 0
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S34_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S34//2MTR/MVA; OPRD2: 0
S34 | 嘉埔SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S34_D1 | [12 empty] | 嘉埔SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S34/11/M1/MW; OPRD2: S34/11/M1/MVAR
S34 | 嘉埔SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S34_D1 | [12 empty] | 嘉埔SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S34/11/M2/MW; OPRD2: S34/11/M2/MVAR
S34 | 嘉埔SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S34_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S34//1MTR/SupLocal; OPRD2: S34//1MTR/Tap Chan; OPRD3: NULL
S34 | 嘉埔SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S34_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S34//2MTR/SupLocal; OPRD2: S34//2MTR/Tap Chan; OPRD3: NULL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/1BUS/V; OPRD2: S34/11/JY21/I_R; OPRD3: S34/11/JY21/I_S; OPRD4: S34/11/JY21/I_T
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/1BUS/V; OPRD2: S34/11/JY22/I_R; OPRD3: S34/11/JY22/I_S; OPRD4: S34/11/JY22/I_T
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/1BUS/V; OPRD2: S34/11/JY23/I_R; OPRD3: S34/11/JY23/I_S; OPRD4: S34/11/JY23/I_T
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/1BUS/V; OPRD2: S34/11/JY24/I_R; OPRD3: S34/11/JY24/I_S; OPRD4: S34/11/JY24/I_T
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/1BUS/V; OPRD2: S34/11/JY25/I_R; OPRD3: S34/11/JY25/I_S; OPRD4: S34/11/JY25/I_T
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY26/I_R; OPRD3: S34/11/JY26/I_S; OPRD4: S34/11/JY26/I_T
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY27/I_R; OPRD3: S34/11/JY27/I_S; OPRD4: S34/11/JY27/I_T
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY28/I_R; OPRD3: S34/11/JY28/I_S; OPRD4: S34/11/JY28/I_T
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY29/I_R; OPRD3: S34/11/JY29/I_S; OPRD4: S34/11/JY29/I_T
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY30/I_R; OPRD3: S34/11/JY30/I_S; OPRD4: S34/11/JY30/I_T
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY31/I_R; OPRD3: S34/11/JY31/I_S; OPRD4: S34/11/JY31/I_T
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S34/11/2BUS/V; OPRD2: S34/11/JY32/I_R; OPRD3: S34/11/JY32/I_S; OPRD4: S34/11/JY32/I_T
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY21/kVA; OPRD2: S34/11/JY21/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY22/kVA; OPRD2: S34/11/JY22/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY23/kVA; OPRD2: S34/11/JY23/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY24/kVA; OPRD2: S34/11/JY24/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY25/kVA; OPRD2: S34/11/JY25/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY26/kVA; OPRD2: S34/11/JY26/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY27/kVA; OPRD2: S34/11/JY27/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY28/kVA; OPRD2: S34/11/JY28/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY29/kVA; OPRD2: S34/11/JY29/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY30/kVA; OPRD2: S34/11/JY30/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY31/kVA; OPRD2: S34/11/JY31/KVAR
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S34_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S34/11/JY32/kVA; OPRD2: S34/11/JY32/KVAR
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S34_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S34/11/M1/MW; OPRD2: S34/11/M2/MW
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S34_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S34/11/M1/MVAR; OPRD2: S34/11/M2/MVAR
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S34_D1 | [12 empty] | 嘉埔SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: S34/11/210/CB; OPRD2: 6.9; OPRD3: 0
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S34_D1 | [12 empty] | 嘉埔SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: S34/11/220/CB; OPRD2: 6.9; OPRD3: 0
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S34_D1 | [12 empty] | 嘉埔SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_18 | OPRD1: S34//1MTR/96B1; OPRD2: S34//1MTR/96PA; OPRD3: S34//1MTR/TRA; OPRD4: S34//1MTR/63Q; OPRD5: S34//1MTR/96D; OPRD6: S34//1MTR/96B2; OPRD7: S34//1MTR/87A; OPRD8: S34//1MTR/51ZA; OPRD9: S34//2MTR/96B1; OPRD10: S34//2MTR/63Q; OPRD11: S34//2MTR/96D; OPRD12: S34//2MTR/96B2; OPRD13: S34//2MTR/96PA; OPRD14: S34//2MTR/51ZA; OPRD15: S34//2MTR/TRA; OPRD16: S34//2MTR/87A; OPRD17: S34/69/1BUS/87A; OPRD18: S34/69/2BUS/87A
S34 | 嘉埔SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S34_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S34//1MTR/TRF; OPRD2: S34//2MTR/TRF
S34 | 嘉埔SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/RTU/RTU_R_L
S34 | 嘉埔SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/StaDev/DCE
S34 | 嘉埔SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/StaDev/Fire
S34 | 嘉埔SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/StaDev/DCA
S34 | 嘉埔SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S34_D1 | [17 empty] | lamp2CC | OPRD1: S34/69/ComPoint/CBF
S34 | 嘉埔SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S34_D1 | [17 empty] | lamp2CC | OPRD1: S34/69/ComPoint/CBA
S34 | 嘉埔SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S34_D1 | [17 empty] | lamp2CC | OPRD1: S34/69/ComPoint/ABS_89A
S34 | 嘉埔SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/StaDev/PSF
S34 | 嘉埔SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S34_A1 | [17 empty] | lamp2CC | OPRD1: S34/0/StaDev/PSA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S34 | 嘉埔SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 嘉埔SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S34/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉埔SS.620_AMP | 嘉埔奮起線 AMP | LINE69 | S34/69/620/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C06R0600 | 540.000000 | 540.000000 | 600.000000 | 600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉埔SS.730_AMP | 欣欣奮起嘉埔線 AMP | LINE69 | S34/69/730/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C06R0600 | 540.000000 | 540.000000 | 600.000000 | 600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線KVA | 11KV埔一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔一線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線KW | 11KV埔一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線KVA | 11KV埔七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔七線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線KW | 11KV埔七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線KVA | 11KV埔九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔九線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線KW | 11KV埔九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線KVA | 11KV埔二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔二線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線KW | 11KV埔二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線KVA | 11KV埔八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔八線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線KW | 11KV埔八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線KVA | 11KV埔十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十一線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線KW | 11KV埔十一線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線KVA | 11KV埔十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十二線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線KW | 11KV埔十二線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線KVA | 11KV埔十線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔十線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線KW | 11KV埔十線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線KVA | 11KV埔三線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔三線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線KW | 11KV埔三線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線KVA | 11KV埔五線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔五線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線KW | 11KV埔五線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線KVA | 11KV埔六線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔六線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線KW | 11KV埔六線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線KVA | 11KV埔四線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  |  |  |  | 埔四線KW | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線KW | 11KV埔四線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S34//1MTR/MVA |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_PF | #1MTR 功率因素 | DTR | S34//1MTR/PF |  | RPDC_PF_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S34//2MTR/MVA |  | MVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_PF | #2MTR 功率因素 | DTR | S34//2MTR/PF |  | RPDC_PF_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S34 | 嘉埔SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S34/11/210/MVAR |  | SC_LBS_11 |  |  | 33 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S34/11/220/MVAR |  | SC_LBS_11 |  |  | 34 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 69 | 69kV | 620_CB | 嘉埔奮起線(620_CB) | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.620_CB_2 | 620(嘉埔奮起線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730_CB | 欣欣奮起嘉埔線(730_CB) | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.730_CB_2 | 730(欣欣奮起嘉埔線) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 600_CB | 600(600_CB) | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.600_CB_2 | 600 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 37 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 38 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 40 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 41 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S34 | 嘉埔SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 嘉埔SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S34/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 43 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 44 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 45 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620_AMP | 嘉埔奮起線 | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.620_AMP_A | 嘉埔奮起線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620_AMP | 嘉埔奮起線 | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.620_AMP_2 | 嘉埔奮起線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 47 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730_AMP | 欣欣奮起嘉埔線 | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.730_AMP_A | 欣欣奮起嘉埔線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730_AMP | 欣欣奮起嘉埔線 | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.730_AMP_2 | 欣欣奮起嘉埔線 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_MVA_2 | #1MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 51 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 53 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S34 | 嘉埔SS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 嘉埔SS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 730_RYFA | 730 | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.730_RYFA_A | 730 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 600_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 嘉埔SS.600_RYFA_A | 600 RYFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S34/0/RTU/ADCH1 |  |  |  | CDC | 57 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S34/0/RTU/ADCH2 |  |  |  | CDC | 58 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S34/0/RTU/ADCL1 |  |  |  | CDC | 59 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S34/0/RTU/ADCL2 |  |  |  | CDC | 60 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S34/69/1BUS/V |  |  |  | CDC | 61 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S34 | 嘉埔SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S34/69/2BUS/V |  |  |  | CDC | 62 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S34 | 嘉埔SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-B7 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S34/11/1BUS/V |  |  |  | CDC | 63 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S34 | 嘉埔SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-B8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S34/11/2BUS/V |  |  |  | CDC | 64 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | MW | [17 empty] | 1-8B | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.620_MW | 嘉埔奮起線 MW | LINE69 | S34/69/620/MW |  |  |  | CDC | 65 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | MVAR | [17 empty] | 1-8C | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.620_MVAR | 嘉埔奮起線 MVAR | LINE69 | S34/69/620/MVAR |  |  |  | CDC | 66 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.730_MW | 欣欣奮起嘉埔線 MW | LINE69 | S34/69/730/MW |  |  |  | CDC | 67 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.730_MVAR | 欣欣奮起嘉埔線 MVAR | LINE69 | S34/69/730/MVAR |  |  |  | CDC | 68 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔一線 | 埔一線 |  | 埔一線KVAR | [17 empty] | 1-99 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線KVAR | 11KV埔一線 KVAR | FEEDER | S34/11/JY21/KVAR |  |  |  | CDC | 69 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔一線 | 埔一線 |  | 埔一線A1 | [17 empty] | 1-9A | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線A1 | 11KV埔一線 R相AMP | FEEDER | S34/11/JY21/I_R |  |  |  | CDC | 70 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔一線 | 埔一線 |  | 埔一線A2 | [17 empty] | 1-9B | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線A2 | 11KV埔一線 S相AMP | FEEDER | S34/11/JY21/I_S |  |  |  | CDC | 71 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔一線 | 埔一線 |  | 埔一線A3 | [17 empty] | 1-9C | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線A3 | 11KV埔一線 T相AMP | FEEDER | S34/11/JY21/I_T |  |  |  | CDC | 72 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔一線 | 埔一線 |  | 埔一線A0 | [17 empty] | 1-9D | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔一線A0 | 11KV埔一線 N相AMP | FEEDER | S34/11/JY21/I_N |  |  |  | CDC | 73 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔七線 | 埔七線 |  | 埔七線KVAR | [17 empty] | 1-C9 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線KVAR | 11KV埔七線 KVAR | FEEDER | S34/11/JY27/KVAR |  |  |  | CDC | 74 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔七線 | 埔七線 |  | 埔七線A1 | [17 empty] | 1-CA | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線A1 | 11KV埔七線 R相AMP | FEEDER | S34/11/JY27/I_R |  |  |  | CDC | 75 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔七線 | 埔七線 |  | 埔七線A2 | [17 empty] | 1-CB | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線A2 | 11KV埔七線 S相AMP | FEEDER | S34/11/JY27/I_S |  |  |  | CDC | 76 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔七線 | 埔七線 |  | 埔七線A3 | [17 empty] | 1-CC | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線A3 | 11KV埔七線 T相AMP | FEEDER | S34/11/JY27/I_T |  |  |  | CDC | 77 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔七線 | 埔七線 |  | 埔七線A0 | [17 empty] | 1-CD | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔七線A0 | 11KV埔七線 N相AMP | FEEDER | S34/11/JY27/I_N |  |  |  | CDC | 78 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔九線 | 埔九線 |  | 埔九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線KVAR | 11KV埔九線 KVAR | FEEDER | S34/11/JY29/KVAR |  |  |  | CDC | 79 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔九線 | 埔九線 |  | 埔九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線A1 | 11KV埔九線 R相AMP | FEEDER | S34/11/JY29/I_R |  |  |  | CDC | 80 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔九線 | 埔九線 |  | 埔九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線A2 | 11KV埔九線 S相AMP | FEEDER | S34/11/JY29/I_S |  |  |  | CDC | 81 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔九線 | 埔九線 |  | 埔九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線A3 | 11KV埔九線 T相AMP | FEEDER | S34/11/JY29/I_T |  |  |  | CDC | 82 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔九線 | 埔九線 |  | 埔九線A0 | [17 empty] | 1-D7 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔九線A0 | 11KV埔九線 N相AMP | FEEDER | S34/11/JY29/I_N |  |  |  | CDC | 83 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔二線 | 埔二線 |  | 埔二線KVAR | [17 empty] | 1-9E | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線KVAR | 11KV埔二線 KVAR | FEEDER | S34/11/JY22/KVAR |  |  |  | CDC | 84 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔二線 | 埔二線 |  | 埔二線A1 | [17 empty] | 1-9F | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線A1 | 11KV埔二線 R相AMP | FEEDER | S34/11/JY22/I_R |  |  |  | CDC | 85 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔二線 | 埔二線 |  | 埔二線A2 | [17 empty] | 1-A0 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線A2 | 11KV埔二線 S相AMP | FEEDER | S34/11/JY22/I_S |  |  |  | CDC | 86 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔二線 | 埔二線 |  | 埔二線A3 | [17 empty] | 1-A1 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線A3 | 11KV埔二線 T相AMP | FEEDER | S34/11/JY22/I_T |  |  |  | CDC | 87 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔二線 | 埔二線 |  | 埔二線A0 | [17 empty] | 1-A2 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔二線A0 | 11KV埔二線 N相AMP | FEEDER | S34/11/JY22/I_N |  |  |  | CDC | 88 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔八線 | 埔八線 |  | 埔八線KVAR | [17 empty] | 1-CE | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線KVAR | 11KV埔八線 KVAR | FEEDER | S34/11/JY28/KVAR |  |  |  | CDC | 89 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔八線 | 埔八線 |  | 埔八線A1 | [17 empty] | 1-CF | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線A1 | 11KV埔八線 R相AMP | FEEDER | S34/11/JY28/I_R |  |  |  | CDC | 90 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔八線 | 埔八線 |  | 埔八線A2 | [17 empty] | 1-D0 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線A2 | 11KV埔八線 S相AMP | FEEDER | S34/11/JY28/I_S |  |  |  | CDC | 91 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔八線 | 埔八線 |  | 埔八線A3 | [17 empty] | 1-D1 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線A3 | 11KV埔八線 T相AMP | FEEDER | S34/11/JY28/I_T |  |  |  | CDC | 92 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔八線 | 埔八線 |  | 埔八線A0 | [17 empty] | 1-D2 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔八線A0 | 11KV埔八線 N相AMP | FEEDER | S34/11/JY28/I_N |  |  |  | CDC | 93 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十一線 | 埔十一線 |  | 埔十一線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線KVAR | 11KV埔十一線 KVAR | FEEDER | S34/11/JY31/KVAR |  |  |  | CDC | 94 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十一線 | 埔十一線 |  | 埔十一線A1 | [17 empty] | 1-DE | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線A1 | 11KV埔十一線 R相AMP | FEEDER | S34/11/JY31/I_R |  |  |  | CDC | 95 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十一線 | 埔十一線 |  | 埔十一線A2 | [17 empty] | 1-DF | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線A2 | 11KV埔十一線 S相AMP | FEEDER | S34/11/JY31/I_S |  |  |  | CDC | 96 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十一線 | 埔十一線 |  | 埔十一線A3 | [17 empty] | 1-E0 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線A3 | 11KV埔十一線 T相AMP | FEEDER | S34/11/JY31/I_T |  |  |  | CDC | 97 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十一線 | 埔十一線 |  | 埔十一線A0 | [17 empty] | 1-E1 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十一線A0 | 11KV埔十一線 N相AMP | FEEDER | S34/11/JY31/I_N |  |  |  | CDC | 98 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十二線 | 埔十二線 |  | 埔十二線KVAR | [17 empty] | 1-E2 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線KVAR | 11KV埔十二線 KVAR | FEEDER | S34/11/JY32/KVAR |  |  |  | CDC | 99 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十二線 | 埔十二線 |  | 埔十二線A1 | [17 empty] | 1-E3 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線A1 | 11KV埔十二線 R相AMP | FEEDER | S34/11/JY32/I_R |  |  |  | CDC | 100 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十二線 | 埔十二線 |  | 埔十二線A2 | [17 empty] | 1-E4 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線A2 | 11KV埔十二線 S相AMP | FEEDER | S34/11/JY32/I_S |  |  |  | CDC | 101 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十二線 | 埔十二線 |  | 埔十二線A3 | [17 empty] | 1-E5 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線A3 | 11KV埔十二線 T相AMP | FEEDER | S34/11/JY32/I_T |  |  |  | CDC | 102 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十二線 | 埔十二線 |  | 埔十二線A0 | [17 empty] | 1-E6 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十二線A0 | 11KV埔十二線 N相AMP | FEEDER | S34/11/JY32/I_N |  |  |  | CDC | 103 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十線 | 埔十線 |  | 埔十線KVAR | [17 empty] | 1-D8 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線KVAR | 11KV埔十線 KVAR | FEEDER | S34/11/JY30/KVAR |  |  |  | CDC | 104 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十線 | 埔十線 |  | 埔十線A1 | [17 empty] | 1-D9 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線A1 | 11KV埔十線 R相AMP | FEEDER | S34/11/JY30/I_R |  |  |  | CDC | 105 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十線 | 埔十線 |  | 埔十線A2 | [17 empty] | 1-DA | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線A2 | 11KV埔十線 S相AMP | FEEDER | S34/11/JY30/I_S |  |  |  | CDC | 106 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十線 | 埔十線 |  | 埔十線A3 | [17 empty] | 1-DB | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線A3 | 11KV埔十線 T相AMP | FEEDER | S34/11/JY30/I_T |  |  |  | CDC | 107 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔十線 | 埔十線 |  | 埔十線A0 | [17 empty] | 1-DC | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔十線A0 | 11KV埔十線 N相AMP | FEEDER | S34/11/JY30/I_N |  |  |  | CDC | 108 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔三線 | 埔三線 |  | 埔三線KVAR | [17 empty] | 1-A3 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線KVAR | 11KV埔三線 KVAR | FEEDER | S34/11/JY23/KVAR |  |  |  | CDC | 109 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔三線 | 埔三線 |  | 埔三線A1 | [17 empty] | 1-A4 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線A1 | 11KV埔三線 R相AMP | FEEDER | S34/11/JY23/I_R |  |  |  | CDC | 110 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔三線 | 埔三線 |  | 埔三線A2 | [17 empty] | 1-A5 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線A2 | 11KV埔三線 S相AMP | FEEDER | S34/11/JY23/I_S |  |  |  | CDC | 111 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔三線 | 埔三線 |  | 埔三線A3 | [17 empty] | 1-A6 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線A3 | 11KV埔三線 T相AMP | FEEDER | S34/11/JY23/I_T |  |  |  | CDC | 112 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔三線 | 埔三線 |  | 埔三線A0 | [17 empty] | 1-A7 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔三線A0 | 11KV埔三線 N相AMP | FEEDER | S34/11/JY23/I_N |  |  |  | CDC | 113 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔五線 | 埔五線 |  | 埔五線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線KVAR | 11KV埔五線 KVAR | FEEDER | S34/11/JY25/KVAR |  |  |  | CDC | 114 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔五線 | 埔五線 |  | 埔五線A1 | [17 empty] | 1-AE | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線A1 | 11KV埔五線 R相AMP | FEEDER | S34/11/JY25/I_R |  |  |  | CDC | 115 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔五線 | 埔五線 |  | 埔五線A2 | [17 empty] | 1-AF | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線A2 | 11KV埔五線 S相AMP | FEEDER | S34/11/JY25/I_S |  |  |  | CDC | 116 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔五線 | 埔五線 |  | 埔五線A3 | [17 empty] | 1-B0 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線A3 | 11KV埔五線 T相AMP | FEEDER | S34/11/JY25/I_T |  |  |  | CDC | 117 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔五線 | 埔五線 |  | 埔五線A0 | [17 empty] | 1-B1 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔五線A0 | 11KV埔五線 N相AMP | FEEDER | S34/11/JY25/I_N |  |  |  | CDC | 118 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔六線 | 埔六線 |  | 埔六線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線KVAR | 11KV埔六線 KVAR | FEEDER | S34/11/JY26/KVAR |  |  |  | CDC | 119 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔六線 | 埔六線 |  | 埔六線A1 | [17 empty] | 1-B3 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線A1 | 11KV埔六線 R相AMP | FEEDER | S34/11/JY26/I_R |  |  |  | CDC | 120 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔六線 | 埔六線 |  | 埔六線A2 | [17 empty] | 1-B4 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線A2 | 11KV埔六線 S相AMP | FEEDER | S34/11/JY26/I_S |  |  |  | CDC | 121 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔六線 | 埔六線 |  | 埔六線A3 | [17 empty] | 1-B5 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線A3 | 11KV埔六線 T相AMP | FEEDER | S34/11/JY26/I_T |  |  |  | CDC | 122 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔六線 | 埔六線 |  | 埔六線A0 | [17 empty] | 1-B6 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔六線A0 | 11KV埔六線 N相AMP | FEEDER | S34/11/JY26/I_N |  |  |  | CDC | 123 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔四線 | 埔四線 |  | 埔四線KVAR | [17 empty] | 1-A8 | [5 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線KVAR | 11KV埔四線 KVAR | FEEDER | S34/11/JY24/KVAR |  |  |  | CDC | 124 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔四線 | 埔四線 |  | 埔四線A1 | [17 empty] | 1-A9 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線A1 | 11KV埔四線 R相AMP | FEEDER | S34/11/JY24/I_R |  |  |  | CDC | 125 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R400R | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔四線 | 埔四線 |  | 埔四線A2 | [17 empty] | 1-AA | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線A2 | 11KV埔四線 S相AMP | FEEDER | S34/11/JY24/I_S |  |  |  | CDC | 126 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔四線 | 埔四線 |  | 埔四線A3 | [17 empty] | 1-AB | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線A3 | 11KV埔四線 T相AMP | FEEDER | S34/11/JY24/I_T |  |  |  | CDC | 127 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C04R0400 | 360.000000 | 360.000000 | 400.000000 | 400.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | 埔四線 | 埔四線 |  | 埔四線A0 | [17 empty] | 1-AC | [5 empty] | A_-400_400(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.埔四線A0 | 11KV埔四線 N相AMP | FEEDER | S34/11/JY24/I_N |  |  |  | CDC | 128 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-88 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 嘉埔SS.600TIE_AMP | 600TIE AMP | TIE | S34/69/600/I |  |  |  | CDC | 129 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-93 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_MW | #1MTR二次側 MW | DTR | S34/11/M1/MW |  |  |  | CDC | 130 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-94 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S34/11/M1/MVAR |  |  |  | CDC | 131 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-95 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S34/11/M1/I_R |  |  |  | CDC | 132 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-96 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S34/11/M1/I_S |  |  |  | CDC | 133 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-97 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S34/11/M1/I_T |  |  |  | CDC | 134 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-8E | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_OIL | #1MTR 油溫 | DTR | S34//1MTR/OilTemp |  |  |  | CDC | 135 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-8D | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_COIL | #1MTR 線溫 | DTR | S34//1MTR/CoilTemp |  |  |  | CDC | 136 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-8F |  | 1-46 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S34//1MTR/TapPosMv |  |  |  | CDC | 137 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C3 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_MW | #2MTR二次側 MW | DTR | S34/11/M2/MW |  |  |  | CDC | 138 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C4 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S34/11/M2/MVAR |  |  |  | CDC | 139 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S34/11/M2/I_R |  |  |  | CDC | 140 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S34/11/M2/I_S |  |  |  | CDC | 141 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S34/11/M2/I_T |  |  |  | CDC | 142 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-91 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_OIL | #2MTR 油溫 | DTR | S34//2MTR/OilTemp |  |  |  | CDC | 143 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-90 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_COIL | #2MTR 線溫 | DTR | S34//2MTR/CoilTemp |  |  |  | CDC | 144 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-92 |  | 1-47 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S34//2MTR/TapPosMv |  |  |  | CDC | 145 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S34 | 嘉埔SS | 0 |  |  |  |  | DCV | [17 empty] | 1-E7 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.直流電源電壓 | 直流電源電壓 | OTHER | S34/0/StaDev/DCV |  |  |  | CDC | 146 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-B9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S34/11/TIE2/I_R |  |  |  | CDC | 147 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-BA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S34/11/TIE2/I_S |  |  |  | CDC | 148 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-BB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S34/11/TIE2/I_T |  |  |  | CDC | 149 | GENERICAIPoint | SS215_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | PHA | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.620_PHA | 嘉埔奮起線(620) 相間RY | LINE69 | S34/69/620/PHA |  |  |  | CDC | 150 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | GDA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.620_GDA | 嘉埔奮起線(620) 接地RY | LINE69 | S34/69/620/GDA |  |  |  | CDC | 151 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 85A | [17 empty] | 1-0A-00 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.620_85A | 嘉埔奮起線(620) 85RY | LINE69 | S34/69/620/85A |  |  |  | CDC | 152 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 74A | [17 empty] | 1-38-07 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.620_74A | 嘉埔奮起線(620) 74RY | LINE69 | S34/69/620/74A |  |  |  | CDC | 153 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | 85UL | [17 empty] | 1-38-06 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.620_85UL | 嘉埔奮起線(620) 85RY U/L | LINE69 | S34/69/620/85UL |  |  |  | CDC | 154 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | CB | [17 empty] | 1-09-07 |  | 1-06 | [5 empty] | 69KV_N | [8 empty] | 嘉埔SS.620_CB | 620(嘉埔奮起線) CB | LINE69 | S34/69/620/CB |  |  |  | CDC | 155 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS1 | 621 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-58 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.621_DS | 621(嘉埔奮起線) DS | LINE69 | S34/69/620/DS1 |  |  |  | CDC | 156 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS2 | 622 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-59 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.622_DS | 622(嘉埔奮起線) DS | LINE69 | S34/69/620/DS2 |  |  |  | CDC | 157 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | DS3 | 623 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-5A | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.623_DS | 623(嘉埔奮起線) DS | LINE69 | S34/69/620/DS3 |  |  |  | CDC | 158 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | E3 | 623E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-5B | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.623E_ES | 623E(嘉埔奮起線) ES | LINE69 | S34/69/620/ES3 |  |  |  | CDC | 159 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | PHA | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.730_PHA | 欣欣奮起嘉埔線(730) 相間RY | LINE69 | S34/69/730/PHA |  |  |  | CDC | 160 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | GDA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.730_GDA | 欣欣奮起嘉埔線(730) 接地RY | LINE69 | S34/69/730/GDA |  |  |  | CDC | 161 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | CB | [17 empty] | 1-09-03 |  | 1-05 | [5 empty] | 69KV_N | [8 empty] | 嘉埔SS.730_CB | 730(欣欣奮起嘉埔線) CB | LINE69 | S34/69/730/CB |  |  |  | CDC | 162 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | DS1 | 731 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.731_DS | 731(欣欣奮起嘉埔線) DS | LINE69 | S34/69/730/DS1 |  |  |  | CDC | 163 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | DS2 | 732 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-55 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.732_DS | 732(欣欣奮起嘉埔線) DS | LINE69 | S34/69/730/DS2 |  |  |  | CDC | 164 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | DS3 | 733 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-56 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.733_DS | 733(欣欣奮起嘉埔線) DS | LINE69 | S34/69/730/DS3 |  |  |  | CDC | 165 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | E3 | 733E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-57 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.733E_ES | 733E(欣欣奮起嘉埔線) ES | LINE69 | S34/69/730/ES3 |  |  |  | CDC | 166 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_PHA | 11KV埔一線(JY21) 相間RY | FEEDER | S34/11/JY21/PHA |  |  |  | CDC | 167 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_GDA | 11KV埔一線(JY21) 接地RY | FEEDER | S34/11/JY21/GDA |  |  |  | CDC | 168 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY21 | 埔一線(JY21) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-28 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_79UL | 11KV埔一線(JY21) 79RY U/L | FEEDER | S34/11/JY21/79UL |  |  |  | CDC | 169 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY21_LCO | 埔一線(JY21) LCO |  | TapPosMv | [17 empty] | 1-33-09 |  | 1-29 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_LCO_TAP | 11KV埔一線(JY21) LCO TAP | FEEDER | S34/11/JY21/IED_ADJ |  |  |  | CDC | 170 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY21 | JY21(11KV埔一線) |  | CB | [17 empty] | 1-0C-02 |  | 1-0B | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_CB | JY21(11KV埔一線) CB | FEEDER | S34/11/JY21/CB |  |  |  | CDC | 171 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_PHA | 11KV埔二線(JY22) 相間RY | FEEDER | S34/11/JY22/PHA |  |  |  | CDC | 172 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_GDA | 11KV埔二線(JY22) 接地RY | FEEDER | S34/11/JY22/GDA |  |  |  | CDC | 173 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY22 | 埔二線(JY22) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-2A | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_79UL | 11KV埔二線(JY22) 79RY U/L | FEEDER | S34/11/JY22/79UL |  |  |  | CDC | 174 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY22_LCO | 埔二線(JY22) LCO |  | TapPosMv | [17 empty] | 1-33-11 |  | 1-2B | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_LCO_TAP | 11KV埔二線(JY22) LCO TAP | FEEDER | S34/11/JY22/IED_ADJ |  |  |  | CDC | 175 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY22 | JY22(11KV埔二線) |  | CB | [17 empty] | 1-0C-05 |  | 1-0C | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_CB | JY22(11KV埔二線) CB | FEEDER | S34/11/JY22/CB |  |  |  | CDC | 176 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_PHA | 11KV埔三線(JY23) 相間RY | FEEDER | S34/11/JY23/PHA |  |  |  | CDC | 177 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_GDA | 11KV埔三線(JY23) 接地RY | FEEDER | S34/11/JY23/GDA |  |  |  | CDC | 178 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY23 | 埔三線(JY23) 79RY |  | 79UL | [17 empty] | 1-33-12 |  | 1-2C | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_79UL | 11KV埔三線(JY23) 79RY U/L | FEEDER | S34/11/JY23/79UL |  |  |  | CDC | 179 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY23_LCO | 埔三線(JY23) LCO |  | TapPosMv | [17 empty] | 1-33-13 |  | 1-2D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_LCO_TAP | 11KV埔三線(JY23) LCO TAP | FEEDER | S34/11/JY23/IED_ADJ |  |  |  | CDC | 180 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY23 | JY23(11KV埔三線) |  | CB | [17 empty] | 1-0D-00 |  | 1-0D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_CB | JY23(11KV埔三線) CB | FEEDER | S34/11/JY23/CB |  |  |  | CDC | 181 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_PHA | 11KV埔四線(JY24) 相間RY | FEEDER | S34/11/JY24/PHA |  |  |  | CDC | 182 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_GDA | 11KV埔四線(JY24) 接地RY | FEEDER | S34/11/JY24/GDA |  |  |  | CDC | 183 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY24 | 埔四線(JY24) 79RY |  | 79UL | [17 empty] | 1-33-14 |  | 1-2E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_79UL | 11KV埔四線(JY24) 79RY U/L | FEEDER | S34/11/JY24/79UL |  |  |  | CDC | 184 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY24_LCO | 埔四線(JY24) LCO |  | TapPosMv | [17 empty] | 1-33-15 |  | 1-2F | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_LCO_TAP | 11KV埔四線(JY24) LCO TAP | FEEDER | S34/11/JY24/IED_ADJ |  |  |  | CDC | 185 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY24 | JY24(11KV埔四線) |  | CB | [17 empty] | 1-0D-03 |  | 1-0E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_CB | JY24(11KV埔四線) CB | FEEDER | S34/11/JY24/CB |  |  |  | CDC | 186 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_PHA | 11KV埔五線(JY25) 相間RY | FEEDER | S34/11/JY25/PHA |  |  |  | CDC | 187 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_GDA | 11KV埔五線(JY25) 接地RY | FEEDER | S34/11/JY25/GDA |  |  |  | CDC | 188 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY25 | 埔五線(JY25) 79RY |  | 79UL | [17 empty] | 1-34-00 |  | 1-30 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_79UL | 11KV埔五線(JY25) 79RY U/L | FEEDER | S34/11/JY25/79UL |  |  |  | CDC | 189 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY25_LCO | 埔五線(JY25) LCO |  | TapPosMv | [17 empty] | 1-34-01 |  | 1-31 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_LCO_TAP | 11KV埔五線(JY25) LCO TAP | FEEDER | S34/11/JY25/IED_ADJ |  |  |  | CDC | 190 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY25 | JY25(11KV埔五線) |  | CB | [17 empty] | 1-0D-06 |  | 1-0F | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_CB | JY25(11KV埔五線) CB | FEEDER | S34/11/JY25/CB |  |  |  | CDC | 191 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | PHA | [17 empty] | 1-0E-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_PHA | 11KV埔六線(JY26) 相間RY | FEEDER | S34/11/JY26/PHA |  |  |  | CDC | 192 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) |  | GDA | [17 empty] | 1-0E-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_GDA | 11KV埔六線(JY26) 接地RY | FEEDER | S34/11/JY26/GDA |  |  |  | CDC | 193 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY26 | 埔六線(JY26) 79RY |  | 79UL | [17 empty] | 1-34-02 |  | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_79UL | 11KV埔六線(JY26) 79RY U/L | FEEDER | S34/11/JY26/79UL |  |  |  | CDC | 194 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY26_LCO | 埔六線(JY26) LCO |  | TapPosMv | [17 empty] | 1-34-03 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_LCO_TAP | 11KV埔六線(JY26) LCO TAP | FEEDER | S34/11/JY26/IED_ADJ |  |  |  | CDC | 195 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY26 | JY26(11KV埔六線) |  | CB | [17 empty] | 1-0E-01 |  | 1-10 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_CB | JY26(11KV埔六線) CB | FEEDER | S34/11/JY26/CB |  |  |  | CDC | 196 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | PHA | [17 empty] | 1-0F-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_PHA | 11KV埔七線(JY27) 相間RY | FEEDER | S34/11/JY27/PHA |  |  |  | CDC | 197 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) |  | GDA | [17 empty] | 1-0F-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_GDA | 11KV埔七線(JY27) 接地RY | FEEDER | S34/11/JY27/GDA |  |  |  | CDC | 198 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY27 | 埔七線(JY27) 79RY |  | 79UL | [17 empty] | 1-34-04 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_79UL | 11KV埔七線(JY27) 79RY U/L | FEEDER | S34/11/JY27/79UL |  |  |  | CDC | 199 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY27_LCO | 埔七線(JY27) LCO |  | TapPosMv | [17 empty] | 1-34-05 |  | 1-35 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_LCO_TAP | 11KV埔七線(JY27) LCO TAP | FEEDER | S34/11/JY27/IED_ADJ |  |  |  | CDC | 200 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY27 | JY27(11KV埔七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-17 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_CB | JY27(11KV埔七線) CB | FEEDER | S34/11/JY27/CB |  |  |  | CDC | 201 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | PHA | [17 empty] | 1-0F-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_PHA | 11KV埔八線(JY28) 相間RY | FEEDER | S34/11/JY28/PHA |  |  |  | CDC | 202 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) |  | GDA | [17 empty] | 1-0F-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_GDA | 11KV埔八線(JY28) 接地RY | FEEDER | S34/11/JY28/GDA |  |  |  | CDC | 203 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY28 | 埔八線(JY28) 79RY |  | 79UL | [17 empty] | 1-34-06 |  | 1-36 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_79UL | 11KV埔八線(JY28) 79RY U/L | FEEDER | S34/11/JY28/79UL |  |  |  | CDC | 204 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY28_LCO | 埔八線(JY28) LCO |  | TapPosMv | [17 empty] | 1-34-07 |  | 1-37 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_LCO_TAP | 11KV埔八線(JY28) LCO TAP | FEEDER | S34/11/JY28/IED_ADJ |  |  |  | CDC | 205 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY28 | JY28(11KV埔八線) |  | CB | [17 empty] | 1-0F-02 |  | 1-18 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_CB | JY28(11KV埔八線) CB | FEEDER | S34/11/JY28/CB |  |  |  | CDC | 206 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | PHA | [17 empty] | 1-0F-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_PHA | 11KV埔九線(JY29) 相間RY | FEEDER | S34/11/JY29/PHA |  |  |  | CDC | 207 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) |  | GDA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_GDA | 11KV埔九線(JY29) 接地RY | FEEDER | S34/11/JY29/GDA |  |  |  | CDC | 208 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY29 | 埔九線(JY29) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-38 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_79UL | 11KV埔九線(JY29) 79RY U/L | FEEDER | S34/11/JY29/79UL |  |  |  | CDC | 209 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY29_LCO | 埔九線(JY29) LCO |  | TapPosMv | [17 empty] | 1-34-09 |  | 1-39 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_LCO_TAP | 11KV埔九線(JY29) LCO TAP | FEEDER | S34/11/JY29/IED_ADJ |  |  |  | CDC | 210 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY29 | JY29(11KV埔九線) |  | CB | [17 empty] | 1-0F-05 |  | 1-19 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_CB | JY29(11KV埔九線) CB | FEEDER | S34/11/JY29/CB |  |  |  | CDC | 211 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_PHA | 11KV埔十線(JY30) 相間RY | FEEDER | S34/11/JY30/PHA |  |  |  | CDC | 212 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_GDA | 11KV埔十線(JY30) 接地RY | FEEDER | S34/11/JY30/GDA |  |  |  | CDC | 213 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY30 | 埔十線(JY30) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-3A | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_79UL | 11KV埔十線(JY30) 79RY U/L | FEEDER | S34/11/JY30/79UL |  |  |  | CDC | 214 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY30_LCO | 埔十線(JY30) LCO |  | TapPosMv | [17 empty] | 1-34-11 |  | 1-3B | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_LCO_TAP | 11KV埔十線(JY30) LCO TAP | FEEDER | S34/11/JY30/IED_ADJ |  |  |  | CDC | 215 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY30 | JY30(11KV埔十線) |  | CB | [17 empty] | 1-10-00 |  | 1-1A | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_CB | JY30(11KV埔十線) CB | FEEDER | S34/11/JY30/CB |  |  |  | CDC | 216 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_PHA | 11KV埔十一線(JY31) 相間RY | FEEDER | S34/11/JY31/PHA |  |  |  | CDC | 217 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_GDA | 11KV埔十一線(JY31) 接地RY | FEEDER | S34/11/JY31/GDA |  |  |  | CDC | 218 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY31 | 埔十一線(JY31) 79RY |  | 79UL | [17 empty] | 1-34-12 |  | 1-3C | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_79UL | 11KV埔十一線(JY31) 79RY U/L | FEEDER | S34/11/JY31/79UL |  |  |  | CDC | 219 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY31_LCO | 埔十一線(JY31) LCO |  | TapPosMv | [17 empty] | 1-34-13 |  | 1-3D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_LCO_TAP | 11KV埔十一線(JY31) LCO TAP | FEEDER | S34/11/JY31/IED_ADJ |  |  |  | CDC | 220 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY31 | JY31(11KV埔十一線) |  | CB | [17 empty] | 1-10-03 |  | 1-1B | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_CB | JY31(11KV埔十一線) CB | FEEDER | S34/11/JY31/CB |  |  |  | CDC | 221 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_PHA | 11KV埔十二線(JY32) 相間RY | FEEDER | S34/11/JY32/PHA |  |  |  | CDC | 222 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_GDA | 11KV埔十二線(JY32) 接地RY | FEEDER | S34/11/JY32/GDA |  |  |  | CDC | 223 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | JY32 | 埔十二線(JY32) 79RY |  | 79UL | [17 empty] | 1-34-14 |  | 1-3E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_79UL | 11KV埔十二線(JY32) 79RY U/L | FEEDER | S34/11/JY32/79UL |  |  |  | CDC | 224 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV | JY32_LCO | 埔十二線(JY32) LCO |  | TapPosMv | [17 empty] | 1-34-15 |  | 1-3F | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_LCO_TAP | 11KV埔十二線(JY32) LCO TAP | FEEDER | S34/11/JY32/IED_ADJ |  |  |  | CDC | 225 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S34 | 嘉埔SS | 11 | 11kV | JY32 | JY32(11KV埔十二線) |  | CB | [17 empty] | 1-10-06 |  | 1-1C | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_CB | JY32(11KV埔十二線) CB | FEEDER | S34/11/JY32/CB |  |  |  | CDC | 226 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-02-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 嘉埔SS.600_CB | 600(TIE) CB | TIE | S34/69/600/CB |  |  |  | CDC | 227 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 600 | TIE(600) |  | 51A | [17 empty] | 1-02-05 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600_51A | 69KV TIE(600) 51RY | TIE | S34/69/600/51A |  |  |  | CDC | 228 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 600 | TIE(600) |  | 51NA | [17 empty] | 1-02-06 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600_51NA | 69KV TIE(600) 51N RY | TIE | S34/69/600/51NA |  |  |  | CDC | 229 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.601_DS | 601(TIE) DS | TIE | S34/69/600/DS1 |  |  |  | CDC | 230 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.602_DS | 602(TIE) DS | TIE | S34/69/600/DS2 |  |  |  | CDC | 231 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-0B-04 |  | 1-09 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.390_CB | 390(#1SSTR) CB | OTHER | S34/11/390/CB |  |  |  | CDC | 232 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-0B-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S34/11/390/PHA |  |  |  | CDC | 233 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-0B-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S34/11/390/GDA |  |  |  | CDC | 234 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-11-04 |  | 1-15 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.490_CB | 490(#2SSTR) CB | OTHER | S34/11/490/CB |  |  |  | CDC | 235 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-11-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2SSTR_51A | #2SSTR 51RY | OTHER | S34/11/490/PHA |  |  |  | CDC | 236 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-11-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | S34/11/490/GDA |  |  |  | CDC | 237 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-00 |  | 1-07 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.750_CB | 750(#1MTR) CB | DTR | S34/69/750/CB |  |  |  | CDC | 238 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-08 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.1M_CB | 1M(#1MTR) CB | DTR | S34/11/M1/CB |  |  |  | CDC | 239 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_51A | #1MTR 51RY | DTR | S34/69/750/51A |  |  |  | CDC | 240 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_51NA | #1MTR 51N RY | DTR | S34/69/750/51NA |  |  |  | CDC | 241 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S34//1MTR/51ZA |  |  |  | CDC | 242 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_87A | #1MTR 87RY | DTR | S34//1MTR/87A |  |  |  | CDC | 243 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-32-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S34//1MTR/87UL |  |  |  | CDC | 244 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S34/11/M1/51A |  |  |  | CDC | 245 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-32-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_TRA | #1MTR 重故障 | DTR | S34//1MTR/TRA |  |  |  | CDC | 246 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-32-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S34//1MTR/TRF |  |  |  | CDC | 247 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-32-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S34//1MTR/SupLocal |  |  |  | CDC | 248 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-32-07 |  | 1-21 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S34//1MTR/Tap Chan |  |  |  | CDC | 249 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.751_DS | 751(#1MTR) DS | DTR | S34/69/750/DS1 |  |  |  | CDC | 250 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.752_DS | 752(#1MTR) DS | DTR | S34/69/750/DS2 |  |  |  | CDC | 251 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_96A | #1MTR 96P RY | DTR | S34//1MTR/96PA |  |  |  | CDC | 252 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S34//1MTR/OLTC_DLY |  |  |  | CDC | 253 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-31-14 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S34//1MTR/AC_Fault |  |  |  | CDC | 254 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-13 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.760_CB | 760(#2MTR) CB | DTR | S34/69/760/CB |  |  |  | CDC | 255 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-02-01 |  | 1-14 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.2M_CB | 2M(#2MTR) CB | DTR | S34/11/M2/CB |  |  |  | CDC | 256 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_51A | #2MTR 51RY | DTR | S34/69/760/51A |  |  |  | CDC | 257 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_51NA | #2MTR 51N RY | DTR | S34/69/760/51NA |  |  |  | CDC | 258 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S34//2MTR/51ZA |  |  |  | CDC | 259 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_87A | #2MTR 87RY | DTR | S34//2MTR/87A |  |  |  | CDC | 260 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-32-08 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S34//2MTR/87UL |  |  |  | CDC | 261 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S34/11/M2/51A |  |  |  | CDC | 262 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-32-09 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_TRA | #2MTR 重故障 | DTR | S34//2MTR/TRA |  |  |  | CDC | 263 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-32-10 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S34//2MTR/TRF |  |  |  | CDC | 264 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S34//2MTR/SupLocal |  |  |  | CDC | 265 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-32-12 |  | 1-23 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S34//2MTR/Tap Chan |  |  |  | CDC | 266 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.761_DS | 761(#2MTR) DS | DTR | S34/69/760/DS1 |  |  |  | CDC | 267 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-3C-06 | 1-3C-07 | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.762_DS | 762(#2MTR) DS | DTR | S34/69/760/DS2 |  |  |  | CDC | 268 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_96A | #2MTR 96P RY | DTR | S34//2MTR/96PA |  |  |  | CDC | 269 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-31-13 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S34//2MTR/OLTC_DLY |  |  |  | CDC | 270 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S34//2MTR/AC_Fault |  |  |  | CDC | 271 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-0A | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_CB | 210(11KV #1SC) CB | SC | S34/11/210/CB |  |  |  | CDC | 272 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-24 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S34/11/210/Tap Chan |  |  |  | CDC | 273 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_SCA | 11KV #1SC 51,51N RY | SC | S34/11/210/SCA |  |  |  | CDC | 274 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0C-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S34/11/210/UVA |  |  |  | CDC | 275 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 1-3C-08 |  | 1-11 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_LBS | 210(11KV #1SC) LBS | SC | S34/11/210/LBS |  |  |  | CDC | 276 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-11-01 |  | 1-1D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_CB | 220(11KV #2SC) CB | SC | S34/11/220/CB |  |  |  | CDC | 277 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-35-00 |  | 1-40 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S34/11/220/Tap Chan |  |  |  | CDC | 278 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_SCA | 11KV #2SC 51,51N RY | SC | S34/11/220/SCA |  |  |  | CDC | 279 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-11-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S34/11/220/UVA |  |  |  | CDC | 280 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 1-3C-10 |  | 1-1E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_LBS | 220(11KV #2SC) LBS | SC | S34/11/220/LBS |  |  |  | CDC | 281 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S34/69/1BUS/BUS_VUA |  |  |  | CDC | 282 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-02-07 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S34/69/1BUS/87A |  |  |  | CDC | 283 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | BUS | S34/69/1BUS/87UL |  |  |  | CDC | 284 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S34/69/2BUS/BUS_VUA |  |  |  | CDC | 285 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-03-00 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S34/69/2BUS/87A |  |  |  | CDC | 286 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | BUS | S34/69/2BUS/87UL |  |  |  | CDC | 287 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S34/11/ComPoint/CBA |  |  |  | CDC | 288 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-33-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S34/11/ComPoint/CBF |  |  |  | CDC | 289 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-38-15 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S34/69/ComPoint/ABS_89A |  |  |  | CDC | 290 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-36-09 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S34/69/ComPoint/CBA |  |  |  | CDC | 291 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-36-08 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S34/69/ComPoint/CBF |  |  |  | CDC | 292 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S34/0/RTU/RTU_R_L |  |  |  | CDC | 293 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S34 | 嘉埔SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TEST_CB | TEST CB | OTHER | S34/0/RTU/Test_CB |  |  |  | CDC | 294 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-38-08 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.火災警報(1) | [嘉埔]火警 | OTHER | S34/0/StaDev/Fire |  |  |  | CDC | 295 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | OPA | [17 empty] | 1-38-12 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S34/0/StaDev/OPA |  |  |  | CDC | 296 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | STUV | [17 empty] | 1-32-15 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S34/0/StaDev/STUV |  |  |  | CDC | 297 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-36-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S34/0/StaDev/CHG1 |  |  |  | CDC | 298 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | DCA | [17 empty] | 1-33-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.直流電源DCA | 直流電源故障警報 | OTHER | S34/0/StaDev/DCA |  |  |  | CDC | 299 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | DCE | [17 empty] | 1-36-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S34/0/StaDev/DCE |  |  |  | CDC | 300 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S34/0/StaDev/3A5Other |  |  |  | CDC | 301 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S34/0/StaDev/4A5Other |  |  |  | CDC | 302 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S34/0/StaDev/5A5Other |  |  |  | CDC | 303 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-37-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S34/0/StaDev/CHG2 |  |  |  | CDC | 304 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S34/0/StaDev/CommACF |  |  |  | CDC | 305 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-37-08 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S34/0/StaDev/Burglar1 |  |  |  | CDC | 306 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-37-09 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S34/0/StaDev/Burglar2 |  |  |  | CDC | 307 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-37-10 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防盜(3) | 無人化防盜(3) | OTHER | S34/0/StaDev/Burglar3 |  |  |  | CDC | 308 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-37-11 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化門禁(1) | 保全(DOOR) | OTHER | S34/0/StaDev/Door1 |  |  |  | CDC | 309 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-38-10 |  | 1-6D | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.開關場照明(A) | 所內開關場照明 | OTHER | S34/0/StaDev/Lights1 |  |  |  | CDC | 310 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S34 | 嘉埔SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-38-11 |  | 1-6E | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.開關場照明(B) | 路燈照明 | OTHER | S34/0/StaDev/Lights2 |  |  |  | CDC | 311 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S34 | 嘉埔SS | 0 |  | 1M | 1M |  | #1MTR63Q | [17 empty] | 1-30-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR63Q | 1M ULTC電驛動作 | OTHER | S34//1MTR/63Q |  |  |  | CDC | 312 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1M | 1M |  | #1MTR96B1 | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR96B1 | 1M 撲氣電驛警報 | OTHER | S34//1MTR/96B1 |  |  |  | CDC | 313 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1M | 1M |  | #1MTR96B2 | [17 empty] | 1-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR96B2 | 1M 撲氣電驛動作 | OTHER | S34//1MTR/96B2 |  |  |  | CDC | 314 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1M | 1M |  | #1MTR96D | [17 empty] | 1-30-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR96D | 1M 放壓電驛動作 | OTHER | S34//1MTR/96D |  |  |  | CDC | 315 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1M | 1M |  | #1MTR96P | [17 empty] | 1-30-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR96P | 1M 突壓電驛動作 | OTHER | S34//1MTR/96P |  |  |  | CDC | 316 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1_MAIN | #1 |  | 51NA | [17 empty] | 1-01-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER | S34/11/M1/51NA |  |  |  | CDC | 317 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | 2M |  | #2MTR63Q | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR63Q | 2M ULTC電驛動作 | OTHER | S34//2MTR/63Q |  |  |  | CDC | 318 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | 2M |  | #2MTR96B1 | [17 empty] | 1-30-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR96B1 | 2M 撲氣電驛警報 | OTHER | S34//2MTR/96B1 |  |  |  | CDC | 319 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | 2M |  | #2MTR96B2 | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR96B2 | 2M 撲氣電驛動作 | OTHER | S34//2MTR/96B2 |  |  |  | CDC | 320 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | 2M |  | #2MTR96D | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR96D | 2M 放壓電驛動作 | OTHER | S34//2MTR/96D |  |  |  | CDC | 321 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | 2M |  | #2MTR96P | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR96P | 2M 突壓電驛動作 | OTHER | S34//2MTR/96P |  |  |  | CDC | 322 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2_MAIN | #2 |  | 51NA | [17 empty] | 1-02-03 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER | S34/11/M2/51NA |  |  |  | CDC | 323 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | _SC | _SC |  | 60A | [17 empty] | 1-36-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.11KV_SC_60A | 60RY | OTHER | S34/11/ComPoint/FDR_60A |  |  |  | CDC | 324 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 79RY | 79RY |  | LOA | [17 empty] | 1-33-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.79RY_LOA | 79RY LOA | OTHER | S34/0/StaDev/LOA |  |  |  | CDC | 325 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-36-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.ACBA | ACBA | OTHER | S34/0/StaDev/ACBA |  |  |  | CDC | 326 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-36-12 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.水位警報(1) | 洩油池水位警報(1) | OTHER | S34/0/StaDev/Water1 |  |  |  | CDC | 327 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-36-13 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.水位警報(2) | 洩油池水位警報(2) | OTHER | S34/0/StaDev/Water2 |  |  |  | CDC | 328 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Water1 | [17 empty] | 1-37-14 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.地下室淹水(1) | 地下室淹水(1) | OTHER | S34/0/StaDev/Water3 |  |  |  | CDC | 329 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Water2 | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.地下室淹水(2) | 地下室淹水(2) | OTHER | S34/0/StaDev/Water4 |  |  |  | CDC | 330 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-38-13 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.安全監控 | 安全監控 | OTHER | S34/0/StaDev/Burglar |  |  |  | CDC | 331 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-36-15 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.所內其他重故障 | 所內其他重故障 | OTHER | S34/0/StaDev/PSA |  |  |  | CDC | 332 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-36-14 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.所內其他輕故障 | 所內其他輕故障 | OTHER | S34/0/StaDev/PSF |  |  |  | CDC | 333 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | Door | [17 empty] | 1-38-09 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.門禁 | 大門側門 | OTHER | S34/0/StaDev/Door |  |  |  | CDC | 334 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  |  |  |  | 無人化防火(1) | [17 empty] | 1-37-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防火(1) | CO2故障 | OTHER | S34/0/StaDev/Fire1 |  |  |  | CDC | 335 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 無人化防火(2) | [17 empty] | 1-37-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防火(2) | CO2火警 | OTHER | S34/0/StaDev/Fire2 |  |  |  | CDC | 336 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 無人化防火(3) | [17 empty] | 1-37-07 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.無人化防火(3) | 無人化防火(3) | OTHER | S34/0/StaDev/Fire3 |  |  |  | CDC | 337 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-38-14 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.維護運轉警報 | 維護運轉警報 | OTHER | S34/0/StaDev/1A5Other |  |  |  | CDC | 338 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1M | #1M |  | 三相51 | [17 empty] | 1-00-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1M_三相51 | #1M 三相51 | OTHER | S34/11/M1/3P51A |  |  |  | CDC | 339 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2M | #2M |  | 三相51 | [17 empty] | 1-02-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2M_三相51 | #2M 三相51 | OTHER | S34/11/M2/3P51A |  |  |  | CDC | 340 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0E-04 |  | 1-16 | [5 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TIE2_CB | 11KV TIE2 CB | TIE | S34/11/TIE2/CB |  |  |  | CDC | 341 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-0E-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TIE2_51A | 11KV TIE2 51RY | TIE | S34/11/TIE2/51A |  |  |  | CDC | 342 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-0E-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S34/11/TIE2/51NA |  |  |  | CDC | 343 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-33-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.所內電源ACB1 | 所內電源ACB1 | OTHER | S34/0/StaDev/ACB1 |  |  |  | CDC | 344 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S34 | 嘉埔SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-33-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.所內電源ACB2 | 所內電源ACB2 | OTHER | S34/0/StaDev/ACB2 |  |  |  | CDC | 345 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S34 | 嘉埔SS | 22 | 22kV | 11_ CBA | 11/ CBA(11_ CBA) |  | IED警報 | [17 empty] | 1-32-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.IED警報 | 11/23KV CBA 重故障(IED故障) | OTHER | S34/0/StaDev/IRFA |  |  |  | CDC | 346 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | TIE | TIE |  | 600GDA(1) | [17 empty] | 1-05-01 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600GDA(1) | 600(TIE) 67NA(B1) | TIE | S34/69/600/GDA1 |  |  |  | CDC | 347 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | TIE | TIE |  | 600GDA(2) | [17 empty] | 1-05-03 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600GDA(2) | 600(TIE) 67NA(B2) | TIE | S34/69/600/GDA2 |  |  |  | CDC | 348 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | TIE | TIE |  | 600PHA(1) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600PHA(1) | 600(TIE) 67A(B1) | TIE | S34/69/600/PHA1 |  |  |  | CDC | 349 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | TIE | TIE |  | 600PHA(2) | [17 empty] | 1-05-02 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.600PHA(2) | 600(TIE) 67A(B2) | TIE | S34/69/600/PHA2 |  |  |  | CDC | 350 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-32-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S34/0/StaDev/7A5Other |  |  |  | CDC | 351 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.開關場水位警報 | 開關場水位警報 | OTHER | S34/0/StaDev/Door3 |  |  |  | CDC | 352 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | 開關場水位二段 | [17 empty] | 1-37-12 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.開關場水位二段 | 開關場水位二段警報 | OTHER | S34/0/StaDev/Door2 |  |  |  | CDC | 353 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | 87A | [17 empty] | 1-09-04 | [7 empty] | 69KV_N | [8 empty] | 嘉埔SS.730_87A | 欣欣奮起嘉埔線(730) 87RY | LINE69 | S34/69/730/87A |  |  |  | CDC | 354 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | CFA | [17 empty] | 1-38-05 | [7 empty] | ADCS_N | [8 empty] | 嘉埔SS.730_CFA | 欣欣奮起嘉埔線(730) CFA | LINE69 | S34/69/730/74A |  |  |  | CDC | 355 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | 87UL | [17 empty] | 1-38-04 |  | 1-44 | [5 empty] | ADCS_N | [8 empty] | 嘉埔SS.730_87UL | 欣欣奮起嘉埔線(730) 87RY U/L | LINE69 | S34/69/730/87UL |  |  |  | CDC | 356 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 730 | 欣欣奮起嘉埔線(730) |  | RYFA | [17 empty] | 1-36-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.730_RYFA | 730 RYFA | OTHER | S34/69/730/RYFA |  |  |  | CDC | 357 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-36-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.600_RYFA | 600 RYFA | OTHER | S34/69/600/RYFA |  |  |  | CDC | 358 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | #1MTR-86A | [17 empty] | 1-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR-86A | #1MTR-86A | OTHER | S34//1MTR/MTR_86A |  |  |  | CDC | 359 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_51ZS | #1MTR 51ZS | OTHER | S34//1MTR/51Z_UL |  |  |  | CDC | 360 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_87UL2 | #1MTR 87UL2 | OTHER | S34//1MTR/1_87UL2 |  |  |  | CDC | 361 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#1MTR_RYFA | #1MTR IED警報 | OTHER | S34//1MTR/RYFA |  |  |  | CDC | 362 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  |  |  |  | #2MTR-86A | [17 empty] | 1-03-02 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR-86A | #2MTR-86A | OTHER | S34//2MTR/MTR_86A |  |  |  | CDC | 363 | GENERICDIPoint | SS215_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_51ZS | #2MTR 51ZS | OTHER | S34//2MTR/51Z_UL |  |  |  | CDC | 364 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_87UL2 | #2MTR 87UL2 | OTHER | S34//2MTR/1_87UL2 |  |  |  | CDC | 365 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S34 | 嘉埔SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.#2MTR_RYFA | #2MTR IED警報 | OTHER | S34//2MTR/RYFA |  |  |  | CDC | 366 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3F-14 | [7 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.PMA | POWER METER警報 | OTHER | S34/0/ComPoint/PMA |  |  |  | CDC | 367 | GENERICDIPoint | SS215_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S34 | 嘉埔SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 368 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 369 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.620LE | 620LE (非取樣點) | LINE69 | S34/69/620/LE0 |  |  |  |  | 370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 620 | 嘉埔奮起線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.620BE | 620BE (非取樣點) | LINE69 | S34/69/620/BE0 |  |  |  |  | 371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | LE0 | 730LE | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.730LE | 730LE (非取樣點) | LINE69 | S34/69/730/LE0 |  |  |  |  | 372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 730 | 欣欣奮起嘉埔線(730) |  | BE0 | 730BE | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.730BE | 730BE (非取樣點) | LINE69 | S34/69/730/BE0 |  |  |  |  | 373 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY21 | JY21_DS |  | DS1 | JY21_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_DS | JY21_DS (非取樣點) | FEEDER | S34/11/JY21/DS |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY21 | JY21_ES |  | LE0 | JY21_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY21_ES | JY21_ES (非取樣點) | FEEDER | S34/11/JY21/ES |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY22 | JY22_DS |  | DS1 | JY22_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_DS | JY22_DS (非取樣點) | FEEDER | S34/11/JY22/DS |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY22 | JY22_ES |  | LE0 | JY22_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY22_ES | JY22_ES (非取樣點) | FEEDER | S34/11/JY22/ES |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY23 | JY23_DS |  | DS1 | JY23_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_DS | JY23_DS (非取樣點) | FEEDER | S34/11/JY23/DS |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY23 | JY23_ES |  | LE0 | JY23_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY23_ES | JY23_ES (非取樣點) | FEEDER | S34/11/JY23/ES |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY24 | JY24_DS |  | DS1 | JY24_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_DS | JY24_DS (非取樣點) | FEEDER | S34/11/JY24/DS |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY24 | JY24_ES |  | LE0 | JY24_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY24_ES | JY24_ES (非取樣點) | FEEDER | S34/11/JY24/ES |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY25 | JY25_DS |  | DS1 | JY25_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_DS | JY25_DS (非取樣點) | FEEDER | S34/11/JY25/DS |  |  |  |  | 382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY25 | JY25_ES |  | LE0 | JY25_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY25_ES | JY25_ES (非取樣點) | FEEDER | S34/11/JY25/ES |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY26 | JY26_DS |  | DS1 | JY26_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_DS | JY26_DS (非取樣點) | FEEDER | S34/11/JY26/DS |  |  |  |  | 384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY26 | JY26_ES |  | LE0 | JY26_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY26_ES | JY26_ES (非取樣點) | FEEDER | S34/11/JY26/ES |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY27 | JY27_DS |  | DS1 | JY27_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_DS | JY27_DS (非取樣點) | FEEDER | S34/11/JY27/DS |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY27 | JY27_ES |  | LE0 | JY27_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY27_ES | JY27_ES (非取樣點) | FEEDER | S34/11/JY27/ES |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY28 | JY28_DS |  | DS1 | JY28_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_DS | JY28_DS (非取樣點) | FEEDER | S34/11/JY28/DS |  |  |  |  | 388 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY28 | JY28_ES |  | LE0 | JY28_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY28_ES | JY28_ES (非取樣點) | FEEDER | S34/11/JY28/ES |  |  |  |  | 389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY29 | JY29_DS |  | DS1 | JY29_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_DS | JY29_DS (非取樣點) | FEEDER | S34/11/JY29/DS |  |  |  |  | 390 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY29 | JY29_ES |  | LE0 | JY29_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY29_ES | JY29_ES (非取樣點) | FEEDER | S34/11/JY29/ES |  |  |  |  | 391 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY30 | JY30_DS |  | DS1 | JY30_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_DS | JY30_DS (非取樣點) | FEEDER | S34/11/JY30/DS |  |  |  |  | 392 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY30 | JY30_ES |  | LE0 | JY30_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY30_ES | JY30_ES (非取樣點) | FEEDER | S34/11/JY30/ES |  |  |  |  | 393 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY31 | JY31_DS |  | DS1 | JY31_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_DS | JY31_DS (非取樣點) | FEEDER | S34/11/JY31/DS |  |  |  |  | 394 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY31 | JY31_ES |  | LE0 | JY31_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY31_ES | JY31_ES (非取樣點) | FEEDER | S34/11/JY31/ES |  |  |  |  | 395 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | JY32 | JY32_DS |  | DS1 | JY32_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_DS | JY32_DS (非取樣點) | FEEDER | S34/11/JY32/DS |  |  |  |  | 396 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | JY32 | JY32_ES |  | LE0 | JY32_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.JY32_ES | JY32_ES (非取樣點) | FEEDER | S34/11/JY32/ES |  |  |  |  | 397 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.601E | 601E (非取樣點) | TIE | S34/69/600/E1 |  |  |  |  | 398 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.602E | 602E (非取樣點) | TIE | S34/69/600/E2 |  |  |  |  | 399 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.391 | 391 (非取樣點) | OTHER | S34/11/390/DS |  |  |  |  | 400 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.391E | 391E (非取樣點) | OTHER | S34/11/390/ES |  |  |  |  | 401 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.491 | 491 (非取樣點) | OTHER | S34/11/490/DS |  |  |  |  | 402 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.491E | 491E (非取樣點) | OTHER | S34/11/490/ES |  |  |  |  | 403 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.750TE | 750TE (非取樣點) | DTR | S34/69/750/TE0 |  |  |  |  | 404 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.750BE | 750BE (非取樣點) | DTR | S34/69/750/BE0 |  |  |  |  | 405 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.1M_DS | 1M_DS (非取樣點) | DTR | S34/11/M1/DS |  |  |  |  | 406 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.1M_ES | 1M_ES (非取樣點) | DTR | S34/11/M1/ES |  |  |  |  | 407 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.760TE | 760TE (非取樣點) | DTR | S34/69/760/TE0 |  |  |  |  | 408 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.760BE | 760BE (非取樣點) | DTR | S34/69/760/BE0 |  |  |  |  | 409 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.2M_DS | 2M_DS (非取樣點) | DTR | S34/11/M2/DS |  |  |  |  | 410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.2M_ES | 2M_ES (非取樣點) | DTR | S34/11/M2/ES |  |  |  |  | 411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.210_ES | 210_ES (非取樣點) | SC | S34/11/210/ES |  |  |  |  | 412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 211DS | 211DS |  | 211DS | 211DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.211DS | 211DS (非取樣點) | SC | S34/11/210/D1 |  |  |  |  | 413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.220_ES | 220_ES (非取樣點) | SC | S34/11/220/ES |  |  |  |  | 414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 221DS | 221DS |  | 221DS | 221DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.221DS | 221DS (非取樣點) | SC | S34/11/220/D1 |  |  |  |  | 415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.69B1E | 69B1E (非取樣點) | BUS | S34/69/1BUS/BE1 |  |  |  |  | 416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 嘉埔SS.69B2E | 69B2E (非取樣點) | BUS | S34/69/2BUS/BE2 |  |  |  |  | 417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 418 | NotelDIPoint | [38 empty] | START/STOP | STOP
S34 | 嘉埔SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S34/11/TIE2/D2 |  |  |  |  | 419 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S34 | 嘉埔SS | 0 |  | BR1DS | BR1DS |  | BR1DS | BR1DS | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.BR1DS | BR1DS (非取樣點) | TIE | S34/11/TIE2/D1 |  |  |  |  | 420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | BR1ES | BR1ES |  | LE0 | BR1ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.BR1ES | BR1ES (非取樣點) | TIE | S34/11/TIE2/E1 |  |  |  |  | 421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S34 | 嘉埔SS | 0 |  | TIE2 | TIE2_ES |  | LE0 | TIE2_ES | [24 empty] | DDCS2_2 | [8 empty] | 嘉埔SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | S34/11/TIE2/ES |  |  |  |  | 422 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo