## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S36 | 新港SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV＃1BUS KV | KV | 69 ＃1 BUS KV(R相) | kV_-90_90(-2000_2000) | aaa | B2/S36_A1 | [8 empty] | 新港SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S36 | 新港SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV＃2BUS KV | KV | 69 ＃2 BUS KV(R相) | kV_-90_90(-2000_2000) | aab | B2/S36_A1 | [8 empty] | 新港SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S36 | 新港SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0062 |  |  | 1-BE |  |  | ＃2 MTR | KV | #2 MTR 11KV R相電壓 | kV_-9_9(-2000_2000) | aaa | B2/S36_D1 | [8 empty] | 新港SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S36 | 新港SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0106 |  |  | 1-EA |  |  | ＃3 MTR | KV | #3 MTR 11KV R相電壓 | kV_-9_9(-2000_2000) | aba | B2/S36_D1 | [8 empty] | 新港SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S36 | 新港SS | 69 | 69kV | 69B1E | 69B1E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aaaz | B2/S36_A1 | [8 empty] | 新港SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-31-15 |  |  | 69KV＃1 BUS | 6VUA | 69KV BUS(1)衡相監視警報 |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-01 |  |  | 69KV #1BUS | 87B1A | 69KV #1BUS 87B1A |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0280 |  | 0015 | 1-33-05 |  | 1-0E | 87 B1S | 87 B1S | 87 B1S |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 69B2E | 69B2E |  | BE2 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BUS | [13 empty] | aaaz | B2/S36_A1 | [8 empty] | 新港SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-32-00 |  |  | 69KV＃2 BUS | 6VUA | 69KV BUS(2)衡相監視警報 |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-03 |  |  | 69KV #2BUS | 87B2A | 69KV #2BUS 87B2A |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0281 |  | 0016 | 1-33-06 |  | 1-0F | 87 B2S | 87 B2S | 87 B2S |  |  | B2/S36_A1 | [8 empty] | 新港SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 610 | MW | 嘉太一路有效電力 | MW_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.610_MW | 新港嘉太一路 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 610 | MVAR | 嘉太一路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.610_MVAR | 新港嘉太一路 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 嘉太一路 610 | 嘉太一路瓦時計量值 | 嘉太一路 610 MWH+ |  |  | B2/S36_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 620 | MW | 嘉太二路有效電力 | MW_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.620_MW | 新港嘉太二路 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 620 | MVAR | 嘉太二路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.620_MVAR | 新港嘉太二路 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 嘉太二路 620 | 嘉太二路瓦時計量值 | 嘉太二路 620 MWH+ |  |  | B2/S36_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 630 | MW | 北港一路有效電力 | MW_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.630_MW | 北港新港一路 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 630 | MVAR | 北港一路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.630_MVAR | 北港新港一路 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 北港一路 630 | 北港一路瓦時計量值 | 北港一路 630 MWH+ |  |  | B2/S36_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 640 | MW | 北港二路有效電力 | MW_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.640_MW | 北港新港二路 MW | LINE69 |  |  |  |  | CDC | 23 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 640 | MVAR | 北港二路無效電力 | MVAR_-144_144(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.640_MVAR | 北港新港二路 MVAR | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 北港二路 640 | 北港二路瓦時計量值 | 北港二路 640 MWH+ |  |  | B2/S36_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 25 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-02 |  |  | 610 | PHA | 嘉太一路 610 PHA |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_PHA | 新港嘉太一路(610) 相間RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-03 |  |  | 610 | GDA | 嘉太一路 610 GDA |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_GDA | 新港嘉太一路(610) 接地RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-01 |  |  | 610 | 87A | 嘉太一路 610 |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_87A | 新港嘉太一路(610) 87RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 1-32-10 |  |  | 610 | 1CFA | 嘉太一路 610 通訊故障 |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_CFA | 新港嘉太一路(610) 610_通訊故障 | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-08-06 |  |  | 620 | PHA | 嘉太二路 620 PHA |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_PHA | 新港嘉太二路(620) 相間RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-08-07 |  |  | 620 | GDA | 嘉太二路 620 GDA |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_GDA | 新港嘉太二路(620) 接地RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-08-05 |  |  | 620 | 87A | 嘉太二路 620 |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_87A | 新港嘉太二路(620) 87RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 1-32-12 |  |  | 620 | 2CFA | 嘉太二路 620 通訊故障 |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_CFA | 新港嘉太二路(620) 620_通訊故障 | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-02 |  |  | 630 | PHA | 北港一路 630 PHA |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_PHA | 北港新港一路(630) 相間RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-03 |  |  | 630 | GDA | 北港一路 630 GDA |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_GDA | 北港新港一路(630) 接地RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-01 |  |  | 630 | 87A | 北港一路 630 |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_87A | 北港新港一路(630) 87RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 1-32-14 |  |  | 630 | CFA | SPARE |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_CFA | 北港新港一路(630) 630_通訊故障 | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-09-06 |  |  | 640 | PHA | 北港二路 640 PHA |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_PHA | 北港新港二路(640) 相間RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-09-07 |  |  | 640 | GDA | 北港二路 640 GDA |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_GDA | 北港新港二路(640) 接地RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-09-05 |  |  | 640 | 85A | 北港二路 640 |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_87A | 北港新港二路(640) 87RY | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 1-33-00 |  |  | 640 | CFA | SPARE |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_CFA | 北港新港二路(640) 640_通訊故障 | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0268 |  | 0011 | 1-32-09 |  | 1-0A | 610 | 187S U/L | 嘉太一路 610 87S |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_87UL | 新港嘉太一路(610) 87RY U/L | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0270 |  | 0012 | 1-32-11 |  | 1-0B | 620 | 287S U/L | 嘉太二路 620 87S |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_87UL | 新港嘉太二路(620) 87RY U/L | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0272 |  | 0013 | 1-32-13 |  | 1-0C | 630 | 87S U/L | SPARE |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_87UL | 北港新港一路(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0274 |  | 0014 | 1-32-15 |  | 1-0D | 640 | 87S U/L | SPARE |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_87UL | 北港新港二路(640) 87RY U/L | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S36S301/T1 |  | 0067 |  | 0002 | 1-08-00 |  | 1-01 | 610 | CB ON/OFF | 嘉太一路 610 52AS |  | aaga | B2/S36_A1 | [8 empty] | 新港SS.610_CB | 610(新港嘉太一路) CB | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S36S302/T1 |  | 0071 |  | 0003 | 1-08-04 |  | 1-02 | 620 | CB ON/OFF | 嘉太二路 620 52AS |  | aada | B2/S36_A1 | [8 empty] | 新港SS.620_CB | 620(新港嘉太二路) CB | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/P04S361/T2 |  | 0075 |  | 0004 | 1-09-00 |  | 1-03 | 630 | CB ON/OFF | 北港一路 630 52AS |  | aaea | B2/S36_A1 | [8 empty] | 新港SS.630_CB | 630(北港新港一路) CB | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/P04S362/T2 |  | 0079 |  | 0005 | 1-09-04 |  | 1-04 | 640 | CB ON/OFF | 北港二路 640 52AS |  | aaba | B2/S36_A1 | [8 empty] | 新港SS.640_CB | 640(北港新港二路) CB | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | DS1 | 611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0379 | 380 | 0020 | 1-39-08 | 1-39-09 | 1-13 | 611 | DS ON | 嘉太一路BUS(1)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.611_DS | 611(新港嘉太一路) DS | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | DS2 | 612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0381 | 382 | 0021 | 1-39-10 | 1-39-11 | 1-14 | 612 | DS ON | 嘉太一路BUS(2)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.612_DS | 612(新港嘉太一路) DS | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | DS1 | 621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0387 | 388 | 0024 | 1-3A-00 | 1-3A-01 | 1-17 | 621 | DS ON | 嘉太二路BUS(1)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.621_DS | 621(新港嘉太二路) DS | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | DS2 | 622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0389 | 390 | 0025 | 1-3A-02 | 1-3A-03 | 1-18 | 622 | DS ON | 嘉太二路BUS(2)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.622_DS | 622(新港嘉太二路) DS | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | DS1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0395 | 396 | 0028 | 1-3A-08 | 1-3A-09 | 1-1B | 631 | DS ON | 北港一路BUS(1)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.631_DS | 631(北港新港一路) DS | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | DS2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0397 | 398 | 0029 | 1-3A-10 | 1-3A-11 | 1-1C | 632 | DS ON | 北港一路BUS(2)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.632_DS | 632(北港新港一路) DS | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0403 | 404 | 0032 | 1-3B-00 | 1-3B-01 | 1-1F | 641 | DS ON | 北港二路BUS(1)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.641_DS | 641(北港新港二路) DS | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0405 | 406 | 0033 | 1-3B-02 | 1-3B-03 | 1-20 | 642 | DS ON | 北港二路BUS(2)側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.642_DS | 642(北港新港二路) DS | LINE69 |  |  |  |  | CDC | 57 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | DS3 | 613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0383 | 384 | 0022 | 1-39-12 | 1-39-13 | 1-15 | 613 | DS ON | 嘉太一路線路側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.613_DS | 613(新港嘉太一路) DS | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | E3 | 613E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0385 | 386 | 0023 | 1-39-14 | 1-39-15 | 1-16 | 613E | DS ON | 嘉太一路接地組 |  |  | B2/S36_A1 | [8 empty] | 新港SS.613E_ES | 613E(新港嘉太一路) ES | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 60 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 61 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | DS3 | 623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0391 | 392 | 0026 | 1-3A-04 | 1-3A-05 | 1-19 | 623 | DS ON | 嘉太二路線路側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.623_DS | 623(新港嘉太二路) DS | LINE69 |  |  |  |  | CDC | 62 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | E3 | 623E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0393 | 394 | 0027 | 1-3A-06 | 1-3A-07 | 1-1A | 623E | DS ON | 嘉太二路接地組 |  |  | B2/S36_A1 | [8 empty] | 新港SS.623E_ES | 623E(新港嘉太二路) ES | LINE69 |  |  |  |  | CDC | 63 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 64 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 65 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | DS3 | 633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0399 | 400 | 0030 | 1-3A-12 | 1-3A-13 | 1-1D | 633 | DS ON | 北港一路線路側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.633_DS | 633(北港新港一路) DS | LINE69 |  |  |  |  | CDC | 66 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | E3 | 633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0401 | 402 | 0031 | 1-3A-14 | 1-3A-15 | 1-1E | 633E | DS ON | 北港一路接地組 |  |  | B2/S36_A1 | [8 empty] | 新港SS.633E_ES | 633E(北港新港一路) ES | LINE69 |  |  |  |  | CDC | 67 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 68 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 69 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0407 | 408 | 0034 | 1-3B-04 | 1-3B-05 | 1-21 | 643 | DS ON | 北港二路線路側 |  |  | B2/S36_A1 | [8 empty] | 新港SS.643_DS | 643(北港新港二路) DS | LINE69 |  |  |  |  | CDC | 70 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | E3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0409 | 410 | 0035 | 1-3B-06 | 1-3B-07 | 1-22 | 643E | DS ON | 北港二路接地組 |  |  | B2/S36_A1 | [8 empty] | 新港SS.643E_ES | 643E(北港新港二路) ES | LINE69 |  |  |  |  | CDC | 71 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 72 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 73 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | JI31 | VAR | 新十一線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十一線KVAR | 11KV新十一線 KVAR | FEEDER |  |  |  |  | CDC | 74 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | JI31 | A1 | 新十一線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十一線A1 | 11KV新十一線 R相AMP | FEEDER |  |  |  |  | CDC | 75 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | JI31 | A2 | 新十一線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十一線A2 | 11KV新十一線 S相AMP | FEEDER |  |  |  |  | CDC | 76 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | JI31 | A3 | 新十一線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十一線A3 | 11KV新十一線 T相AMP | FEEDER |  |  |  |  | CDC | 77 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | JI31 | NA | 新十一線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十一線A0 | 11KV新十一線 N相AMP | FEEDER |  |  |  |  | CDC | 78 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0031 |  |  | 1-5F |  |  | JI31 | 新十一線瓦時計量值 | 新十一線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 79 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | JI32 | VAR | 新十二線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十二線KVAR | 11KV新十二線 KVAR | FEEDER |  |  |  |  | CDC | 80 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | JI32 | A1 | 新十二線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十二線A1 | 11KV新十二線 R相AMP | FEEDER |  |  |  |  | CDC | 81 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | JI32 | A2 | 新十二線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十二線A2 | 11KV新十二線 S相AMP | FEEDER |  |  |  |  | CDC | 82 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | JI32 | A3 | 新十二線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十二線A3 | 11KV新十二線 T相AMP | FEEDER |  |  |  |  | CDC | 83 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | JI32 | NA | 新十二線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十二線A0 | 11KV新十二線 N相AMP | FEEDER |  |  |  |  | CDC | 84 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | JI32 | 新十二線瓦時計量值 | 新十二線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 85 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | JI33 | VAR | 新十三線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十三線KVAR | 11KV新十三線 KVAR | FEEDER |  |  |  |  | CDC | 86 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | JI33 | A1 | 新十三線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十三線A1 | 11KV新十三線 R相AMP | FEEDER |  |  |  |  | CDC | 87 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | JI33 | A2 | 新十三線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十三線A2 | 11KV新十三線 S相AMP | FEEDER |  |  |  |  | CDC | 88 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | JI33 | A3 | 新十三線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十三線A3 | 11KV新十三線 T相AMP | FEEDER |  |  |  |  | CDC | 89 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | JI33 | NA | 新十三線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十三線A0 | 11KV新十三線 N相AMP | FEEDER |  |  |  |  | CDC | 90 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0033 |  |  | 2-41 |  |  | JI33 | 新十三線瓦時計量值 | 新十三線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 91 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | JI34 | VAR | 新十四線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十四線KVAR | 11KV新十四線 KVAR | FEEDER |  |  |  |  | CDC | 92 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | JI34 | A1 | 新十四線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十四線A1 | 11KV新十四線 R相AMP | FEEDER |  |  |  |  | CDC | 93 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | JI34 | A2 | 新十四線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十四線A2 | 11KV新十四線 S相AMP | FEEDER |  |  |  |  | CDC | 94 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | JI34 | A3 | 新十四線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十四線A3 | 11KV新十四線 T相AMP | FEEDER |  |  |  |  | CDC | 95 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | JI34 | NA | 新十四線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十四線A0 | 11KV新十四線 N相AMP | FEEDER |  |  |  |  | CDC | 96 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0034 |  |  | 2-42 |  |  | JI34 | 新十四線瓦時計量值 | 新十四線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 97 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | JI35 | VAR | 新十五線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十五線KVAR | 11KV新十五線 KVAR | FEEDER |  |  |  |  | CDC | 98 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | JI35 | A1 | 新十五線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十五線A1 | 11KV新十五線 R相AMP | FEEDER |  |  |  |  | CDC | 99 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | JI35 | A2 | 新十五線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十五線A2 | 11KV新十五線 S相AMP | FEEDER |  |  |  |  | CDC | 100 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | JI35 | A3 | 新十五線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十五線A3 | 11KV新十五線 T相AMP | FEEDER |  |  |  |  | CDC | 101 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | JI35 | NA | 新十五線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十五線A0 | 11KV新十五線 N相AMP | FEEDER |  |  |  |  | CDC | 102 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0035 |  |  | 2-43 |  |  | JI35 | 新十五線瓦時計量值 | 新十五線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 103 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | JI36 | VAR | 新十六線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十六線KVAR | 11KV新十六線 KVAR | FEEDER |  |  |  |  | CDC | 104 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | JI36 | A1 | 新十六線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十六線A1 | 11KV新十六線 R相AMP | FEEDER |  |  |  |  | CDC | 105 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | JI36 | A2 | 新十六線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十六線A2 | 11KV新十六線 S相AMP | FEEDER |  |  |  |  | CDC | 106 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | JI36 | A3 | 新十六線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十六線A3 | 11KV新十六線 T相AMP | FEEDER |  |  |  |  | CDC | 107 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | JI36 | NA | 新十六線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十六線A0 | 11KV新十六線 N相AMP | FEEDER |  |  |  |  | CDC | 108 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0036 |  |  | 2-44 |  |  | JI36 | 新十六線瓦時計量值 | 新十六線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 109 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | JI37 | VAR | 新十七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十七線KVAR | 11KV新十七線 KVAR | FEEDER |  |  |  |  | CDC | 110 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | JI37 | A1 | 新十七線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十七線A1 | 11KV新十七線 R相AMP | FEEDER |  |  |  |  | CDC | 111 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | JI37 | A2 | 新十七線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十七線A2 | 11KV新十七線 S相AMP | FEEDER |  |  |  |  | CDC | 112 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | JI37 | A3 | 新十七線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十七線A3 | 11KV新十七線 T相AMP | FEEDER |  |  |  |  | CDC | 113 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | JI37 | NA | 新十七線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十七線A0 | 11KV新十七線 N相AMP | FEEDER |  |  |  |  | CDC | 114 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0037 |  |  | 2-45 |  |  | JI37 | 新十七線瓦時計量值 | 新十七線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 115 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | JI38 | VAR | 新十八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十八線KVAR | 11KV新十八線 KVAR | FEEDER |  |  |  |  | CDC | 116 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | JI38 | A1 | 新十八線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十八線A1 | 11KV新十八線 R相AMP | FEEDER |  |  |  |  | CDC | 117 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | JI38 | A2 | 新十八線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十八線A2 | 11KV新十八線 S相AMP | FEEDER |  |  |  |  | CDC | 118 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | JI38 | A3 | 新十八線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十八線A3 | 11KV新十八線 T相AMP | FEEDER |  |  |  |  | CDC | 119 | AI_FEEDER |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | JI38 | NA | 新十八線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十八線A0 | 11KV新十八線 N相AMP | FEEDER |  |  |  |  | CDC | 120 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0038 |  |  | 2-46 |  |  | JI38 | 新十八線瓦時計量值 | 新十八線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 121 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-04 |  |  | JI27 | PHA | 新七線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI27_PHA | 11KV新七線(JI27) 相間RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-0F-05 |  |  | JI27 | GDA | 新七線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI27_GDA | 11KV新七線(JI27) 接地RY | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0304 |  | 0095 | 1-34-13 |  | 1-5E | JI27 | 79S U/L | 新七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI27_79UL | 11KV新七線(JI27) 79RY U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0333 |  | 0141 | 1-36-10 |  | 2-0C | JI27 | ADJ(U/L) | 新七線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI27_LCO_TAP | 11KV新七線(JI27) LCO TAP | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-0F-07 |  |  | JI28 | PHA | 新八線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI28_PHA | 11KV新八線(JI28) 相間RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-00 |  |  | JI28 | GDA | 新八線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI28_GDA | 11KV新八線(JI28) 接地RY | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0305 |  | 0096 | 1-34-14 |  | 1-5F | JI28 | 79S U/L | 新八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI28_79UL | 11KV新八線(JI28) 79RY U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0334 |  | 0142 | 1-36-11 |  | 2-0D | JI28 | ADJ(U/L) | 新八線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI28_LCO_TAP | 11KV新八線(JI28) LCO TAP | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-02 |  |  | JI29 | PHA | 新九線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI29_PHA | 11KV新九線(JI29) 相間RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-03 |  |  | JI29 | GDA | 新九線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI29_GDA | 11KV新九線(JI29) 接地RY | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0306 |  | 0097 | 1-34-15 |  | 1-60 | JI29 | 79S U/L | 新九線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI29_79UL | 11KV新九線(JI29) 79RY U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0335 |  | 0143 | 1-36-12 |  | 2-0E | JI29 | ADJ(U/L) | 新九線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI29_LCO_TAP | 11KV新九線(JI29) LCO TAP | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-10-05 |  |  | JI30 | PHA | 新十線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI30_PHA | 11KV新十線(JI30) 相間RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-10-06 |  |  | JI30 | GDA | 新十線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI30_GDA | 11KV新十線(JI30) 接地RY | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  | 0098 | 1-35-00 |  | 1-61 | JI30 | 79S U/L | 新十線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI30_79UL | 11KV新十線(JI30) 79RY U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0336 |  | 0144 | 1-36-13 |  | 2-0F | JI30 | ADJ(U/L) | 新十線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI30_LCO_TAP | 11KV新十線(JI30) LCO TAP | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-00 |  |  | JI31 | PHA | 新十一線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI31_PHA | 11KV新十一線(JI31) 相間RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-01 |  |  | JI31 | GDA | 新十一線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI31_GDA | 11KV新十一線(JI31) 接地RY | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0308 |  | 0099 | 1-35-01 |  | 1-62 | JI31 | 79S U/L | 新十一線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI31_79UL | 11KV新十一線(JI31) 79RY U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0337 |  | 0145 | 1-36-14 |  | 2-10 | JI31 | ADJ(U/L) | 新十一線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI31_LCO_TAP | 11KV新十一線(JI31) LCO TAP | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-03 |  |  | JI32 | PHA | 新十二線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI32_PHA | 11KV新十二線(JI32) 相間RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-04 |  |  | JI32 | GDA | 新十二線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI32_GDA | 11KV新十二線(JI32) 接地RY | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0100 | 1-35-02 |  | 1-63 | JI32 | 79S U/L | 新十二線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI32_79UL | 11KV新十二線(JI32) 79RY U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0338 |  | 0146 | 1-36-15 |  | 2-11 | JI32 | ADJ(U/L) | 新十二線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI32_LCO_TAP | 11KV新十二線(JI32) LCO TAP | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-00 |  |  | JI33 | PHA | 新十三線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI33_PHA | 11KV新十三線(JI33) 相間RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-01 |  |  | JI33 | GDA | 新十三線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI33_GDA | 11KV新十三線(JI33) 接地RY | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0318 |  | 0118 | 1-35-11 |  | 1-75 | JI33 | 79S U/L | 新十三線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI33_79UL | 11KV新十三線(JI33) 79RY U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0339 |  | 0147 | 1-37-00 |  | 2-12 | JI33 | ADJ(U/L) | 新十三線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI33_LCO_TAP | 11KV新十三線(JI33) LCO TAP | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-03 |  |  | JI34 | PHA | 新十四線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI34_PHA | 11KV新十四線(JI34) 相間RY | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-04 |  |  | JI34 | GDA | 新十四線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI34_GDA | 11KV新十四線(JI34) 接地RY | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0319 |  | 0119 | 1-35-12 |  | 1-76 | JI34 | 79S U/L | 新十四線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI34_79UL | 11KV新十四線(JI34) 79RY U/L | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0340 |  | 0148 | 1-37-01 |  | 2-13 | JI34 | ADJ(U/L) | 新十四線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI34_LCO_TAP | 11KV新十四線(JI34) LCO TAP | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-13-06 |  |  | JI35 | PHA | 新十五線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI35_PHA | 11KV新十五線(JI35) 相間RY | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-13-07 |  |  | JI35 | GDA | 新十五線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI35_GDA | 11KV新十五線(JI35) 接地RY | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0320 |  | 0120 | 1-35-13 |  | 1-77 | JI35 | 79S U/L | 新十五線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI35_79UL | 11KV新十五線(JI35) 79RY U/L | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0341 |  | 0149 | 1-37-02 |  | 2-14 | JI35 | ADJ(U/L) | 新十五線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI35_LCO_TAP | 11KV新十五線(JI35) LCO TAP | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-01 |  |  | JI36 | PHA | 新十六線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI36_PHA | 11KV新十六線(JI36) 相間RY | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-02 |  |  | JI36 | GDA | 新十六線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI36_GDA | 11KV新十六線(JI36) 接地RY | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0321 |  | 0121 | 1-35-14 |  | 1-78 | JI36 | 79S U/L | 新十六線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI36_79UL | 11KV新十六線(JI36) 79RY U/L | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0342 |  | 0150 | 1-37-03 |  | 2-15 | JI36 | ADJ(U/L) | 新六線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI36_LCO_TAP | 11KV新十六線(JI36) LCO TAP | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-04 |  |  | JI37 | PHA | 新十七線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI37_PHA | 11KV新十七線(JI37) 相間RY | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-14-05 |  |  | JI37 | GDA | 新十七線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI37_GDA | 11KV新十七線(JI37) 接地RY | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0322 |  | 0122 | 1-35-15 |  | 1-79 | JI37 | 79S U/L | 新十七線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI37_79UL | 11KV新十七線(JI37) 79RY U/L | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0343 |  | 0151 | 1-37-04 |  | 2-16 | JI37 | ADJ(U/L) | 新十七線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI37_LCO_TAP | 11KV新十七線(JI37) LCO TAP | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-14-07 |  |  | JI38 | PHA | 新十八線 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI38_PHA | 11KV新十八線(JI38) 相間RY | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-00 |  |  | JI38 | GDA | 新十八線 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI38_GDA | 11KV新十八線(JI38) 接地RY | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  | 0123 | 1-36-00 |  | 1-7A | JI38 | 79S U/L | 新十八線復閉電驛(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI38_79UL | 11KV新十八線(JI38) 79RY U/L | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0344 |  | 0152 | 1-37-05 |  | 2-17 | JI38 | ADJ(U/L) | 新十八線分流器(使用 / 閉鎖)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.JI38_LCO_TAP | 11KV新十八線(JI38) LCO TAP | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI27/T1 |  |  | 0126 |  | 0085 | 1-0F-03 |  | 1-54 | JI27 | CB ON/OFF | 新七線 52AS |  | aacb | B2/S36_D1 | [8 empty] | 新港SS.JI27_CB | JI27(11KV新七線) CB | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI27_DS | JI27_DS (非取樣點) | FEEDER | [5 empty] | 171 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI27_ES | JI27_ES (非取樣點) | FEEDER | [5 empty] | 172 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI28/T1 |  |  | 0129 |  | 0086 | 1-0F-06 |  | 1-55 | JI28 | CB ON/OFF | 新八線 52AS |  | aadb | B2/S36_D1 | [8 empty] | 新港SS.JI28_CB | JI28(11KV新八線) CB | FEEDER |  |  |  |  | CDC | 173 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI28_DS | JI28_DS (非取樣點) | FEEDER | [5 empty] | 174 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI28_ES | JI28_ES (非取樣點) | FEEDER | [5 empty] | 175 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI29/T1 |  |  | 0132 |  | 0087 | 1-10-01 |  | 1-56 | JI29 | CB ON/OFF | 新九線 52AS |  | aafb | B2/S36_D1 | [8 empty] | 新港SS.JI29_CB | JI29(11KV新九線) CB | FEEDER |  |  |  |  | CDC | 176 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI29_DS | JI29_DS (非取樣點) | FEEDER | [5 empty] | 177 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI29_ES | JI29_ES (非取樣點) | FEEDER | [5 empty] | 178 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI30/T1 |  |  | 0135 |  | 0088 | 1-10-04 |  | 1-57 | JI30 | CB ON/OFF | 新十線 52AS |  | aagb | B2/S36_D1 | [8 empty] | 新港SS.JI30_CB | JI30(11KV新十線) CB | FEEDER |  |  |  |  | CDC | 179 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI30_DS | JI30_DS (非取樣點) | FEEDER | [5 empty] | 180 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI30_ES | JI30_ES (非取樣點) | FEEDER | [5 empty] | 181 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI31/T1 |  |  | 0138 |  | 0089 | 1-10-07 |  | 1-58 | JI31 | CB ON/OFF | 新十一線 52AS |  | aahb | B2/S36_D1 | [8 empty] | 新港SS.JI31_CB | JI31(11KV新十一線) CB | FEEDER |  |  |  |  | CDC | 182 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI31_DS | JI31_DS (非取樣點) | FEEDER | [5 empty] | 183 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI31_ES | JI31_ES (非取樣點) | FEEDER | [5 empty] | 184 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BUS | L/JI32/T1 |  |  | 0141 |  | 0090 | 1-11-02 |  | 1-59 | JI32 | CB ON/OFF | 新十二線 52AS |  | aaib | B2/S36_D1 | [8 empty] | 新港SS.JI32_CB | JI32(11KV新十二線) CB | FEEDER |  |  |  |  | CDC | 185 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI32_DS | JI32_DS (非取樣點) | FEEDER | [5 empty] | 186 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI32_ES | JI32_ES (非取樣點) | FEEDER | [5 empty] | 187 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI33/T1 |  |  | 0154 |  | 0108 | 1-12-07 |  | 1-6B | JI33 | CB ON/OFF | 新十三線 52AS |  | abab | B2/S36_D1 | [8 empty] | 新港SS.JI33_CB | JI33(11KV新十三線) CB | FEEDER |  |  |  |  | CDC | 188 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI33_DS | JI33_DS (非取樣點) | FEEDER | [5 empty] | 189 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI33_ES | JI33_ES (非取樣點) | FEEDER | [5 empty] | 190 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI34/T1 |  |  | 0157 |  | 0109 | 1-13-02 |  | 1-6C | JI34 | CB ON/OFF | 新十四線 52AS |  | abbb | B2/S36_D1 | [8 empty] | 新港SS.JI34_CB | JI34(11KV新十四線) CB | FEEDER |  |  |  |  | CDC | 191 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI34_DS | JI34_DS (非取樣點) | FEEDER | [5 empty] | 192 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI34_ES | JI34_ES (非取樣點) | FEEDER | [5 empty] | 193 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI35/T1 |  |  | 0160 |  | 0110 | 1-13-05 |  | 1-6D | JI35 | CB ON/OFF | 新十五線 52AS |  | abdb | B2/S36_D1 | [8 empty] | 新港SS.JI35_CB | JI35(11KV新十五線) CB | FEEDER |  |  |  |  | CDC | 194 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI35_DS | JI35_DS (非取樣點) | FEEDER | [5 empty] | 195 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI35_ES | JI35_ES (非取樣點) | FEEDER | [5 empty] | 196 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI36/T1 |  |  | 0163 |  | 0111 | 1-14-00 |  | 1-6E | JI36 | CB ON/OFF | 新十六線 52AS |  | abeb | B2/S36_D1 | [8 empty] | 新港SS.JI36_CB | JI36(11KV新十六線) CB | FEEDER |  |  |  |  | CDC | 197 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI36_DS | JI36_DS (非取樣點) | FEEDER | [5 empty] | 198 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI36_ES | JI36_ES (非取樣點) | FEEDER | [5 empty] | 199 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI37/T1 |  |  | 0166 |  | 0112 | 1-14-03 |  | 1-6F | JI37 | CB ON/OFF | 新十七線 52AS |  | abfb | B2/S36_D1 | [8 empty] | 新港SS.JI37_CB | JI37(11KV新十七線) CB | FEEDER |  |  |  |  | CDC | 200 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI37_DS | JI37_DS (非取樣點) | FEEDER | [5 empty] | 201 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI37_ES | JI37_ES (非取樣點) | FEEDER | [5 empty] | 202 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/JI38/T1 |  |  | 0169 |  | 0113 | 1-14-06 |  | 1-70 | JI38 | CB ON/OFF | 新十八線 52AS |  | abgb | B2/S36_D1 | [8 empty] | 新港SS.JI38_CB | JI38(11KV新十八線) CB | FEEDER |  |  |  |  | CDC | 203 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI38_DS | JI38_DS (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.JI38_ES | JI38_ES (非取樣點) | FEEDER | [5 empty] | 205 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 600 | R-A | 600 TIE (R相)電流 | A_-1200_1200(-2000_2000) |  | B2/S36_A1 | [8 empty] | 新港SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 206 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | ＃2 TIE | A1 | 二號聯絡斷路器 R相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 207 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | ＃2 TIE | A2 | 二號聯絡斷路器 S相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 208 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | ＃2 TIE | A3 | 二號聯絡斷路器 T相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 209 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0039 |  | 0008 | 1-04-04 |  | 1-07 | 69KV TIE(600) | 600 52AS | 69KV TIE(600) 52AS |  | aahz | B2/S36_A1 | [8 empty] | 新港SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 210 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-05-05 |  |  | SPARE |  |  |  |  | B2/S36_A1 | [8 empty] | 新港SS.600_51A | 69KV TIE(600) 51RY | TIE |  |  |  |  | CDC | 211 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-05-06 |  |  | SPARE |  |  |  |  | B2/S36_A1 | [8 empty] | 新港SS.600_51NA | 69KV TIE(600) 51N RY | TIE |  |  |  |  | CDC | 212 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2BUS | B/3BUS |  |  | 0123 |  | 0083 | 1-0F-00 |  | 1-52 | ＃2 TIE | CB ON/OFF | 二號聯絡斷路器 52AS |  | zzzz | B2/S36_D1 | [8 empty] | 新港SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 213 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-01 |  |  | ＃2 TIE | PHA | 二號聯絡斷路器 PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 214 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-02 |  |  | ＃2 TIE | GDA | 二號聯絡斷路器 GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 215 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0425 | 426 | 0042 | 1-3C-06 | 1-3C-07 | 1-29 | 601 TIE | DS ON | 601 TIE (B1) |  |  | B2/S36_A1 | [8 empty] | 新港SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 216 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0427 | 428 | 0043 | 1-3C-08 | 1-3C-09 | 1-2A | 602 TIE | DS ON | 602 TIE (B2) |  |  | B2/S36_A1 | [8 empty] | 新港SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 217 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.601E | 601E (非取樣點) | TIE | [5 empty] | 218 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_A1 | [8 empty] | 新港SS.602E | 602E (非取樣點) | TIE | [5 empty] | 219 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | BR3DS(非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.BR3DS | BR3DS (非取樣點) | TIE | [5 empty] | 220 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | BR3(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.BR3ES | BR3ES (非取樣點) | TIE | [5 empty] | 221 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 222 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | ＃2 MCB | MW | 二號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 223 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | ＃2 MCB | MVAR | 二號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 224 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | ＃2 MCB | A1 | 二號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 225 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | ＃2 MCB | A2 | 二號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 226 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | ＃2 MCB | A3 | 二號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 227 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | ＃3 MCB | MW | 三號主變二次側有效電力 | MW_-36_36(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 228 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | ＃3 MCB | MVAR | 三號主變二次側無效電力 | MVAR_-36_36(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 229 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | ＃3 MCB | A1 | 三號主變二次側R相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 230 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | ＃3 MCB | A2 | 三號主變二次側S相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 231 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | ＃3 MCB | A3 | 三號主變二次側T相電流 | A_-2000_2000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 232 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | ＃2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 233 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | ＃2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 234 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0067 |  | 0091 | 1-C3 |  | 1-5A | ＃2 MTR | TAP | 二號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 235 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S36 | 新港SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | ＃2 MCB | 二號主變瓦時計量值 | 二號主變二次側CB MWH |  |  | B1/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 236 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | ＃2 MCB | 二號主變乏時計量值 | 二號主變二次側CB MVAR+ |  |  | B1/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 237 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | ＃3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 238 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | ＃3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 239 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0109 |  | 0114 | 1-ED |  | 1-71 | ＃3 MTR | TAP | 三號主變OLTC位置 | TAP_-4.5_12.5(0_2000) |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 240 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S36 | 新港SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | ＃3 MCB | 三號主變瓦時計量值 | 三號主變二次側CB MWH+ |  |  | B1/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 241 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS |  |  | 3MTR | #3MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | ＃3 MCB | 三號主變乏時計量值 | 三號主變二次側CB MVAR+ |  |  | B1/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 242 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0019 |  | 0081 | 1-02-00 |  | 1-50 | 760 | CB 52AS | 二號主變一次側 52AS |  | aacb | B3/S36_D1 | [8 empty] | 新港SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 243 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S36_D1 | [8 empty] | 新港SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 244 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S36_D1 | [8 empty] | 新港SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 245 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/3MTR |  | 0029 |  | 0104 | 1-03-02 |  | 1-67 | 770 | CB 52AS | 三號主變一次側 52AS |  | aafb | B3/S36_D1 | [8 empty] | 新港SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 246 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S36_D1 | [8 empty] | 新港SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 247 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S36_D1 | [8 empty] | 新港SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 248 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB | 2M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2MTR |  |  | 0020 |  | 0082 | 1-02-01 |  | 1-51 | ＃2 MCB | CB 52AS | 二號主變二次側 52AS |  | aaea | B2/S36_D1 | [8 empty] | 新港SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 249 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | T/3MTR |  |  | 0030 |  | 0105 | 1-03-03 |  | 1-68 | ＃3 MCB | CB 52AS | 三號主變二次側 52AS |  | abca | B2/S36_D1 | [8 empty] | 新港SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 250 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-02 |  |  | 760 | 51A | 二號主變一次側 51A |  |  | B3/S36_D1 | [8 empty] | 新港SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 251 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-03 |  |  | 760 | 51NA | 二號主變一次側 51NA |  |  | B3/S36_D1 | [8 empty] | 新港SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 252 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-01 |  |  | ＃2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 253 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-02-05 |  |  | ＃2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 254 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-34-10 |  |  | ＃2 MTR | 287S U/L | 二號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 255 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  | 0127 | 1-12-03 |  | 1-7E | ＃2 MCB | #2M 11KV 81A | ＃2 MCB 81A |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR |  |  |  |  | CDC | 256 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-04 |  |  | 770 | 51A | 三號主變一次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 257 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-03-05 |  |  | 770 | 51NA | 三號主變一次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 258 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-03 |  |  | ＃3 MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 259 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-03-07 |  |  | ＃3 MTR | 87A | 三號主變差動電驛 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 260 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  |  | 1-35-08 |  |  | ＃3 MTR | 387S U/L | 三號主變差動電驛(使用 / 閉鎖)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 261 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  | 0128 | 1-15-07 |  | 1-7F | ＃3 MCB | #3M 11KV 81A | ＃3MAIN 81A |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR |  |  |  |  | CDC | 262 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-02-06 |  |  | ＃2 MCB | 51A | 二號主變二次側 51A |  |  | B2/S36_D1 | [8 empty] | 新港SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 263 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0298 |  |  | 1-34-07 |  |  | ＃2 MTR | 2TRA | 二號主變重故障警報 |  | a | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 264 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0299 |  |  | 1-34-08 |  |  | ＃2 MTR | 2TRF | 二號主變輕故障警報 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 265 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-34-11 |  |  | ＃2 MTR | R/L | 二號主變OLTC(中心 / 現場)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 266 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S36 | 新港SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0303 |  | 0092 | 1-34-12 |  | 1-5B | ＃2 MTR | A/M | 二號主變OLTC(自動 / 手動)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 267 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-00 |  |  | ＃3 MCB | 51A | 三號主變二次側 51A |  |  | B2/S36_D1 | [8 empty] | 新港SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 268 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0312 |  |  | 1-35-05 |  |  | ＃3 MTR | 3TRA | 三號主變重故障警報 |  | a | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 269 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0313 |  |  | 1-35-06 |  |  | ＃3 MTR | 3TRF | 三號主變輕故障警報 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 270 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-35-09 |  |  | ＃3 MTR | R/L | 三號主變OLTC(中心 / 現場)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 271 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S36 | 新港SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0115 | 1-35-10 |  | 1-72 | ＃3 MTR | A/M | 三號主變OLTC(自動 / 手動)指示 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 272 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0367 | 368 | 0048 | 1-38-12 | 1-38-13 | 1-2F | 761 | DS ON | ＃2 MTR 二號主變一次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 273 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0369 | 370 | 0049 | 1-38-14 | 1-38-15 | 1-30 | 762 | DS ON | ＃2 MTR 二號主變二次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 274 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0371 | 372 | 0050 | 1-39-00 | 1-39-01 | 1-31 | 771 | DS ON | ＃3 MTR 三號主變一次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.771_DS | 771(#3MTR) DS | DTR |  |  |  |  | CDC | 275 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0373 | 374 | 0051 | 1-39-02 | 1-39-03 | 1-32 | 772 | DS ON | ＃3 MTR 三號主變二次側 |  |  | B3/S36_D1 | [8 empty] | 新港SS.772_DS | 772(#3MTR) DS | DTR |  |  |  |  | CDC | 276 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | D1 | 2M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 277 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | E1 | 2M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 278 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-04 |  |  | ＃2 MTR | 96A | 二號主變 96P RY |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 279 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-34-09 |  |  | ＃2 MTR | 248T | 二號主變OLTC遲滯警報 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 280 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 1-35-04 |  |  | ＃2 MTR | 227C | 二號主變AC電源欠壓 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 281 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | D1 | 3M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 282 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | E1 | 3M_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 283 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-03-06 |  |  | ＃3 MTR | 96A | 三號主變 96P RY |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 284 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0314 |  |  | 1-35-07 |  |  | ＃3 MTR | 348T | 三號主變OLTC遲滯警報 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 285 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0325 |  |  | 1-36-02 |  |  | ＃3 MTR | 327C | 三號主變AC電源欠壓 |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 286 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | T/2SSTR |  |  | 0147 |  | 0101 | 1-12-00 |  | 1-64 | #2 SSTR CB | 52AS | #2 SSTR CB 52AS |  | aaba | B2/S36_D1 | [8 empty] | 新港SS.490_CB | 490(#2SSTR) CB | OTHER |  |  |  |  | CDC | 287 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  | B2,B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-01 |  |  | #2 SSTR CB | PHA | #2 SSTR CB PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 288 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  | B2,B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-02 |  |  | #2 SSTR CB | GDA | #2 SSTR CB GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  |  |  |  | CDC | 289 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 290 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 291 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | 590 | #3SSTR(590) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | T/3SSTR |  |  | 0175 |  | 0124 | 1-15-04 |  | 1-7B | #3 SSTR CB | 52AS | #3 SSTR CB 52AS |  | abia | B2/S36_D1 | [8 empty] | 新港SS.590_CB | 590(#3SSTR) CB | OTHER |  |  |  |  | CDC | 292 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 590 | #3SSTR(590) |  | PHA |  | B2,B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-15-05 |  |  | #3 SSTR CB | PHA | #3 SSTR CB PHA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#3SSTR_51A | #3SSTR 51RY | OTHER |  |  |  |  | CDC | 293 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 590 | #3SSTR(590) |  | GDA |  | B2,B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-15-06 |  |  | #3 SSTR CB | GDA | #3 SSTR CB GDA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER |  |  |  |  | CDC | 294 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 590 | #3SSTR(590) |  | D1 | 591(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.591 | 591 (非取樣點) | OTHER | [5 empty] | 295 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 590 | #3SSTR(590) |  | E1 | 591E(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.591E | 591E (非取樣點) | OTHER | [5 empty] | 296 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BUS | A/LBS220^C/2SC(A) |  |  | 0144 |  | 0084 | 1-11-05 |  | 1-53 | ＃2 SC | CB ON/OFF | 11KV 二號 SC 52AS |  | aaab | B2/S36_D1 | [8 empty] | 新港SS.230_CB | 230(11KV #2SC) CB | SC |  |  |  |  | CDC | 297 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0093 | 1-35-03 |  | 1-5C | ＃2 SC | A/M | 二號SC乏控器(自動 / 手動)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.230_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 298 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 230_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 299 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | A/LBS230^C/3SC(A) |  |  | 0172 |  | 0107 | 1-15-01 |  | 1-6A | ＃3 SC | CB ON/OFF | 11KV 三號SC 52AS |  | abhb | B2/S36_D1 | [8 empty] | 新港SS.240_CB | 240(11KV #3SC) CB | SC |  |  |  |  | CDC | 300 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0324 |  | 0116 | 1-36-01 |  | 1-73 | ＃3 SC | A/M | 三號SC乏控器(自動 / 手動)指示 |  |  | B2/S36_D1 | [8 empty] | 新港SS.240_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 301 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 240_ES(非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 302 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0145 |  |  | 1-11-06 |  |  | ＃2 SC | SCA | 11KV二號 SC 11KV SCA |  |  | B2/S36_D1 | [8 empty] | 新港SS.230_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 303 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0146 |  |  | 1-11-07 |  |  | ＃2 SC | UVA | 11KV二號 SC 11KV UVA |  |  | B2/S36_D1 | [8 empty] | 新港SS.230_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 304 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0173 |  |  | 1-15-02 |  |  | ＃3 SC | SCA | 11KV三號 SC SCA |  |  | B2/S36_D1 | [8 empty] | 新港SS.240_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 305 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0174 |  |  | 1-15-03 |  |  | ＃3 SC | UVA | 11KV三號 SC UVA |  |  | B2/S36_D1 | [8 empty] | 新港SS.240_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 306 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 231(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.231DS | 231DS (非取樣點) | SC | [5 empty] | 307 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 241(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.241DS | 241DS (非取樣點) | SC | [5 empty] | 308 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS1 | 230 | B3,Element | [7 empty] | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0435 |  | 0094 | 1-3D-00 |  | 1-5D | 23KV SC-2 LBS | DS ON | 23KV SC-2 LBS |  |  | B2/S36_D1 | [8 empty] | 新港SS.230_LBS | 230(11KV #2SC) LBS | SC |  |  |  |  | CDC | 309 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS1 | 240 | B3,Element | [7 empty] | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0437 |  | 0117 | 1-3D-02 |  | 1-74 | 23KV SC-3 LBS | DS ON | 23KV SC-3 LBS |  |  | B2/S36_D1 | [8 empty] | 新港SS.240_LBS | 240(11KV #3SC) LBS | SC |  |  |  |  | CDC | 310 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10 ﹪A I 轉換卡檢查參考點200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 311 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90 ﹪A I 轉換卡檢查參考點1800 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 312 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 313 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 314 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10 ﹪A I轉換卡檢查參考點200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 315 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90 ﹪A I轉換卡檢查參考點1800 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 316 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0278 |  |  | 1-33-03 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 新港SS.TEST_CB | TEST CB | OTHER |  | DNP_Cmd_EMPTY |  |  | CDC | 317 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0227 |  |  | 1-30-00 |  |  | 直流充電機 | CHG1 | 直流充電機故障 |  |  | B3/S36_D1 | [8 empty] | 新港SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0228 |  |  | 1-30-01 |  |  | 通訊充電機 | CHG2 | 通訊充電機故障 |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-30-02 |  |  | 直流電源 | DCE | DC接地故障(＋.－) |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0233 |  |  | 1-30-06 |  |  | 所內電源 | STUV | 所內用電警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0234 |  |  | 1-30-07 |  |  | 充油電纜 | OPA | 油壓電力電纜警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-30-08 |  |  | 一般火警 | FIRE | 一般火災警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.火災警報(1) | [新港]火警 | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0239 |  |  | 1-30-12 |  |  | NFB監視 | DCA | 配電盤DC-NFB跳脫警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0246 |  |  | 1-31-03 |  |  | 無人化防盜警報(1) |  | 無人化防盜警報(1) |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0247 |  |  | 1-31-04 |  |  | 無人化防盜警報(2) |  | 無人化防盜警報(2) |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0248 |  |  | 1-31-05 |  |  | 無人化門禁警報(1) | 保全總機(DOOR) | 無人化門禁警報(1) 保全總機(DOOR) |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化門禁(1) | 保全(DOOR) | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0249 |  |  | 1-31-06 |  |  | 無人化門禁警報(2) |  | 無人化門禁警報(2) |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化門禁(2) | 無人化門禁(2) | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0254 |  |  | 1-31-11 |  |  | 69KV CB 輕故障 | 6CBF | 69KV CB 輕警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-31-12 |  |  | 69KV CB 重故障 | 6CBA | 69KV CB 重警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0256 |  |  | 1-31-13 |  |  | 11KV CB 輕故障 | 1CBF | 11KV CB NFB跳脫警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-31-14 |  |  | 11KV CB 重故障 | 1CBA | 11KV CB NFB跳脫警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0250 |  |  | 1-31-07 |  |  | Locate Empty | OLTEA | 通訊設備光纖主故障OLMA |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0251 |  |  | 1-31-08 |  |  | Locate Empty | OLTEF | 通訊設備光纖次故障OLMI |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊PCM警報 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0252 |  |  | 1-31-09 |  |  | Locate Empty | PCMA | 博碼調變器故障 |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0231 |  | 0052 | 1-30-04 |  | 1-33 | 所內開關場 | FLA | 開關場照明 |  |  | B3/S36_D1 | [8 empty] | 新港SS.開關場照明(A) | 所內開關場照明 | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0232 |  | 0053 | 1-30-05 |  | 1-34 | 所內配電盤 | FLB | 市區路燈照明 |  |  | B3/S36_D1 | [8 empty] | 新港SS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-02-07 |  |  | ＃2 MCB | 51NA | 二號主變二次側 51NA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#2MAIN_51NA | #2MAIN 51NA | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-01 |  |  | ＃3 MCB | 51NA | 三號主變二次側 51NA |  |  | B2/S36_D1 | [8 empty] | 新港SS.#3MAIN_51NA | #3MAIN 51NA | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | M2 | #2MTR(M2) |  | 3P51A | #2M_三相51A | B2,B3,Element | Status | 3相 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-00 |  |  | ＃2 MCB | 三相51A | ＃2 MCB 三相51A |  |  | B2/S36_D1 | [8 empty] | 新港SS.#2M_三相51A | #2M 三相51A | OTHER |  |  |  |  | CDC | 340 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | M3 | #3MTR(M3) |  | 3P51A | #3M_三相51A | B2,B3,Element | Status | 3相 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-02 |  |  | ＃3 MCB | 三相51A | ＃3MCB三相51A(MA) |  |  | B2/S36_D1 | [8 empty] | 新港SS.#3M_三相51A | #3M 三相51A | OTHER |  |  |  |  | CDC | 341 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Door | 大門側門 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0230 |  |  | 1-30-03 |  |  | 門禁 | DOOR | 大門開關 |  |  | B3/S36_D1 | [8 empty] | 新港SS.門禁 | 大門側門 | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0236 |  |  | 1-30-09 |  |  | 安全監控 | SUPA | 所內安全監控 |  |  | B3/S36_D1 | [8 empty] | 新港SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | PSF | 所內其他輕故障 | Element | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0237 |  |  | 1-30-10 |  |  | 變電所內 | PSF | 所內其他輕故障警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.所內其他輕故障 | 所內其他輕故障 | OTHER |  |  |  |  | CDC | 344 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | PSA | 所內其他重故障 | Element | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0238 |  |  | 1-30-11 |  |  | 變電所內 | PSA | 所內其他重故障警報 |  |  | ELEM/S36_D1 | [8 empty] | 新港SS.所內其他重故障 | 所內其他重故障 | OTHER |  |  |  |  | CDC | 345 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0263 |  |  | 1-32-04 |  |  | ATS | ACBA | ACBA |  |  | B3/S36_D1 | [8 empty] | 新港SS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 346 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  | Element | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-32-05 |  |  | ACB 1S |  | ACB 1S |  |  | B3/S36_D1 | [8 empty] | 新港SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 347 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  | Element | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0265 |  |  | 1-32-06 |  |  | ACB 2S |  | ACB 2S |  |  | B3/S36_D1 | [8 empty] | 新港SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 348 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | ACB3 |  | Element | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-32-07 |  |  | ACB 3S |  | ACB 3S |  |  | B3/S36_D1 | [8 empty] | 新港SS.所內電源ACB3 | 所內電源ACB3 | OTHER |  |  |  |  | CDC | 349 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | TRIP監視 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-32-08 |  |  | TRIP監視 |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.TRIP監視 | TRIP監視 | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0261 |  |  | 1-32-02 |  |  | SC 60RY | SC 60A | SC 60A 過欠壓警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.11KV_SC_60A | 11KV SC 60RY | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報(1) | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0240 |  |  | 1-30-13 |  |  | 洩油池水位警報 1 |  | 洩油池水位警報 1 |  |  | B3/S36_D1 | [8 empty] | 新港SS.水位警報(1) | 洩油池水位警報(1) | OTHER |  |  |  |  | CDC | 352 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報(2) | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0241 |  |  | 1-30-14 |  |  | 洩油池水位警報 2 |  | 洩油池水位警報 2 |  |  | B3/S36_D1 | [8 empty] | 新港SS.水位警報(2) | 洩油池水位警報(2) | OTHER |  |  |  |  | CDC | 353 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 1-37-12 |  |  | ＃2 MTR | #2 MTR 96B1 |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR96B1 | 2M 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 354 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 1-37-13 |  |  | ＃2 MTR | #2 MTR 96B2 |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR96B2 | 2M 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 355 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 1-37-14 |  |  | ＃2 MTR | #2 MTR 96D |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR96D | 2M 放壓電驛動作 | OTHER |  |  |  |  | CDC | 356 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 1-37-15 |  |  | ＃2 MTR | #2 MTR 96P |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR96P | 2M 突壓電驛動作 | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0355 |  |  | 1-38-00 |  |  | ＃2 MTR | #2 MTR 63Q |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#2MTR63Q | 2M ULTC電驛動作 | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 1-38-01 |  |  | ＃3 MTR | #3 MTR 96B1 |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR96B1 | 3M 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 1-38-02 |  |  | ＃3 MTR | #3 MTR 96B2 |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR96B2 | 3M 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 1-38-03 |  |  | ＃3 MTR | #3 MTR 96D |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR96D | 3M 放壓電驛動作 | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 1-38-04 |  |  | ＃3 MTR | #3 MTR 96P |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR96P | 3M 突壓電驛動作 | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS |  |  | 3MTR | #3MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 1-38-05 |  |  | ＃3 MTR | #3 MTR 63Q |  |  |  | B1/S36_D1 | [8 empty] | 新港SS.#3MTR63Q | 3M ULTC電驛動作 | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-04-05 |  |  | 69KV TIE(600) | 600 67A(B1) | 600 TIE 67A(B1)51A |  |  | B2/S36_A1 | [8 empty] | 新港SS.600PHA(1) | 600(TIE) 67A(B1) | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-04-06 |  |  | 69KV TIE(600) | 600 67NA(B1) | 600 67NA(B1)51NA |  |  | B2/S36_A1 | [8 empty] | 新港SS.600GDA(1) | 600(TIE) 67NA(B1) | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-04-07 |  |  | 69KV TIE(600) | 600 67A(B2) | 600 TIE67A(B2) |  |  | B2/S36_A1 | [8 empty] | 新港SS.600PHA(2) | 600(TIE) 67A(B2) | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-00 |  |  | 69KV TIE(600) | 600 67A(B2) | 600 67NA(B2) |  |  | B2/S36_A1 | [8 empty] | 新港SS.600GDA(2) | 600(TIE) 67NA(B2) | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-00 |  |  | Locate Empty |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.69KV_59A | 69KV BUS 59A過壓警報 | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | LOA |  | Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0262 |  |  | 1-32-03 |  |  | 79 RY閉鎖 | LOA | LOA 79 RY閉鎖 |  |  | B3/S36_D1 | [8 empty] | 新港SS.79RY_LOA | 79RY LOA | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Fire1 | 無人化防火(1) | Element | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0245 |  |  | 1-31-02 |  |  | 無人化防火警報(2) | CO2 FAULT | 無人化防火警報(2) CO2 FAULT |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化防火(1) | CO2故障 | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Fire2 | 無人化防火(2) | Element | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0244 |  |  | 1-31-01 |  |  | 無人化防火警報(1) | CO2 FIRE | 無人化防火警報(1) CO2 FIRE |  |  | B3/S36_D1 | [8 empty] | 新港SS.無人化防火(2) | CO2火警 | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Water4 |  | Element | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0242 |  |  | 1-30-15 |  |  | 地下室水位警報 1 |  | 地下室水位警報 1 |  |  | B3/S36_D1 | [8 empty] | 新港SS.地下室淹水(1) | 地下室淹水(1) | OTHER |  |  |  |  | CDC | 372 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Water5 | 地下室淹水(2) | Element | Status | 淹水警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0243 |  |  | 1-31-00 |  |  | 地下室水位警報 2 |  | 地下室水位警報 2 |  |  | B3/S36_D1 | [8 empty] | 新港SS.地下室淹水(2) | 地下室淹水(2) | OTHER |  |  |  |  | CDC | 373 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Comm_A | 通訊電源故障 | Element | Status | 通訊處理單元故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 1-31-10 |  |  | Locate Empty | 光纖通訊系統 電源故障 | 光纖通訊系統 電源故障 |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊電源故障 | 通訊電源故障 | OTHER |  |  |  |  | CDC | 374 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 維護運轉警報 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0260 |  |  | 1-32-01 |  |  | 維護運轉警報 | 69AL | 69KV ABS NFB跳脫警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.維護運轉警報 | 維護運轉警報 | OTHER |  |  |  |  | CDC | 375 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 8A5Other | 現場設備斷訊 | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0282 |  |  | 1-33-07 |  |  | 現場設備斷訊 |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.現場設備斷訊 | 現場設備斷訊 | OTHER |  |  |  |  | CDC | 376 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | IRFA | IED警報 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0446 |  |  | 1-3D-11 |  |  | 11KV IED重警報 |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.IED警報 | 11/23KV CBA 重故障(IED故障) | OTHER |  |  |  |  | CDC | 377 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JI27 | VAR | 新七線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新七線KVAR | 11KV新七線 KVAR | FEEDER |  |  |  |  | CDC | 378 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JI27 | A1 | 新七線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新七線A1 | 11KV新七線 R相AMP | FEEDER |  |  |  |  | CDC | 379 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JI27 | A2 | 新七線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新七線A2 | 11KV新七線 S相AMP | FEEDER |  |  |  |  | CDC | 380 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JI27 | A3 | 新七線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新七線A3 | 11KV新七線 T相AMP | FEEDER |  |  |  |  | CDC | 381 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | JI27 | NA | 新七線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新七線A0 | 11KV新七線 N相AMP | FEEDER |  |  |  |  | CDC | 382 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | JI29 | VAR | 新九線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新九線KVAR | 11KV新九線 KVAR | FEEDER |  |  |  |  | CDC | 383 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | JI29 | A1 | 新九線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新九線A1 | 11KV新九線 R相AMP | FEEDER |  |  |  |  | CDC | 384 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | JI29 | A2 | 新九線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新九線A2 | 11KV新九線 S相AMP | FEEDER |  |  |  |  | CDC | 385 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | JI29 | A3 | 新九線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新九線A3 | 11KV新九線 T相AMP | FEEDER |  |  |  |  | CDC | 386 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | JI29 | NA | 新九線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新九線A0 | 11KV新九線 N相AMP | FEEDER |  |  |  |  | CDC | 387 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JI28 | VAR | 新八線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新八線KVAR | 11KV新八線 KVAR | FEEDER |  |  |  |  | CDC | 388 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JI28 | A1 | 新八線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新八線A1 | 11KV新八線 R相AMP | FEEDER |  |  |  |  | CDC | 389 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JI28 | A2 | 新八線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新八線A2 | 11KV新八線 S相AMP | FEEDER |  |  |  |  | CDC | 390 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JI28 | A3 | 新八線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新八線A3 | 11KV新八線 T相AMP | FEEDER |  |  |  |  | CDC | 391 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JI28 | NA | 新八線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新八線A0 | 11KV新八線 N相AMP | FEEDER |  |  |  |  | CDC | 392 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | JI30 | VAR | 新十線無效電力 | KVAR_-9000_9000(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十線KVAR | 11KV新十線 KVAR | FEEDER |  |  |  |  | CDC | 393 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | JI30 | A1 | 新十線R相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十線A1 | 11KV新十線 R相AMP | FEEDER |  |  |  |  | CDC | 394 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | JI30 | A2 | 新十線S相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十線A2 | 11KV新十線 S相AMP | FEEDER |  |  |  |  | CDC | 395 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | JI30 | A3 | 新十線T相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十線A3 | 11KV新十線 T相AMP | FEEDER |  |  |  |  | CDC | 396 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | JI30 | NA | 新十線零相電流 | A_-500_500(-2000_2000) |  | B2/S36_D1 | [8 empty] | 新港SS.新十線A0 | 11KV新十線 N相AMP | FEEDER |  |  |  |  | CDC | 397 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 充電機 電壓 | DC-V | 直流電源電壓 VDC | DCVolt_-150_150(-2000_2000) |  | B3/S36_D1 | [8 empty] | 新港SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 398 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 路燈電源監視 | INSERT | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0345 |  |  | 1-37-06 |  |  | 路燈電源監視 |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | [5 empty] | 399 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊室溫度異常 | INSERT | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0361 |  |  | 1-38-06 |  |  | 通訊室溫度異常 |  |  |  |  | B3/S36_D1 | [8 empty] | 新港SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | [5 empty] | 400 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0052 |  |  | 1-06-01 |  |  | 630 | 630 RYFA | 北港一路 |  |  | B2/S36_A1 | [8 empty] | 新港SS.630_RYFA | 630 IED警報 | OTHER | [5 empty] | 401 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0053 |  |  | 1-06-02 |  |  | 640 | 640 RYFA | 北港二路 |  |  | B2/S36_A1 | [8 empty] | 新港SS.640_RYFA | 640 IED警報 | OTHER | [5 empty] | 402 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | 1A5Other | 69-BM-RESET | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0054 |  | 0129 | 1-06-03 |  | 2-00 | 69KV | 69 B.M.Reset | 69KV Bay Module |  |  | B3/S36_D1 | [8 empty] | 新港SS.69-BM-RESET | 69-BM-RESET | OTHER | [5 empty] | 403 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | OFF/ON | ON
S36 | 新港SS | 11 | 11kV | ComPoint |  |  | 1A5Other | 11-BM-RESET | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0055 |  | 0130 | 1-06-04 |  | 2-01 | 11KV | 11 B.M.Reset | 11KV Bay Module |  |  | B3/S36_D1 | [8 empty] | 新港SS.11-BM-RESET | 11-BM-RESET | OTHER | [5 empty] | 404 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | OFF/ON | ON
S36 | 新港SS | 0 |  | StaDev | 所內設施 |  | Water3 | 開關場水位警報 | INSERT | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-33-04 |  |  | 開關場水位監視警報 |  | 開關場水位監視警報 |  |  | B3/S36_D1 | [8 empty] | 新港SS.開關場水位警報 | 開關場水位警報 | OTHER | [5 empty] | 405 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0419 |  |  | 1-3C-00 |  |  | 610 | RYFA | 嘉太一路610 IED 警報 |  |  | B2/S36_A1 | [8 empty] | 新港SS.610_RYFA | 610 IED警報 | OTHER | [5 empty] | 406 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0420 |  |  | 1-3C-01 |  |  | 620 | RYFA | 嘉太二路620 IED 警報 |  |  | B2/S36_A1 | [8 empty] | 新港SS.620_RYFA | 620 IED警報 | OTHER | [5 empty] | 407 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0050 |  |  | 1-05-07 |  |  | SPARE |  |  |  |  | B2/S36_A1 | [8 empty] | 新港SS.600_RYFA | 600 IED警報 | OTHER | [5 empty] | 408 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | BFA |  | INSERT | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0283 |  |  | 1-33-08 |  |  | 87BF | 87BF | 69KV BUS RY 87BF |  |  | B3/S36_D1 | [8 empty] | 新港SS.BUSRY_BF | BUSRY BF | OTHER | [5 empty] | 409 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | ComPoint |  |  | 87CTFA |  | INSERT | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-33-09 |  |  | CTFA | CTFA | 69KV BUS RY CTFA |  |  | B3/S36_D1 | [8 empty] | 新港SS.BUSRY_CTFA | BUSRY CTFA | OTHER | [5 empty] | 410 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0027 |  |  | 1-5B |  |  | JI27 | 新七線瓦時計量值 | 新七線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 411 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | JI28 | 新八線瓦時計量值 | 新八線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 412 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0029 |  |  | 1-5D |  |  | JI29 | 新九線瓦時計量值 | 新九線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 413 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | JI30 | 新十線瓦時計量值 | 新十線 KWH |  |  | B2/S36_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 414 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S36 | 新港SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S36_D1 | [8 empty] | 新港SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | [5 empty] | 415 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S36 | 新港SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S36_D1 | [12 empty] | 新港SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S36/69/1BUS/V; OPRD2: S36/69/2BUS/V
S36 | 新港SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S36_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S36/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S36 | 新港SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S36_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: S36/11/M2/MW; OPRD2: S36/11/M3/MW; OPRD3: S36/69/610/MW; OPRD4: S36/69/620/MW; OPRD5: S36/69/630/MW; OPRD6: S36/69/640/MW
S36 | 新港SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S36_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S36/0/CalcPoint/OPRN2_MW
S36 | 新港SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S36_D1 | [17 empty] | none
S36 | 新港SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S36_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S36/0/CalcPoint/OPRN1; OPRD2: S36/0/CalcPoint/OPRN2; OPRD3: S36/0/CalcPoint/PRFL_UL
S36 | 新港SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S36_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S36/11/M2/MW; OPRD2: S36/11/M2/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S36_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S36/11/M3/MW; OPRD2: S36/11/M3/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS | 69 | 69kV | 610 | 新港～嘉太一路(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S36_A1 | [12 empty] | 新港SS.610_AMP | 新港嘉太一路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: S36/69/610/MW; OPRD2: S36/69/610/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS | 69 | 69kV | 620 | 新港～嘉太二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S36_A1 | [12 empty] | 新港SS.620_AMP | 新港嘉太二路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: S36/69/620/MW; OPRD2: S36/69/620/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS | 69 | 69kV | 630 | 北港～新港一路(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S36_A1 | [12 empty] | 新港SS.630_AMP | 北港新港一路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: S36/69/630/MW; OPRD2: S36/69/630/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS | 69 | 69kV | 640 | 北港～新港二路(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S36_A1 | [12 empty] | 新港SS.640_AMP | 北港新港二路 AMP | LINE69 | AMP_CAL | C12R0953 | amp_cal | OPRD1: S36/69/640/MW; OPRD2: S36/69/640/MVAR; OPRD3: S36/0/CalcPoint/Vbs2
S36 | 新港SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S36_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S36/11/2BUS/V
S36 | 新港SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S36_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S36/11/3BUS/V
S36 | 新港SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S36_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新港SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S36/11/M2/MW; OPRD2: S36/11/M2/MVAR
S36 | 新港SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S36_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新港SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S36/11/M3/MW; OPRD2: S36/11/M3/MVAR
S36 | 新港SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S36_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S36//2MTR/MVA; OPRD2: 0
S36 | 新港SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S36_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S36//3MTR/MVA; OPRD2: 0
S36 | 新港SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S36_D1 | [12 empty] | 新港SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S36/11/M2/MW; OPRD2: S36/11/M2/MVAR
S36 | 新港SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S36_D1 | [12 empty] | 新港SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S36/11/M3/MW; OPRD2: S36/11/M3/MVAR
S36 | 新港SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S36_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S36//2MTR/SupLocal; OPRD2: S36//2MTR/Tap Chan; OPRD3: NULL
S36 | 新港SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S36_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S36//3MTR/SupLocal; OPRD2: S36//3MTR/Tap Chan; OPRD3: NULL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI27/I_R; OPRD3: S36/11/JI27/I_S; OPRD4: S36/11/JI27/I_T
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI28/I_R; OPRD3: S36/11/JI28/I_S; OPRD4: S36/11/JI28/I_T
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI29/I_R; OPRD3: S36/11/JI29/I_S; OPRD4: S36/11/JI29/I_T
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI30/I_R; OPRD3: S36/11/JI30/I_S; OPRD4: S36/11/JI30/I_T
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI31/I_R; OPRD3: S36/11/JI31/I_S; OPRD4: S36/11/JI31/I_T
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/2BUS/V; OPRD2: S36/11/JI32/I_R; OPRD3: S36/11/JI32/I_S; OPRD4: S36/11/JI32/I_T
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI33/I_R; OPRD3: S36/11/JI33/I_S; OPRD4: S36/11/JI33/I_T
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI34/I_R; OPRD3: S36/11/JI34/I_S; OPRD4: S36/11/JI34/I_T
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI35/I_R; OPRD3: S36/11/JI35/I_S; OPRD4: S36/11/JI35/I_T
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI36/I_R; OPRD3: S36/11/JI36/I_S; OPRD4: S36/11/JI36/I_T
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI37/I_R; OPRD3: S36/11/JI37/I_S; OPRD4: S36/11/JI37/I_T
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S36/11/3BUS/V; OPRD2: S36/11/JI38/I_R; OPRD3: S36/11/JI38/I_S; OPRD4: S36/11/JI38/I_T
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI27/kVA; OPRD2: S36/11/JI27/KVAR
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI28/kVA; OPRD2: S36/11/JI28/KVAR
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI29/kVA; OPRD2: S36/11/JI29/KVAR
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI30/kVA; OPRD2: S36/11/JI30/KVAR
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI31/kVA; OPRD2: S36/11/JI31/KVAR
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI32/kVA; OPRD2: S36/11/JI32/KVAR
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI33/kVA; OPRD2: S36/11/JI33/KVAR
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI34/kVA; OPRD2: S36/11/JI34/KVAR
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI35/kVA; OPRD2: S36/11/JI35/KVAR
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI36/kVA; OPRD2: S36/11/JI36/KVAR
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI37/kVA; OPRD2: S36/11/JI37/KVAR
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S36_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S36/11/JI38/kVA; OPRD2: S36/11/JI38/KVAR
S36 | 新港SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S36_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S36/11/M2/MW; OPRD2: S36/11/M3/MW
S36 | 新港SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S36_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S36/11/M2/MVAR; OPRD2: S36/11/M3/MVAR
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S36_D1 | [12 empty] | 新港SS.230_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: S36/11/230/CB; OPRD2: 6.9; OPRD3: 0
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S36_D1 | [12 empty] | 新港SS.240_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: S36/11/240/CB; OPRD2: 6.9; OPRD3: 0
S36 | 新港SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S36_D1 | [12 empty] | 新港SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_18 | OPRD1: S36//2MTR/96B1; OPRD2: S36//2MTR/96PA; OPRD3: S36//2MTR/TRA; OPRD4: S36//2MTR/63Q; OPRD5: S36//2MTR/96D; OPRD6: S36//2MTR/96B2; OPRD7: S36//2MTR/87A; OPRD8: S36//2MTR/51ZA; OPRD9: S36//3MTR/96B1; OPRD10: S36//3MTR/63Q; OPRD11: S36//3MTR/96D; OPRD12: S36//3MTR/96B2; OPRD13: S36//3MTR/96PA; OPRD14: S36//3MTR/51ZA; OPRD15: S36//3MTR/TRA; OPRD16: S36//3MTR/87A; OPRD17: S36/69/1BUS/87A; OPRD18: S36/69/2BUS/87A
S36 | 新港SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S36_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S36//2MTR/TRF; OPRD2: S36//3MTR/TRF
S36 | 新港SS | 11 | 11kV | M2_A1 | #2MTR(M2) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/11/M2/81A
S36 | 新港SS | 11 | 11kV | M3_A1 | #3MTR(M3) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/11/M3/81A
S36 | 新港SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/0/StaDev/DCE
S36 | 新港SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/0/StaDev/Fire
S36 | 新港SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/0/StaDev/DCA
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/CBF
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/CBA
S36 | 新港SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/0/StaDev/PSF
S36 | 新港SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S36_A1 | [17 empty] | lamp2CC | OPRD1: S36/0/StaDev/PSA
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/59A
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | 1A5Other | 69-BM-RESET |  | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/1A5Other
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | BFA |  |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/BFA
S36 | 新港SS | 69 | 69kV | ComPoint_D1 |  |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S36_D1 | [17 empty] | lamp2CC | OPRD1: S36/69/ComPoint/87CTFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S36 | 新港SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 新港SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S36/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 新港SS.610_AMP | 新港嘉太一路 AMP | LINE69 | S36/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 新港SS.620_AMP | 新港嘉太二路 AMP | LINE69 | S36/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 新港SS.630_AMP | 北港新港一路 AMP | LINE69 | S36/69/630/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 新港SS.640_AMP | 北港新港二路 AMP | LINE69 | S36/69/640/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C12R0953 | 857.700012 | 857.700012 | 953.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S36 | 新港SS | 0 |  |  |  |  | 新七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新七線KVA | 11KV新七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新七線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新七線KW | 11KV新七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新九線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新九線KVA | 11KV新九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新九線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新九線KW | 11KV新九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新八線KVA | 11KV新八線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新八線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新八線KW | 11KV新八線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十一線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十一線KVA | 11KV新十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十一線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十一線KW | 11KV新十一線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十七線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十七線KVA | 11KV新十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十七線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十七線KW | 11KV新十七線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十二線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十二線KVA | 11KV新十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十二線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十二線KW | 11KV新十二線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十八線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十八線KVA | 11KV新十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十八線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十八線KW | 11KV新十八線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十三線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十三線KVA | 11KV新十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十三線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十三線KW | 11KV新十三線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十五線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十五線KVA | 11KV新十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十五線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十五線KW | 11KV新十五線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十六線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十六線KVA | 11KV新十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十六線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十六線KW | 11KV新十六線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十四線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十四線KVA | 11KV新十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十四線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十四線KW | 11KV新十四線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十線KVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十線KVA | 11KV新十線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  |  |  |  | 新十線KW | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.新十線KW | 11KV新十線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S36//2MTR/MVA |  | MVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_PF | #2MTR 功率因素 | DTR | S36//2MTR/PF |  | RPDC_PF_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S36//3MTR/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_PF | #3MTR 功率因素 | DTR | S36//3MTR/PF |  | RPDC_PF_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S36 | 新港SS | 11 | 11kV | 230_SC | #2SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.230_SC_MVAR | 11KV#2SC MVAR | SC | S36/11/230/MVAR |  | SC_LBS_11 |  |  | 35 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 11 | 11kV | 240_SC | #3SC | 6 | MVAR | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.240_SC_MVAR | 11KV#3SC MVAR | SC | S36/11/240/MVAR |  | SC_LBS_11 |  |  | 36 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 69 | 69kV | 610_CB | 新港嘉太一路(610_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.610_CB_2 | 610(新港嘉太一路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 37 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 620_CB | 新港嘉太二路(620_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.620_CB_2 | 620(新港嘉太二路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 38 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 630_CB | 北港新港一路(630_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.630_CB_2 | 630(北港新港一路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 39 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 640_CB | 北港新港二路(640_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.640_CB_2 | 640(北港新港二路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 40 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 600_CB | 600(600_CB) | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.600_CB_2 | 600 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 41 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 新港SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 42 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 新港SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 43 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 充油電纜OPA | 充油電纜低油壓警報 | [27 empty] | ADCS_N | [8 empty] | 新港SS.充油電纜OPA_A | 充油電纜低油壓警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 44 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 新港SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S36/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 45 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 46 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | STATION_FAULT_2 |  |  | 47 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610_AMP | 新港嘉太一路 | [27 empty] | ADCS_N | [8 empty] | 新港SS.610_AMP_A | 新港嘉太一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 610_AMP | 新港嘉太一路 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.610_AMP_2 | 新港嘉太一路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 620_AMP | 新港嘉太二路 | [27 empty] | ADCS_N | [8 empty] | 新港SS.620_AMP_A | 新港嘉太二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 620_AMP | 新港嘉太二路 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.620_AMP_2 | 新港嘉太二路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 51 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 630_AMP | 北港新港一路 | [27 empty] | ADCS_N | [8 empty] | 新港SS.630_AMP_A | 北港新港一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 630_AMP | 北港新港一路 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.630_AMP_2 | 北港新港一路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 53 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 640_AMP | 北港新港二路 | [27 empty] | ADCS_N | [8 empty] | 新港SS.640_AMP_A | 北港新港二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 54 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 69 | 69kV | 640_AMP | 北港新港二路 | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.640_AMP_2 | 北港新港二路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 55 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_MVA_2 | #2MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 56 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 57 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_MVA_2 | #3MTR MVA 點燈 (D2) | DTR |  |  | MAP_SET |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S36 | 新港SS | 0 |  | 630_RYFA | 630 | [27 empty] | ADCS_N | [8 empty] | 新港SS.630_RYFA_A | 630 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 60 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 640_RYFA | 640 | [27 empty] | ADCS_N | [8 empty] | 新港SS.640_RYFA_A | 640 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 61 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 610_RYFA | 610 | [27 empty] | ADCS_N | [8 empty] | 新港SS.610_RYFA_A | 610 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 62 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 620_RYFA | 620 | [27 empty] | ADCS_N | [8 empty] | 新港SS.620_RYFA_A | 620 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 63 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 600_RYFA | 600 | [27 empty] | ADCS_N | [8 empty] | 新港SS.600_RYFA_A | 600 IED警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 64 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 691BUS_27BA | 69#1BUS | [27 empty] | ADCS_N | [8 empty] | 新港SS.69#1BUS_27BA_A | 69#1BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 65 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 692BUS_27BA | 69#2BUS | [27 empty] | ADCS_N | [8 empty] | 新港SS.69#2BUS_27BA_A | 69#2BUS 27BA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 66 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | BUSRY_BF | BUSRY | [27 empty] | ADCS_N | [8 empty] | 新港SS.BUSRY_BF_A | BUSRY BF (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 67 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | BUSRY_CTFA | BUSRY | [27 empty] | ADCS_N | [8 empty] | 新港SS.BUSRY_CTFA_A | BUSRY CTFA (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 68 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S36/0/RTU/ADCH1 |  |  |  | CDC | 69 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S36/0/RTU/ADCH2 |  |  |  | CDC | 70 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S36/0/RTU/ADCH3 |  |  |  | CDC | 71 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S36/0/RTU/ADCL1 |  |  |  | CDC | 72 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S36/0/RTU/ADCL2 |  |  |  | CDC | 73 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S36/0/RTU/ADCL3 |  |  |  | CDC | 74 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S36 | 新港SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S36/69/1BUS/V |  |  |  | CDC | 75 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S36 | 新港SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S36/69/2BUS/V |  |  |  | CDC | 76 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S36 | 新港SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BE | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S36/11/2BUS/V |  |  |  | CDC | 77 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S36 | 新港SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-EA | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S36/11/3BUS/V |  |  |  | CDC | 78 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | MW | [17 empty] | 1-85 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.610_MW | 新港嘉太一路 MW | LINE69 | S36/69/610/MW |  |  |  | CDC | 79 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | MVAR | [17 empty] | 1-86 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.610_MVAR | 新港嘉太一路 MVAR | LINE69 | S36/69/610/MVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | MW | [17 empty] | 1-87 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.620_MW | 新港嘉太二路 MW | LINE69 | S36/69/620/MW |  |  |  | CDC | 81 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | MVAR | [17 empty] | 1-88 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.620_MVAR | 新港嘉太二路 MVAR | LINE69 | S36/69/620/MVAR |  |  |  | CDC | 82 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.630_MW | 北港新港一路 MW | LINE69 | S36/69/630/MW |  |  |  | CDC | 83 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.630_MVAR | 北港新港一路 MVAR | LINE69 | S36/69/630/MVAR |  |  |  | CDC | 84 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | MW | [17 empty] | 1-8B | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.640_MW | 北港新港二路 MW | LINE69 | S36/69/640/MW |  |  |  | CDC | 85 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | MVAR | [17 empty] | 1-8C | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.640_MVAR | 北港新港二路 MVAR | LINE69 | S36/69/640/MVAR |  |  |  | CDC | 86 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新七線 | 新七線 |  | 新七線KVAR | [17 empty] | 1-C9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新七線KVAR | 11KV新七線 KVAR | FEEDER | S36/11/JI27/KVAR |  |  |  | CDC | 87 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新七線 | 新七線 |  | 新七線A1 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新七線A1 | 11KV新七線 R相AMP | FEEDER | S36/11/JI27/I_R |  |  |  | CDC | 88 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新七線 | 新七線 |  | 新七線A2 | [17 empty] | 1-CB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新七線A2 | 11KV新七線 S相AMP | FEEDER | S36/11/JI27/I_S |  |  |  | CDC | 89 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新七線 | 新七線 |  | 新七線A3 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新七線A3 | 11KV新七線 T相AMP | FEEDER | S36/11/JI27/I_T |  |  |  | CDC | 90 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新七線 | 新七線 |  | 新七線A0 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新七線A0 | 11KV新七線 N相AMP | FEEDER | S36/11/JI27/I_N |  |  |  | CDC | 91 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新九線 | 新九線 |  | 新九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新九線KVAR | 11KV新九線 KVAR | FEEDER | S36/11/JI29/KVAR |  |  |  | CDC | 92 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新九線 | 新九線 |  | 新九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新九線A1 | 11KV新九線 R相AMP | FEEDER | S36/11/JI29/I_R |  |  |  | CDC | 93 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新九線 | 新九線 |  | 新九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新九線A2 | 11KV新九線 S相AMP | FEEDER | S36/11/JI29/I_S |  |  |  | CDC | 94 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新九線 | 新九線 |  | 新九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新九線A3 | 11KV新九線 T相AMP | FEEDER | S36/11/JI29/I_T |  |  |  | CDC | 95 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新九線 | 新九線 |  | 新九線A0 | [17 empty] | 1-D7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新九線A0 | 11KV新九線 N相AMP | FEEDER | S36/11/JI29/I_N |  |  |  | CDC | 96 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新八線 | 新八線 |  | 新八線KVAR | [17 empty] | 1-CE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新八線KVAR | 11KV新八線 KVAR | FEEDER | S36/11/JI28/KVAR |  |  |  | CDC | 97 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新八線 | 新八線 |  | 新八線A1 | [17 empty] | 1-CF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新八線A1 | 11KV新八線 R相AMP | FEEDER | S36/11/JI28/I_R |  |  |  | CDC | 98 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新八線 | 新八線 |  | 新八線A2 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新八線A2 | 11KV新八線 S相AMP | FEEDER | S36/11/JI28/I_S |  |  |  | CDC | 99 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新八線 | 新八線 |  | 新八線A3 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新八線A3 | 11KV新八線 T相AMP | FEEDER | S36/11/JI28/I_T |  |  |  | CDC | 100 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新八線 | 新八線 |  | 新八線A0 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新八線A0 | 11KV新八線 N相AMP | FEEDER | S36/11/JI28/I_N |  |  |  | CDC | 101 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十一線 | 新十一線 |  | 新十一線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十一線KVAR | 11KV新十一線 KVAR | FEEDER | S36/11/JI31/KVAR |  |  |  | CDC | 102 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十一線 | 新十一線 |  | 新十一線A1 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十一線A1 | 11KV新十一線 R相AMP | FEEDER | S36/11/JI31/I_R |  |  |  | CDC | 103 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十一線 | 新十一線 |  | 新十一線A2 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十一線A2 | 11KV新十一線 S相AMP | FEEDER | S36/11/JI31/I_S |  |  |  | CDC | 104 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十一線 | 新十一線 |  | 新十一線A3 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十一線A3 | 11KV新十一線 T相AMP | FEEDER | S36/11/JI31/I_T |  |  |  | CDC | 105 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十一線 | 新十一線 |  | 新十一線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十一線A0 | 11KV新十一線 N相AMP | FEEDER | S36/11/JI31/I_N |  |  |  | CDC | 106 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十七線 | 新十七線 |  | 新十七線KVAR | [17 empty] | 2-89 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十七線KVAR | 11KV新十七線 KVAR | FEEDER | S36/11/JI37/KVAR |  |  |  | CDC | 107 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十七線 | 新十七線 |  | 新十七線A1 | [17 empty] | 2-8A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十七線A1 | 11KV新十七線 R相AMP | FEEDER | S36/11/JI37/I_R |  |  |  | CDC | 108 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十七線 | 新十七線 |  | 新十七線A2 | [17 empty] | 2-8B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十七線A2 | 11KV新十七線 S相AMP | FEEDER | S36/11/JI37/I_S |  |  |  | CDC | 109 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十七線 | 新十七線 |  | 新十七線A3 | [17 empty] | 2-8C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十七線A3 | 11KV新十七線 T相AMP | FEEDER | S36/11/JI37/I_T |  |  |  | CDC | 110 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十七線 | 新十七線 |  | 新十七線A0 | [17 empty] | 2-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十七線A0 | 11KV新十七線 N相AMP | FEEDER | S36/11/JI37/I_N |  |  |  | CDC | 111 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十二線 | 新十二線 |  | 新十二線KVAR | [17 empty] | 1-E2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十二線KVAR | 11KV新十二線 KVAR | FEEDER | S36/11/JI32/KVAR |  |  |  | CDC | 112 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十二線 | 新十二線 |  | 新十二線A1 | [17 empty] | 1-E3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十二線A1 | 11KV新十二線 R相AMP | FEEDER | S36/11/JI32/I_R |  |  |  | CDC | 113 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十二線 | 新十二線 |  | 新十二線A2 | [17 empty] | 1-E4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十二線A2 | 11KV新十二線 S相AMP | FEEDER | S36/11/JI32/I_S |  |  |  | CDC | 114 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十二線 | 新十二線 |  | 新十二線A3 | [17 empty] | 1-E5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十二線A3 | 11KV新十二線 T相AMP | FEEDER | S36/11/JI32/I_T |  |  |  | CDC | 115 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十二線 | 新十二線 |  | 新十二線A0 | [17 empty] | 1-E6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十二線A0 | 11KV新十二線 N相AMP | FEEDER | S36/11/JI32/I_N |  |  |  | CDC | 116 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十八線 | 新十八線 |  | 新十八線KVAR | [17 empty] | 2-8E | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十八線KVAR | 11KV新十八線 KVAR | FEEDER | S36/11/JI38/KVAR |  |  |  | CDC | 117 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十八線 | 新十八線 |  | 新十八線A1 | [17 empty] | 2-8F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十八線A1 | 11KV新十八線 R相AMP | FEEDER | S36/11/JI38/I_R |  |  |  | CDC | 118 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十八線 | 新十八線 |  | 新十八線A2 | [17 empty] | 2-90 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十八線A2 | 11KV新十八線 S相AMP | FEEDER | S36/11/JI38/I_S |  |  |  | CDC | 119 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十八線 | 新十八線 |  | 新十八線A3 | [17 empty] | 2-91 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十八線A3 | 11KV新十八線 T相AMP | FEEDER | S36/11/JI38/I_T |  |  |  | CDC | 120 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十八線 | 新十八線 |  | 新十八線A0 | [17 empty] | 2-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十八線A0 | 11KV新十八線 N相AMP | FEEDER | S36/11/JI38/I_N |  |  |  | CDC | 121 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十三線 | 新十三線 |  | 新十三線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十三線KVAR | 11KV新十三線 KVAR | FEEDER | S36/11/JI33/KVAR |  |  |  | CDC | 122 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十三線 | 新十三線 |  | 新十三線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十三線A1 | 11KV新十三線 R相AMP | FEEDER | S36/11/JI33/I_R |  |  |  | CDC | 123 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十三線 | 新十三線 |  | 新十三線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十三線A2 | 11KV新十三線 S相AMP | FEEDER | S36/11/JI33/I_S |  |  |  | CDC | 124 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十三線 | 新十三線 |  | 新十三線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十三線A3 | 11KV新十三線 T相AMP | FEEDER | S36/11/JI33/I_T |  |  |  | CDC | 125 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十三線 | 新十三線 |  | 新十三線A0 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十三線A0 | 11KV新十三線 N相AMP | FEEDER | S36/11/JI33/I_N |  |  |  | CDC | 126 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十五線 | 新十五線 |  | 新十五線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十五線KVAR | 11KV新十五線 KVAR | FEEDER | S36/11/JI35/KVAR |  |  |  | CDC | 127 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十五線 | 新十五線 |  | 新十五線A1 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十五線A1 | 11KV新十五線 R相AMP | FEEDER | S36/11/JI35/I_R |  |  |  | CDC | 128 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十五線 | 新十五線 |  | 新十五線A2 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十五線A2 | 11KV新十五線 S相AMP | FEEDER | S36/11/JI35/I_S |  |  |  | CDC | 129 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十五線 | 新十五線 |  | 新十五線A3 | [17 empty] | 2-82 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十五線A3 | 11KV新十五線 T相AMP | FEEDER | S36/11/JI35/I_T |  |  |  | CDC | 130 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十五線 | 新十五線 |  | 新十五線A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十五線A0 | 11KV新十五線 N相AMP | FEEDER | S36/11/JI35/I_N |  |  |  | CDC | 131 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十六線 | 新十六線 |  | 新十六線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十六線KVAR | 11KV新十六線 KVAR | FEEDER | S36/11/JI36/KVAR |  |  |  | CDC | 132 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十六線 | 新十六線 |  | 新十六線A1 | [17 empty] | 2-85 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十六線A1 | 11KV新十六線 R相AMP | FEEDER | S36/11/JI36/I_R |  |  |  | CDC | 133 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十六線 | 新十六線 |  | 新十六線A2 | [17 empty] | 2-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十六線A2 | 11KV新十六線 S相AMP | FEEDER | S36/11/JI36/I_S |  |  |  | CDC | 134 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十六線 | 新十六線 |  | 新十六線A3 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十六線A3 | 11KV新十六線 T相AMP | FEEDER | S36/11/JI36/I_T |  |  |  | CDC | 135 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十六線 | 新十六線 |  | 新十六線A0 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十六線A0 | 11KV新十六線 N相AMP | FEEDER | S36/11/JI36/I_N |  |  |  | CDC | 136 | GENERICAIPoint | SS217_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十四線 | 新十四線 |  | 新十四線KVAR | [17 empty] | 1-F8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十四線KVAR | 11KV新十四線 KVAR | FEEDER | S36/11/JI34/KVAR |  |  |  | CDC | 137 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十四線 | 新十四線 |  | 新十四線A1 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十四線A1 | 11KV新十四線 R相AMP | FEEDER | S36/11/JI34/I_R |  |  |  | CDC | 138 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十四線 | 新十四線 |  | 新十四線A2 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十四線A2 | 11KV新十四線 S相AMP | FEEDER | S36/11/JI34/I_S |  |  |  | CDC | 139 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十四線 | 新十四線 |  | 新十四線A3 | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十四線A3 | 11KV新十四線 T相AMP | FEEDER | S36/11/JI34/I_T |  |  |  | CDC | 140 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十四線 | 新十四線 |  | 新十四線A0 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十四線A0 | 11KV新十四線 N相AMP | FEEDER | S36/11/JI34/I_N |  |  |  | CDC | 141 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十線 | 新十線 |  | 新十線KVAR | [17 empty] | 1-D8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十線KVAR | 11KV新十線 KVAR | FEEDER | S36/11/JI30/KVAR |  |  |  | CDC | 142 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十線 | 新十線 |  | 新十線A1 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十線A1 | 11KV新十線 R相AMP | FEEDER | S36/11/JI30/I_R |  |  |  | CDC | 143 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十線 | 新十線 |  | 新十線A2 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十線A2 | 11KV新十線 S相AMP | FEEDER | S36/11/JI30/I_S |  |  |  | CDC | 144 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十線 | 新十線 |  | 新十線A3 | [17 empty] | 1-DB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十線A3 | 11KV新十線 T相AMP | FEEDER | S36/11/JI30/I_T |  |  |  | CDC | 145 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | 新十線 | 新十線 |  | 新十線A0 | [17 empty] | 1-DC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.新十線A0 | 11KV新十線 N相AMP | FEEDER | S36/11/JI30/I_N |  |  |  | CDC | 146 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-91 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 新港SS.600TIE_AMP | 600TIE AMP | TIE | S36/69/600/I |  |  |  | CDC | 147 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-BB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S36/11/TIE2/I_R |  |  |  | CDC | 148 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-BC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S36/11/TIE2/I_S |  |  |  | CDC | 149 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-BD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S36/11/TIE2/I_T |  |  |  | CDC | 150 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C4 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_MW | #2MTR二次側 MW | DTR | S36/11/M2/MW |  |  |  | CDC | 151 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C5 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S36/11/M2/MVAR |  |  |  | CDC | 152 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S36/11/M2/I_R |  |  |  | CDC | 153 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S36/11/M2/I_S |  |  |  | CDC | 154 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S36/11/M2/I_T |  |  |  | CDC | 155 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-C2 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_OIL | #2MTR 油溫 | DTR | S36//2MTR/OilTemp |  |  |  | CDC | 156 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BF | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_COIL | #2MTR 線溫 | DTR | S36//2MTR/CoilTemp |  |  |  | CDC | 157 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-C3 |  | 1-5A |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S36//2MTR/TapPosMv |  |  |  | CDC | 158 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-EE | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_MW | #3MTR二次側 MW | DTR | S36/11/M3/MW |  |  |  | CDC | 159 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-EF | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S36/11/M3/MVAR |  |  |  | CDC | 160 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-F0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S36/11/M3/I_R |  |  |  | CDC | 161 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-F1 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S36/11/M3/I_S |  |  |  | CDC | 162 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-F2 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S36/11/M3/I_T |  |  |  | CDC | 163 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-EC | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_OIL | #3MTR 油溫 | DTR | S36//3MTR/OilTemp |  |  |  | CDC | 164 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-EB | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_COIL | #3MTR 線溫 | DTR | S36//3MTR/CoilTemp |  |  |  | CDC | 165 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-ED |  | 1-71 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS2_2 | [8 empty] | 新港SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S36//3MTR/TapPosMv |  |  |  | CDC | 166 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S36 | 新港SS | 0 |  |  |  |  | DCV | [17 empty] | 1-84 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS2_2 | [8 empty] | 新港SS.直流電源電壓 | 直流電源電壓 | OTHER | S36/0/StaDev/DCV |  |  |  | CDC | 167 | GENERICAIPoint | SS217_L1 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 新港SS.610_PHA | 新港嘉太一路(610) 相間RY | LINE69 | S36/69/610/PHA |  |  |  | CDC | 168 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 新港SS.610_GDA | 新港嘉太一路(610) 接地RY | LINE69 | S36/69/610/GDA |  |  |  | CDC | 169 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 新港SS.610_CB | 610(新港嘉太一路) CB | LINE69 | S36/69/610/CB |  |  |  | CDC | 170 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | DS1 | 611 | [16 empty] | 1-39-08 | 1-39-09 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 新港SS.611_DS | 611(新港嘉太一路) DS | LINE69 | S36/69/610/DS1 |  |  |  | CDC | 171 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | DS2 | 612 | [16 empty] | 1-39-10 | 1-39-11 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 新港SS.612_DS | 612(新港嘉太一路) DS | LINE69 | S36/69/610/DS2 |  |  |  | CDC | 172 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | DS3 | 613 | [16 empty] | 1-39-12 | 1-39-13 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 新港SS.613_DS | 613(新港嘉太一路) DS | LINE69 | S36/69/610/DS3 |  |  |  | CDC | 173 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | E3 | 613E | [16 empty] | 1-39-14 | 1-39-15 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 新港SS.613E_ES | 613E(新港嘉太一路) ES | LINE69 | S36/69/610/ES3 |  |  |  | CDC | 174 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 新港SS.620_PHA | 新港嘉太二路(620) 相間RY | LINE69 | S36/69/620/PHA |  |  |  | CDC | 175 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 新港SS.620_GDA | 新港嘉太二路(620) 接地RY | LINE69 | S36/69/620/GDA |  |  |  | CDC | 176 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 新港SS.620_CB | 620(新港嘉太二路) CB | LINE69 | S36/69/620/CB |  |  |  | CDC | 177 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | DS1 | 621 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 新港SS.621_DS | 621(新港嘉太二路) DS | LINE69 | S36/69/620/DS1 |  |  |  | CDC | 178 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | DS2 | 622 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 新港SS.622_DS | 622(新港嘉太二路) DS | LINE69 | S36/69/620/DS2 |  |  |  | CDC | 179 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | DS3 | 623 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 新港SS.623_DS | 623(新港嘉太二路) DS | LINE69 | S36/69/620/DS3 |  |  |  | CDC | 180 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | E3 | 623E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 新港SS.623E_ES | 623E(新港嘉太二路) ES | LINE69 | S36/69/620/ES3 |  |  |  | CDC | 181 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 新港SS.630_PHA | 北港新港一路(630) 相間RY | LINE69 | S36/69/630/PHA |  |  |  | CDC | 182 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 新港SS.630_GDA | 北港新港一路(630) 接地RY | LINE69 | S36/69/630/GDA |  |  |  | CDC | 183 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 新港SS.630_CB | 630(北港新港一路) CB | LINE69 | S36/69/630/CB |  |  |  | CDC | 184 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | DS1 | 631 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 新港SS.631_DS | 631(北港新港一路) DS | LINE69 | S36/69/630/DS1 |  |  |  | CDC | 185 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | DS2 | 632 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 新港SS.632_DS | 632(北港新港一路) DS | LINE69 | S36/69/630/DS2 |  |  |  | CDC | 186 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | DS3 | 633 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 新港SS.633_DS | 633(北港新港一路) DS | LINE69 | S36/69/630/DS3 |  |  |  | CDC | 187 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | E3 | 633E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 新港SS.633E_ES | 633E(北港新港一路) ES | LINE69 | S36/69/630/ES3 |  |  |  | CDC | 188 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 新港SS.640_PHA | 北港新港二路(640) 相間RY | LINE69 | S36/69/640/PHA |  |  |  | CDC | 189 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 新港SS.640_GDA | 北港新港二路(640) 接地RY | LINE69 | S36/69/640/GDA |  |  |  | CDC | 190 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 新港SS.640_CB | 640(北港新港二路) CB | LINE69 | S36/69/640/CB |  |  |  | CDC | 191 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | DS1 | 641 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 新港SS.641_DS | 641(北港新港二路) DS | LINE69 | S36/69/640/DS1 |  |  |  | CDC | 192 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | DS2 | 642 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 新港SS.642_DS | 642(北港新港二路) DS | LINE69 | S36/69/640/DS2 |  |  |  | CDC | 193 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | DS3 | 643 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 新港SS.643_DS | 643(北港新港二路) DS | LINE69 | S36/69/640/DS3 |  |  |  | CDC | 194 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | E3 | 643E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-22 | [5 empty] | ADCS_N | [8 empty] | 新港SS.643E_ES | 643E(北港新港二路) ES | LINE69 | S36/69/640/ES3 |  |  |  | CDC | 195 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | PHA | [17 empty] | 1-0F-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_PHA | 11KV新七線(JI27) 相間RY | FEEDER | S36/11/JI27/PHA |  |  |  | CDC | 196 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) |  | GDA | [17 empty] | 1-0F-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_GDA | 11KV新七線(JI27) 接地RY | FEEDER | S36/11/JI27/GDA |  |  |  | CDC | 197 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI27 | 新七線(JI27) 79RY |  | 79UL | [17 empty] | 1-34-13 |  | 1-5E | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_79UL | 11KV新七線(JI27) 79RY U/L | FEEDER | S36/11/JI27/79UL |  |  |  | CDC | 198 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI27_LCO | 新七線(JI27) LCO |  | TapPosMv | [17 empty] | 1-36-10 |  | 2-0C | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_LCO_TAP | 11KV新七線(JI27) LCO TAP | FEEDER | S36/11/JI27/IED_ADJ |  |  |  | CDC | 199 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI27 | JI27(11KV新七線) |  | CB | [17 empty] | 1-0F-03 |  | 1-54 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_CB | JI27(11KV新七線) CB | FEEDER | S36/11/JI27/CB |  |  |  | CDC | 200 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_PHA | 11KV新八線(JI28) 相間RY | FEEDER | S36/11/JI28/PHA |  |  |  | CDC | 201 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_GDA | 11KV新八線(JI28) 接地RY | FEEDER | S36/11/JI28/GDA |  |  |  | CDC | 202 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI28 | 新八線(JI28) 79RY |  | 79UL | [17 empty] | 1-34-14 |  | 1-5F | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_79UL | 11KV新八線(JI28) 79RY U/L | FEEDER | S36/11/JI28/79UL |  |  |  | CDC | 203 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI28_LCO | 新八線(JI28) LCO |  | TapPosMv | [17 empty] | 1-36-11 |  | 2-0D | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_LCO_TAP | 11KV新八線(JI28) LCO TAP | FEEDER | S36/11/JI28/IED_ADJ |  |  |  | CDC | 204 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI28 | JI28(11KV新八線) |  | CB | [17 empty] | 1-0F-06 |  | 1-55 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_CB | JI28(11KV新八線) CB | FEEDER | S36/11/JI28/CB |  |  |  | CDC | 205 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_PHA | 11KV新九線(JI29) 相間RY | FEEDER | S36/11/JI29/PHA |  |  |  | CDC | 206 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_GDA | 11KV新九線(JI29) 接地RY | FEEDER | S36/11/JI29/GDA |  |  |  | CDC | 207 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI29 | 新九線(JI29) 79RY |  | 79UL | [17 empty] | 1-34-15 |  | 1-60 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_79UL | 11KV新九線(JI29) 79RY U/L | FEEDER | S36/11/JI29/79UL |  |  |  | CDC | 208 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI29_LCO | 新九線(JI29) LCO |  | TapPosMv | [17 empty] | 1-36-12 |  | 2-0E | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_LCO_TAP | 11KV新九線(JI29) LCO TAP | FEEDER | S36/11/JI29/IED_ADJ |  |  |  | CDC | 209 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI29 | JI29(11KV新九線) |  | CB | [17 empty] | 1-10-01 |  | 1-56 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_CB | JI29(11KV新九線) CB | FEEDER | S36/11/JI29/CB |  |  |  | CDC | 210 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_PHA | 11KV新十線(JI30) 相間RY | FEEDER | S36/11/JI30/PHA |  |  |  | CDC | 211 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_GDA | 11KV新十線(JI30) 接地RY | FEEDER | S36/11/JI30/GDA |  |  |  | CDC | 212 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI30 | 新十線(JI30) 79RY |  | 79UL | [17 empty] | 1-35-00 |  | 1-61 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_79UL | 11KV新十線(JI30) 79RY U/L | FEEDER | S36/11/JI30/79UL |  |  |  | CDC | 213 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI30_LCO | 新十線(JI30) LCO |  | TapPosMv | [17 empty] | 1-36-13 |  | 2-0F | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_LCO_TAP | 11KV新十線(JI30) LCO TAP | FEEDER | S36/11/JI30/IED_ADJ |  |  |  | CDC | 214 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI30 | JI30(11KV新十線) |  | CB | [17 empty] | 1-10-04 |  | 1-57 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_CB | JI30(11KV新十線) CB | FEEDER | S36/11/JI30/CB |  |  |  | CDC | 215 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | PHA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_PHA | 11KV新十一線(JI31) 相間RY | FEEDER | S36/11/JI31/PHA |  |  |  | CDC | 216 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) |  | GDA | [17 empty] | 1-11-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_GDA | 11KV新十一線(JI31) 接地RY | FEEDER | S36/11/JI31/GDA |  |  |  | CDC | 217 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI31 | 新十一線(JI31) 79RY |  | 79UL | [17 empty] | 1-35-01 |  | 1-62 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_79UL | 11KV新十一線(JI31) 79RY U/L | FEEDER | S36/11/JI31/79UL |  |  |  | CDC | 218 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI31_LCO | 新十一線(JI31) LCO |  | TapPosMv | [17 empty] | 1-36-14 |  | 2-10 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_LCO_TAP | 11KV新十一線(JI31) LCO TAP | FEEDER | S36/11/JI31/IED_ADJ |  |  |  | CDC | 219 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI31 | JI31(11KV新十一線) |  | CB | [17 empty] | 1-10-07 |  | 1-58 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_CB | JI31(11KV新十一線) CB | FEEDER | S36/11/JI31/CB |  |  |  | CDC | 220 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | PHA | [17 empty] | 1-11-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_PHA | 11KV新十二線(JI32) 相間RY | FEEDER | S36/11/JI32/PHA |  |  |  | CDC | 221 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) |  | GDA | [17 empty] | 1-11-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_GDA | 11KV新十二線(JI32) 接地RY | FEEDER | S36/11/JI32/GDA |  |  |  | CDC | 222 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI32 | 新十二線(JI32) 79RY |  | 79UL | [17 empty] | 1-35-02 |  | 1-63 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_79UL | 11KV新十二線(JI32) 79RY U/L | FEEDER | S36/11/JI32/79UL |  |  |  | CDC | 223 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI32_LCO | 新十二線(JI32) LCO |  | TapPosMv | [17 empty] | 1-36-15 |  | 2-11 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_LCO_TAP | 11KV新十二線(JI32) LCO TAP | FEEDER | S36/11/JI32/IED_ADJ |  |  |  | CDC | 224 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI32 | JI32(11KV新十二線) |  | CB | [17 empty] | 1-11-02 |  | 1-59 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_CB | JI32(11KV新十二線) CB | FEEDER | S36/11/JI32/CB |  |  |  | CDC | 225 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_PHA | 11KV新十三線(JI33) 相間RY | FEEDER | S36/11/JI33/PHA |  |  |  | CDC | 226 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_GDA | 11KV新十三線(JI33) 接地RY | FEEDER | S36/11/JI33/GDA |  |  |  | CDC | 227 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI33 | 新十三線(JI33) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-75 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_79UL | 11KV新十三線(JI33) 79RY U/L | FEEDER | S36/11/JI33/79UL |  |  |  | CDC | 228 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI33_LCO | 新十三線(JI33) LCO |  | TapPosMv | [17 empty] | 1-37-00 |  | 2-12 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_LCO_TAP | 11KV新十三線(JI33) LCO TAP | FEEDER | S36/11/JI33/IED_ADJ |  |  |  | CDC | 229 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI33 | JI33(11KV新十三線) |  | CB | [17 empty] | 1-12-07 |  | 1-6B | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_CB | JI33(11KV新十三線) CB | FEEDER | S36/11/JI33/CB |  |  |  | CDC | 230 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | PHA | [17 empty] | 1-13-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_PHA | 11KV新十四線(JI34) 相間RY | FEEDER | S36/11/JI34/PHA |  |  |  | CDC | 231 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) |  | GDA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_GDA | 11KV新十四線(JI34) 接地RY | FEEDER | S36/11/JI34/GDA |  |  |  | CDC | 232 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI34 | 新十四線(JI34) 79RY |  | 79UL | [17 empty] | 1-35-12 |  | 1-76 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_79UL | 11KV新十四線(JI34) 79RY U/L | FEEDER | S36/11/JI34/79UL |  |  |  | CDC | 233 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI34_LCO | 新十四線(JI34) LCO |  | TapPosMv | [17 empty] | 1-37-01 |  | 2-13 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_LCO_TAP | 11KV新十四線(JI34) LCO TAP | FEEDER | S36/11/JI34/IED_ADJ |  |  |  | CDC | 234 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI34 | JI34(11KV新十四線) |  | CB | [17 empty] | 1-13-02 |  | 1-6C | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_CB | JI34(11KV新十四線) CB | FEEDER | S36/11/JI34/CB |  |  |  | CDC | 235 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | PHA | [17 empty] | 1-13-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_PHA | 11KV新十五線(JI35) 相間RY | FEEDER | S36/11/JI35/PHA |  |  |  | CDC | 236 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) |  | GDA | [17 empty] | 1-13-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_GDA | 11KV新十五線(JI35) 接地RY | FEEDER | S36/11/JI35/GDA |  |  |  | CDC | 237 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI35 | 新十五線(JI35) 79RY |  | 79UL | [17 empty] | 1-35-13 |  | 1-77 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_79UL | 11KV新十五線(JI35) 79RY U/L | FEEDER | S36/11/JI35/79UL |  |  |  | CDC | 238 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI35_LCO | 新十五線(JI35) LCO |  | TapPosMv | [17 empty] | 1-37-02 |  | 2-14 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_LCO_TAP | 11KV新十五線(JI35) LCO TAP | FEEDER | S36/11/JI35/IED_ADJ |  |  |  | CDC | 239 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI35 | JI35(11KV新十五線) |  | CB | [17 empty] | 1-13-05 |  | 1-6D | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_CB | JI35(11KV新十五線) CB | FEEDER | S36/11/JI35/CB |  |  |  | CDC | 240 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | PHA | [17 empty] | 1-14-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_PHA | 11KV新十六線(JI36) 相間RY | FEEDER | S36/11/JI36/PHA |  |  |  | CDC | 241 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) |  | GDA | [17 empty] | 1-14-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_GDA | 11KV新十六線(JI36) 接地RY | FEEDER | S36/11/JI36/GDA |  |  |  | CDC | 242 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI36 | 新十六線(JI36) 79RY |  | 79UL | [17 empty] | 1-35-14 |  | 1-78 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_79UL | 11KV新十六線(JI36) 79RY U/L | FEEDER | S36/11/JI36/79UL |  |  |  | CDC | 243 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI36_LCO | 新十六線(JI36) LCO |  | TapPosMv | [17 empty] | 1-37-03 |  | 2-15 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_LCO_TAP | 11KV新十六線(JI36) LCO TAP | FEEDER | S36/11/JI36/IED_ADJ |  |  |  | CDC | 244 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI36 | JI36(11KV新十六線) |  | CB | [17 empty] | 1-14-00 |  | 1-6E | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_CB | JI36(11KV新十六線) CB | FEEDER | S36/11/JI36/CB |  |  |  | CDC | 245 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | PHA | [17 empty] | 1-14-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_PHA | 11KV新十七線(JI37) 相間RY | FEEDER | S36/11/JI37/PHA |  |  |  | CDC | 246 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) |  | GDA | [17 empty] | 1-14-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_GDA | 11KV新十七線(JI37) 接地RY | FEEDER | S36/11/JI37/GDA |  |  |  | CDC | 247 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI37 | 新十七線(JI37) 79RY |  | 79UL | [17 empty] | 1-35-15 |  | 1-79 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_79UL | 11KV新十七線(JI37) 79RY U/L | FEEDER | S36/11/JI37/79UL |  |  |  | CDC | 248 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI37_LCO | 新十七線(JI37) LCO |  | TapPosMv | [17 empty] | 1-37-04 |  | 2-16 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_LCO_TAP | 11KV新十七線(JI37) LCO TAP | FEEDER | S36/11/JI37/IED_ADJ |  |  |  | CDC | 249 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI37 | JI37(11KV新十七線) |  | CB | [17 empty] | 1-14-03 |  | 1-6F | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_CB | JI37(11KV新十七線) CB | FEEDER | S36/11/JI37/CB |  |  |  | CDC | 250 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_PHA | 11KV新十八線(JI38) 相間RY | FEEDER | S36/11/JI38/PHA |  |  |  | CDC | 251 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_GDA | 11KV新十八線(JI38) 接地RY | FEEDER | S36/11/JI38/GDA |  |  |  | CDC | 252 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | JI38 | 新十八線(JI38) 79RY |  | 79UL | [17 empty] | 1-36-00 |  | 1-7A | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_79UL | 11KV新十八線(JI38) 79RY U/L | FEEDER | S36/11/JI38/79UL |  |  |  | CDC | 253 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV | JI38_LCO | 新十八線(JI38) LCO |  | TapPosMv | [17 empty] | 1-37-05 |  | 2-17 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_LCO_TAP | 11KV新十八線(JI38) LCO TAP | FEEDER | S36/11/JI38/IED_ADJ |  |  |  | CDC | 254 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S36 | 新港SS | 11 | 11kV | JI38 | JI38(11KV新十八線) |  | CB | [17 empty] | 1-14-06 |  | 1-70 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_CB | JI38(11KV新十八線) CB | FEEDER | S36/11/JI38/CB |  |  |  | CDC | 255 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-04 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 新港SS.600_CB | 600(TIE) CB | TIE | S36/69/600/CB |  |  |  | CDC | 256 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 600 | TIE(600) |  | 51A | [17 empty] | 1-05-05 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600_51A | 69KV TIE(600) 51RY | TIE | S36/69/600/51A |  |  |  | CDC | 257 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 600 | TIE(600) |  | 51NA | [17 empty] | 1-05-06 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600_51NA | 69KV TIE(600) 51N RY | TIE | S36/69/600/51NA |  |  |  | CDC | 258 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3C-06 | 1-3C-07 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 新港SS.601_DS | 601(TIE) DS | TIE | S36/69/600/DS1 |  |  |  | CDC | 259 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 新港SS.602_DS | 602(TIE) DS | TIE | S36/69/600/DS2 |  |  |  | CDC | 260 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-00 |  | 1-52 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.TIE2_CB | 11KV TIE2 CB | TIE | S36/11/TIE2/CB |  |  |  | CDC | 261 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-0F-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.TIE2_51A | 11KV TIE2 51RY | TIE | S36/11/TIE2/51A |  |  |  | CDC | 262 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-0F-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S36/11/TIE2/51NA |  |  |  | CDC | 263 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-12-00 |  | 1-64 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.490_CB | 490(#2SSTR) CB | OTHER | S36/11/490/CB |  |  |  | CDC | 264 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-12-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2SSTR_51A | #2SSTR 51RY | OTHER | S36/11/490/PHA |  |  |  | CDC | 265 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-12-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | S36/11/490/GDA |  |  |  | CDC | 266 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 590 | #3SSTR(590) |  | CB | [17 empty] | 1-15-04 |  | 1-7B | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.590_CB | 590(#3SSTR) CB | OTHER | S36/11/590/CB |  |  |  | CDC | 267 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-15-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3SSTR_51A | #3SSTR 51RY | OTHER | S36/11/590/PHA |  |  |  | CDC | 268 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-15-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | S36/11/590/GDA |  |  |  | CDC | 269 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-02-00 |  | 1-50 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.760_CB | 760(#2MTR) CB | DTR | S36/69/760/CB |  |  |  | CDC | 270 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-02-01 |  | 1-51 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.2M_CB | 2M(#2MTR) CB | DTR | S36/11/M2/CB |  |  |  | CDC | 271 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-02-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_51A | #2MTR 51RY | DTR | S36/69/760/51A |  |  |  | CDC | 272 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-02-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_51NA | #2MTR 51N RY | DTR | S36/69/760/51NA |  |  |  | CDC | 273 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S36//2MTR/51ZA |  |  |  | CDC | 274 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_87A | #2MTR 87RY | DTR | S36//2MTR/87A |  |  |  | CDC | 275 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-10 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S36//2MTR/87UL |  |  |  | CDC | 276 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S36/11/M2/51A |  |  |  | CDC | 277 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_TRA | #2MTR 重故障 | DTR | S36//2MTR/TRA |  |  |  | CDC | 278 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S36//2MTR/TRF |  |  |  | CDC | 279 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-11 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S36//2MTR/SupLocal |  |  |  | CDC | 280 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-12 |  | 1-5B | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S36//2MTR/Tap Chan |  |  |  | CDC | 281 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-38-12 | 1-38-13 | 1-2F | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.761_DS | 761(#2MTR) DS | DTR | S36/69/760/DS1 |  |  |  | CDC | 282 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-38-14 | 1-38-15 | 1-30 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.762_DS | 762(#2MTR) DS | DTR | S36/69/760/DS2 |  |  |  | CDC | 283 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-02-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_96A | #2MTR 96P RY | DTR | S36//2MTR/96PA |  |  |  | CDC | 284 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-09 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S36//2MTR/OLTC_DLY |  |  |  | CDC | 285 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-35-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S36//2MTR/AC_Fault |  |  |  | CDC | 286 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-03-02 |  | 1-67 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.770_CB | 770(#3MTR) CB | DTR | S36/69/770/CB |  |  |  | CDC | 287 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-03-03 |  | 1-68 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.3M_CB | 3M(#3MTR) CB | DTR | S36/11/M3/CB |  |  |  | CDC | 288 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_51A | #3MTR 51RY | DTR | S36/69/770/51A |  |  |  | CDC | 289 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_51NA | #3MTR 51N RY | DTR | S36/69/770/51NA |  |  |  | CDC | 290 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S36//3MTR/51ZA |  |  |  | CDC | 291 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_87A | #3MTR 87RY | DTR | S36//3MTR/87A |  |  |  | CDC | 292 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S36//3MTR/87UL |  |  |  | CDC | 293 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-04-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S36/11/M3/51A |  |  |  | CDC | 294 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_TRA | #3MTR 重故障 | DTR | S36//3MTR/TRA |  |  |  | CDC | 295 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S36//3MTR/TRF |  |  |  | CDC | 296 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-09 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S36//3MTR/SupLocal |  |  |  | CDC | 297 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-10 |  | 1-72 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S36//3MTR/Tap Chan |  |  |  | CDC | 298 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-39-00 | 1-39-01 | 1-31 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.771_DS | 771(#3MTR) DS | DTR | S36/69/770/DS1 |  |  |  | CDC | 299 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-39-02 | 1-39-03 | 1-32 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.772_DS | 772(#3MTR) DS | DTR | S36/69/770/DS2 |  |  |  | CDC | 300 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_96A | #3MTR 96P RY | DTR | S36//3MTR/96PA |  |  |  | CDC | 301 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S36//3MTR/OLTC_DLY |  |  |  | CDC | 302 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-36-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S36//3MTR/AC_Fault |  |  |  | CDC | 303 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | CB | [17 empty] | 1-11-05 |  | 1-53 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.230_CB | 230(11KV #2SC) CB | SC | S36/11/230/CB |  |  |  | CDC | 304 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | SC_A_M | [17 empty] | 1-35-03 |  | 1-5C | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.230_A/M | 11KV #2SC 乏控器 A/M | SC | S36/11/230/Tap Chan |  |  |  | CDC | 305 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | SCA | [17 empty] | 1-11-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.230_SCA | 11KV #2SC 51,51N RY | SC | S36/11/230/SCA |  |  |  | CDC | 306 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | UVA | [17 empty] | 1-11-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.230_UVA | 11KV #2SC 27RY(欠壓) | SC | S36/11/230/UVA |  |  |  | CDC | 307 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230 | #2SC(230) |  | LBS | [17 empty] | 1-3D-00 |  | 1-5D | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.230_LBS | 230(11KV #2SC) LBS | SC | S36/11/230/LBS1 |  |  |  | CDC | 308 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | CB | [17 empty] | 1-15-01 |  | 1-6A | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.240_CB | 240(11KV #3SC) CB | SC | S36/11/240/CB |  |  |  | CDC | 309 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | SC_A_M | [17 empty] | 1-36-01 |  | 1-73 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.240_A/M | 11KV #3SC 乏控器 A/M | SC | S36/11/240/Tap Chan |  |  |  | CDC | 310 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | SCA | [17 empty] | 1-15-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.240_SCA | 11KV #3SC 51,51N RY | SC | S36/11/240/SCA |  |  |  | CDC | 311 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | UVA | [17 empty] | 1-15-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.240_UVA | 11KV #3SC 27RY(欠壓) | SC | S36/11/240/UVA |  |  |  | CDC | 312 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 240 | #3SC(240) |  | LBS | [17 empty] | 1-3D-02 |  | 1-74 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.240_LBS | 240(11KV #3SC) LBS | SC | S36/11/240/LBS1 |  |  |  | CDC | 313 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-05-01 | [7 empty] | 69KV_N | [8 empty] | 新港SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S36/69/1BUS/87A |  |  |  | CDC | 314 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-33-05 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 新港SS.69#1BUS_87UL | 69#1BUS 87RY U/L | OTHER | S36/69/1BUS/87UL |  |  |  | CDC | 315 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 69KV_N | [8 empty] | 新港SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S36/69/2BUS/87A |  |  |  | CDC | 316 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 692BUS | 69#2BUS |  | 87UL | [17 empty] | 1-33-06 |  | 1-0F | [5 empty] | ADCS_N | [8 empty] | 新港SS.69#2BUS_87UL | 69#2BUS 87RY U/L | OTHER | S36/69/2BUS/87UL |  |  |  | CDC | 317 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-14 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S36/11/ComPoint/CBA |  |  |  | CDC | 318 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-13 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S36/11/ComPoint/CBF |  |  |  | CDC | 319 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S36/69/ComPoint/CBA |  |  |  | CDC | 320 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S36/69/ComPoint/CBF |  |  |  | CDC | 321 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.火災警報(1) | [新港]火警 | OTHER | S36/0/StaDev/Fire |  |  |  | CDC | 322 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | OPA | [17 empty] | 1-30-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | S36/0/StaDev/OPA |  |  |  | CDC | 323 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S36/0/StaDev/STUV |  |  |  | CDC | 324 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S36/0/StaDev/CHG1 |  |  |  | CDC | 325 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-12 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.直流電源DCA | 直流電源故障警報 | OTHER | S36/0/StaDev/DCA |  |  |  | CDC | 326 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S36/0/StaDev/DCE |  |  |  | CDC | 327 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-31-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S36/0/StaDev/3A5Other |  |  |  | CDC | 328 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-31-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S36/0/StaDev/4A5Other |  |  |  | CDC | 329 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-31-09 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S36/0/StaDev/5A5Other |  |  |  | CDC | 330 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S36/0/StaDev/CHG2 |  |  |  | CDC | 331 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S36/0/StaDev/Burglar1 |  |  |  | CDC | 332 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S36/0/StaDev/Burglar2 |  |  |  | CDC | 333 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化門禁(1) | 保全(DOOR) | OTHER | S36/0/StaDev/Door1 |  |  |  | CDC | 334 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化門禁(2) | 無人化門禁(2) | OTHER | S36/0/StaDev/Door2 |  |  |  | CDC | 335 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-04 |  | 1-33 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.開關場照明(A) | 所內開關場照明 | OTHER | S36/0/StaDev/Lights1 |  |  |  | CDC | 336 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S36 | 新港SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-05 |  | 1-34 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.開關場照明(B) | 路燈照明 | OTHER | S36/0/StaDev/Lights2 |  |  |  | CDC | 337 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S36 | 新港SS | 0 |  | 2MAIN | #2MAIN |  | 51NA | [17 empty] | 1-02-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MAIN_51NA | #2MAIN 51NA | OTHER | S36/11/M2/51NA |  |  |  | CDC | 338 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | 2M |  | #2MTR63Q | [17 empty] | 1-38-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR63Q | 2M ULTC電驛動作 | OTHER | S36//2MTR/63Q |  |  |  | CDC | 339 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | 2M |  | #2MTR96B1 | [17 empty] | 1-37-12 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR96B1 | 2M 撲氣電驛警報 | OTHER | S36//2MTR/96B1 |  |  |  | CDC | 340 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | 2M |  | #2MTR96B2 | [17 empty] | 1-37-13 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR96B2 | 2M 撲氣電驛動作 | OTHER | S36//2MTR/96B2 |  |  |  | CDC | 341 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | 2M |  | #2MTR96D | [17 empty] | 1-37-14 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR96D | 2M 放壓電驛動作 | OTHER | S36//2MTR/96D |  |  |  | CDC | 342 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | 2M |  | #2MTR96P | [17 empty] | 1-37-15 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR96P | 2M 突壓電驛動作 | OTHER | S36//2MTR/96P |  |  |  | CDC | 343 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2M | #2M |  | 三相51A | [17 empty] | 1-03-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#2M_三相51A | #2M 三相51A | OTHER | S36/11/M2/3P51A |  |  |  | CDC | 344 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3MAIN | #3MAIN |  | 51NA | [17 empty] | 1-04-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MAIN_51NA | #3MAIN 51NA | OTHER | S36/11/M3/51NA |  |  |  | CDC | 345 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | 3M |  | #3MTR63Q | [17 empty] | 1-38-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR63Q | 3M ULTC電驛動作 | OTHER | S36//3MTR/63Q |  |  |  | CDC | 346 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | 3M |  | #3MTR96B1 | [17 empty] | 1-38-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR96B1 | 3M 撲氣電驛警報 | OTHER | S36//3MTR/96B1 |  |  |  | CDC | 347 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | 3M |  | #3MTR96B2 | [17 empty] | 1-38-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR96B2 | 3M 撲氣電驛動作 | OTHER | S36//3MTR/96B2 |  |  |  | CDC | 348 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | 3M |  | #3MTR96D | [17 empty] | 1-38-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR96D | 3M 放壓電驛動作 | OTHER | S36//3MTR/96D |  |  |  | CDC | 349 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | 3M |  | #3MTR96P | [17 empty] | 1-38-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR96P | 3M 突壓電驛動作 | OTHER | S36//3MTR/96P |  |  |  | CDC | 350 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 3M | #3M |  | 三相51A | [17 empty] | 1-04-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.#3M_三相51A | #3M 三相51A | OTHER | S36/11/M3/3P51A |  |  |  | CDC | 351 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | _SC | SC |  | 60A | [17 empty] | 1-32-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.11KV_SC_60A | 11KV SC 60RY | OTHER | S36/11/ComPoint/FDR_60A |  |  |  | CDC | 352 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | TIE | TIE |  | 600GDA(1) | [17 empty] | 1-04-06 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600GDA(1) | 600(TIE) 67NA(B1) | OTHER | S36/69/600/GDA1 |  |  |  | CDC | 353 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | TIE | TIE |  | 600GDA(2) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600GDA(2) | 600(TIE) 67NA(B2) | OTHER | S36/69/600/GDA2 |  |  |  | CDC | 354 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | TIE | TIE |  | 600PHA(1) | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600PHA(1) | 600(TIE) 67A(B1) | OTHER | S36/69/600/PHA1 |  |  |  | CDC | 355 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 0 |  | TIE | TIE |  | 600PHA(2) | [17 empty] | 1-04-07 | [7 empty] | 69KV_N | [8 empty] | 新港SS.600PHA(2) | 600(TIE) 67A(B2) | OTHER | S36/69/600/PHA2 |  |  |  | CDC | 356 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | BUS | BUS |  | 59A | [17 empty] | 1-0B-00 | [7 empty] | 69KV_N | [8 empty] | 新港SS.69KV_59A | 69KV BUS 59A過壓警報 | OTHER | S36/69/ComPoint/59A |  |  |  | CDC | 357 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 79RY | 79RY |  | LOA | [17 empty] | 1-32-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.79RY_LOA | 79RY LOA | OTHER | S36/0/StaDev/LOA |  |  |  | CDC | 358 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | TRIP監視 | [17 empty] | 1-32-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.TRIP監視 | TRIP監視 | OTHER | S36/0/StaDev/1A5Other |  |  |  | CDC | 359 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-30-13 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.水位警報(1) | 洩油池水位警報(1) | OTHER | S36/0/StaDev/Water1 |  |  |  | CDC | 360 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-30-14 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.水位警報(2) | 洩油池水位警報(2) | OTHER | S36/0/StaDev/Water2 |  |  |  | CDC | 361 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Water1 | [17 empty] | 1-30-15 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.地下室淹水(1) | 地下室淹水(1) | OTHER | S36/0/StaDev/Water4 |  |  |  | CDC | 362 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Water2 | [17 empty] | 1-31-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.地下室淹水(2) | 地下室淹水(2) | OTHER | S36/0/StaDev/Water5 |  |  |  | CDC | 363 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-09 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.安全監控 | 安全監控 | OTHER | S36/0/StaDev/Burglar |  |  |  | CDC | 364 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-11 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內其他重故障 | 所內其他重故障 | OTHER | S36/0/StaDev/PSA |  |  |  | CDC | 365 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-10 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內其他輕故障 | 所內其他輕故障 | OTHER | S36/0/StaDev/PSF |  |  |  | CDC | 366 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-03 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.門禁 | 大門側門 | OTHER | S36/0/StaDev/Door |  |  |  | CDC | 367 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  |  |  |  | 通訊電源故障 | [17 empty] | 1-31-10 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊電源故障 | 通訊電源故障 | OTHER | S36/0/StaDev/Comm_A |  |  |  | CDC | 368 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 無人化防火(1) | [17 empty] | 1-31-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化防火(1) | CO2故障 | OTHER | S36/0/StaDev/Fire1 |  |  |  | CDC | 369 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 無人化防火(2) | [17 empty] | 1-31-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.無人化防火(2) | CO2火警 | OTHER | S36/0/StaDev/Fire2 |  |  |  | CDC | 370 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-05 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S36/0/StaDev/ACB1 |  |  |  | CDC | 371 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S36 | 新港SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S36/0/StaDev/ACB2 |  |  |  | CDC | 372 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S36 | 新港SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-32-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內電源ACBA | 所內電源故障警報 | OTHER | S36/0/StaDev/ACBA |  |  |  | CDC | 373 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 現場設備斷訊 | [17 empty] | 1-33-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.現場設備斷訊 | 現場設備斷訊 | OTHER | S36/0/StaDev/8A5Other |  |  |  | CDC | 374 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-33-03 |  | 1-00 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.TEST_CB | TEST CB | OTHER | S36/0/RTU/Test_CB |  |  |  | CDC | 375 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  |  |  |  | 維護運轉警報 | [17 empty] | 1-32-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.維護運轉警報 | 維護運轉警報 | OTHER | S36/0/StaDev/2A5Other |  |  |  | CDC | 376 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | ACB3 | [17 empty] | 1-32-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.所內電源ACB3 | 所內電源ACB3 | OTHER | S36/0/StaDev/ACB3 |  |  |  | CDC | 377 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S36 | 新港SS | 22 | 22kV | 11_ CBA | 11/ CBA(11_ CBA) |  | IED警報 | [17 empty] | 1-3D-11 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.IED警報 | 11/23KV CBA 重故障(IED故障) | OTHER | S36/0/StaDev/IRFA |  |  |  | CDC | 378 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-12-03 |  | 1-7E | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S36/11/M2/81A |  |  |  | CDC | 379 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S36 | 新港SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-15-07 |  | 1-7F | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S36/11/M3/81A |  |  |  | CDC | 380 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S36 | 新港SS | 0 |  |  |  |  | 路燈電源監視 | [17 empty] | 1-37-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.路燈電源監視 | 路燈操作線電源監視 | OTHER | S36/0/StaDev/6A5Other |  |  |  | CDC | 381 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 通訊室溫度異常 | [17 empty] | 1-38-06 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.通訊室溫度異常 | 通訊室溫度異常 | OTHER | S36/0/StaDev/7A5Other |  |  |  | CDC | 382 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 新港SS.630_87A | 北港新港一路(630) 87RY | LINE69 | S36/69/630/87A |  |  |  | CDC | 383 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | CFA | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 新港SS.630_CFA | 北港新港一路(630) 630_通訊故障 | LINE69 | S36/69/630/74A |  |  |  | CDC | 384 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | 87UL | [17 empty] | 1-32-13 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 新港SS.630_87UL | 北港新港一路(630) 87RY U/L | LINE69 | S36/69/630/87UL |  |  |  | CDC | 385 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 新港SS.640_87A | 北港新港二路(640) 87RY | LINE69 | S36/69/640/87A |  |  |  | CDC | 386 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | CFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 新港SS.640_CFA | 北港新港二路(640) 640_通訊故障 | LINE69 | S36/69/640/74A |  |  |  | CDC | 387 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | 87UL | [17 empty] | 1-32-15 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 新港SS.640_87UL | 北港新港二路(640) 87RY U/L | LINE69 | S36/69/640/87UL |  |  |  | CDC | 388 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 0 |  | 630 | 北港新港一路(630) |  | RYFA | [17 empty] | 1-06-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.630_RYFA | 630 IED警報 | OTHER | S36/69/630/RYFA |  |  |  | CDC | 389 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 640 | 北港新港二路(640) |  | RYFA | [17 empty] | 1-06-02 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.640_RYFA | 640 IED警報 | OTHER | S36/69/640/RYFA |  |  |  | CDC | 390 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  |  |  |  | 69-BM-RESET | [17 empty] | 1-06-03 |  | 2-00 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.69-BM-RESET | 69-BM-RESET | OTHER | S36/69/ComPoint/1A5Other |  |  |  | CDC | 391 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | OFF/ON | ON
S36 | 新港SS | 0 |  |  |  |  | 11-BM-RESET | [17 empty] | 1-06-04 |  | 2-01 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.11-BM-RESET | 11-BM-RESET | OTHER | S36/11/ComPoint/1A5Other |  |  |  | CDC | 392 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | OFF/ON | ON
S36 | 新港SS | 0 |  |  |  |  | CLR-BM-RESET | [17 empty] | 1-06-05 |  | 2-02 | [5 empty] | DDCS2_2 | [8 empty] | 新港SS.CLR-BM-RESET | CLR-BM-RESET | OTHER |  |  |  |  | CDC | 393 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | OFF/ON | ON
S36 | 新港SS | 0 |  |  |  |  | 開關場水位警報 | [17 empty] | 1-33-04 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.開關場水位警報 | 開關場水位警報 | OTHER | S36/0/StaDev/Water3 |  |  |  | CDC | 394 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 新港SS.610_87A | 新港嘉太一路(610) 87RY | LINE69 | S36/69/610/87A |  |  |  | CDC | 395 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | CFA | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 新港SS.610_CFA | 新港嘉太一路(610) 610_通訊故障 | LINE69 | S36/69/610/74A |  |  |  | CDC | 396 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | 87UL | [17 empty] | 1-32-09 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 新港SS.610_87UL | 新港嘉太一路(610) 87RY U/L | LINE69 | S36/69/610/87UL |  |  |  | CDC | 397 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 新港SS.620_87A | 新港嘉太二路(620) 87RY | LINE69 | S36/69/620/87A |  |  |  | CDC | 398 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | CFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 新港SS.620_CFA | 新港嘉太二路(620) 620_通訊故障 | LINE69 | S36/69/620/74A |  |  |  | CDC | 399 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | 87UL | [17 empty] | 1-32-11 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 新港SS.620_87UL | 新港嘉太二路(620) 87RY U/L | LINE69 | S36/69/620/87UL |  |  |  | CDC | 400 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S36 | 新港SS | 0 |  | 610 | 新港嘉太一路(610) |  | RYFA | [17 empty] | 1-3C-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.610_RYFA | 610 IED警報 | OTHER | S36/69/610/RYFA |  |  |  | CDC | 401 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 620 | 新港嘉太二路(620) |  | RYFA | [17 empty] | 1-3C-01 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.620_RYFA | 620 IED警報 | OTHER | S36/69/620/RYFA |  |  |  | CDC | 402 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-05-07 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.600_RYFA | 600 IED警報 | OTHER | S36/69/600/RYFA |  |  |  | CDC | 403 | GENERICDIPoint | SS217_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 691BUS | 69#1BUS |  | 27BA | [17 empty] | 1-31-15 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.69#1BUS_27BA | 69#1BUS 27BA | OTHER | S36/69/1BUS/BUS_VUA |  |  |  | CDC | 404 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | 692BUS | 69#2BUS |  | 27BA | [17 empty] | 1-32-00 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.69#2BUS_27BA | 69#2BUS 27BA | OTHER | S36/69/2BUS/BUS_VUA |  |  |  | CDC | 405 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | BUSRY | BUSRY |  | BF | [17 empty] | 1-33-08 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.BUSRY_BF | BUSRY BF | OTHER | S36/69/ComPoint/BFA |  |  |  | CDC | 406 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 0 |  | BUSRY | BUSRY |  | 87CTFA | [17 empty] | 1-33-09 | [7 empty] | DDCS2_2 | [8 empty] | 新港SS.BUSRY_CTFA | BUSRY CTFA | OTHER | S36/69/ComPoint/87CTFA |  |  |  | CDC | 407 | GENERICDIPoint | SS217_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S36 | 新港SS | 11 | 11kV | 230_SC | #2SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.230_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 408 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 11 | 11kV | 240_SC | #3SC | 6 | CAP | [25 empty] | DDCS2_2 | [8 empty] | 新港SS.240_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 409 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 新港SS.610LE | 610LE (非取樣點) | LINE69 | S36/69/610/LE0 |  |  |  |  | 410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 610 | 新港嘉太一路(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 新港SS.610BE | 610BE (非取樣點) | LINE69 | S36/69/610/BE0 |  |  |  |  | 411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 新港SS.620LE | 620LE (非取樣點) | LINE69 | S36/69/620/LE0 |  |  |  |  | 412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 620 | 新港嘉太二路(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 新港SS.620BE | 620BE (非取樣點) | LINE69 | S36/69/620/BE0 |  |  |  |  | 413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 新港SS.630LE | 630LE (非取樣點) | LINE69 | S36/69/630/LE0 |  |  |  |  | 414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 630 | 北港新港一路(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 新港SS.630BE | 630BE (非取樣點) | LINE69 | S36/69/630/BE0 |  |  |  |  | 415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 新港SS.640LE | 640LE (非取樣點) | LINE69 | S36/69/640/LE0 |  |  |  |  | 416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 640 | 北港新港二路(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 新港SS.640BE | 640BE (非取樣點) | LINE69 | S36/69/640/BE0 |  |  |  |  | 417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI27 | JI27_DS |  | DS1 | JI27_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_DS | JI27_DS (非取樣點) | FEEDER | S36/11/JI27/DS |  |  |  |  | 418 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI27 | JI27_ES |  | LE0 | JI27_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI27_ES | JI27_ES (非取樣點) | FEEDER | S36/11/JI27/ES |  |  |  |  | 419 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI28 | JI28_DS |  | DS1 | JI28_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_DS | JI28_DS (非取樣點) | FEEDER | S36/11/JI28/DS |  |  |  |  | 420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI28 | JI28_ES |  | LE0 | JI28_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI28_ES | JI28_ES (非取樣點) | FEEDER | S36/11/JI28/ES |  |  |  |  | 421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI29 | JI29_DS |  | DS1 | JI29_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_DS | JI29_DS (非取樣點) | FEEDER | S36/11/JI29/DS |  |  |  |  | 422 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI29 | JI29_ES |  | LE0 | JI29_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI29_ES | JI29_ES (非取樣點) | FEEDER | S36/11/JI29/ES |  |  |  |  | 423 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI30 | JI30_DS |  | DS1 | JI30_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_DS | JI30_DS (非取樣點) | FEEDER | S36/11/JI30/DS |  |  |  |  | 424 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI30 | JI30_ES |  | LE0 | JI30_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI30_ES | JI30_ES (非取樣點) | FEEDER | S36/11/JI30/ES |  |  |  |  | 425 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI31 | JI31_DS |  | DS1 | JI31_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_DS | JI31_DS (非取樣點) | FEEDER | S36/11/JI31/DS |  |  |  |  | 426 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI31 | JI31_ES |  | LE0 | JI31_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI31_ES | JI31_ES (非取樣點) | FEEDER | S36/11/JI31/ES |  |  |  |  | 427 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI32 | JI32_DS |  | DS1 | JI32_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_DS | JI32_DS (非取樣點) | FEEDER | S36/11/JI32/DS |  |  |  |  | 428 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI32 | JI32_ES |  | LE0 | JI32_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI32_ES | JI32_ES (非取樣點) | FEEDER | S36/11/JI32/ES |  |  |  |  | 429 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI33 | JI33_DS |  | DS1 | JI33_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_DS | JI33_DS (非取樣點) | FEEDER | S36/11/JI33/DS |  |  |  |  | 430 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI33 | JI33_ES |  | LE0 | JI33_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI33_ES | JI33_ES (非取樣點) | FEEDER | S36/11/JI33/ES |  |  |  |  | 431 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI34 | JI34_DS |  | DS1 | JI34_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_DS | JI34_DS (非取樣點) | FEEDER | S36/11/JI34/DS |  |  |  |  | 432 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI34 | JI34_ES |  | LE0 | JI34_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI34_ES | JI34_ES (非取樣點) | FEEDER | S36/11/JI34/ES |  |  |  |  | 433 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI35 | JI35_DS |  | DS1 | JI35_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_DS | JI35_DS (非取樣點) | FEEDER | S36/11/JI35/DS |  |  |  |  | 434 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI35 | JI35_ES |  | LE0 | JI35_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI35_ES | JI35_ES (非取樣點) | FEEDER | S36/11/JI35/ES |  |  |  |  | 435 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI36 | JI36_DS |  | DS1 | JI36_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_DS | JI36_DS (非取樣點) | FEEDER | S36/11/JI36/DS |  |  |  |  | 436 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI36 | JI36_ES |  | LE0 | JI36_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI36_ES | JI36_ES (非取樣點) | FEEDER | S36/11/JI36/ES |  |  |  |  | 437 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI37 | JI37_DS |  | DS1 | JI37_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_DS | JI37_DS (非取樣點) | FEEDER | S36/11/JI37/DS |  |  |  |  | 438 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI37 | JI37_ES |  | LE0 | JI37_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI37_ES | JI37_ES (非取樣點) | FEEDER | S36/11/JI37/ES |  |  |  |  | 439 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | JI38 | JI38_DS |  | DS1 | JI38_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_DS | JI38_DS (非取樣點) | FEEDER | S36/11/JI38/DS |  |  |  |  | 440 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | JI38 | JI38_ES |  | LE0 | JI38_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.JI38_ES | JI38_ES (非取樣點) | FEEDER | S36/11/JI38/ES |  |  |  |  | 441 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 新港SS.601E | 601E (非取樣點) | TIE | S36/69/600/E1 |  |  |  |  | 442 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 新港SS.602E | 602E (非取樣點) | TIE | S36/69/600/E2 |  |  |  |  | 443 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S36/11/TIE2/DS |  |  |  |  | 444 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | TIE2 | TIE2_ES |  | LE0 | TIE2_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.TIE2_ES | TIE2_ES (非取樣點) | TIE | S36/11/TIE2/ES |  |  |  |  | 445 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.491 | 491 (非取樣點) | OTHER | S36/11/490/DS |  |  |  |  | 446 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.491E | 491E (非取樣點) | OTHER | S36/11/490/ES |  |  |  |  | 447 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 591 | 591 |  | 591 | 591 | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.591 | 591 (非取樣點) | OTHER | S36/11/590/DS |  |  |  |  | 448 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 591E | 591E |  | 591E | 591E | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.591E | 591E (非取樣點) | OTHER | S36/11/590/ES |  |  |  |  | 449 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.760TE | 760TE (非取樣點) | DTR | S36/69/760/TE0 |  |  |  |  | 450 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.760BE | 760BE (非取樣點) | DTR | S36/69/760/BE0 |  |  |  |  | 451 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.2M_DS | 2M_DS (非取樣點) | DTR | S36/11/M2/DS |  |  |  |  | 452 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.2M_ES | 2M_ES (非取樣點) | DTR | S36/11/M2/ES |  |  |  |  | 453 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.770TE | 770TE (非取樣點) | DTR | S36/69/770/TE0 |  |  |  |  | 454 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.770BE | 770BE (非取樣點) | DTR | S36/69/770/BE0 |  |  |  |  | 455 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.3M_DS | 3M_DS (非取樣點) | DTR | S36/11/M3/DS |  |  |  |  | 456 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.3M_ES | 3M_ES (非取樣點) | DTR | S36/11/M3/ES |  |  |  |  | 457 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 230 | #2SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.230_ES | 230_ES (非取樣點) | SC | S36/11/230/ES |  |  |  |  | 458 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 231DS | 231DS |  | 231DS | 231DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.231DS | 231DS (非取樣點) | SC | S36/11/230/DS |  |  |  |  | 459 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 240 | #3SC(240) |  | LE0 | 240_ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.240_ES | 240_ES (非取樣點) | SC | S36/11/240/ES |  |  |  |  | 460 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 241DS | 241DS |  | 241DS | 241DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.241DS | 241DS (非取樣點) | SC | S36/11/240/DS |  |  |  |  | 461 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S36 | 新港SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 新港SS.69B1E | 69B1E (非取樣點) | BUS | S36/69/1BUS/BE1 |  |  |  |  | 462 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 新港SS.69B2E | 69B2E (非取樣點) | BUS | S36/69/2BUS/BE2 |  |  |  |  | 463 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 464 | NotelDIPoint | [38 empty] | START/STOP | STOP
S36 | 新港SS | 0 |  | BR3DS | BR3DS |  | BR3DS | BR3DS | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.BR3DS | BR3DS (非取樣點) | TIE | S36/11/BR3/D2 |  |  |  |  | 465 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S36 | 新港SS | 0 |  | BR3ES | BR3ES |  | LE0 | BR3ES | [24 empty] | DDCS2_2 | [8 empty] | 新港SS.BR3ES | BR3ES (非取樣點) | TIE | S36/11/BR3/E2 |  |  |  |  | 466 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo