## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S40 | 官田SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KVBUS | KV | 69KVBUS PT | kV_-90_90(-2000_2000) | aaa | B2/S40_A1 | [8 empty] | 官田SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S40 | 官田SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV #1 BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S40_D1 | [8 empty] | 官田SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2 MCB(A) BUS | KV | 二號 BUS (A)PT | kV_-9_9(-2000_2000) | aba | B2/S40_D1 | [8 empty] | 官田SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | 11KV #3 BUS | KV | 三號 BUS PT | kV_-9_9(-2000_2000) | ada | B2/S40_D1 | [8 empty] | 官田SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S40_A1 | [8 empty] | 官田SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA | 衡相監視 |  |  | B2/S40_A1 | [8 empty] | 官田SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 620 | MW | 官田台汽官大統益線 | MW_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.620_MW | 官田台汽官線 MW | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 620 | MVAR | 官田台汽官大統益線 | MVAR_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.620_MVAR | 官田台汽官線 MVAR | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 620 | MWH(+) | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 10 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 630 | MW | 官田隆田一路 | MW_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.630_MW | 官田隆田一路 MW | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 630 | MVAR | 官田隆田一路 | MVAR_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.630_MVAR | 官田隆田一路 MVAR | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 630 | MWH(+) | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 13 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 660 | MW | 新營官田二路 | MW_-144_144(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.660_MW | 新營二路 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 660 | MVAR | 新營官田二路 | MVAR_-144_144(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.660_MVAR | 新營二路 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 660 | MWH(+) | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 610 | MW | 69KV備一線 | MW_-144_144(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.610_MW | 備用線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 610 | MVAR | 69KV備一線 | MVAR_-144_144(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.610_MVAR | 備用線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 610 | MWH(+) | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 640 | MW | 官田隆田二路 | MW_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.640_MW | 官田隆田二路 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 640 | MVAR | 官田隆田二路 | MVAR_-120_120(-2000_2000) |  | B2/S40_A1 | [8 empty] | 官田SS.640_MVAR | 官田隆田二路 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 620 | PHA | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_PHA | 官田台汽官線(620) 相間RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 620 | GDA | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_GDA | 官田台汽官線(620) 接地RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 620 | 87A | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_85A | 官田台汽官線(620) 85RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | Locate Empty |  |  |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_74A | 官田台汽官線(620) 74RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 630 | PHA | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_PHA | 官田隆田一路(630) 相間RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 630 | GDA | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_GDA | 官田隆田一路(630) 接地RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 630 | 87A | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_87A | 官隆ㄧ路(630) 87RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | 74A |  | DEL | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | Locate Empty |  |  |  |  | B2/S40_A1 | [15 empty] | CDC | 29 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 660 | PHA | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_PHA | 新營二路(660) 相間RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 660 | GDA | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_GDA | 新營二路(660) 接地RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 660 | 87A | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_87A | 新營二路(660) 87RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 74A |  | DEL | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | Locate Empty |  |  |  |  | B2/S40_A1 | [15 empty] | CDC | 33 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 610 | PHA | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.610_PHA | 備用線(610) 相間RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 610 | GDA | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.610_GDA | 備用線(610) 接地RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 610 | 85A | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.610_85A | 備用線(610) 85RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 610 | 74 A | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.610_74A | 備用線(610) 74RY | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 640 | PHA | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_PHA | 官田隆田二路(640) 相間RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 640 | GDA | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_GDA | 官田隆田二路(640) 接地RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 640 | 87A | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_87A | 官隆二路(640) 87RY | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | 74A | 已無此點(需DEL) | DEL | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 1-32-09 |  |  | Locate Empty |  |  |  |  | B2/S40_A1 | [15 empty] | CDC | 41 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 620 | 87 U/L | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_85UL | 官田台汽官線(620) 85RY U/L | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 630 | 87 U/L | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_87UL | 官隆ㄧ路(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 660 | 87 U/L | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_87UL | 新營二路(660) 87RY U/L | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 610 | 85 U/L | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.610_85UL | 備用線(610) 85RY U/L | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0013 | 1-32-08 |  | 1-0D | 640 | 87U/L | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_87UL | 官隆二路(640) 87RY U/L | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 620 | CB ON/OFF | 官田台汽官大統益線 |  | aaca | B2/S40_A1 | [8 empty] | 官田SS.620_CB | 620(官田台汽官線) CB | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0000 |  | 0017 | 1-00-00 |  | 1-11 | 620 81RY | 81A | 620大統益 低頻率電驛 |  |  | B2/S40_A1 | [8 empty] | 官田SS.620_81A/S | (620) 81RY A/S | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 630 | CB ON/OFF | 官田隆田一路 |  | aafa | B2/S40_A1 | [8 empty] | 官田SS.630_CB | 630(官田隆田一路) CB | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 660 | CB ON/OFF | 新營官田二路 |  | aaha | B2/S40_A1 | [8 empty] | 官田SS.660_CB | 660(新營二路) CB | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 610 | CB ON/OFF | 69KV備一線 |  | aada | B2/S40_A1 | [8 empty] | 官田SS.610_CB | 610(備用線) CB | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0080 |  | 0005 | 1-0A-00 |  | 1-05 | 640 | CB ON/OFF | 官田隆田二路 |  | aaea | B2/S40_A1 | [8 empty] | 官田SS.640_CB | 640(官田隆田二路) CB | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | DS1 | 621 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0018 | 1-38-08 | 1-38-09 | 1-12 | 621 | ABS ON | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.621_ABS | 621(官田台汽官線) ABS | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | DS2 | 622 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0019 | 1-38-10 | 1-38-11 | 1-13 | 622 | ABS ON | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.622_ABS | 622(官田台汽官線) ABS | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | DS1 | 631 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0021 | 1-38-14 | 1-38-15 | 1-15 | 631 | ABS ON | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.631_ABS | 631(官田隆田一路) ABS | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | DS2 | 632 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0022 | 1-39-00 | 1-39-01 | 1-16 | 632 | ABS ON | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.632_ABS | 632(官田隆田一路) ABS | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | DS1 | 661 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0024 | 1-39-04 | 1-39-05 | 1-18 | 661 | ABS ON | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.661_ABS | 661(新營二路) ABS | LINE69 |  |  |  |  | CDC | 57 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | DS2 | 662 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0025 | 1-39-06 | 1-39-07 | 1-19 | 662 | ABS ON | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.662_ABS | 662(新營二路) ABS | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | DS1 | 611 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0027 | 1-39-10 | 1-39-11 | 1-1B | 611 | ABS ON | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.611_ABS | 611(備用線) ABS | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | DS2 | 612 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0028 | 1-39-12 | 1-39-13 | 1-1C | 612 | ABS ON | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.612_ABS | 612(備用線) ABS | LINE69 |  |  |  |  | CDC | 60 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | DS1 | 641 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0416 | 417 | 0030 | 1-3A-00 | 1-3A-01 | 1-1E | 641 | ABS ON | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.641_ABS | 641(官田隆田二路) ABS | LINE69 |  |  |  |  | CDC | 61 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | DS2 | 642 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0418 | 419 | 0031 | 1-3A-02 | 1-3A-03 | 1-1F | 642 | ABS ON | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.642_ABS | 642(官田隆田二路) ABS | LINE69 |  |  |  |  | CDC | 62 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0396 | 397 | 0020 | 1-38-12 | 1-38-13 | 1-14 | 622E | ABS ON | 官田台汽官大統益線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.622E_ES | 622E(官田台汽官線) ES | LINE69 |  |  |  |  | CDC | 63 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | BE0 | 620BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 64 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0402 | 403 | 0023 | 1-39-02 | 1-39-03 | 1-17 | 632E | ABS ON | 官田隆田一路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.632E_ES | 632E(官田隆田一路) ES | LINE69 |  |  |  |  | CDC | 65 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | BE0 | 630BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 66 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | ES2 | 662E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0408 | 409 | 0026 | 1-39-08 | 1-39-09 | 1-1A | 662E | ABS ON | 新營官田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.662E_ES | 662E(新營二路) ES | LINE69 |  |  |  |  | CDC | 67 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | BE0 | 660BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 68 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0029 | 1-39-14 | 1-39-15 | 1-1D | 612E | ABS ON | 69KV備一線 |  |  | B2/S40_A1 | [8 empty] | 官田SS.612E_ES | 612E(備用線) ES | LINE69 |  |  |  |  | CDC | 69 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | BE0 | 610BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 70 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | ES2 | 642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0420 | 421 | 0032 | 1-3A-04 | 1-3A-05 | 1-20 | 642E | ABS ON | 官田隆田二路 |  |  | B2/S40_A1 | [8 empty] | 官田SS.642E_ES | 642E(官田隆田二路) ES | LINE69 |  |  |  |  | CDC | 71 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | BE0 | 640BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 72 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F1 PH RY | PHA | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_PHA | 11KV官一線(VG21) 相間RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F1 GD RY | GDA | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_GDA | 11KV官一線(VG21) 接地RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | F1 CB | 79 U/L | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_79UL | 11KV官一線(VG21) 79RY U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_ADJ | 11KV官一線(VG21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | F2 PH RY | PHA | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_PHA | 11KV官二線(VG22) 相間RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F2 GD RY | GDA | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_GDA | 11KV官二線(VG22) 接地RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | F2 CB | 79 U/L | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_79UL | 11KV官二線(VG22) 79RY U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_ADJ | 11KV官二線(VG22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F3 PH RY | PHA | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_PHA | 11KV官三線(VG23) 相間RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | F3 GD RY | GDA | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_GDA | 11KV官三線(VG23) 接地RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | F3 CB | 79 U/L | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_79UL | 11KV官三線(VG23) 79RY U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_ADJ | 11KV官三線(VG23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | F4 PH RY | PHA | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_PHA | 11KV官正線(VG24) 相間RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | F4 GD RY | GDA | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_GDA | 11KV官正線(VG24) 接地RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | F4 CB | 79 U/L | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_79UL | 11KV官正線(VG24) 79RY U/L | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_ADJ | 11KV官正線(VG24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | F5 PH RY | PHA | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_PHA | 11KV官五線(VG25) 相間RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | F5 GD RY | GDA | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_GDA | 11KV官五線(VG25) 接地RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | F5 CB | 79 U/L | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_79UL | 11KV官五線(VG25) 79RY U/L | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_ADJ | 11KV官五線(VG25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | F6 PH RY | PHA | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_PHA | 11KV官六線(VG26) 相間RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | F6 GD RY | GDA | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_GDA | 11KV官六線(VG26) 接地RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | F6 CB | 79 U/L | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_79UL | 11KV官六線(VG26) 79RY U/L | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | F6 LCO | ADJ(U/L) | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_ADJ | 11KV官六線(VG26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F7 PH RY | PHA | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_PHA | 11KV官七線(VG27) 相間RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F7 GD RY | GDA | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_GDA | 11KV官七線(VG27) 接地RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | F7 CB | 79 U/L | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_79UL | 11KV官七線(VG27) 79RY U/L | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | F7 LCO | ADJ(U/L) | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_ADJ | 11KV官七線(VG27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | F8 PH RY | PHA | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_PHA | 11KV官八線(VG28) 相間RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F8 GD RY | GDA | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_GDA | 11KV官八線(VG28) 接地RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | F8 CB | 79 U/L | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_79UL | 11KV官八線(VG28) 79RY U/L | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | F8 LCO | ADJ(U/L) | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_ADJ | 11KV官八線(VG28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F9 PH RY | PHA | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_PHA | 11KV官九線(VG29) 相間RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | F9 GD RY | GDA | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_GDA | 11KV官九線(VG29) 接地RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | F9 CB | 79 U/L | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_79UL | 11KV官九線(VG29) 79RY U/L | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | F9 LCO | ADJ(U/L) | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_ADJ | 11KV官九線(VG29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F10 PH RY | PHA | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_PHA | 11KV官十線(VG30) 相間RY | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F10 GD RY | GDA | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_GDA | 11KV官十線(VG30) 接地RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | F10 CB | 79 U/L | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_79UL | 11KV官十線(VG30) 79RY U/L | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | F10 LCO | ADJ(U/L) | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_ADJ | 11KV官十線(VG30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | F11 PH RY | PHA | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_PHA | 11KV官忠線(VG31) 相間RY | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | F11 GD RY | GDA | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_GDA | 11KV官忠線(VG31) 接地RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0100 | 1-35-07 |  | 1-64 | F11 CB | 79 U/L | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_79UL | 11KV官忠線(VG31) 79RY U/L | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | F11 LCO | ADJ(U/L) | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_ADJ | 11KV官忠線(VG31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F12 PH RY | PHA | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_PHA | 11KV官孝線(VG32) 相間RY | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F12 GD RY | GDA | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_GDA | 11KV官孝線(VG32) 接地RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0101 | 1-35-08 |  | 1-65 | F12 CB | 79 U/L | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_79UL | 11KV官孝線(VG32) 79RY U/L | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | F12 LCO | ADJ(U/L) | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_ADJ | 11KV官孝線(VG32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | F13 PH RY | PHA | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_PHA | 11KV官仁線(VG33) 相間RY | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F13 GD RY | GDA | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_GDA | 11KV官仁線(VG33) 接地RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0102 | 1-35-09 |  | 1-66 | F13 CB | 79 U/L | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_79UL | 11KV官仁線(VG33) 79RY U/L | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | F13 LCO | ADJ(U/L) | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_ADJ | 11KV官仁線(VG33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F14 PH RY | PHA | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_PHA | 11KV官愛線(VG34) 相間RY | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | F14 GD RY | GDA | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_GDA | 11KV官愛線(VG34) 接地RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0103 | 1-35-10 |  | 1-67 | F14 CB | 79 U/L | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_79UL | 11KV官愛線(VG34) 79RY U/L | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | F14 LCO | ADJ(U/L) | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_ADJ | 11KV官愛線(VG34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F15 PH RY | PHA | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_PHA | 11KV官信線(VG35) 相間RY | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F15 GD RY | GDA | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_GDA | 11KV官信線(VG35) 接地RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0104 | 1-35-11 |  | 1-68 | F15 CB | 79 U/L | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_79UL | 11KV官信線(VG35) 79RY U/L | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | F15 LCO | ADJ(U/L) | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_ADJ | 11KV官信線(VG35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VG21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | F1 CB | CB ON/OFF | 官一線 |  | aaab | B2/S40_D1 | [8 empty] | 官田SS.VG21_CB | VG21(11KV官一線) CB | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG21_ES | VG21_ES (非取樣點) | FEEDER | [5 empty] | 134 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VG22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | F2 CB | CB ON/OFF | 官二線 |  | aabb | B2/S40_D1 | [8 empty] | 官田SS.VG22_CB | VG22(11KV官二線) CB | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG22_ES | VG22_ES (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VG23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F3 CB | CB ON/OFF | 官三線 |  | aadb | B2/S40_D1 | [8 empty] | 官田SS.VG23_CB | VG23(11KV官三線) CB | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG23_ES | VG23_ES (非取樣點) | FEEDER | [5 empty] | 138 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VG24/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | F4 CB | CB ON/OFF | 官正線 |  | aaeb | B2/S40_D1 | [8 empty] | 官田SS.VG24_CB | VG24(11KV官正線) CB | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG24_ES | VG24_ES (非取樣點) | FEEDER | [5 empty] | 140 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VG25/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | F5 CB | CB ON/OFF | 官五線 |  | aafb | B2/S40_D1 | [8 empty] | 官田SS.VG25_CB | VG25(11KV官五線) CB | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG25_ES | VG25_ES (非取樣點) | FEEDER | [5 empty] | 142 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VG26/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | F6 CB | CB ON/OFF | 官六線 |  | abab | B2/S40_D1 | [8 empty] | 官田SS.VG26_CB | VG26(11KV官六線) CB | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG26_ES | VG26_ES (非取樣點) | FEEDER | [5 empty] | 144 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VG27/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | F7 CB | CB ON/OFF | 官七線 |  | abcb | B2/S40_D1 | [8 empty] | 官田SS.VG27_CB | VG27(11KV官七線) CB | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG27_ES | VG27_ES (非取樣點) | FEEDER | [5 empty] | 146 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VG28/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | F8 CB | CB ON/OFF | 官八線 |  | abeb | B2/S40_D1 | [8 empty] | 官田SS.VG28_CB | VG28(11KV官八線) CB | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG28_ES | VG28_ES (非取樣點) | FEEDER | [5 empty] | 148 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBUS | L/VG29/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | F9 CB | CB ON/OFF | 官九線 |  | acab | B2/S40_D1 | [8 empty] | 官田SS.VG29_CB | VG29(11KV官九線) CB | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG29_ES | VG29_ES (非取樣點) | FEEDER | [5 empty] | 150 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBUS | L/VG30/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | F10 CB | CB ON/OFF | 官十線 |  | accb | B2/S40_D1 | [8 empty] | 官田SS.VG30_CB | VG30(11KV官十線) CB | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG30_ES | VG30_ES (非取樣點) | FEEDER | [5 empty] | 152 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/VG31/T1 |  |  | 0140 |  | 0092 | 1-11-04 |  | 1-5C | F11 CB | CB ON/OFF | 官忠線 |  | adab | B2/S40_D1 | [8 empty] | 官田SS.VG31_CB | VG31(11KV官忠線) CB | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG31_ES | VG31_ES (非取樣點) | FEEDER | [5 empty] | 154 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/VG32/T1 |  |  | 0141 |  | 0093 | 1-11-05 |  | 1-5D | F12 CB | CB ON/OFF | 官孝線 |  | adcb | B2/S40_D1 | [8 empty] | 官田SS.VG32_CB | VG32(11KV官孝線) CB | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG32_ES | VG32_ES (非取樣點) | FEEDER | [5 empty] | 156 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/VG33/T1 |  |  | 0142 |  | 0094 | 1-11-06 |  | 1-5E | F13 CB | CB ON/OFF | 官仁線 |  | adeb | B2/S40_D1 | [8 empty] | 官田SS.VG33_CB | VG33(11KV官仁線) CB | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG33_ES | VG33_ES (非取樣點) | FEEDER | [5 empty] | 158 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/VG34/T1 |  |  | 0143 |  | 0095 | 1-11-07 |  | 1-5F | F14 CB | CB ON/OFF | 官愛線 |  | adfb | B2/S40_D1 | [8 empty] | 官田SS.VG34_CB | VG34(11KV官愛線) CB | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG34_ES | VG34_ES (非取樣點) | FEEDER | [5 empty] | 160 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BUS | L/VG35/T1 |  |  | 0144 |  | 0096 | 1-12-00 |  | 1-60 | F15 CB | CB ON/OFF | 官信線 |  | adgb | B2/S40_D1 | [8 empty] | 官田SS.VG35_CB | VG35(11KV官信線) CB | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG35_ES | VG35_ES (非取樣點) | FEEDER | [5 empty] | 162 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1 TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 163 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1 TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 164 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1 TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 165 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2 TIE R相電流 | A1 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 166 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2 TIE S相電流 | A2 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 167 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2 TIE T相電流 | A3 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 168 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1BUS | B/2ABUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | zzzz | B2/S40_D1 | [8 empty] | 官田SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 169 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIE PH RY | PHA | #1 TIE CB |  |  | B2/S40_D1 | [8 empty] | 官田SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 170 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1 TIE GD RY | GDA | #1 TIE CB |  |  | B2/S40_D1 | [8 empty] | 官田SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 171 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2BBUS | B/3BUS |  |  | 0123 |  | 0071 | 1-0F-03 |  | 1-47 | #2 TIE CB | CB ON/OFF | #2 TIE CB |  | zzzz | B2/S40_D1 | [8 empty] | 官田SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 172 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2 TIEPH RY | PHA | #2 TIE CB |  |  | B2/S40_D1 | [8 empty] | 官田SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 173 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #2 TIEGD RY | GDA | #2 TIE CB |  |  | B2/S40_D1 | [8 empty] | 官田SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 174 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 175 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 176 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | (非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | [5 empty] | 177 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | (非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | [5 empty] | 178 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 179 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 180 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 181 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 182 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 183 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 MTR | MW | 二號主變 | MW_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 184 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 MTR | MVAR | 二號主變 | MVAR_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 185 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 MTR R電流 | A1 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 186 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 MTR S電流 | A2 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 187 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 MTR T電流 | A3 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 188 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 MTR | MW | 三號主變 | MW_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 189 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 MTR | MVAR | 三號主變 | MVAR_-36_36(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 190 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 MTR R電流 | A1 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 191 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 MTR S電流 | A2 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 192 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 MTR T電流 | A3 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 193 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 194 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 195 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 196 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH | 一號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 197 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 198 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 199 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 200 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 201 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2TR | MWH | 二號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 202 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2TR | MVARH(+) | 二號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 203 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 204 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 205 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 MTR | TAP | 三號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 206 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3TR | MWH | 三號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 207 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3TR | MVARH(+) | 三號主變 |  |  | B1/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 208 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aabb | B3/S40_D1 | [8 empty] | 官田SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 209 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 210 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 211 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aagb | B3/S40_D1 | [8 empty] | 官田SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 212 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 213 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 214 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aaib | B3/S40_D1 | [8 empty] | 官田SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 215 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 216 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S40_D1 | [8 empty] | 官田SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 217 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1 MTR | CB ON/OFF | 一號主變二次側 |  | aaca | B2/S40_D1 | [8 empty] | 官田SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 218 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | CB | 2MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2 MTR A | CB ON/OFF | 二號主變二次側(A) |  | abba | B2/S40_D1 | [8 empty] | 官田SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 219 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | CB | 2MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBUS | T/2MTR |  |  | 0012 |  | 0070 | 1-01-04 |  | 1-46 | #2 MTR B | CB ON/OFF | 二號主變二次側(B) |  | acba | B2/S40_D1 | [8 empty] | 官田SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 220 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | T/3MTR |  |  | 0023 |  | 0089 | 1-02-07 |  | 1-59 | #3 MTR | CB ON/OFF | 三號主變二次側(A) |  | adda | B2/S40_D1 | [8 empty] | 官田SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 221 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 222 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 223 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1 MTR | 51Z | 一號主變 51Z RY |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 224 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 225 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1 MTR | 87 LS | 一號 主變87 RY (使用/閉鎖) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 226 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 227 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 228 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 229 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 230 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2 MTR | 87 LS (未使用) | 二號 主變87 RY (使用/閉鎖) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 231 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 770 | PHA | 三號主變 51 RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 232 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 770 | GDA | 三號主變 51N RY |  |  | B3/S40_D1 | [8 empty] | 官田SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 233 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3 MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 234 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3MTR | 87A | 三號主變差動電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 235 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3 MTR | 87 LS (未使用) | 三號 主變87 RY (使用/閉鎖) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 236 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1 MTR | PHA | 一號主變二次側 51 RY |  |  | B2/S40_D1 | [8 empty] | 官田SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 237 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1 MTR | TRA | 一號主變重故障 |  | a | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 238 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1 MTR | TRF | 一號主變輕故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 239 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1 MTR | S/L | 一號主變 OLTC (中心/現場) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 240 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1 MTR | A/M | 一號主變 OLTC (自動/手動) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 241 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2 MTR A | PHA | 二號主變二次(A)51 RY |  |  | B2/S40_D1 | [8 empty] | 官田SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 242 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2 MTR B | PHA | 二號主變二次(B)51 RY |  |  | B2/S40_D1 | [8 empty] | 官田SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 243 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-34-00 |  |  | #2 MTR | TRA | 二號主變重故障 |  | a | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 244 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2 MTR | TRF | 二號主變輕故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 245 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2 MTR | S/L | 二號主變 OLTC (中心/現場) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 246 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2 MTR | A/M | 二號主變 OLTC (自動/手動) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 247 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3 MTR | PHA | 三號主變二次51 RY |  |  | B2/S40_D1 | [8 empty] | 官田SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 248 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0336 |  |  | 1-35-00 |  |  | #3 MTR | 3TRA | 三號主變重故障 |  | a | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 249 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3 MTR | 3TRF | 三號主變輕故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 250 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3 MTR | S/L | 三號主變 OLTC (中心/現場) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 251 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3 MTR | A/M | 三號主變 OLTC (自動/手動) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 252 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | 一號主變 |  |  | B3/S40_D1 | [8 empty] | 官田SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 253 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | 二號主變 |  |  | B3/S40_D1 | [8 empty] | 官田SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 254 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0044 | 1-38-04 | 1-38-05 | 1-2C | 771 | ABS ON | 三號主變 |  |  | B3/S40_D1 | [8 empty] | 官田SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 255 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1 MTR | 96A | 一號主變 96PA 電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 256 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1 MTR | TAPA | 一號主變TAP遲滯 (48TX) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 257 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1 MTR | 1ACF | 一號主變AC電源失效 (27欠壓) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 258 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2 MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 259 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2 MTR | TAPA | 二號主變TAP遲滯 (48TX) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 260 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2MTR | 2ACF | 二號主變AC電源失效(27欠壓) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 261 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3MTR | 96A | 三號主變 96D,63A RY |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 262 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3 MTR | TAPA | 三號主變TAP遲滯(48TX) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 263 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | #3 MTR | #3ACF | 三號主變AC電源失效(27欠壓) |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 264 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1SSTR |  |  | 0180 |  | 0066 | 1-16-04 |  | 1-42 | #1 SSTR CB | CB ON/OFF | #1 SSTR |  | aagb | B2/S40_D1 | [8 empty] | 官田SS.390_CB | 390(#1SSTR) CB | OTHER |  |  |  |  | CDC | 265 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | #1 SSTR PH RY | PHA | #1 SSTR |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 266 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | #1 SSTR GD RY | GDA | #1 SSTR |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  |  |  |  | CDC | 267 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 268 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 269 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 490 | #3SSTR(490) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | T/3SSTR |  |  | 0183 |  | 0067 | 1-16-07 |  | 1-43 | #2 SSTR CB | CB ON/OFF | #2 SSTR |  | adhb | B2/S40_D1 | [8 empty] | 官田SS.490_CB | 490(#3SSTR) CB | OTHER |  |  |  |  | CDC | 270 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 490 | #3SSTR(490) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | #2 SSTR PH RY | PHA | #2 SSTR |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3SSTR_51A | #3SSTR 51RY | OTHER |  |  |  |  | CDC | 271 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 490 | #3SSTR(490) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #2 SSTR GD RY | GDA | #2 SSTR |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER |  |  |  |  | CDC | 272 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 490 | #3SSTR(490) |  | D1 | 491(非取樣點) | ADD | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 273 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 490 | #3SSTR(490) |  | E1 | 491E(非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 274 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | SC 69KV |  | aaaa | B2/S40_A1 | [8 empty] | 官田SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 275 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_A1 | [8 empty] | 官田SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 276 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | aahb | B2/S40_D1 | [8 empty] | 官田SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 277 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1 SC | A/M | 一號 SC 乏控器 (自動/手動) |  |  | B2/S40_D1 | [8 empty] | 官田SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 278 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 279 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC | CB ON/OFF | #2 11KV SC |  | aceb | B2/S40_D1 | [8 empty] | 官田SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 280 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2 SC | A/M | 二號 SC 乏控器 (自動/手動) |  |  | B2/S40_D1 | [8 empty] | 官田SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 281 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.220ES | 220ES (非取樣點) | SC | [5 empty] | 282 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BUS | C/3SC |  |  | 0139 |  | 0091 | 1-11-03 |  | 1-5B | #3 11KV SC | CB ON/OFF | #3 11KV SC |  | adib | B2/S40_D1 | [8 empty] | 官田SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 283 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0099 | 1-35-06 |  | 1-63 | #3 SC | A/M | 三號 SC 乏控器 (自動/手動) |  |  | B2/S40_D1 | [8 empty] | 官田SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 284 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.230ES | 230ES (非取樣點) | SC | [5 empty] | 285 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | B3,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0390 | 391 | 0039 | 1-38-06 | 1-38-07 | 1-27 | 811 | ABS ON | 69KVSC |  |  | B2/S40_A1 | [8 empty] | 官田SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 286 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 810 | PHA GDA | SC 69KV 51 51N RY |  |  | B2/S40_A1 | [8 empty] | 官田SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 287 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 810 | UVA OVA | SC 69KV 27 59N RY |  |  | B2/S40_A1 | [8 empty] | 官田SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 288 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1 SC5151NRY | SCA | #1 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 289 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1 SC2759RY | UVA | #1 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 290 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2 SC5151NRY | SCA | #2 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 291 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2 SC2759RY | UVA | #2 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 292 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | #3SC5151NRY | SCA | #3 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 293 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #3SC2759RY | UVA | #3 11KV SC |  |  | B2/S40_D1 | [8 empty] | 官田SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 294 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.11KV_#1SCDS | 11KV_#1SCDS (非取樣點) | SC | [5 empty] | 295 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.11KV_#2SCDS | 11KV_#2SCDS (非取樣點) | SC | [5 empty] | 296 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.11KV_#3SCDS | 11KV_#3SCDS (非取樣點) | SC | [5 empty] | 297 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 298 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 299 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 300 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 301 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 302 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 303 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 官田SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 304 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 305 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 其他重故障 |  | 其他重故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 306 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  | 其他輕故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 307 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 308 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 309 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池警報 |  | 洩油池警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 310 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 開關場 |  | 水氣霧釋放 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化門禁(1) | 水氣霧釋放 | OTHER |  |  |  |  | CDC | 311 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 控制室旁 |  | 所内淹水高水位 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化門禁(2) | 所內淹水高水位 | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 控制室旁 |  | 所内淹水低水位 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化門禁(3) | 所內淹水低水位 | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | 開關場 |  | 水氣霧警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化防盜(1) | 水氣霧警報 | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | 開關場 |  | 水氣霧故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化防盜(2) | 水氣霧故障 | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | MCSG |  | MCSG偵煙警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.無人化防盜(3) | MCSG偵煙警報 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場照明(A) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S40_D1 | [8 empty] | 官田SS.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明(B) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S40_D1 | [8 empty] | 官田SS.開關場照明(B) | 開關場照明(B) | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 控制室 |  | CO2 警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.火災警報(1) | CO2警報 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 控制室 |  | CO2 故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.火災警報(2) | CO2故障 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.火災警報(3) | 火災警報(3) | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內電源欠壓 |  |  | B3/S40_D1 | [8 empty] | 官田SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 | DCA | NFB跳脫監視 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.直流電源DCA | NFB跳脫監視 | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCE | 直流電源接地故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS 89A | ABS NFB跳脫警報 |  |  | B3/S40_D1 | [8 empty] | 官田SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV SC | 69KVSC AL | 69KVSC警報 |  |  | B2/S40_A1 | [8 empty] | 官田SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | Door |  |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S40_D1 | [8 empty] | 官田SS.門禁 | 門禁 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F1 81 RY | 81A | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_81A/S | 11KV官一線(VG21) 81RY | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F2 81 RY | 81A | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_81A/S | 11KV官二線(VG22) 81RY | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F3 81 RY | 81A | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_81A/S | 11KV官三線(VG23) 81RY | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F4 81 RY | 81A | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_81A/S | 11KV官正線(VG24) 81RY | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | F5 81 RY | 81A | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_81A/S | 11KV官五線(VG25) 81RY | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | F6 81 RY | 81A | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_81A/S | 11KV官六線(VG26) 81RY | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F7 81 RY | 81A | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_81A/S | 11KV官七線(VG27) 81RY | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F8 81 RY | 81A | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_81A/S | 11KV官八線(VG28) 81RY | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | F9 81 RY | 81A | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_81A/S | 11KV官九線(VG29) 81RY | OTHER |  |  |  |  | CDC | 340 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F10 81 RY | 81A | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_81A/S | 11KV官十線(VG30) 81RY | OTHER |  |  |  |  | CDC | 341 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 81 RY | 81A | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_81A/S | 11KV官忠線(VG31) 81RY | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | F12 81 RY | 81A | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_81A/S | 11KV官孝線(VG32) 81RY | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 81 RY | 81A | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_81A/S | 11KV官仁線(VG33) 81RY | OTHER |  |  |  |  | CDC | 344 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F14 81 RY | 81A | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_81A/S | 11KV官愛線(VG34) 81RY | OTHER |  |  |  |  | CDC | 345 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | F15 81 RY | 81A | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_81A/S | 11KV官信線(VG35) 81RY | OTHER |  |  |  |  | CDC | 346 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  | 0065 | 1-14-00 |  | 1-41 | #1 TR 81 RY | 81A | #1 Main |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1MA_81A/S | #1MA 81RY | OTHER |  |  |  |  | CDC | 347 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL |  | B2,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0107 | 1-33-13 |  | 1-6B | #1 MTR 81 RY | 81 U/L | #1 Main 81使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1MA_81U/L | #1MA 81RY U/L | OTHER |  |  |  |  | CDC | 348 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  | 0086 | 1-14-01 |  | 1-56 | #2 TRA 81 RY | 81A | #2A Main |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2MA_81A/S | #2MA 81RY | OTHER |  |  |  |  | CDC | 349 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81UL |  | B2,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0108 | 1-34-13 |  | 1-6C | #2 MTR A | 81 U/L | #2A Main 81使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2MA_81U/L | #2MA 81RY U/L | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  | 0087 | 1-14-02 |  | 1-57 | #2 TRB 81 RY | 81A | #2B Main |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2MB_81A/S | #2MB 81RY | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81UL |  | B2,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0334 |  | 0109 | 1-34-14 |  | 1-6D | #2 MTR B | 81 U/L | #2B Main 81使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2MB_81U/L | #2MB 81RY U/L | OTHER |  |  |  |  | CDC | 352 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81AS |  | B2,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  | 0105 | 1-14-03 |  | 1-69 | #3 TRA 81 RY | 81A | #3A Main |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3MA_81A/S | #3MA 81RY | OTHER |  |  |  |  | CDC | 353 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0110 | 1-35-13 |  | 1-6E | #3 MTR | 81 U/L | #3 Main 81RY (使用/閉鎖) |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3MA_81U/L | #3MA 81RY U/L | OTHER |  |  |  |  | CDC | 354 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0448 |  |  | 1-3C-00 |  |  | F1 79 RY | 79LOA | 官一線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_79_LOA | 11KV官一線(VG21) 79LOA | OTHER |  |  |  |  | CDC | 355 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0449 |  |  | 1-3C-01 |  |  | F2 79 RY | 79LOA | 官二線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_79_LOA | 11KV官二線(VG22) 79LOA | OTHER |  |  |  |  | CDC | 356 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | F3 79 RY | 79LOA | 官三線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_79_LOA | 11KV官三線(VG23) 79LOA | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0451 |  |  | 1-3C-03 |  |  | F4 79 RY | 79LOA | 官正線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_79_LOA | 11KV官正線(VG24) 79LOA | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0452 |  |  | 1-3C-04 |  |  | F5 79 RY | 79LOA | 官五線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_79_LOA | 11KV官五線(VG25) 79LOA | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0453 |  |  | 1-3C-05 |  |  | F6 79 RY | 79LOA | 官六線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_79_LOA | 11KV官六線(VG26) 79LOA | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0454 |  |  | 1-3C-06 |  |  | F7 79 RY | 79LOA | 官七線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_79_LOA | 11KV官七線(VG27) 79LOA | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0455 |  |  | 1-3C-07 |  |  | F8 79 RY | 79LOA | 官八線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_79_LOA | 11KV官八線(VG28) 79LOA | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0456 |  |  | 1-3C-08 |  |  | F9 79 RY | 79LOA | 官九線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_79_LOA | 11KV官九線(VG29) 79LOA | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0457 |  |  | 1-3C-09 |  |  | F10 79 RY | 79LOA | 官十線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_79_LOA | 11KV官十線(VG30) 79LOA | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0458 |  |  | 1-3C-10 |  |  | F11 79 RY | 79LOA | 官忠線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_79_LOA | 11KV官忠線(VG31) 79LOA | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0459 |  |  | 1-3C-11 |  |  | F12 79 RY | 79LOA | 官孝線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_79_LOA | 11KV官孝線(VG32) 79LOA | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0460 |  |  | 1-3C-12 |  |  | F13 79 RY | 79LOA | 官仁線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_79_LOA | 11KV官仁線(VG33) 79LOA | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0461 |  |  | 1-3C-13 |  |  | F14 79 RY | 79LOA | 官愛線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_79_LOA | 11KV官愛線(VG34) 79LOA | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0462 |  |  | 1-3C-14 |  |  | F15 79 RY | 79LOA | 官信線 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_79_LOA | 11KV官信線(VG35) 79LOA | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | ComPoint |  |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | IED | RYFA | 11KV IED 故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.11KV_RYFA | 11KV數位電驛故障 | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | PM | PMA | PowerMeter 故障 |  |  | ELEM/S40_D1 | [8 empty] | 官田SS.PMA | POWER METER故障 | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 官一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官一線KVAR | 11KV官一線 KVAR | FEEDER |  |  |  |  | CDC | 372 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 官一線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官一線A1 | 11KV官一線 R相AMP | FEEDER |  |  |  |  | CDC | 373 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 官一線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官一線A2 | 11KV官一線 S相AMP | FEEDER |  |  |  |  | CDC | 374 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 官一線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官一線A3 | 11KV官一線 T相AMP | FEEDER |  |  |  |  | CDC | 375 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 官一線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官一線A0 | 11KV官一線 N相AMP | FEEDER |  |  |  |  | CDC | 376 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 乏 | VAR | 官七線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官七線KVAR | 11KV官七線 KVAR | FEEDER |  |  |  |  | CDC | 377 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 R相電流 | A1 | 官七線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官七線A1 | 11KV官七線 R相AMP | FEEDER |  |  |  |  | CDC | 378 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 S相電流 | A2 | 官七線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官七線A2 | 11KV官七線 S相AMP | FEEDER |  |  |  |  | CDC | 379 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F7 T相電流 | A3 | 官七線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官七線A3 | 11KV官七線 T相AMP | FEEDER |  |  |  |  | CDC | 380 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F7 N相電流 | AMP | 官七線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官七線A0 | 11KV官七線 N相AMP | FEEDER |  |  |  |  | CDC | 381 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 乏 | VAR | 官九線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官九線KVAR | 11KV官九線 KVAR | FEEDER |  |  |  |  | CDC | 382 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 R相電流 | A1 | 官九線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官九線A1 | 11KV官九線 R相AMP | FEEDER |  |  |  |  | CDC | 383 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 S相電流 | A2 | 官九線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官九線A2 | 11KV官九線 S相AMP | FEEDER |  |  |  |  | CDC | 384 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 T相電流 | A3 | 官九線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官九線A3 | 11KV官九線 T相AMP | FEEDER |  |  |  |  | CDC | 385 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F9 N相電流 | AMP | 官九線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官九線A0 | 11KV官九線 N相AMP | FEEDER |  |  |  |  | CDC | 386 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 官二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官二線KVAR | 11KV官二線 KVAR | FEEDER |  |  |  |  | CDC | 387 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 官二線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官二線A1 | 11KV官二線 R相AMP | FEEDER |  |  |  |  | CDC | 388 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 官二線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官二線A2 | 11KV官二線 S相AMP | FEEDER |  |  |  |  | CDC | 389 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 官二線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官二線A3 | 11KV官二線 T相AMP | FEEDER |  |  |  |  | CDC | 390 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 官二線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官二線A0 | 11KV官二線 N相AMP | FEEDER |  |  |  |  | CDC | 391 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 乏 | VAR | 官八線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官八線KVAR | 11KV官八線 KVAR | FEEDER |  |  |  |  | CDC | 392 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 R相電流 | A1 | 官八線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官八線A1 | 11KV官八線 R相AMP | FEEDER |  |  |  |  | CDC | 393 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 S相電流 | A2 | 官八線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官八線A2 | 11KV官八線 S相AMP | FEEDER |  |  |  |  | CDC | 394 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 T相電流 | A3 | 官八線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官八線A3 | 11KV官八線 T相AMP | FEEDER |  |  |  |  | CDC | 395 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F8 N相電流 | AMP | 官八線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官八線A0 | 11KV官八線 N相AMP | FEEDER |  |  |  |  | CDC | 396 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F10 乏 | VAR | 官十線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官十線KVAR | 11KV官十線 KVAR | FEEDER |  |  |  |  | CDC | 397 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 R相電流 | A1 | 官十線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官十線A1 | 11KV官十線 R相AMP | FEEDER |  |  |  |  | CDC | 398 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 S相電流 | A2 | 官十線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官十線A2 | 11KV官十線 S相AMP | FEEDER |  |  |  |  | CDC | 399 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 T相電流 | A3 | 官十線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官十線A3 | 11KV官十線 T相AMP | FEEDER |  |  |  |  | CDC | 400 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F10 N相電流 | AMP | 官十線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官十線A0 | 11KV官十線 N相AMP | FEEDER |  |  |  |  | CDC | 401 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 官三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官三線KVAR | 11KV官三線 KVAR | FEEDER |  |  |  |  | CDC | 402 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 官三線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官三線A1 | 11KV官三線 R相AMP | FEEDER |  |  |  |  | CDC | 403 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 官三線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官三線A2 | 11KV官三線 S相AMP | FEEDER |  |  |  |  | CDC | 404 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 官三線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官三線A3 | 11KV官三線 T相AMP | FEEDER |  |  |  |  | CDC | 405 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 官三線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官三線A0 | 11KV官三線 N相AMP | FEEDER |  |  |  |  | CDC | 406 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 官五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官五線KVAR | 11KV官五線 KVAR | FEEDER |  |  |  |  | CDC | 407 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 官五線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官五線A1 | 11KV官五線 R相AMP | FEEDER |  |  |  |  | CDC | 408 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 官五線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官五線A2 | 11KV官五線 S相AMP | FEEDER |  |  |  |  | CDC | 409 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 官五線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官五線A3 | 11KV官五線 T相AMP | FEEDER |  |  |  |  | CDC | 410 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 官五線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官五線A0 | 11KV官五線 N相AMP | FEEDER |  |  |  |  | CDC | 411 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 乏 | VAR | 官仁線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官仁線KVAR | 11KV官仁線 KVAR | FEEDER |  |  |  |  | CDC | 412 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 R相電流 | A1 | 官仁線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官仁線A1 | 11KV官仁線 R相AMP | FEEDER |  |  |  |  | CDC | 413 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 S相電流 | A2 | 官仁線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官仁線A2 | 11KV官仁線 S相AMP | FEEDER |  |  |  |  | CDC | 414 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 T相電流 | A3 | 官仁線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官仁線A3 | 11KV官仁線 T相AMP | FEEDER |  |  |  |  | CDC | 415 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F13 N相電流 | AMP | 官仁線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官仁線A0 | 11KV官仁線 N相AMP | FEEDER |  |  |  |  | CDC | 416 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 乏 | VAR | 官六線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官六線KVAR | 11KV官六線 KVAR | FEEDER |  |  |  |  | CDC | 417 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F6 R相電流 | A1 | 官六線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官六線A1 | 11KV官六線 R相AMP | FEEDER |  |  |  |  | CDC | 418 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F6 S相電流 | A2 | 官六線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官六線A2 | 11KV官六線 S相AMP | FEEDER |  |  |  |  | CDC | 419 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F6 T相電流 | A3 | 官六線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官六線A3 | 11KV官六線 T相AMP | FEEDER |  |  |  |  | CDC | 420 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | F6 N相電流 | AMP | 官六線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官六線A0 | 11KV官六線 N相AMP | FEEDER |  |  |  |  | CDC | 421 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 官正線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官正線KVAR | 11KV官正線 KVAR | FEEDER |  |  |  |  | CDC | 422 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 官正線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官正線A1 | 11KV官正線 R相AMP | FEEDER |  |  |  |  | CDC | 423 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 官正線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官正線A2 | 11KV官正線 S相AMP | FEEDER |  |  |  |  | CDC | 424 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 官正線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官正線A3 | 11KV官正線 T相AMP | FEEDER |  |  |  |  | CDC | 425 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 官正線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官正線A0 | 11KV官正線 N相AMP | FEEDER |  |  |  |  | CDC | 426 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 乏 | VAR | 官孝線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官孝線KVAR | 11KV官孝線 KVAR | FEEDER |  |  |  |  | CDC | 427 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 R相電流 | A1 | 官孝線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官孝線A1 | 11KV官孝線 R相AMP | FEEDER |  |  |  |  | CDC | 428 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 S相電流 | A2 | 官孝線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官孝線A2 | 11KV官孝線 S相AMP | FEEDER |  |  |  |  | CDC | 429 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F12 T相電流 | A3 | 官孝線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官孝線A3 | 11KV官孝線 T相AMP | FEEDER |  |  |  |  | CDC | 430 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F12 N相電流 | AMP | 官孝線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官孝線A0 | 11KV官孝線 N相AMP | FEEDER |  |  |  |  | CDC | 431 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 乏 | VAR | 官忠線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官忠線KVAR | 11KV官忠線 KVAR | FEEDER |  |  |  |  | CDC | 432 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 R相電流 | A1 | 官忠線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官忠線A1 | 11KV官忠線 R相AMP | FEEDER |  |  |  |  | CDC | 433 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F11 S相電流 | A2 | 官忠線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官忠線A2 | 11KV官忠線 S相AMP | FEEDER |  |  |  |  | CDC | 434 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F11 T相電流 | A3 | 官忠線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官忠線A3 | 11KV官忠線 T相AMP | FEEDER |  |  |  |  | CDC | 435 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F11 N相電流 | AMP | 官忠線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官忠線A0 | 11KV官忠線 N相AMP | FEEDER |  |  |  |  | CDC | 436 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 乏 | VAR | 官信線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官信線KVAR | 11KV官信線 KVAR | FEEDER |  |  |  |  | CDC | 437 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 R相電流 | A1 | 官信線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官信線A1 | 11KV官信線 R相AMP | FEEDER |  |  |  |  | CDC | 438 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 S相電流 | A2 | 官信線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官信線A2 | 11KV官信線 S相AMP | FEEDER |  |  |  |  | CDC | 439 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F15 T相電流 | A3 | 官信線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官信線A3 | 11KV官信線 T相AMP | FEEDER |  |  |  |  | CDC | 440 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F15 N相電流 | AMP | 官信線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官信線A0 | 11KV官信線 N相AMP | FEEDER |  |  |  |  | CDC | 441 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 乏 | VAR | 官愛線 | KVAR_-9000_9000(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官愛線KVAR | 11KV官愛線 KVAR | FEEDER |  |  |  |  | CDC | 442 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 R相電流 | A1 | 官愛線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官愛線A1 | 11KV官愛線 R相AMP | FEEDER |  |  |  |  | CDC | 443 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F14 S相電流 | A2 | 官愛線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官愛線A2 | 11KV官愛線 S相AMP | FEEDER |  |  |  |  | CDC | 444 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F14 T相電流 | A3 | 官愛線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官愛線A3 | 11KV官愛線 T相AMP | FEEDER |  |  |  |  | CDC | 445 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F14 N相電流 | AMP | 官愛線 | A_-500_500(-2000_2000) |  | B2/S40_D1 | [8 empty] | 官田SS.官愛線A0 | 11KV官愛線 N相AMP | FEEDER |  |  |  |  | CDC | 446 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S40_D1 | [8 empty] | 官田SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 447 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0381 |  |  | 1-37-13 |  |  | 640 | 87CFA | 640通訊故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_87CFA | 640 87RY通訊故障 | OTHER | [5 empty] | 448 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0380 |  |  | 1-37-12 |  |  | 640 | 87RYFA | 640數位電驛故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.640_87RYFA | 640 數位電驛故障 | OTHER | [5 empty] | 449 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1MTR | #1 63Q | #1MTR ULTC保護 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | [5 empty] | 450 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #1MTR | #1 96B1 | #1MTR撲氣一段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 451 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #1MTR | #1 96B2 | #1MTR撲氣二段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | [5 empty] | 452 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1MTR | #1 96D | #1MTR放壓裝置 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | [5 empty] | 453 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1MTR | #1 96P | #1MTR突壓電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | [5 empty] | 454 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #2MTR | #2 63Q | #2MTR ULTC保護 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | [5 empty] | 455 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #2MTR | #2 96B1 | #2MTR撲氣一段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 456 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #2MTR | #2 96B2 | #2MTR撲氣二段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | [5 empty] | 457 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #2MTR | #2 96D | #2MTR放壓裝置 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | [5 empty] | 458 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2MTR | #2 96P | #2MTR突壓電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | [5 empty] | 459 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #3MTR | #3 63Q | #3MTR ULTC保護 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | [5 empty] | 460 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #3MTR | #3 96B1 | #3MTR撲氣一段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 461 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #3MTR | #3 96B2 | #3MTR撲氣二段 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | [5 empty] | 462 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #3MTR | #3 96D | #3MTR放壓裝置 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | [5 empty] | 463 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #3MTR | #3 96P | #3MTR突壓電驛 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | [5 empty] | 464 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0375 |  |  | 1-37-07 |  |  | 630 | 87CFA | 630通訊故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_87CFA | 630 87RY通訊故障 | OTHER | [5 empty] | 465 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0374 |  |  | 1-37-06 |  |  | 630 | 87RYFA | 630數位電驛故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.630_RYFA | 630 數位電驛故障 | OTHER | [5 empty] | 466 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0377 |  |  | 1-37-09 |  |  | 660 | 87CFA | 660通訊故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_87CFA | 660 87RY通訊故障 | OTHER | [5 empty] | 467 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0376 |  |  | 1-37-08 |  |  | 660 | 87RYFA | 660數位電驛故障 |  |  | B2/S40_A1 | [8 empty] | 官田SS.660_RYFA | 660 數位電驛故障 | OTHER | [5 empty] | 468 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0467 |  |  | 1-3D-03 |  |  | #1MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 469 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0470 |  |  | 1-3D-06 |  |  | #1MTR 871S | 871S | #1MTR 87RY 1S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 470 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0471 |  |  | 1-3D-07 |  |  | #1MTR 872S | 872S | #1MTR 87RY 2S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 471 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 1MTR | #1MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0463 |  |  | 1-3C-15 |  |  | #1MTR IED | RYFA | #1MTR及饋線 IED 故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | [5 empty] | 472 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0468 |  |  | 1-3D-04 |  |  | #2MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 473 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0472 |  |  | 1-3D-08 |  |  | #2MTR 871S | 871S | #2MTR 87RY 1S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 474 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0473 |  |  | 1-3D-09 |  |  | #2MTR 872S | 872S | #2MTR 87RY 2S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 475 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 2MTR | #2MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0464 |  |  | 1-3D-00 |  |  | #2MTR IED | RYFA | #2MTR及饋線 IED 故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | [5 empty] | 476 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0469 |  |  | 1-3D-05 |  |  | #3MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 477 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0474 |  |  | 1-3D-10 |  |  | #3MTR 871S | 871S | #3MTR 87RY 1S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 478 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0475 |  |  | 1-3D-11 |  |  | #3MTR 872S | 872S | #3MTR 87RY 2S 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 479 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 3MTR | #3MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0465 |  |  | 1-3D-01 |  |  | #3MTR IED | RYFA | #3MTR及饋線 IED 故障 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | [5 empty] | 480 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | ComPoint |  |  | 81A_RYFA |  | INSERT | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0466 |  |  | 1-3D-02 |  |  | 81RY IED | RYFA | 81RY IED 故障 |  |  | B3/S40_D1 | [8 empty] | 官田SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | [5 empty] | 481 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0476 |  |  | 1-3D-12 |  |  | #1MTR 51ZS | 51Z S | #1MTR 51Z RY 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 482 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0477 |  |  | 1-3D-13 |  |  | #2MTR 51ZS | 51Z S | #2MTR 51Z RY 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 483 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0478 |  |  | 1-3D-14 |  |  | #3MTR 51ZS | 51Z S | #3MTR 51Z RY 使用/閉鎖 |  |  | B1/S40_D1 | [8 empty] | 官田SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 484 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 CB | KWH | 官一線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 485 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 CB | KWH | 官二線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 486 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 CB | KWH | 官三線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 487 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 CB | KWH | 官正線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 488 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 CB | KWH | 官五線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 489 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 CB | KWH | 官六線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 490 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 CB | KWH | 官七線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 491 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 CB | KWH | 官八線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 492 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 CB | KWH | 官九線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 493 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 CB | KWH | 官十線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 494 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F11 CB | KWH | 官忠線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 495 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F12 CB | KWH | 官孝線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 496 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F13 CB | KWH | 官仁線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 497 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F14 CB | KWH | 官愛線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 498 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F15 CB | KWH | 官信線 |  |  | B2/S40_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 499 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S40 | 官田SS |  |  | 1GIS | #1GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1 GIS CB | CBA | #1 GIS斷路器重故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1GIS_CBA | #1GIS重故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 1GIS | #1GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1 GIS CB | CBF | #1 GIS斷路器輕故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#1GIS_CBF | #1GIS輕故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2GIS | #2GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2 GIS CB | CBA | #2 GIS斷路器重故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2GIS_CBA | #2GIS重故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 2GIS | #2GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2 GIS CB | CBF | #2 GIS斷路器輕故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#2GIS_CBF | #2GIS輕故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3GIS | #3GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3 GIS CB | CBA | #3 GIS斷路器重故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3GIS_CBA | #3GIS重故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS |  |  | 3GIS | #3GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3 GIS CB | CBF | #3 GIS斷路器輕故障 |  |  | B2/S40_D1 | [8 empty] | 官田SS.#3GIS_CBF | #3GIS輕故障 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | F1 81 U/L | F1 81 U/L | 官一線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG21_81U/L | 11KV官一線(VG21) 81RY U/L | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | F2 81 U/L | F2 81 U/L | 官二線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG22_81U/L | 11KV官二線(VG22) 81RY U/L | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0490 |  |  | 1-3E-10 |  |  | F3 81 U/L | F3 81 U/L | 官三線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG23_81U/L | 11KV官三線(VG23) 81RY U/L | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0491 |  |  | 1-3E-11 |  |  | F4 81 U/L | F4 81 U/L | 官正線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG24_81U/L | 11KV官正線(VG24) 81RY U/L | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | F5 81 U/L | F5 81 U/L | 官五線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG25_81U/L | 11KV官五線(VG25) 81RY U/L | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | F6 81 U/L | F6 81 U/L | 官六線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG26_81U/L | 11KV官六線(VG26) 81RY U/L | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | F7 81 U/L | F7 81 U/L | 官七線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG27_81U/L | 11KV官七線(VG27) 81RY U/L | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | F8 81 U/L | F8 81 U/L | 官八線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG28_81U/L | 11KV官八線(VG28) 81RY U/L | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | F9 81 U/L | F9 81 U/L | 官九線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG29_81U/L | 11KV官九線(VG29) 81RY U/L | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | F10 81 U/L | F10 81 U/L | 官十線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG30_81U/L | 11KV官十線(VG30) 81RY U/L | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | F11 81 U/L | F11 81 U/L | 官忠線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG31_81U/L | 11KV官忠線(VG31) 81RY U/L | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | F12 81 U/L | F12 81 U/L | 官孝線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG32_81U/L | 11KV官孝線(VG32) 81RY U/L | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | F13 81 U/L | F13 81 U/L | 官仁線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG33_81U/L | 11KV官仁線(VG33) 81RY U/L | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | F14 81 U/L | F14 81 U/L | 官愛線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG34_81U/L | 11KV官愛線(VG34) 81RY U/L | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | F15 81 U/L | F15 81 U/L | 官信線 81RY使用/閉鎖 |  |  | B2/S40_D1 | [8 empty] | 官田SS.VG35_81U/L | 11KV官信線(VG35) 81RY U/L | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 521 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 522 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | E1 | 3M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 523 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG31_DS | VG31_DS (非取樣點) | FEEDER | [5 empty] | 524 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG32_DS | VG32_DS (非取樣點) | FEEDER | [5 empty] | 525 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG33_DS | VG33_DS (非取樣點) | FEEDER | [5 empty] | 526 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG34_DS | VG34_DS (非取樣點) | FEEDER | [5 empty] | 527 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG35_DS | VG35_DS (非取樣點) | FEEDER | [5 empty] | 528 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M3 | #3MTR(M3) |  | D1 | 3M_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 529 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG21 | 官二線(VG22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG21_DS | VG21_DS (非取樣點) | FEEDER | [5 empty] | 530 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG22 | 官三線(VG23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG22_DS | VG22_DS (非取樣點) | FEEDER | [5 empty] | 531 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG23 | 官正線(VG24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG23_DS | VG23_DS (非取樣點) | FEEDER | [5 empty] | 532 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG24 | 官五線(VG25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG24_DS | VG24_DS (非取樣點) | FEEDER | [5 empty] | 533 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG25 | 官六線(VG26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG25_DS | VG25_DS (非取樣點) | FEEDER | [5 empty] | 534 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG26 | 官七線(VG27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG26_DS | VG26_DS (非取樣點) | FEEDER | [5 empty] | 535 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG27 | 官八線(VG28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG27_DS | VG27_DS (非取樣點) | FEEDER | [5 empty] | 536 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG28 | 官九線(VG29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG28_DS | VG28_DS (非取樣點) | FEEDER | [5 empty] | 537 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG29 | 官十線(VG30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG29_DS | VG29_DS (非取樣點) | FEEDER | [5 empty] | 538 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG30 | 官忠線(VG31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.VG30_DS | VG30_DS (非取樣點) | FEEDER | [5 empty] | 539 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 540 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | 2M_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 541 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | D1 | 2MA_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 542 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | D1 | 2MB_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 543 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | E1 | 2MA_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 544 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | E1 | 2MB_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 545 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | 101E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.101E | 101E (非取樣點) | TIE | [5 empty] | 546 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E2 | 102E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.102E | 102E (非取樣點) | TIE | [5 empty] | 547 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | 201E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.201E | 201E (非取樣點) | TIE | [5 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | 202E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S40_D1 | [8 empty] | 官田SS.202E | 202E (非取樣點) | TIE | [5 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 11B1E | 11B1E |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aafb | B2/S40_D1 | [8 empty] | 官田SS.11B1E | 11B1E (非取樣點) | BUS | [5 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 11B2E | 11B2E |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2ABUS | [13 empty] | abdb | B2/S40_D1 | [8 empty] | 官田SS.11B2E | 11B2E (非取樣點) | BUS | [5 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 11B2BE | 11B2BE |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BBUS | [13 empty] | acdb | B2/S40_D1 | [8 empty] | 官田SS.11B2BE | 11B2BE (非取樣點) | BUS | [5 empty] | 552 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 11B3E | 11B3E |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/3BUS | [13 empty] | adbb | B2/S40_D1 | [8 empty] | 官田SS.11B3E | 11B3E (非取樣點) | BUS | [5 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2 MCB(A) BUS | KV | 二號 BUS (A)PT | kV_-9_9(-2000_2000) | aca | B2/S40_D1 | [8 empty] | 官田SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S40 | 官田SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S40_D1 | [12 empty] | 官田SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S40/69/1BUS/V
S40 | 官田SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S40_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S40/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S40 | 官田SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S40_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_7 | OPRD1: S40/11/M1/MW; OPRD2: S40/11/M3/MW; OPRD3: S40/69/610/MW; OPRD4: S40/69/620/MW; OPRD5: S40/69/630/MW; OPRD6: S40/69/640/MW; OPRD7: S40/69/660/MW
S40 | 官田SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S40_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S40/0/CalcPoint/OPRN2_MW
S40 | 官田SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S40_D1 | [17 empty] | none
S40 | 官田SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S40_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S40/0/CalcPoint/OPRN1; OPRD2: S40/0/CalcPoint/OPRN2; OPRD3: S40/0/CalcPoint/PRFL_UL
S40 | 官田SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S40_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S40/11/M1/MW; OPRD2: S40/11/M1/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S40_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S40/11/M3/MW; OPRD2: S40/11/M3/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 69 | 69kV | 610 | 預備線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.610_AMP | 備用線 AMP | LINE69 | AMP_CAL | C12R0905 | amp_cal | OPRD1: S40/69/610/MW; OPRD2: S40/69/610/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 69 | 69kV | 620 | 官田～台汽官、大統益線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.620_AMP | 官田台汽官線 AMP | LINE69 | AMP_CAL | C10R0641 | amp_cal | OPRD1: S40/69/620/MW; OPRD2: S40/69/620/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 69 | 69kV | 630 | 官田～隆田一路(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.630_AMP | 官田隆田一路 AMP | LINE69 | AMP_CAL | C10R0983 | amp_cal | OPRD1: S40/69/630/MW; OPRD2: S40/69/630/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 69 | 69kV | 640 | 官田～隆田二路(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.640_AMP | 官田隆田二路 AMP | LINE69 | AMP_CAL | C10R0983 | amp_cal | OPRD1: S40/69/640/MW; OPRD2: S40/69/640/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 69 | 69kV | 660 | 新營～官田二路(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.660_AMP | 新營二路 AMP | LINE69 | AMP_CAL | C12R0905 | amp_cal | OPRD1: S40/69/660/MW; OPRD2: S40/69/660/MVAR; OPRD3: S40/0/CalcPoint/Vbs1
S40 | 官田SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S40_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S40/11/1BUS/V
S40 | 官田SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S40_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S40/11/2BUS/V
S40 | 官田SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S40_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S40/11/3BUS/V
S40 | 官田SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S40_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 官田SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S40/11/M1/MW; OPRD2: S40/11/M1/MVAR
S40 | 官田SS |  |  | 2MTR(A) | #2MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S40_D1 | LG_15 | 14.25 | 16.5 | 18.75 | 30 |  | -14.25 | -16.5 | -18.75 | -30 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S40/11/M2A/MW; OPRD2: S40/11/M2A/MVAR
S40 | 官田SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S40_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 官田SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S40/11/M3/MW; OPRD2: S40/11/M3/MVAR
S40 | 官田SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S40_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S40//1MTR/MVA; OPRD2: 0
S40 | 官田SS |  |  | 2MTR(A) | #2MTR(A) |  | LOAD | [9 empty] | B1/S40_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S40//2MTR(A)/MVA; OPRD2: 0
S40 | 官田SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S40_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S40//3MTR/MVA; OPRD2: 0
S40 | 官田SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S40_D1 | [12 empty] | 官田SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S40/11/M1/MW; OPRD2: S40/11/M1/MVAR
S40 | 官田SS |  |  | 2MTR(A) | #2MTR(A) |  | PF | [9 empty] | B1/S40_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S40/11/M2A/MW; OPRD2: S40/11/M2A/MVAR
S40 | 官田SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S40_D1 | [12 empty] | 官田SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S40/11/M3/MW; OPRD2: S40/11/M3/MVAR
S40 | 官田SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S40_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S40//1MTR/SupLocal; OPRD2: S40//1MTR/Tap Chan; OPRD3: NULL
S40 | 官田SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S40_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S40//2MTR/SupLocal; OPRD2: S40//2MTR/Tap Chan; OPRD3: NULL
S40 | 官田SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S40_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S40//3MTR/SupLocal; OPRD2: S40//3MTR/Tap Chan; OPRD3: NULL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/1BUS/V; OPRD2: S40/11/VG21/I_R; OPRD3: S40/11/VG21/I_S; OPRD4: S40/11/VG21/I_T
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/1BUS/V; OPRD2: S40/11/VG22/I_R; OPRD3: S40/11/VG22/I_S; OPRD4: S40/11/VG22/I_T
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/1BUS/V; OPRD2: S40/11/VG23/I_R; OPRD3: S40/11/VG23/I_S; OPRD4: S40/11/VG23/I_T
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/1BUS/V; OPRD2: S40/11/VG24/I_R; OPRD3: S40/11/VG24/I_S; OPRD4: S40/11/VG24/I_T
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/1BUS/V; OPRD2: S40/11/VG25/I_R; OPRD3: S40/11/VG25/I_S; OPRD4: S40/11/VG25/I_T
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S40/11/VG26/I_R; OPRD3: S40/11/VG26/I_S; OPRD4: S40/11/VG26/I_T
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S40/11/VG27/I_R; OPRD3: S40/11/VG27/I_S; OPRD4: S40/11/VG27/I_T
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S40/11/VG28/I_R; OPRD3: S40/11/VG28/I_S; OPRD4: S40/11/VG28/I_T
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S40/11/VG29/I_R; OPRD3: S40/11/VG29/I_S; OPRD4: S40/11/VG29/I_T
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S40/11/VG30/I_R; OPRD3: S40/11/VG30/I_S; OPRD4: S40/11/VG30/I_T
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/3BUS/V; OPRD2: S40/11/VG31/I_R; OPRD3: S40/11/VG31/I_S; OPRD4: S40/11/VG31/I_T
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/3BUS/V; OPRD2: S40/11/VG32/I_R; OPRD3: S40/11/VG32/I_S; OPRD4: S40/11/VG32/I_T
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/3BUS/V; OPRD2: S40/11/VG33/I_R; OPRD3: S40/11/VG33/I_S; OPRD4: S40/11/VG33/I_T
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/3BUS/V; OPRD2: S40/11/VG34/I_R; OPRD3: S40/11/VG34/I_S; OPRD4: S40/11/VG34/I_T
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S40/11/3BUS/V; OPRD2: S40/11/VG35/I_R; OPRD3: S40/11/VG35/I_S; OPRD4: S40/11/VG35/I_T
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG21/kVA; OPRD2: S40/11/VG21/KVAR
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG22/kVA; OPRD2: S40/11/VG22/KVAR
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG23/kVA; OPRD2: S40/11/VG23/KVAR
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG24/kVA; OPRD2: S40/11/VG24/KVAR
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG25/kVA; OPRD2: S40/11/VG25/KVAR
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG26/kVA; OPRD2: S40/11/VG26/KVAR
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG27/kVA; OPRD2: S40/11/VG27/KVAR
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG28/kVA; OPRD2: S40/11/VG28/KVAR
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG29/kVA; OPRD2: S40/11/VG29/KVAR
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG30/kVA; OPRD2: S40/11/VG30/KVAR
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG31/kVA; OPRD2: S40/11/VG31/KVAR
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG32/kVA; OPRD2: S40/11/VG32/KVAR
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG33/kVA; OPRD2: S40/11/VG33/KVAR
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG34/kVA; OPRD2: S40/11/VG34/KVAR
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S40_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S40/11/VG35/kVA; OPRD2: S40/11/VG35/KVAR
S40 | 官田SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S40_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S40/11/M1/MW; OPRD2: S40/11/M3/MW
S40 | 官田SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S40_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S40/11/M1/MVAR; OPRD2: S40/11/M3/MVAR
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S40_D1 | [12 empty] | 官田SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S40/11/210/CB; OPRD2: 6.9; OPRD3: 0
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S40_D1 | [12 empty] | 官田SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S40/11/220/CB; OPRD2: 6.9; OPRD3: 0
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S40_D1 | [12 empty] | 官田SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S40/11/230/CB; OPRD2: 6.9; OPRD3: 0
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S40_A1 | [12 empty] | 官田SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S40/69/810/CB; OPRD2: 69; OPRD3: 0
S40 | 官田SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S40_D1 | [12 empty] | 官田SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_24 | OPRD1: S40//1MTR/63Q; OPRD2: S40//1MTR/96PA; OPRD3: S40//1MTR/TRA; OPRD4: S40//1MTR/96D; OPRD5: S40//1MTR/96B2; OPRD6: S40//1MTR/96B1; OPRD7: S40//1MTR/51ZA; OPRD8: S40//1MTR/87A; OPRD9: S40//2MTR/51ZA; OPRD10: S40//2MTR/63Q; OPRD11: S40//2MTR/96D; OPRD12: S40//2MTR/96B2; OPRD13: S40//2MTR/96B1; OPRD14: S40//2MTR/96PA; OPRD15: S40//2MTR/TRA; OPRD16: S40//2MTR/87A; OPRD17: S40//3MTR/96B2; OPRD18: S40//3MTR/96B1; OPRD19: S40//3MTR/63Q; OPRD20: S40//3MTR/96D; OPRD21: S40//3MTR/87A; OPRD22: S40//3MTR/51ZA; OPRD23: S40//3MTR/96PA; OPRD24: S40//3MTR/TRA
S40 | 官田SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S40_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S40//1MTR/TRF; OPRD2: S40//2MTR/TRF; OPRD3: S40//3MTR/TRF
S40 | 官田SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/RTU/RTU_R_L
S40 | 官田SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/StaDev/PSA
S40 | 官田SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/StaDev/PSF
S40 | 官田SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/StaDev/DCA
S40 | 官田SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/StaDev/DCE
S40 | 官田SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S40_D1 | [17 empty] | lamp2CC | OPRD1: S40/69/ComPoint/CBA
S40 | 官田SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S40_D1 | [17 empty] | lamp2CC | OPRD1: S40/69/ComPoint/CBF
S40 | 官田SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S40_D1 | [17 empty] | lamp2CC | OPRD1: S40/69/ComPoint/ABS_89A
S40 | 官田SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S40_A1 | [17 empty] | lamp2CC | OPRD1: S40/0/StaDev/PMA
S40 | 官田SS | 69 | 69kV | ComPoint_D1 |  |  | 81A_RYFA |  |  | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP |  | B3/S40_D1 | [17 empty] | lamp2CC | OPRD1: S40/69/ComPoint/81A_RYFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S40 | 官田SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 官田SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S40/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 官田SS.610_AMP | 備用線 AMP | LINE69 | S40/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0905 | 814.500000 | 814.500000 | 905.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 官田SS.620_AMP | 官田台汽官線 AMP | LINE69 | S40/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C10R0641 | 576.000000 | 576.000000 | 641.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 官田SS.630_AMP | 官田隆田一路 AMP | LINE69 | S40/69/630/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C10R0983 | 884.700012 | 884.700012 | 983.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | I | [25 empty] | ADCS_N | [8 empty] | 官田SS.660_AMP | 新營二路 AMP | LINE69 | S40/69/660/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C12R0905 | 814.500000 | 814.500000 | 905.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S40 | 官田SS | 0 |  |  |  |  | 官一線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官一線KVA | 11KV官一線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官一線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官一線KW | 11KV官一線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官七線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官七線KVA | 11KV官七線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官七線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官七線KW | 11KV官七線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官九線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官九線KVA | 11KV官九線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官九線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官九線KW | 11KV官九線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官二線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官二線KVA | 11KV官二線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官二線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官二線KW | 11KV官二線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官八線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官八線KVA | 11KV官八線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官八線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官八線KW | 11KV官八線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官十線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官十線KVA | 11KV官十線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官十線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官十線KW | 11KV官十線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官三線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官三線KVA | 11KV官三線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官三線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官三線KW | 11KV官三線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官五線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官五線KVA | 11KV官五線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官五線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官五線KW | 11KV官五線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官仁線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官仁線KVA | 11KV官仁線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官仁線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官仁線KW | 11KV官仁線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官六線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官六線KVA | 11KV官六線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官六線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官六線KW | 11KV官六線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官正線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官正線KVA | 11KV官正線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官正線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官正線KW | 11KV官正線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官孝線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官孝線KVA | 11KV官孝線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官孝線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官孝線KW | 11KV官孝線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官忠線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官忠線KVA | 11KV官忠線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官忠線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官忠線KW | 11KV官忠線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官信線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官信線KVA | 11KV官信線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官信線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官信線KW | 11KV官信線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官愛線KVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官愛線KVA | 11KV官愛線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  |  |  |  | 官愛線KW | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.官愛線KW | 11KV官愛線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S40//1MTR/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_PF | #1MTR 功率因素 | DTR | S40//1MTR/PF |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S40//3MTR/MVA |  | MVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_PF | #3MTR 功率因素 | DTR | S40//3MTR/PF |  | RPDC_PF_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S40 | 官田SS | 11 | 11kV | 210_SC | #1SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S40/11/210/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 11 | 11kV | 220_SC | #2SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S40/11/220/MVAR |  | SC_CAL_11 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 11 | 11kV | 230_SC | #3SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S40/11/230/MVAR |  | SC_CAL_11 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 69 | 69kV | 810_SC | #1SC | 14.4 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S40/69/810/MVAR |  | SC_CAL_69 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 官田SS.640_AMP | 官田隆田二路 AMP | LINE69 | S40/69/640/I |  | AMP_CAL |  |  | 47 | CalcAIPoint | [21 empty] | C10R0983 | 884.700012 | 884.700012 | 983.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S40 | 官田SS | 69 | 69kV | 610_CB | 備用線(610_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.610_CB_3 | 610(備用線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 48 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 620_CB | 官田台汽官線(620_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.620_CB_3 | 620(官田台汽官線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 49 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 630_CB | 官田隆田一路(630_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.630_CB_3 | 630(官田隆田一路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 50 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 660_CB | 新營二路(660_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.660_CB_3 | 660(新營二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 51 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.810_CB_3 | 810(69KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 52 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | _CBA | _CBA | [27 empty] | ADCS_N | [8 empty] | 官田SS.69KV_CBA_A | 69KV斷路器重故障(AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 53 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 官田SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 54 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | RTU_S_L | RTU | [27 empty] | ADCS_N | [8 empty] | 官田SS.RTU_S/L_A | RTU SUPY/LOCAL (AD) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 55 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S40 | 官田SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 官田SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S40/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 57 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | STATION_FAULT_3 |  |  | 58 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610_AMP | 備用線 | [27 empty] | ADCS_N | [8 empty] | 官田SS.610_AMP_A | 備用線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 610_AMP | 備用線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.610_AMP_3 | 備用線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 620_AMP | 官田台汽官線 | [27 empty] | ADCS_N | [8 empty] | 官田SS.620_AMP_A | 官田台汽官線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 620_AMP | 官田台汽官線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.620_AMP_3 | 官田台汽官線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 630_AMP | 官田隆田一路 | [27 empty] | ADCS_N | [8 empty] | 官田SS.630_AMP_A | 官田隆田一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 630_AMP | 官田隆田一路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.630_AMP_3 | 官田隆田一路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 660_AMP | 新營二路 | [27 empty] | ADCS_N | [8 empty] | 官田SS.660_AMP_A | 新營二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 660_AMP | 新營二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.660_AMP_3 | 新營二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 66 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 1MTR_MVA | #1MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_MVA_3 | #1MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 68 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 2MTR_MVA | #2MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_MVA_3 | #2MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 69 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 70 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 3MTR_MVA | #3MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_MVA_3 | #3MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 71 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 640_AMP | 官田隆田二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.640_AMP_3 | 官田隆田二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 73 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S40 | 官田SS | 69 | 69kV | 640_CB | 官田隆田二路(640_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.640_CB_3 | 640(官田隆田二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 官田SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 75 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 630_87CFA | 630 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.630_87CFA_3 | 630 87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 76 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 630_RYFA | 630 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.630_RYFA_3 | 630 數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 77 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 660_87CFA | 660 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.660_87CFA_3 | 660 87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 78 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 660_RYFA | 660 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.660_RYFA_3 | 660 數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 79 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | SC警報 | SC警報 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.69KVSC警報_3 | 69KVSC警報 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 80 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S40/0/RTU/ADCH1 |  |  |  | CDC | 81 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S40/0/RTU/ADCH2 |  |  |  | CDC | 82 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S40/0/RTU/ADCH3 |  |  |  | CDC | 83 | GENERICAIPoint | SS300_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S40/0/RTU/ADCL1 |  |  |  | CDC | 84 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S40/0/RTU/ADCL2 |  |  |  | CDC | 85 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S40/0/RTU/ADCL3 |  |  |  | CDC | 86 | GENERICAIPoint | SS300_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S40 | 官田SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S40/69/1BUS/V |  |  |  | CDC | 87 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S40 | 官田SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S40/11/1BUS/V |  |  |  | CDC | 88 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S40/11/2BUS/V |  |  |  | CDC | 89 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S40/11/3BUS/V |  |  |  | CDC | 90 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.610_MW | 備用線 MW | LINE69 | S40/69/610/MW |  |  |  | CDC | 91 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.610_MVAR | 備用線 MVAR | LINE69 | S40/69/610/MVAR |  |  |  | CDC | 92 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.620_MW | 官田台汽官線 MW | LINE69 | S40/69/620/MW |  |  |  | CDC | 93 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.620_MVAR | 官田台汽官線 MVAR | LINE69 | S40/69/620/MVAR |  |  |  | CDC | 94 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.630_MW | 官田隆田一路 MW | LINE69 | S40/69/630/MW |  |  |  | CDC | 95 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.630_MVAR | 官田隆田一路 MVAR | LINE69 | S40/69/630/MVAR |  |  |  | CDC | 96 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.660_MW | 新營二路 MW | LINE69 | S40/69/660/MW |  |  |  | CDC | 97 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.660_MVAR | 新營二路 MVAR | LINE69 | S40/69/660/MVAR |  |  |  | CDC | 98 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官一線 | 官一線 |  | 官一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官一線KVAR | 11KV官一線 KVAR | FEEDER | S40/11/VG21/KVAR |  |  |  | CDC | 99 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官一線 | 官一線 |  | 官一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官一線A1 | 11KV官一線 R相AMP | FEEDER | S40/11/VG21/I_R |  |  |  | CDC | 100 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官一線 | 官一線 |  | 官一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官一線A2 | 11KV官一線 S相AMP | FEEDER | S40/11/VG21/I_S |  |  |  | CDC | 101 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官一線 | 官一線 |  | 官一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官一線A3 | 11KV官一線 T相AMP | FEEDER | S40/11/VG21/I_T |  |  |  | CDC | 102 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官一線 | 官一線 |  | 官一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官一線A0 | 11KV官一線 N相AMP | FEEDER | S40/11/VG21/I_N |  |  |  | CDC | 103 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官七線 | 官七線 |  | 官七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官七線KVAR | 11KV官七線 KVAR | FEEDER | S40/11/VG27/KVAR |  |  |  | CDC | 104 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官七線 | 官七線 |  | 官七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官七線A1 | 11KV官七線 R相AMP | FEEDER | S40/11/VG27/I_R |  |  |  | CDC | 105 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官七線 | 官七線 |  | 官七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官七線A2 | 11KV官七線 S相AMP | FEEDER | S40/11/VG27/I_S |  |  |  | CDC | 106 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官七線 | 官七線 |  | 官七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官七線A3 | 11KV官七線 T相AMP | FEEDER | S40/11/VG27/I_T |  |  |  | CDC | 107 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官七線 | 官七線 |  | 官七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官七線A0 | 11KV官七線 N相AMP | FEEDER | S40/11/VG27/I_N |  |  |  | CDC | 108 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官九線 | 官九線 |  | 官九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官九線KVAR | 11KV官九線 KVAR | FEEDER | S40/11/VG29/KVAR |  |  |  | CDC | 109 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官九線 | 官九線 |  | 官九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官九線A1 | 11KV官九線 R相AMP | FEEDER | S40/11/VG29/I_R |  |  |  | CDC | 110 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官九線 | 官九線 |  | 官九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官九線A2 | 11KV官九線 S相AMP | FEEDER | S40/11/VG29/I_S |  |  |  | CDC | 111 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官九線 | 官九線 |  | 官九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官九線A3 | 11KV官九線 T相AMP | FEEDER | S40/11/VG29/I_T |  |  |  | CDC | 112 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官九線 | 官九線 |  | 官九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官九線A0 | 11KV官九線 N相AMP | FEEDER | S40/11/VG29/I_N |  |  |  | CDC | 113 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官二線 | 官二線 |  | 官二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官二線KVAR | 11KV官二線 KVAR | FEEDER | S40/11/VG22/KVAR |  |  |  | CDC | 114 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官二線 | 官二線 |  | 官二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官二線A1 | 11KV官二線 R相AMP | FEEDER | S40/11/VG22/I_R |  |  |  | CDC | 115 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官二線 | 官二線 |  | 官二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官二線A2 | 11KV官二線 S相AMP | FEEDER | S40/11/VG22/I_S |  |  |  | CDC | 116 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官二線 | 官二線 |  | 官二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官二線A3 | 11KV官二線 T相AMP | FEEDER | S40/11/VG22/I_T |  |  |  | CDC | 117 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官二線 | 官二線 |  | 官二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官二線A0 | 11KV官二線 N相AMP | FEEDER | S40/11/VG22/I_N |  |  |  | CDC | 118 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官八線 | 官八線 |  | 官八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官八線KVAR | 11KV官八線 KVAR | FEEDER | S40/11/VG28/KVAR |  |  |  | CDC | 119 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官八線 | 官八線 |  | 官八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官八線A1 | 11KV官八線 R相AMP | FEEDER | S40/11/VG28/I_R |  |  |  | CDC | 120 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官八線 | 官八線 |  | 官八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官八線A2 | 11KV官八線 S相AMP | FEEDER | S40/11/VG28/I_S |  |  |  | CDC | 121 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官八線 | 官八線 |  | 官八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官八線A3 | 11KV官八線 T相AMP | FEEDER | S40/11/VG28/I_T |  |  |  | CDC | 122 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官八線 | 官八線 |  | 官八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官八線A0 | 11KV官八線 N相AMP | FEEDER | S40/11/VG28/I_N |  |  |  | CDC | 123 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官十線 | 官十線 |  | 官十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官十線KVAR | 11KV官十線 KVAR | FEEDER | S40/11/VG30/KVAR |  |  |  | CDC | 124 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官十線 | 官十線 |  | 官十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官十線A1 | 11KV官十線 R相AMP | FEEDER | S40/11/VG30/I_R |  |  |  | CDC | 125 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官十線 | 官十線 |  | 官十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官十線A2 | 11KV官十線 S相AMP | FEEDER | S40/11/VG30/I_S |  |  |  | CDC | 126 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官十線 | 官十線 |  | 官十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官十線A3 | 11KV官十線 T相AMP | FEEDER | S40/11/VG30/I_T |  |  |  | CDC | 127 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官十線 | 官十線 |  | 官十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官十線A0 | 11KV官十線 N相AMP | FEEDER | S40/11/VG30/I_N |  |  |  | CDC | 128 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官三線 | 官三線 |  | 官三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官三線KVAR | 11KV官三線 KVAR | FEEDER | S40/11/VG23/KVAR |  |  |  | CDC | 129 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官三線 | 官三線 |  | 官三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官三線A1 | 11KV官三線 R相AMP | FEEDER | S40/11/VG23/I_R |  |  |  | CDC | 130 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官三線 | 官三線 |  | 官三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官三線A2 | 11KV官三線 S相AMP | FEEDER | S40/11/VG23/I_S |  |  |  | CDC | 131 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官三線 | 官三線 |  | 官三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官三線A3 | 11KV官三線 T相AMP | FEEDER | S40/11/VG23/I_T |  |  |  | CDC | 132 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官三線 | 官三線 |  | 官三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官三線A0 | 11KV官三線 N相AMP | FEEDER | S40/11/VG23/I_N |  |  |  | CDC | 133 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官五線 | 官五線 |  | 官五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官五線KVAR | 11KV官五線 KVAR | FEEDER | S40/11/VG25/KVAR |  |  |  | CDC | 134 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官五線 | 官五線 |  | 官五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官五線A1 | 11KV官五線 R相AMP | FEEDER | S40/11/VG25/I_R |  |  |  | CDC | 135 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官五線 | 官五線 |  | 官五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官五線A2 | 11KV官五線 S相AMP | FEEDER | S40/11/VG25/I_S |  |  |  | CDC | 136 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官五線 | 官五線 |  | 官五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官五線A3 | 11KV官五線 T相AMP | FEEDER | S40/11/VG25/I_T |  |  |  | CDC | 137 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官五線 | 官五線 |  | 官五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官五線A0 | 11KV官五線 N相AMP | FEEDER | S40/11/VG25/I_N |  |  |  | CDC | 138 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官仁線 | 官仁線 |  | 官仁線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官仁線KVAR | 11KV官仁線 KVAR | FEEDER | S40/11/VG33/KVAR |  |  |  | CDC | 139 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官仁線 | 官仁線 |  | 官仁線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官仁線A1 | 11KV官仁線 R相AMP | FEEDER | S40/11/VG33/I_R |  |  |  | CDC | 140 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官仁線 | 官仁線 |  | 官仁線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官仁線A2 | 11KV官仁線 S相AMP | FEEDER | S40/11/VG33/I_S |  |  |  | CDC | 141 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官仁線 | 官仁線 |  | 官仁線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官仁線A3 | 11KV官仁線 T相AMP | FEEDER | S40/11/VG33/I_T |  |  |  | CDC | 142 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官仁線 | 官仁線 |  | 官仁線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官仁線A0 | 11KV官仁線 N相AMP | FEEDER | S40/11/VG33/I_N |  |  |  | CDC | 143 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官六線 | 官六線 |  | 官六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官六線KVAR | 11KV官六線 KVAR | FEEDER | S40/11/VG26/KVAR |  |  |  | CDC | 144 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官六線 | 官六線 |  | 官六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官六線A1 | 11KV官六線 R相AMP | FEEDER | S40/11/VG26/I_R |  |  |  | CDC | 145 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官六線 | 官六線 |  | 官六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官六線A2 | 11KV官六線 S相AMP | FEEDER | S40/11/VG26/I_S |  |  |  | CDC | 146 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官六線 | 官六線 |  | 官六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官六線A3 | 11KV官六線 T相AMP | FEEDER | S40/11/VG26/I_T |  |  |  | CDC | 147 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官六線 | 官六線 |  | 官六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官六線A0 | 11KV官六線 N相AMP | FEEDER | S40/11/VG26/I_N |  |  |  | CDC | 148 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官正線 | 官正線 |  | 官正線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官正線KVAR | 11KV官正線 KVAR | FEEDER | S40/11/VG24/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官正線 | 官正線 |  | 官正線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官正線A1 | 11KV官正線 R相AMP | FEEDER | S40/11/VG24/I_R |  |  |  | CDC | 150 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官正線 | 官正線 |  | 官正線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官正線A2 | 11KV官正線 S相AMP | FEEDER | S40/11/VG24/I_S |  |  |  | CDC | 151 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官正線 | 官正線 |  | 官正線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官正線A3 | 11KV官正線 T相AMP | FEEDER | S40/11/VG24/I_T |  |  |  | CDC | 152 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官正線 | 官正線 |  | 官正線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官正線A0 | 11KV官正線 N相AMP | FEEDER | S40/11/VG24/I_N |  |  |  | CDC | 153 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官孝線 | 官孝線 |  | 官孝線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官孝線KVAR | 11KV官孝線 KVAR | FEEDER | S40/11/VG32/KVAR |  |  |  | CDC | 154 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官孝線 | 官孝線 |  | 官孝線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官孝線A1 | 11KV官孝線 R相AMP | FEEDER | S40/11/VG32/I_R |  |  |  | CDC | 155 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官孝線 | 官孝線 |  | 官孝線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官孝線A2 | 11KV官孝線 S相AMP | FEEDER | S40/11/VG32/I_S |  |  |  | CDC | 156 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官孝線 | 官孝線 |  | 官孝線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官孝線A3 | 11KV官孝線 T相AMP | FEEDER | S40/11/VG32/I_T |  |  |  | CDC | 157 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官孝線 | 官孝線 |  | 官孝線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官孝線A0 | 11KV官孝線 N相AMP | FEEDER | S40/11/VG32/I_N |  |  |  | CDC | 158 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官忠線 | 官忠線 |  | 官忠線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官忠線KVAR | 11KV官忠線 KVAR | FEEDER | S40/11/VG31/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官忠線 | 官忠線 |  | 官忠線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官忠線A1 | 11KV官忠線 R相AMP | FEEDER | S40/11/VG31/I_R |  |  |  | CDC | 160 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官忠線 | 官忠線 |  | 官忠線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官忠線A2 | 11KV官忠線 S相AMP | FEEDER | S40/11/VG31/I_S |  |  |  | CDC | 161 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官忠線 | 官忠線 |  | 官忠線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官忠線A3 | 11KV官忠線 T相AMP | FEEDER | S40/11/VG31/I_T |  |  |  | CDC | 162 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官忠線 | 官忠線 |  | 官忠線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官忠線A0 | 11KV官忠線 N相AMP | FEEDER | S40/11/VG31/I_N |  |  |  | CDC | 163 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官信線 | 官信線 |  | 官信線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官信線KVAR | 11KV官信線 KVAR | FEEDER | S40/11/VG35/KVAR |  |  |  | CDC | 164 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官信線 | 官信線 |  | 官信線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官信線A1 | 11KV官信線 R相AMP | FEEDER | S40/11/VG35/I_R |  |  |  | CDC | 165 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官信線 | 官信線 |  | 官信線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官信線A2 | 11KV官信線 S相AMP | FEEDER | S40/11/VG35/I_S |  |  |  | CDC | 166 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官信線 | 官信線 |  | 官信線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官信線A3 | 11KV官信線 T相AMP | FEEDER | S40/11/VG35/I_T |  |  |  | CDC | 167 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官信線 | 官信線 |  | 官信線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官信線A0 | 11KV官信線 N相AMP | FEEDER | S40/11/VG35/I_N |  |  |  | CDC | 168 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官愛線 | 官愛線 |  | 官愛線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官愛線KVAR | 11KV官愛線 KVAR | FEEDER | S40/11/VG34/KVAR |  |  |  | CDC | 169 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官愛線 | 官愛線 |  | 官愛線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官愛線A1 | 11KV官愛線 R相AMP | FEEDER | S40/11/VG34/I_R |  |  |  | CDC | 170 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官愛線 | 官愛線 |  | 官愛線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官愛線A2 | 11KV官愛線 S相AMP | FEEDER | S40/11/VG34/I_S |  |  |  | CDC | 171 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官愛線 | 官愛線 |  | 官愛線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官愛線A3 | 11KV官愛線 T相AMP | FEEDER | S40/11/VG34/I_T |  |  |  | CDC | 172 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | 官愛線 | 官愛線 |  | 官愛線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.官愛線A0 | 11KV官愛線 N相AMP | FEEDER | S40/11/VG34/I_N |  |  |  | CDC | 173 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S40/11/TIE1/I_R |  |  |  | CDC | 174 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S40/11/TIE1/I_S |  |  |  | CDC | 175 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S40/11/TIE1/I_T |  |  |  | CDC | 176 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S40/11/TIE2/I_R |  |  |  | CDC | 177 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S40/11/TIE2/I_S |  |  |  | CDC | 178 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S40/11/TIE2/I_T |  |  |  | CDC | 179 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_MW | #1MTR二次側 MW | DTR | S40/11/M1/MW |  |  |  | CDC | 180 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S40/11/M1/MVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S40/11/M1/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S40/11/M1/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S40/11/M1/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_OIL | #1MTR 油溫 | DTR | S40//1MTR/OilTemp |  |  |  | CDC | 185 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_COIL | #1MTR 線溫 | DTR | S40//1MTR/CoilTemp |  |  |  | CDC | 186 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S40//1MTR/TapPosMv |  |  |  | CDC | 187 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_MW | #2MTR二次側 MW | DTR | S40/11/M2A/MW |  |  |  | CDC | 188 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S40/11/M2A/MVAR |  |  |  | CDC | 189 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S40/11/M2A/I_R |  |  |  | CDC | 190 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S40/11/M2A/I_S |  |  |  | CDC | 191 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S40/11/M2A/I_T |  |  |  | CDC | 192 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_OIL | #2MTR 油溫 | DTR | S40//2MTR/OilTemp |  |  |  | CDC | 193 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_COIL | #2MTR 線溫 | DTR | S40//2MTR/CoilTemp |  |  |  | CDC | 194 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S40//2MTR/TapPosMv |  |  |  | CDC | 195 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_MW | #3MTR二次側 MW | DTR | S40/11/M3/MW |  |  |  | CDC | 196 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S40/11/M3/MVAR |  |  |  | CDC | 197 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S40/11/M3/I_R |  |  |  | CDC | 198 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S40/11/M3/I_S |  |  |  | CDC | 199 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S40/11/M3/I_T |  |  |  | CDC | 200 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_OIL | #3MTR 油溫 | DTR | S40//3MTR/OilTemp |  |  |  | CDC | 201 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_COIL | #3MTR 線溫 | DTR | S40//3MTR/CoilTemp |  |  |  | CDC | 202 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 官田SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S40//3MTR/TapPosMv |  |  |  | CDC | 203 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S40 | 官田SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS3_2 | [8 empty] | 官田SS.直流電源電壓 | 直流電源電壓 | OTHER | S40/0/StaDev/DCV |  |  |  | CDC | 204 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.640_MW | 官田隆田二路 MW | LINE69 | S40/69/640/MW |  |  |  | CDC | 205 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 官田SS.640_MVAR | 官田隆田二路 MVAR | LINE69 | S40/69/640/MVAR |  |  |  | CDC | 206 | GENERICAIPoint | SS300_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 官田SS.610_PHA | 備用線(610) 相間RY | LINE69 | S40/69/610/PHA |  |  |  | CDC | 207 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 官田SS.610_GDA | 備用線(610) 接地RY | LINE69 | S40/69/610/GDA |  |  |  | CDC | 208 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | 85A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 官田SS.610_85A | 備用線(610) 85RY | LINE69 | S40/69/610/85A |  |  |  | CDC | 209 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | 74A | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 官田SS.610_74A | 備用線(610) 74RY | LINE69 | S40/69/610/74A |  |  |  | CDC | 210 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | 85UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 官田SS.610_85UL | 備用線(610) 85RY U/L | LINE69 | S40/69/610/85UL |  |  |  | CDC | 211 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 官田SS.610_CB | 610(備用線) CB | LINE69 | S40/69/610/CB |  |  |  | CDC | 212 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | ABS1 | 611 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 官田SS.611_ABS | 611(備用線) ABS | LINE69 | S40/69/610/DS1 |  |  |  | CDC | 213 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | ABS2 | 612 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 官田SS.612_ABS | 612(備用線) ABS | LINE69 | S40/69/610/DS2 |  |  |  | CDC | 214 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | E2 | 612E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 官田SS.612E_ES | 612E(備用線) ES | LINE69 | S40/69/610/ES2 |  |  |  | CDC | 215 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 官田SS.620_PHA | 官田台汽官線(620) 相間RY | LINE69 | S40/69/620/PHA |  |  |  | CDC | 216 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 官田SS.620_GDA | 官田台汽官線(620) 接地RY | LINE69 | S40/69/620/GDA |  |  |  | CDC | 217 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | 85A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 官田SS.620_85A | 官田台汽官線(620) 85RY | LINE69 | S40/69/620/85A |  |  |  | CDC | 218 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | 74A | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 官田SS.620_74A | 官田台汽官線(620) 74RY | LINE69 | S40/69/620/74A |  |  |  | CDC | 219 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | 85UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 官田SS.620_85UL | 官田台汽官線(620) 85RY U/L | LINE69 | S40/69/620/85UL |  |  |  | CDC | 220 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 官田SS.620_CB | 620(官田台汽官線) CB | LINE69 | S40/69/620/CB |  |  |  | CDC | 221 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | 81AS | [17 empty] | 1-00-00 |  | 1-11 | [5 empty] | 69KV_N | [8 empty] | 官田SS.620_81A/S | (620) 81RY A/S | LINE69 | S40/69/620/81AS |  |  |  | CDC | 222 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | ABS1 | 621 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 官田SS.621_ABS | 621(官田台汽官線) ABS | LINE69 | S40/69/620/DS1 |  |  |  | CDC | 223 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | ABS2 | 622 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 官田SS.622_ABS | 622(官田台汽官線) ABS | LINE69 | S40/69/620/DS2 |  |  |  | CDC | 224 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | E2 | 622E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 官田SS.622E_ES | 622E(官田台汽官線) ES | LINE69 | S40/69/620/ES2 |  |  |  | CDC | 225 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 官田SS.630_PHA | 官田隆田一路(630) 相間RY | LINE69 | S40/69/630/PHA |  |  |  | CDC | 226 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 官田SS.630_GDA | 官田隆田一路(630) 接地RY | LINE69 | S40/69/630/GDA |  |  |  | CDC | 227 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 官田SS.630_CB | 630(官田隆田一路) CB | LINE69 | S40/69/630/CB |  |  |  | CDC | 228 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | ABS1 | 631 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 官田SS.631_ABS | 631(官田隆田一路) ABS | LINE69 | S40/69/630/DS1 |  |  |  | CDC | 229 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | ABS2 | 632 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 官田SS.632_ABS | 632(官田隆田一路) ABS | LINE69 | S40/69/630/DS2 |  |  |  | CDC | 230 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | E2 | 632E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 官田SS.632E_ES | 632E(官田隆田一路) ES | LINE69 | S40/69/630/ES2 |  |  |  | CDC | 231 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 官田SS.660_PHA | 新營二路(660) 相間RY | LINE69 | S40/69/660/PHA |  |  |  | CDC | 232 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 官田SS.660_GDA | 新營二路(660) 接地RY | LINE69 | S40/69/660/GDA |  |  |  | CDC | 233 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 官田SS.660_CB | 660(新營二路) CB | LINE69 | S40/69/660/CB |  |  |  | CDC | 234 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | ABS1 | 661 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 官田SS.661_ABS | 661(新營二路) ABS | LINE69 | S40/69/660/DS1 |  |  |  | CDC | 235 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | ABS2 | 662 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 官田SS.662_ABS | 662(新營二路) ABS | LINE69 | S40/69/660/DS2 |  |  |  | CDC | 236 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | E2 | 662E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 官田SS.662E_ES | 662E(新營二路) ES | LINE69 | S40/69/660/ES2 |  |  |  | CDC | 237 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_PHA | 11KV官一線(VG21) 相間RY | FEEDER | S40/11/VG21/PHA |  |  |  | CDC | 238 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_GDA | 11KV官一線(VG21) 接地RY | FEEDER | S40/11/VG21/GDA |  |  |  | CDC | 239 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_79UL | 11KV官一線(VG21) 79RY U/L | FEEDER | S40/11/VG21/79UL |  |  |  | CDC | 240 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_ADJ | 11KV官一線(VG21) LCO分流器 U/L | FEEDER | S40/11/VG21/ADJ |  |  |  | CDC | 241 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG21 | VG21(11KV官一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_CB | VG21(11KV官一線) CB | FEEDER | S40/11/VG21/CB |  |  |  | CDC | 242 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_PHA | 11KV官二線(VG22) 相間RY | FEEDER | S40/11/VG22/PHA |  |  |  | CDC | 243 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_GDA | 11KV官二線(VG22) 接地RY | FEEDER | S40/11/VG22/GDA |  |  |  | CDC | 244 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_79UL | 11KV官二線(VG22) 79RY U/L | FEEDER | S40/11/VG22/79UL |  |  |  | CDC | 245 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_ADJ | 11KV官二線(VG22) LCO分流器 U/L | FEEDER | S40/11/VG22/ADJ |  |  |  | CDC | 246 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG22 | VG22(11KV官二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_CB | VG22(11KV官二線) CB | FEEDER | S40/11/VG22/CB |  |  |  | CDC | 247 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_PHA | 11KV官三線(VG23) 相間RY | FEEDER | S40/11/VG23/PHA |  |  |  | CDC | 248 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_GDA | 11KV官三線(VG23) 接地RY | FEEDER | S40/11/VG23/GDA |  |  |  | CDC | 249 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_79UL | 11KV官三線(VG23) 79RY U/L | FEEDER | S40/11/VG23/79UL |  |  |  | CDC | 250 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_ADJ | 11KV官三線(VG23) LCO分流器 U/L | FEEDER | S40/11/VG23/ADJ |  |  |  | CDC | 251 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG23 | VG23(11KV官三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_CB | VG23(11KV官三線) CB | FEEDER | S40/11/VG23/CB |  |  |  | CDC | 252 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_PHA | 11KV官正線(VG24) 相間RY | FEEDER | S40/11/VG24/PHA |  |  |  | CDC | 253 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_GDA | 11KV官正線(VG24) 接地RY | FEEDER | S40/11/VG24/GDA |  |  |  | CDC | 254 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_79UL | 11KV官正線(VG24) 79RY U/L | FEEDER | S40/11/VG24/79UL |  |  |  | CDC | 255 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_ADJ | 11KV官正線(VG24) LCO分流器 U/L | FEEDER | S40/11/VG24/ADJ |  |  |  | CDC | 256 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG24 | VG24(11KV官正線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_CB | VG24(11KV官正線) CB | FEEDER | S40/11/VG24/CB |  |  |  | CDC | 257 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_PHA | 11KV官五線(VG25) 相間RY | FEEDER | S40/11/VG25/PHA |  |  |  | CDC | 258 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_GDA | 11KV官五線(VG25) 接地RY | FEEDER | S40/11/VG25/GDA |  |  |  | CDC | 259 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_79UL | 11KV官五線(VG25) 79RY U/L | FEEDER | S40/11/VG25/79UL |  |  |  | CDC | 260 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_ADJ | 11KV官五線(VG25) LCO分流器 U/L | FEEDER | S40/11/VG25/ADJ |  |  |  | CDC | 261 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG25 | VG25(11KV官五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_CB | VG25(11KV官五線) CB | FEEDER | S40/11/VG25/CB |  |  |  | CDC | 262 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_PHA | 11KV官六線(VG26) 相間RY | FEEDER | S40/11/VG26/PHA |  |  |  | CDC | 263 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_GDA | 11KV官六線(VG26) 接地RY | FEEDER | S40/11/VG26/GDA |  |  |  | CDC | 264 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_79UL | 11KV官六線(VG26) 79RY U/L | FEEDER | S40/11/VG26/79UL |  |  |  | CDC | 265 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_ADJ | 11KV官六線(VG26) LCO分流器 U/L | FEEDER | S40/11/VG26/ADJ |  |  |  | CDC | 266 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG26 | VG26(11KV官六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_CB | VG26(11KV官六線) CB | FEEDER | S40/11/VG26/CB |  |  |  | CDC | 267 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_PHA | 11KV官七線(VG27) 相間RY | FEEDER | S40/11/VG27/PHA |  |  |  | CDC | 268 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_GDA | 11KV官七線(VG27) 接地RY | FEEDER | S40/11/VG27/GDA |  |  |  | CDC | 269 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_79UL | 11KV官七線(VG27) 79RY U/L | FEEDER | S40/11/VG27/79UL |  |  |  | CDC | 270 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_ADJ | 11KV官七線(VG27) LCO分流器 U/L | FEEDER | S40/11/VG27/ADJ |  |  |  | CDC | 271 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG27 | VG27(11KV官七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_CB | VG27(11KV官七線) CB | FEEDER | S40/11/VG27/CB |  |  |  | CDC | 272 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_PHA | 11KV官八線(VG28) 相間RY | FEEDER | S40/11/VG28/PHA |  |  |  | CDC | 273 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_GDA | 11KV官八線(VG28) 接地RY | FEEDER | S40/11/VG28/GDA |  |  |  | CDC | 274 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_79UL | 11KV官八線(VG28) 79RY U/L | FEEDER | S40/11/VG28/79UL |  |  |  | CDC | 275 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_ADJ | 11KV官八線(VG28) LCO分流器 U/L | FEEDER | S40/11/VG28/ADJ |  |  |  | CDC | 276 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG28 | VG28(11KV官八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_CB | VG28(11KV官八線) CB | FEEDER | S40/11/VG28/CB |  |  |  | CDC | 277 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_PHA | 11KV官九線(VG29) 相間RY | FEEDER | S40/11/VG29/PHA |  |  |  | CDC | 278 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_GDA | 11KV官九線(VG29) 接地RY | FEEDER | S40/11/VG29/GDA |  |  |  | CDC | 279 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_79UL | 11KV官九線(VG29) 79RY U/L | FEEDER | S40/11/VG29/79UL |  |  |  | CDC | 280 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_ADJ | 11KV官九線(VG29) LCO分流器 U/L | FEEDER | S40/11/VG29/ADJ |  |  |  | CDC | 281 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG29 | VG29(11KV官九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_CB | VG29(11KV官九線) CB | FEEDER | S40/11/VG29/CB |  |  |  | CDC | 282 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_PHA | 11KV官十線(VG30) 相間RY | FEEDER | S40/11/VG30/PHA |  |  |  | CDC | 283 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_GDA | 11KV官十線(VG30) 接地RY | FEEDER | S40/11/VG30/GDA |  |  |  | CDC | 284 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_79UL | 11KV官十線(VG30) 79RY U/L | FEEDER | S40/11/VG30/79UL |  |  |  | CDC | 285 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_ADJ | 11KV官十線(VG30) LCO分流器 U/L | FEEDER | S40/11/VG30/ADJ |  |  |  | CDC | 286 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG30 | VG30(11KV官十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_CB | VG30(11KV官十線) CB | FEEDER | S40/11/VG30/CB |  |  |  | CDC | 287 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_PHA | 11KV官忠線(VG31) 相間RY | FEEDER | S40/11/VG31/PHA |  |  |  | CDC | 288 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_GDA | 11KV官忠線(VG31) 接地RY | FEEDER | S40/11/VG31/GDA |  |  |  | CDC | 289 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_79UL | 11KV官忠線(VG31) 79RY U/L | FEEDER | S40/11/VG31/79UL |  |  |  | CDC | 290 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_ADJ | 11KV官忠線(VG31) LCO分流器 U/L | FEEDER | S40/11/VG31/ADJ |  |  |  | CDC | 291 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG31 | VG31(11KV官忠線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_CB | VG31(11KV官忠線) CB | FEEDER | S40/11/VG31/CB |  |  |  | CDC | 292 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_PHA | 11KV官孝線(VG32) 相間RY | FEEDER | S40/11/VG32/PHA |  |  |  | CDC | 293 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_GDA | 11KV官孝線(VG32) 接地RY | FEEDER | S40/11/VG32/GDA |  |  |  | CDC | 294 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_79UL | 11KV官孝線(VG32) 79RY U/L | FEEDER | S40/11/VG32/79UL |  |  |  | CDC | 295 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_ADJ | 11KV官孝線(VG32) LCO分流器 U/L | FEEDER | S40/11/VG32/ADJ |  |  |  | CDC | 296 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG32 | VG32(11KV官孝線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_CB | VG32(11KV官孝線) CB | FEEDER | S40/11/VG32/CB |  |  |  | CDC | 297 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_PHA | 11KV官仁線(VG33) 相間RY | FEEDER | S40/11/VG33/PHA |  |  |  | CDC | 298 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_GDA | 11KV官仁線(VG33) 接地RY | FEEDER | S40/11/VG33/GDA |  |  |  | CDC | 299 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_79UL | 11KV官仁線(VG33) 79RY U/L | FEEDER | S40/11/VG33/79UL |  |  |  | CDC | 300 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_ADJ | 11KV官仁線(VG33) LCO分流器 U/L | FEEDER | S40/11/VG33/ADJ |  |  |  | CDC | 301 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG33 | VG33(11KV官仁線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_CB | VG33(11KV官仁線) CB | FEEDER | S40/11/VG33/CB |  |  |  | CDC | 302 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_PHA | 11KV官愛線(VG34) 相間RY | FEEDER | S40/11/VG34/PHA |  |  |  | CDC | 303 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_GDA | 11KV官愛線(VG34) 接地RY | FEEDER | S40/11/VG34/GDA |  |  |  | CDC | 304 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_79UL | 11KV官愛線(VG34) 79RY U/L | FEEDER | S40/11/VG34/79UL |  |  |  | CDC | 305 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_ADJ | 11KV官愛線(VG34) LCO分流器 U/L | FEEDER | S40/11/VG34/ADJ |  |  |  | CDC | 306 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG34 | VG34(11KV官愛線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_CB | VG34(11KV官愛線) CB | FEEDER | S40/11/VG34/CB |  |  |  | CDC | 307 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_PHA | 11KV官信線(VG35) 相間RY | FEEDER | S40/11/VG35/PHA |  |  |  | CDC | 308 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_GDA | 11KV官信線(VG35) 接地RY | FEEDER | S40/11/VG35/GDA |  |  |  | CDC | 309 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_79UL | 11KV官信線(VG35) 79RY U/L | FEEDER | S40/11/VG35/79UL |  |  |  | CDC | 310 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_ADJ | 11KV官信線(VG35) LCO分流器 U/L | FEEDER | S40/11/VG35/ADJ |  |  |  | CDC | 311 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S40 | 官田SS | 11 | 11kV | VG35 | VG35(11KV官信線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_CB | VG35(11KV官信線) CB | FEEDER | S40/11/VG35/CB |  |  |  | CDC | 312 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE1_CB | 11KV TIE1 CB | TIE | S40/11/TIE1/CB |  |  |  | CDC | 313 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE1_51A | 11KV TIE1 51RY | TIE | S40/11/TIE1/51A |  |  |  | CDC | 314 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S40/11/TIE1/51NA |  |  |  | CDC | 315 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE2_CB | 11KV TIE2 CB | TIE | S40/11/TIE2/CB |  |  |  | CDC | 316 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE2_51A | 11KV TIE2 51RY | TIE | S40/11/TIE2/51A |  |  |  | CDC | 317 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S40/11/TIE2/51NA |  |  |  | CDC | 318 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.750_CB | 750(#1MTR) CB | DTR | S40/69/750/CB |  |  |  | CDC | 319 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.1M_CB | 1M(#1MTR) CB | DTR | S40/11/M1/CB |  |  |  | CDC | 320 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_51A | #1MTR 51RY | DTR | S40/69/750/51A |  |  |  | CDC | 321 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_51NA | #1MTR 51N RY | DTR | S40/69/750/51NA |  |  |  | CDC | 322 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S40//1MTR/51ZA |  |  |  | CDC | 323 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_87A | #1MTR 87RY | DTR | S40//1MTR/87A |  |  |  | CDC | 324 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S40//1MTR/87UL |  |  |  | CDC | 325 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S40/11/M1/51A |  |  |  | CDC | 326 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_TRA | #1MTR 重故障 | DTR | S40//1MTR/TRA |  |  |  | CDC | 327 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S40//1MTR/TRF |  |  |  | CDC | 328 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S40//1MTR/SupLocal |  |  |  | CDC | 329 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S40//1MTR/Tap Chan |  |  |  | CDC | 330 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.751_ABS | 751(#1MTR) ABS | DTR | S40/69/750/DS1 |  |  |  | CDC | 331 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_96A | #1MTR 96P RY | DTR | S40//1MTR/96PA |  |  |  | CDC | 332 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S40//1MTR/OLTC_DLY |  |  |  | CDC | 333 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S40//1MTR/AC_Fault |  |  |  | CDC | 334 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.760_CB | 760(#2MTR) CB | DTR | S40/69/760/CB |  |  |  | CDC | 335 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.2MA_CB | 2MA(#2MTR) CB | DTR | S40/11/M2A/CB |  |  |  | CDC | 336 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-46 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.2MB_CB | 2MB(#2MTR) CB | DTR | S40/11/M2B/CB |  |  |  | CDC | 337 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_51A | #2MTR 51RY | DTR | S40/69/760/51A |  |  |  | CDC | 338 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_51NA | #2MTR 51N RY | DTR | S40/69/760/51NA |  |  |  | CDC | 339 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S40//2MTR/51ZA |  |  |  | CDC | 340 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_87A | #2MTR 87RY | DTR | S40//2MTR/87A |  |  |  | CDC | 341 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S40//2MTR/87UL |  |  |  | CDC | 342 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S40/11/M2A/51A |  |  |  | CDC | 343 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S40/11/M2B/51A |  |  |  | CDC | 344 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_TRA | #2MTR 重故障 | DTR | S40//2MTR/TRA |  |  |  | CDC | 345 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S40//2MTR/TRF |  |  |  | CDC | 346 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S40//2MTR/SupLocal |  |  |  | CDC | 347 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S40//2MTR/Tap Chan |  |  |  | CDC | 348 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.761_ABS | 761(#2MTR) ABS | DTR | S40/69/760/DS1 |  |  |  | CDC | 349 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_96A | #2MTR 96P RY | DTR | S40//2MTR/96PA |  |  |  | CDC | 350 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S40//2MTR/OLTC_DLY |  |  |  | CDC | 351 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S40//2MTR/AC_Fault |  |  |  | CDC | 352 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.770_CB | 770(#3MTR) CB | DTR | S40/69/770/CB |  |  |  | CDC | 353 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.3M_CB | 3M(#3MTR) CB | DTR | S40/11/M3/CB |  |  |  | CDC | 354 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_51A | #3MTR 51RY | DTR | S40/69/770/51A |  |  |  | CDC | 355 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_51NA | #3MTR 51N RY | DTR | S40/69/770/51NA |  |  |  | CDC | 356 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S40//3MTR/51ZA |  |  |  | CDC | 357 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_87A | #3MTR 87RY | DTR | S40//3MTR/87A |  |  |  | CDC | 358 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S40//3MTR/87UL |  |  |  | CDC | 359 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S40/11/M3/51A |  |  |  | CDC | 360 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_TRA | #3MTR 重故障 | DTR | S40//3MTR/TRA |  |  |  | CDC | 361 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S40//3MTR/TRF |  |  |  | CDC | 362 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S40//3MTR/SupLocal |  |  |  | CDC | 363 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S40//3MTR/Tap Chan |  |  |  | CDC | 364 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.771_ABS | 771(#3MTR) ABS | DTR | S40/69/770/DS1 |  |  |  | CDC | 365 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_96A | #3MTR 96P RY | DTR | S40//3MTR/96PA |  |  |  | CDC | 366 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S40//3MTR/OLTC_DLY |  |  |  | CDC | 367 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S40//3MTR/AC_Fault |  |  |  | CDC | 368 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.210_CB | 210(11KV #1SC) CB | SC | S40/11/210/CB |  |  |  | CDC | 369 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S40/11/210/Tap Chan |  |  |  | CDC | 370 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.210_SCA | 11KV #1SC 51,51N RY | SC | S40/11/210/SCA |  |  |  | CDC | 371 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S40/11/210/UVA |  |  |  | CDC | 372 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.220_CB | 220(11KV #2SC) CB | SC | S40/11/220/CB |  |  |  | CDC | 373 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S40/11/220/Tap Chan |  |  |  | CDC | 374 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.220_SCA | 11KV #2SC 51,51N RY | SC | S40/11/220/SCA |  |  |  | CDC | 375 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S40/11/220/UVA |  |  |  | CDC | 376 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.230_CB | 230(11KV #3SC) CB | SC | S40/11/230/CB |  |  |  | CDC | 377 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S40/11/230/Tap Chan |  |  |  | CDC | 378 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.230_SCA | 11KV #3SC 51,51N RY | SC | S40/11/230/SCA |  |  |  | CDC | 379 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S40/11/230/UVA |  |  |  | CDC | 380 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 官田SS.810_CB | 810(69KV #1SC) CB | SC | S40/69/810/CB |  |  |  | CDC | 381 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 官田SS.811_ABS | 811(69KV #1SC) ABS | SC | S40/69/810/DS1 |  |  |  | CDC | 382 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 官田SS.810_SCA | 69KV #1SC 51,51N RY | SC | S40/69/810/SCA |  |  |  | CDC | 383 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 官田SS.810_OUVA | 69KV #1SC 27,59RY | SC | S40/69/810/UVA |  |  |  | CDC | 384 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 官田SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S40/69/1BUS/BUS_VUA |  |  |  | CDC | 385 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S40/11/ComPoint/CBA |  |  |  | CDC | 386 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S40/11/ComPoint/CBF |  |  |  | CDC | 387 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S40/69/ComPoint/ABS_89A |  |  |  | CDC | 388 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S40/69/ComPoint/CBA |  |  |  | CDC | 389 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S40/69/ComPoint/CBF |  |  |  | CDC | 390 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S40/0/RTU/RTU_R_L |  |  |  | CDC | 391 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S40 | 官田SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.TEST_CB | TEST CB | OTHER | S40/0/RTU/Test_CB |  |  |  | CDC | 392 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-31-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.火災警報(1) | CO2警報 | OTHER | S40/0/StaDev/Fire1 |  |  |  | CDC | 393 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.火災警報(2) | CO2故障 | OTHER | S40/0/StaDev/Fire2 |  |  |  | CDC | 394 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-30-10 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.火災警報(3) | 火災警報(3) | OTHER | S40/0/StaDev/Fire3 |  |  |  | CDC | 395 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.其他重故障 | 變電所內其他重故障 | OTHER | S40/0/StaDev/PSA |  |  |  | CDC | 396 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S40/0/StaDev/PSF |  |  |  | CDC | 397 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S40/0/StaDev/STUV |  |  |  | CDC | 398 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S40/0/StaDev/CHG1 |  |  |  | CDC | 399 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.直流電源DCA | NFB跳脫監視 | OTHER | S40/0/StaDev/DCA |  |  |  | CDC | 400 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S40/0/StaDev/DCE |  |  |  | CDC | 401 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S40/0/StaDev/OilLeak |  |  |  | CDC | 402 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S40/0/StaDev/CHG2 |  |  |  | CDC | 403 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化防盜(1) | 水氣霧警報 | OTHER | S40/0/StaDev/Burglar1 |  |  |  | CDC | 404 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化防盜(2) | 水氣霧故障 | OTHER | S40/0/StaDev/Burglar2 |  |  |  | CDC | 405 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化防盜(3) | MCSG偵煙警報 | OTHER | S40/0/StaDev/Burglar3 |  |  |  | CDC | 406 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化門禁(1) | 水氣霧釋放 | OTHER | S40/0/StaDev/Door1 |  |  |  | CDC | 407 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化門禁(2) | 所內淹水高水位 | OTHER | S40/0/StaDev/Door2 |  |  |  | CDC | 408 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.無人化門禁(3) | 所內淹水低水位 | OTHER | S40/0/StaDev/Door3 |  |  |  | CDC | 409 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.開關場照明(A) | 開關場照明(A) | OTHER | S40/0/StaDev/Lights1 |  |  |  | CDC | 410 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S40 | 官田SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.開關場照明(B) | 開關場照明(B) | OTHER | S40/0/StaDev/Lights2 |  |  |  | CDC | 411 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S40 | 官田SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | 69KV_N | [8 empty] | 官田SS.69KVSC警報 | 69KVSC警報 | OTHER | S40/69/810/60A |  |  |  | CDC | 412 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.門禁 | 門禁 | OTHER | S40/0/StaDev/Door |  |  |  | CDC | 413 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-16-04 |  | 1-42 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.390_CB | 390(#1SSTR) CB | OTHER | S40/11/390/CB |  |  |  | CDC | 414 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-16-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S40/11/390/PHA |  |  |  | CDC | 415 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-16-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S40/11/390/GDA |  |  |  | CDC | 416 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 490 | #3SSTR(490) |  | CB | [17 empty] | 1-16-07 |  | 1-43 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.490_CB | 490(#3SSTR) CB | OTHER | S40/11/490/CB |  |  |  | CDC | 417 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-17-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3SSTR_51A | #3SSTR 51RY | OTHER | S40/11/490/PHA |  |  |  | CDC | 418 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-17-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | S40/11/490/GDA |  |  |  | CDC | 419 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MA | #1MA |  | 81AS | [17 empty] | 1-14-00 |  | 1-41 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MA_81A/S | #1MA 81RY | OTHER | S40/11/M1/81AS |  |  |  | CDC | 420 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 0 |  | 1MA | #1MA |  | 81UL | [17 empty] | 1-33-13 |  | 1-6B | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | S40/11/M1/81UL |  |  |  | CDC | 421 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MA | #2MA |  | 81AS | [17 empty] | 1-14-01 |  | 1-56 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MA_81A/S | #2MA 81RY | OTHER | S40/11/M2A/81AS |  |  |  | CDC | 422 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 0 |  | 2MA | #2MA |  | 81UL | [17 empty] | 1-34-13 |  | 1-6C | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | S40/11/M2A/81UL |  |  |  | CDC | 423 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MB | #2MB |  | 81AS | [17 empty] | 1-14-02 |  | 1-57 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MB_81A/S | #2MB 81RY | OTHER | S40/11/M2B/81AS |  |  |  | CDC | 424 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 0 |  | 2MB | #2MB |  | 81UL | [17 empty] | 1-34-14 |  | 1-6D | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | S40/11/M2B/81UL |  |  |  | CDC | 425 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 3MA | #3MA |  | 81AS | [17 empty] | 1-14-03 |  | 1-69 | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MA_81A/S | #3MA 81RY | OTHER | S40/11/M3/81AS |  |  |  | CDC | 426 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 0 |  | 3MA | #3MA |  | 81UL | [17 empty] | 1-35-13 |  | 1-6E | [5 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | S40/11/M3/81UL |  |  |  | CDC | 427 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV |  |  |  | RYFA | [17 empty] | 1-33-14 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | S40/11/ComPoint/RYFA |  |  |  | CDC | 428 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-33-15 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.PMA | POWER METER故障 | OTHER | S40/0/StaDev/PMA |  |  |  | CDC | 429 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21_79 | 官一線(VG21) |  | LOA | [17 empty] | 1-3C-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_79_LOA | 11KV官一線(VG21) 79LOA | OTHER | S40/11/VG21/LOA |  |  |  | CDC | 430 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) |  | 81AS | [17 empty] | 1-14-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_81A/S | 11KV官一線(VG21) 81RY | OTHER | S40/11/VG21/81AS |  |  |  | CDC | 431 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG22_79 | 官二線(VG22) |  | LOA | [17 empty] | 1-3C-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_79_LOA | 11KV官二線(VG22) 79LOA | OTHER | S40/11/VG22/LOA |  |  |  | CDC | 432 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) |  | 81AS | [17 empty] | 1-14-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_81A/S | 11KV官二線(VG22) 81RY | OTHER | S40/11/VG22/81AS |  |  |  | CDC | 433 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG23_79 | 官三線(VG23) |  | LOA | [17 empty] | 1-3C-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_79_LOA | 11KV官三線(VG23) 79LOA | OTHER | S40/11/VG23/LOA |  |  |  | CDC | 434 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) |  | 81AS | [17 empty] | 1-14-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_81A/S | 11KV官三線(VG23) 81RY | OTHER | S40/11/VG23/81AS |  |  |  | CDC | 435 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG24_79 | 官正線(VG24) |  | LOA | [17 empty] | 1-3C-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_79_LOA | 11KV官正線(VG24) 79LOA | OTHER | S40/11/VG24/LOA |  |  |  | CDC | 436 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) |  | 81AS | [17 empty] | 1-15-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_81A/S | 11KV官正線(VG24) 81RY | OTHER | S40/11/VG24/81AS |  |  |  | CDC | 437 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG25_79 | 官五線(VG25) |  | LOA | [17 empty] | 1-3C-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_79_LOA | 11KV官五線(VG25) 79LOA | OTHER | S40/11/VG25/LOA |  |  |  | CDC | 438 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) |  | 81AS | [17 empty] | 1-15-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_81A/S | 11KV官五線(VG25) 81RY | OTHER | S40/11/VG25/81AS |  |  |  | CDC | 439 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG26_79 | 官六線(VG26) |  | LOA | [17 empty] | 1-3C-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_79_LOA | 11KV官六線(VG26) 79LOA | OTHER | S40/11/VG26/LOA |  |  |  | CDC | 440 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) |  | 81AS | [17 empty] | 1-15-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_81A/S | 11KV官六線(VG26) 81RY | OTHER | S40/11/VG26/81AS |  |  |  | CDC | 441 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG27_79 | 官七線(VG27) |  | LOA | [17 empty] | 1-3C-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_79_LOA | 11KV官七線(VG27) 79LOA | OTHER | S40/11/VG27/LOA |  |  |  | CDC | 442 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) |  | 81AS | [17 empty] | 1-15-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_81A/S | 11KV官七線(VG27) 81RY | OTHER | S40/11/VG27/81AS |  |  |  | CDC | 443 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG28_79 | 官八線(VG28) |  | LOA | [17 empty] | 1-3C-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_79_LOA | 11KV官八線(VG28) 79LOA | OTHER | S40/11/VG28/LOA |  |  |  | CDC | 444 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) |  | 81AS | [17 empty] | 1-15-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_81A/S | 11KV官八線(VG28) 81RY | OTHER | S40/11/VG28/81AS |  |  |  | CDC | 445 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG29_79 | 官九線(VG29) |  | LOA | [17 empty] | 1-3C-08 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_79_LOA | 11KV官九線(VG29) 79LOA | OTHER | S40/11/VG29/LOA |  |  |  | CDC | 446 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) |  | 81AS | [17 empty] | 1-15-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_81A/S | 11KV官九線(VG29) 81RY | OTHER | S40/11/VG29/81AS |  |  |  | CDC | 447 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG30_79 | 官十線(VG30) |  | LOA | [17 empty] | 1-3C-09 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_79_LOA | 11KV官十線(VG30) 79LOA | OTHER | S40/11/VG30/LOA |  |  |  | CDC | 448 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) |  | 81AS | [17 empty] | 1-15-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_81A/S | 11KV官十線(VG30) 81RY | OTHER | S40/11/VG30/81AS |  |  |  | CDC | 449 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG31_79 | 官忠線(VG31) |  | LOA | [17 empty] | 1-3C-10 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_79_LOA | 11KV官忠線(VG31) 79LOA | OTHER | S40/11/VG31/LOA |  |  |  | CDC | 450 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) |  | 81AS | [17 empty] | 1-15-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_81A/S | 11KV官忠線(VG31) 81RY | OTHER | S40/11/VG31/81AS |  |  |  | CDC | 451 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG32_79 | 官孝線(VG32) |  | LOA | [17 empty] | 1-3C-11 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_79_LOA | 11KV官孝線(VG32) 79LOA | OTHER | S40/11/VG32/LOA |  |  |  | CDC | 452 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) |  | 81AS | [17 empty] | 1-16-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_81A/S | 11KV官孝線(VG32) 81RY | OTHER | S40/11/VG32/81AS |  |  |  | CDC | 453 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG33_79 | 官仁線(VG33) |  | LOA | [17 empty] | 1-3C-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_79_LOA | 11KV官仁線(VG33) 79LOA | OTHER | S40/11/VG33/LOA |  |  |  | CDC | 454 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) |  | 81AS | [17 empty] | 1-16-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_81A/S | 11KV官仁線(VG33) 81RY | OTHER | S40/11/VG33/81AS |  |  |  | CDC | 455 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG34_79 | 官愛線(VG34) |  | LOA | [17 empty] | 1-3C-13 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_79_LOA | 11KV官愛線(VG34) 79LOA | OTHER | S40/11/VG34/LOA |  |  |  | CDC | 456 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) |  | 81AS | [17 empty] | 1-16-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_81A/S | 11KV官愛線(VG34) 81RY | OTHER | S40/11/VG34/81AS |  |  |  | CDC | 457 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 11 | 11kV | VG35_79 | 官信線(VG35) |  | LOA | [17 empty] | 1-3C-14 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_79_LOA | 11KV官信線(VG35) 79LOA | OTHER | S40/11/VG35/LOA |  |  |  | CDC | 458 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) |  | 81AS | [17 empty] | 1-16-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_81A/S | 11KV官信線(VG35) 81RY | OTHER | S40/11/VG35/81AS |  |  |  | CDC | 459 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 官田SS.640_PHA | 官田隆田二路(640) 相間RY | LINE69 | S40/69/640/PHA |  |  |  | CDC | 460 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | 69KV_N | [8 empty] | 官田SS.640_GDA | 官田隆田二路(640) 接地RY | LINE69 | S40/69/640/GDA |  |  |  | CDC | 461 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | CB | [17 empty] | 1-0A-00 |  | 1-05 | [5 empty] | 69KV_N | [8 empty] | 官田SS.640_CB | 640(官田隆田二路) CB | LINE69 | S40/69/640/CB |  |  |  | CDC | 462 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | ABS1 | 641 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 官田SS.641_ABS | 641(官田隆田二路) ABS | LINE69 | S40/69/640/DS1 |  |  |  | CDC | 463 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | ABS2 | 642 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 官田SS.642_ABS | 642(官田隆田二路) ABS | LINE69 | S40/69/640/DS2 |  |  |  | CDC | 464 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | E2 | 642E | [16 empty] | 1-3A-04 | 1-3A-05 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 官田SS.642E_ES | 642E(官田隆田二路) ES | LINE69 | S40/69/640/ES2 |  |  |  | CDC | 465 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 官田SS.640_87A | 官隆二路(640) 87RY | LINE69 | S40/69/640/87A |  |  |  | CDC | 466 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 官田SS.640_87UL | 官隆二路(640) 87RY U/L | LINE69 | S40/69/640/87UL |  |  |  | CDC | 467 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 640 | 官田隆田二路(640) |  | 87CFA | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 官田SS.640_87CFA | 640 87RY通訊故障 | OTHER | S40/69/640/87CFA |  |  |  | CDC | 468 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 640 | 官田隆田二路(640) |  | 87RYFA | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 官田SS.640_87RYFA | 640 數位電驛故障 | OTHER | S40/69/640/RYFA |  |  |  | CDC | 469 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-06-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | S40//1MTR/63Q |  |  |  | CDC | 470 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-05-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | S40//1MTR/96B1 |  |  |  | CDC | 471 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-05-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | S40//1MTR/96B2 |  |  |  | CDC | 472 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-05-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | S40//1MTR/96D |  |  |  | CDC | 473 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-05-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | S40//1MTR/96P |  |  |  | CDC | 474 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-06-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | S40//2MTR/63Q |  |  |  | CDC | 475 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-06-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | S40//2MTR/96B1 |  |  |  | CDC | 476 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-06-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | S40//2MTR/96B2 |  |  |  | CDC | 477 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-06-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | S40//2MTR/96D |  |  |  | CDC | 478 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-06-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | S40//2MTR/96P |  |  |  | CDC | 479 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-07-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | S40//3MTR/63Q |  |  |  | CDC | 480 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-06-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | S40//3MTR/96B1 |  |  |  | CDC | 481 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-06-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | S40//3MTR/96B2 |  |  |  | CDC | 482 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-07-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | S40//3MTR/96D |  |  |  | CDC | 483 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-07-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | S40//3MTR/96P |  |  |  | CDC | 484 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 官田SS.630_87A | 官隆ㄧ路(630) 87RY | LINE69 | S40/69/630/87A |  |  |  | CDC | 485 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 官田SS.630_87UL | 官隆ㄧ路(630) 87RY U/L | LINE69 | S40/69/630/87UL |  |  |  | CDC | 486 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 630 | 官田隆田一路(630) |  | 87CFA | [17 empty] | 1-37-07 | [7 empty] | 69KV_N | [8 empty] | 官田SS.630_87CFA | 630 87RY通訊故障 | OTHER | S40/69/630/87CFA |  |  |  | CDC | 487 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 630 | 官田隆田一路(630) |  | RYFA | [17 empty] | 1-37-06 | [7 empty] | 69KV_N | [8 empty] | 官田SS.630_RYFA | 630 數位電驛故障 | OTHER | S40/69/630/RYFA |  |  |  | CDC | 488 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 官田SS.660_87A | 新營二路(660) 87RY | LINE69 | S40/69/660/87A |  |  |  | CDC | 489 | GENERICDIPoint | SS300_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 官田SS.660_87UL | 新營二路(660) 87RY U/L | LINE69 | S40/69/660/87UL |  |  |  | CDC | 490 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 660 | 新營二路(660) |  | 87CFA | [17 empty] | 1-37-09 | [7 empty] | 69KV_N | [8 empty] | 官田SS.660_87CFA | 660 87RY通訊故障 | OTHER | S40/69/660/87CFA |  |  |  | CDC | 491 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 660 | 新營二路(660) |  | RYFA | [17 empty] | 1-37-08 | [7 empty] | 69KV_N | [8 empty] | 官田SS.660_RYFA | 660 數位電驛故障 | OTHER | S40/69/660/RYFA |  |  |  | CDC | 492 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-3D-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | S40//1MTR/MTR_86A |  |  |  | CDC | 493 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 871S | [17 empty] | 1-3D-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | S40//1MTR/1_87UL1 |  |  |  | CDC | 494 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 872S | [17 empty] | 1-3D-07 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | S40//1MTR/1_87UL2 |  |  |  | CDC | 495 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-3C-15 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | S40//1MTR/RYFA |  |  |  | CDC | 496 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-3D-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | S40//2MTR/MTR_86A |  |  |  | CDC | 497 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 871S | [17 empty] | 1-3D-08 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | S40//2MTR/1_87UL1 |  |  |  | CDC | 498 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 872S | [17 empty] | 1-3D-09 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | S40//2MTR/1_87UL2 |  |  |  | CDC | 499 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-3D-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | S40//2MTR/RYFA |  |  |  | CDC | 500 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-3D-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | S40//3MTR/MTR_86A |  |  |  | CDC | 501 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 871S | [17 empty] | 1-3D-10 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | S40//3MTR/1_87UL1 |  |  |  | CDC | 502 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 872S | [17 empty] | 1-3D-11 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | S40//3MTR/1_87UL2 |  |  |  | CDC | 503 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 1-3D-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | S40//3MTR/RYFA |  |  |  | CDC | 504 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 81RY | 81RY |  | RYFA | [17 empty] | 1-3D-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | S40/69/ComPoint/81A_RYFA |  |  |  | CDC | 505 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3D-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | S40//1MTR/51Z_UL |  |  |  | CDC | 506 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3D-13 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | S40//2MTR/51Z_UL |  |  |  | CDC | 507 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3D-14 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | S40//3MTR/51Z_UL |  |  |  | CDC | 508 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 1GIS | #1GIS |  | CBA | [17 empty] | 1-3E-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1GIS_CBA | #1GIS重故障 | OTHER | S40/11/1GIS/CBA |  |  |  | CDC | 509 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 1GIS | #1GIS |  | CBF | [17 empty] | 1-3E-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#1GIS_CBF | #1GIS輕故障 | OTHER | S40/11/1GIS/CBF |  |  |  | CDC | 510 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2GIS | #2GIS |  | CBA | [17 empty] | 1-3E-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2GIS_CBA | #2GIS重故障 | OTHER | S40/11/2GIS/CBA |  |  |  | CDC | 511 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 2GIS | #2GIS |  | CBF | [17 empty] | 1-3E-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#2GIS_CBF | #2GIS輕故障 | OTHER | S40/11/2GIS/CBF |  |  |  | CDC | 512 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3GIS | #3GIS |  | CBA | [17 empty] | 1-3E-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3GIS_CBA | #3GIS重故障 | OTHER | S40/11/3GIS/CBA |  |  |  | CDC | 513 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 0 |  | 3GIS | #3GIS |  | CBF | [17 empty] | 1-3E-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.#3GIS_CBF | #3GIS輕故障 | OTHER | S40/11/3GIS/CBF |  |  |  | CDC | 514 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S40 | 官田SS | 11 | 11kV | VG21 | 官一線(VG21) 81RY |  | 81UL | [17 empty] | 1-3E-08 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_81U/L | 11KV官一線(VG21) 81RY U/L | OTHER | S40/11/VG21/81UL |  |  |  | CDC | 515 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG22 | 官二線(VG22) 81RY |  | 81UL | [17 empty] | 1-3E-09 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_81U/L | 11KV官二線(VG22) 81RY U/L | OTHER | S40/11/VG22/81UL |  |  |  | CDC | 516 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG23 | 官三線(VG23) 81RY |  | 81UL | [17 empty] | 1-3E-10 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_81U/L | 11KV官三線(VG23) 81RY U/L | OTHER | S40/11/VG23/81UL |  |  |  | CDC | 517 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG24 | 官正線(VG24) 81RY |  | 81UL | [17 empty] | 1-3E-11 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_81U/L | 11KV官正線(VG24) 81RY U/L | OTHER | S40/11/VG24/81UL |  |  |  | CDC | 518 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG25 | 官五線(VG25) 81RY |  | 81UL | [17 empty] | 1-3E-12 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_81U/L | 11KV官五線(VG25) 81RY U/L | OTHER | S40/11/VG25/81UL |  |  |  | CDC | 519 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG26 | 官六線(VG26) 81RY |  | 81UL | [17 empty] | 1-3E-13 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_81U/L | 11KV官六線(VG26) 81RY U/L | OTHER | S40/11/VG26/81UL |  |  |  | CDC | 520 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG27 | 官七線(VG27) 81RY |  | 81UL | [17 empty] | 1-3E-14 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_81U/L | 11KV官七線(VG27) 81RY U/L | OTHER | S40/11/VG27/81UL |  |  |  | CDC | 521 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG28 | 官八線(VG28) 81RY |  | 81UL | [17 empty] | 1-3E-15 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_81U/L | 11KV官八線(VG28) 81RY U/L | OTHER | S40/11/VG28/81UL |  |  |  | CDC | 522 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG29 | 官九線(VG29) 81RY |  | 81UL | [17 empty] | 1-3F-00 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_81U/L | 11KV官九線(VG29) 81RY U/L | OTHER | S40/11/VG29/81UL |  |  |  | CDC | 523 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG30 | 官十線(VG30) 81RY |  | 81UL | [17 empty] | 1-3F-01 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_81U/L | 11KV官十線(VG30) 81RY U/L | OTHER | S40/11/VG30/81UL |  |  |  | CDC | 524 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG31 | 官忠線(VG31) 81RY |  | 81UL | [17 empty] | 1-3F-02 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_81U/L | 11KV官忠線(VG31) 81RY U/L | OTHER | S40/11/VG31/81UL |  |  |  | CDC | 525 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG32 | 官孝線(VG32) 81RY |  | 81UL | [17 empty] | 1-3F-03 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_81U/L | 11KV官孝線(VG32) 81RY U/L | OTHER | S40/11/VG32/81UL |  |  |  | CDC | 526 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG33 | 官仁線(VG33) 81RY |  | 81UL | [17 empty] | 1-3F-04 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_81U/L | 11KV官仁線(VG33) 81RY U/L | OTHER | S40/11/VG33/81UL |  |  |  | CDC | 527 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG34 | 官愛線(VG34) 81RY |  | 81UL | [17 empty] | 1-3F-05 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_81U/L | 11KV官愛線(VG34) 81RY U/L | OTHER | S40/11/VG34/81UL |  |  |  | CDC | 528 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | VG35 | 官信線(VG35) 81RY |  | 81UL | [17 empty] | 1-3F-06 | [7 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_81U/L | 11KV官信線(VG35) 81RY U/L | OTHER | S40/11/VG35/81UL |  |  |  | CDC | 529 | GENERICDIPoint | SS300_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S40 | 官田SS | 11 | 11kV | 210_SC | #1SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 530 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 11 | 11kV | 220_SC | #2SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 531 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 11 | 11kV | 230_SC | #3SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 532 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 69 | 69kV | 810_SC | #1SC | 14.4 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 官田SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 533 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.610BE | 610BE (非取樣點) | LINE69 | S40/69/610/BE0 |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 620 | 官田台汽官線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.620BE | 620BE (非取樣點) | LINE69 | S40/69/620/BE0 |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.630BE | 630BE (非取樣點) | LINE69 | S40/69/630/BE0 |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | BE0 | 660BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.660BE | 660BE (非取樣點) | LINE69 | S40/69/660/BE0 |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG21 | VG21_ES |  | LE0 | VG21_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_ES | VG21_ES (非取樣點) | FEEDER | S40/11/VG21/ES |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG22 | VG22_ES |  | LE0 | VG22_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_ES | VG22_ES (非取樣點) | FEEDER | S40/11/VG22/ES |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG23 | VG23_ES |  | LE0 | VG23_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_ES | VG23_ES (非取樣點) | FEEDER | S40/11/VG23/ES |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG24 | VG24_ES |  | LE0 | VG24_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_ES | VG24_ES (非取樣點) | FEEDER | S40/11/VG24/ES |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG25 | VG25_ES |  | LE0 | VG25_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_ES | VG25_ES (非取樣點) | FEEDER | S40/11/VG25/ES |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG26 | VG26_ES |  | LE0 | VG26_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_ES | VG26_ES (非取樣點) | FEEDER | S40/11/VG26/ES |  |  |  |  | 543 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG27 | VG27_ES |  | LE0 | VG27_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_ES | VG27_ES (非取樣點) | FEEDER | S40/11/VG27/ES |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG28 | VG28_ES |  | LE0 | VG28_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_ES | VG28_ES (非取樣點) | FEEDER | S40/11/VG28/ES |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG29 | VG29_ES |  | LE0 | VG29_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_ES | VG29_ES (非取樣點) | FEEDER | S40/11/VG29/ES |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG30 | VG30_ES |  | LE0 | VG30_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_ES | VG30_ES (非取樣點) | FEEDER | S40/11/VG30/ES |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG31 | VG31_ES |  | LE0 | VG31_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_ES | VG31_ES (非取樣點) | FEEDER | S40/11/VG31/ES |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG32 | VG32_ES |  | LE0 | VG32_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_ES | VG32_ES (非取樣點) | FEEDER | S40/11/VG32/ES |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG33 | VG33_ES |  | LE0 | VG33_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_ES | VG33_ES (非取樣點) | FEEDER | S40/11/VG33/ES |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG34 | VG34_ES |  | LE0 | VG34_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_ES | VG34_ES (非取樣點) | FEEDER | S40/11/VG34/ES |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG35 | VG35_ES |  | LE0 | VG35_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_ES | VG35_ES (非取樣點) | FEEDER | S40/11/VG35/ES |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S40/11/TIE1/D1 |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S40/11/TIE2/D1 |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.750TE | 750TE (非取樣點) | DTR | S40/69/750/TE0 |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.750BE | 750BE (非取樣點) | DTR | S40/69/750/BE0 |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.1M_ES | 1M_ES (非取樣點) | DTR | S40/11/M1/ES |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.760TE | 760TE (非取樣點) | DTR | S40/69/760/TE0 |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.760BE | 760BE (非取樣點) | DTR | S40/69/760/BE0 |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2M_ES | 2M_ES (非取樣點) | DTR | S40/11/M2/ES |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.770TE | 770TE (非取樣點) | DTR | S40/69/770/TE0 |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.770BE | 770BE (非取樣點) | DTR | S40/69/770/BE0 |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.3M_ES | 3M_ES (非取樣點) | DTR | S40/11/M3/ES |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.210ES | 210ES (非取樣點) | SC | S40/11/210/ES |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | _1SCDS | _#1SCDS |  | #1SCDS | 11KV_#1SCDS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_#1SCDS | 11KV_#1SCDS (非取樣點) | SC | S40/11/210/DS |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 220ES | 220ES |  | 220ES | 220ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.220ES | 220ES (非取樣點) | SC | S40/11/220/ES |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | _2SCDS | _#2SCDS |  | #2SCDS | 11KV_#2SCDS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_#2SCDS | 11KV_#2SCDS (非取樣點) | SC | S40/11/220/DS |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 230ES | 230ES |  | 230ES | 230ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.230ES | 230ES (非取樣點) | SC | S40/11/230/ES |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 11 | 11kV | _3SCDS | _#3SCDS |  | #3SCDS | 11KV_#3SCDS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.11KV_#3SCDS | 11KV_#3SCDS (非取樣點) | SC | S40/11/230/DS |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.810BE | 810BE (非取樣點) | SC | S40/69/810/BE0 |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 官田SS.69B1E | 69B1E (非取樣點) | BUS | S40/69/1BUS/BE1 |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 572 | NotelDIPoint | [38 empty] | START/STOP | STOP
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | PW1UL | 660_PW1UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.660_PW1UL | 新營二路(660)PW1_UL(非取樣點) | LINE69 | [5 empty] | 573 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | PW2UL | 660_PW2UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.660_PW2UL | 新營二路(660)PW2_UL(非取樣點) | LINE69 | [5 empty] | 574 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S40 | 官田SS | 69 | 69kV | 660 | 新營二路(660) |  | HCBUL | 660_HCBUL | [24 empty] | ADCS_N | [8 empty] | 官田SS.660_HCBUL | 新營二路(660)HCB_UL(非取樣點) | LINE69 | [5 empty] | 575 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | PW1UL | 610_PW1UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.610_PW1UL | 新營一路(610)PW1_UL(非取樣點) | LINE69 | [5 empty] | 576 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | PW2UL | 610_PW2UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.610_PW2UL | 新營一路(610)PW2_UL(非取樣點) | LINE69 | [5 empty] | 577 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S40 | 官田SS | 69 | 69kV | 610 | 備用線(610) |  | HCBUL | 610_HCBUL | [24 empty] | ADCS_N | [8 empty] | 官田SS.610_HCBUL | 新營一路(610)HCB_UL(非取樣點) | LINE69 | [5 empty] | 578 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | PW1UL | 630_PW1UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.630_PW1UL | 隆田線(630)PW1_UL(非取樣點) | LINE69 | [5 empty] | 579 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | PW2UL | 630_PW2UL | [24 empty] | ADCS_N | [8 empty] | 官田SS.630_PW2UL | 隆田線(630)PW2_UL(非取樣點) | LINE69 | [5 empty] | 580 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S40 | 官田SS | 69 | 69kV | 630 | 官田隆田一路(630) |  | HCBUL | 630_HCBUL | [24 empty] | ADCS_N | [8 empty] | 官田SS.630_HCBUL | 隆田線(630)HCB_UL(非取樣點) | LINE69 | [5 empty] | 581 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S40 | 官田SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.391 | 391 (非取樣點) | OTHER | S40/11/390/D1 |  |  |  |  | 582 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.391E | 391E (非取樣點) | OTHER | S40/11/390/E1 |  |  |  |  | 583 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.491 | 491 (非取樣點) | OTHER | S40/11/490/D1 |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.491E | 491E (非取樣點) | OTHER | S40/11/490/E1 |  |  |  |  | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 69 | 69kV | 640 | 官田隆田二路(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.640BE | 640BE (非取樣點) | LINE69 | S40/69/640/BE0 |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | VG31 | VG31_DS |  | DS1 | VG31_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG31_DS | VG31_DS (非取樣點) | FEEDER | S40/11/VG31/DS |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG32 | VG32_DS |  | DS1 | VG32_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG32_DS | VG32_DS (非取樣點) | FEEDER | S40/11/VG32/DS |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG33 | VG33_DS |  | DS1 | VG33_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG33_DS | VG33_DS (非取樣點) | FEEDER | S40/11/VG33/DS |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG34 | VG34_DS |  | DS1 | VG34_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG34_DS | VG34_DS (非取樣點) | FEEDER | S40/11/VG34/DS |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG35 | VG35_DS |  | DS1 | VG35_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG35_DS | VG35_DS (非取樣點) | FEEDER | S40/11/VG35/DS |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.3M_DS | 3M_DS (非取樣點) | DTR | S40/11/M3/DS |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG21 | VG21_DS |  | DS1 | VG21_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG21_DS | VG21_DS (非取樣點) | FEEDER | S40/11/VG21/DS |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG22 | VG22_DS |  | DS1 | VG22_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG22_DS | VG22_DS (非取樣點) | FEEDER | S40/11/VG22/DS |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG23 | VG23_DS |  | DS1 | VG23_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG23_DS | VG23_DS (非取樣點) | FEEDER | S40/11/VG23/DS |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG24 | VG24_DS |  | DS1 | VG24_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG24_DS | VG24_DS (非取樣點) | FEEDER | S40/11/VG24/DS |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG25 | VG25_DS |  | DS1 | VG25_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG25_DS | VG25_DS (非取樣點) | FEEDER | S40/11/VG25/DS |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG26 | VG26_DS |  | DS1 | VG26_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG26_DS | VG26_DS (非取樣點) | FEEDER | S40/11/VG26/DS |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG27 | VG27_DS |  | DS1 | VG27_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG27_DS | VG27_DS (非取樣點) | FEEDER | S40/11/VG27/DS |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG28 | VG28_DS |  | DS1 | VG28_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG28_DS | VG28_DS (非取樣點) | FEEDER | S40/11/VG28/DS |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG29 | VG29_DS |  | DS1 | VG29_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG29_DS | VG29_DS (非取樣點) | FEEDER | S40/11/VG29/DS |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | VG30 | VG30_DS |  | DS1 | VG30_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.VG30_DS | VG30_DS (非取樣點) | FEEDER | S40/11/VG30/DS |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.1M_DS | 1M_DS (非取樣點) | DTR | S40/11/M1/DS |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2M_DS | 2M_DS (非取樣點) | DTR | S40/11/M2/DS |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S40/11/M2A/DS |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S40/11/M2B/DS |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S40/11/M2A/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S40/11/M2B/ES |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | TIE1 | TIE1_DS2 |  | DS2 | TIE1_DS2 | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | S40/11/TIE1/D2 |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | TIE2 | TIE2_DS2 |  | DS2 | TIE2_DS2 | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | S40/11/TIE2/D2 |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S40 | 官田SS | 0 |  | 100 | 100 |  | E1 | 101E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.101E | 101E (非取樣點) | TIE | S40/11/TIE1/E1 |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 100 | 100 |  | E2 | 102E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.102E | 102E (非取樣點) | TIE | S40/11/TIE1/E2 |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 200 | 200 |  | E1 | 201E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.201E | 201E (非取樣點) | TIE | S40/11/TIE2/E1 |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 200 | 200 |  | E2 | 202E | [24 empty] | DDCS3_2 | [8 empty] | 官田SS.202E | 202E (非取樣點) | TIE | S40/11/TIE2/E2 |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 11B1E | 11B1E |  | BE1 | 11B1E | [24 empty] | ADCS_N | [8 empty] | 官田SS.11B1E | 11B1E (非取樣點) | BUS | S40/11/1BUS/BE1 |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 11B2E | 11B2E |  | BE2 | 11B2E | [24 empty] | ADCS_N | [8 empty] | 官田SS.11B2E | 11B2E (非取樣點) | BUS | S40/11/2BUS/BE2 |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 11B2BE | 11B2BE |  | B2BE0 | 11B2BE | [24 empty] | ADCS_N | [8 empty] | 官田SS.11B2BE | 11B2BE (非取樣點) | BUS | S40/11/2BUS/BE0 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S40 | 官田SS | 0 |  | 11B3E | 11B3E |  | BE3 | 11B3E | [24 empty] | ADCS_N | [8 empty] | 官田SS.11B3E | 11B3E (非取樣點) | BUS | S40/11/3BUS/BE3 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo