## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS #1 | KV | 69KV BUS1 PT | kV_-90_90(-2000_2000) | aaa | B2/S43_A1 | [8 empty] | 學甲SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S43 | 學甲SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV #1 BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S43_D1 | [8 empty] | 學甲SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2 BUS | KV | 二號 BUS PT | kV_-9_9(-2000_2000) | aba | B2/S43_D1 | [8 empty] | 學甲SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | 11KV #3 BUS | KV | 三號 BUS PT | kV_-9_9(-2000_2000) | ada | B2/S43_D1 | [8 empty] | 學甲SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S43_A1 | [8 empty] | 學甲SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA1 | 69KV BUS #1衡相監視 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 620 | MW | 學甲佳里二路 | MW_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.620_MW | 學甲佳里二路 MW | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 620 | MVAR | 學甲佳里二路 | MVAR_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.620_MVAR | 學甲佳里二路 MVAR | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 620 | MWH(+) | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 10 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 720 | MW | 新營學甲二路 | MW_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.720_MW | 新營學甲二路 MW | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 720 | MVAR | 新營學甲二路 | MVAR_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.720_MVAR | 新營學甲二路 MVAR | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 720 | MWH(+) | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 13 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 630 | MW | 永華學甲線 | MW_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.630_MW | 永華線 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 630 | MVAR | 永華學甲線 | MVAR_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.630_MVAR | 永華線 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 630 | MWH(+) | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 650 | MW | 學甲新西線 | MW_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.650_MW | 新西線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 650 | MVAR | 學甲新西線 | MVAR_-96_96(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.650_MVAR | 新西線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 650 | MWH(+) | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 910 | MW | 新營學甲一路 | MW_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.910_MW | 新營學甲一路 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 910 | MVAR | 新營學甲一路 | MVAR_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.910_MVAR | 新營學甲一路 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | 910 | MWH(+) | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 730 | MW | 學甲佳里一路 | MW_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.730_MW | 學甲佳里一路 MW | LINE69 |  |  |  |  | CDC | 23 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 730 | MVAR | 學甲佳里一路 | MVAR_-144_144(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.730_MVAR | 學甲佳里一路 MVAR | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0034 |  |  | 2-42 |  |  | 730 | MWH(+) | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 25 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 620 | PHA | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_PHA | 學甲佳里二路(620) 相間RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 620 | GDA | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_GDA | 學甲佳里二路(620) 接地RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 620 | 87A | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_87A | 學甲佳里二路(620) 87RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | Locate Empty |  |  |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 29 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 720 | PHA | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_PHA | 新營學甲二路(720) 相間RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 720 | GDA | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_GDA | 新營學甲二路(720) 接地RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 720 | 87A | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_87A | 新營學甲二路(720) 87RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | Locate Empty |  |  |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 33 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 630 | PHA | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_PHA | 永華線(630) 相間RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 630 | GDA | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_GDA | 永華線(630) 接地RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 630 | 87A | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_87A | 永華線(630) 87RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | Locate Empty |  |  |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 37 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 650 | PHA | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_PHA | 新西線(650) 相間RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 650 | GDA | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_GDA | 新西線(650) 接地RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 650 | 87A | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_87A | 新西線(650) 87RY | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | Locate Empty |  |  |  |  | B2/S43_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 41 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 910 | PHA | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.910_PHA | 新營學甲一路(910) 相間RY | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 910 | GDA | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.910_GDA | 新營學甲一路(910) 接地RY | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 910 | 87A | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.910_87A | 新營學甲一路(910) 87RY | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 730 | PHA | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.730_PHA | 學甲佳里一路(730) 相間RY | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 730 | GDA | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.730_GDA | 學甲佳里一路(730) 接地RY | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 730 | 87A | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.730_87A | 學甲佳里一路(730) 87RY | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 620 | 187 U/L | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_87UL | 學甲佳里二路(620) 87RY U/L | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 720 | 87 U/L | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_87UL | 新營學甲二路(720) 87RY U/L | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 630 | 87 U/L | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_87UL | 永華線(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 650 | 87 U/L | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_87UL | 新西線(650) 87RY U/L | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87UL |  | Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0013 | 1-32-08 |  | 1-0D | 910 | 87 U/L | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.910_87UL | 新營學甲一路(910) 87RY U/L | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | 87UL |  | Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0298 |  | 0014 | 1-32-10 |  | 1-0E | 730 | 87 U/L | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.730_87UL | 學甲佳里一路(730) 87RY U/L | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 620 | CB ON/OFF | 學甲佳里二路 |  | aaca | B2/S43_A1 | [8 empty] | 學甲SS.620_CB | 620(學甲佳里二路) CB | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 720 | CB ON/OFF | 新營學甲二路 |  | aada | B2/S43_A1 | [8 empty] | 學甲SS.720_CB | 720(新營學甲二路) CB | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 630 | CB ON/OFF | 永華學甲線 |  | aaea | B2/S43_A1 | [8 empty] | 學甲SS.630_CB | 630(永華線) CB | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 650 | CB ON/OFF | 學甲新西線 |  | aaga | B2/S43_A1 | [8 empty] | 學甲SS.650_CB | 650(新西線) CB | LINE69 |  |  |  |  | CDC | 57 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0080 |  | 0005 | 1-0A-00 |  | 1-05 | 910 | CB ON/OFF | 新營學甲一路 |  | abaa | B2/S43_A1 | [8 empty] | 學甲SS.910_CB | 910(新營學甲一路) CB | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0084 |  | 0006 | 1-0A-04 |  | 1-06 | 730 | CB ON/OFF | 學甲佳里一路 |  | abba | B2/S43_A1 | [8 empty] | 學甲SS.730_CB | 730(學甲佳里一路) CB | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0018 | 1-38-08 | 1-38-09 | 1-12 | 621 | ABS ON | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.621_ABS | 621(學甲佳里二路) ABS | LINE69 |  |  |  |  | CDC | 60 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0019 | 1-38-10 | 1-38-11 | 1-13 | 622 | ABS ON | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.622_ABS | 622(學甲佳里二路) ABS | LINE69 |  |  |  |  | CDC | 61 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | ABS1 | 721 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0021 | 1-38-14 | 1-38-15 | 1-15 | 721 | ABS ON | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.721_ABS | 721(新營學甲二路) ABS | LINE69 |  |  |  |  | CDC | 62 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | ABS2 | 722 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0022 | 1-39-00 | 1-39-01 | 1-16 | 722 | ABS ON | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.722_ABS | 722(新營學甲二路) ABS | LINE69 |  |  |  |  | CDC | 63 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | ABS1 | 631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0024 | 1-39-04 | 1-39-05 | 1-18 | 631 | ABS ON | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.631_ABS | 631(永華線) ABS | LINE69 |  |  |  |  | CDC | 64 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | ABS2 | 632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0025 | 1-39-06 | 1-39-07 | 1-19 | 632 | ABS ON | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.632_ABS | 632(永華線) ABS | LINE69 |  |  |  |  | CDC | 65 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | ABS1 | 651 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0027 | 1-39-10 | 1-39-11 | 1-1B | 651 | ABS ON | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.651_ABS | 651(新西線) ABS | LINE69 |  |  |  |  | CDC | 66 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | ABS2 | 652 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0028 | 1-39-12 | 1-39-13 | 1-1C | 652 | ABS ON | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.652_ABS | 652(新西線) ABS | LINE69 |  |  |  |  | CDC | 67 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | ABS1 | 911 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0416 | 417 | 0030 | 1-3A-00 | 1-3A-01 | 1-1E | 911 | ABS ON | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.911_DS | 911(新營學甲一路) DS | LINE69 |  |  |  |  | CDC | 68 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | ABS2 | 912 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0418 | 419 | 0031 | 1-3A-02 | 1-3A-03 | 1-1F | 912 | ABS ON | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.912_DS | 912(新營學甲一路) DS | LINE69 |  |  |  |  | CDC | 69 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | ABS1 | 731 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0422 | 423 | 0033 | 1-3A-06 | 1-3A-07 | 1-21 | 731 | DS ON | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.731_DS | 731(學甲佳里一路) DS | LINE69 |  |  |  |  | CDC | 70 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | ABS2 | 732 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0424 | 425 | 0034 | 1-3A-08 | 1-3A-09 | 1-22 | 732 | DS ON | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.732_DS | 732(學甲佳里一路) DS | LINE69 |  |  |  |  | CDC | 71 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0396 | 397 | 0020 | 1-38-12 | 1-38-13 | 1-14 | 622E | ABS ON | 學甲佳里二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.622E_ES | 622E(學甲佳里二路) ES | LINE69 |  |  |  |  | CDC | 72 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | BE0 | 620BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 73 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | ES2 | 722E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0402 | 403 | 0023 | 1-39-02 | 1-39-03 | 1-17 | 722E | ABS ON | 新營學甲二路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.722E_ES | 722E(新營學甲二路) ES | LINE69 |  |  |  |  | CDC | 74 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | BE0 | 720BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 75 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0408 | 409 | 0026 | 1-39-08 | 1-39-09 | 1-1A | 632E | ABS ON | 永華學甲線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.632E_ES | 632E(永華線) ES | LINE69 |  |  |  |  | CDC | 76 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | BE0 | 630BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 77 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | ES2 | 652E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0029 | 1-39-14 | 1-39-15 | 1-1D | 652E | ABS ON | 學甲新西線 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.652E_ES | 652E(新西線) ES | LINE69 |  |  |  |  | CDC | 78 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | BE0 | 650BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 79 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | ES2 | 912E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0420 | 421 | 0032 | 1-3A-04 | 1-3A-05 | 1-20 | 912E | ABS ON | 新營學甲一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.912E_ES | 912E(新營學甲一路) ES | LINE69 |  |  |  |  | CDC | 80 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | LE0 | 910LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.910LE | 910LE (非取樣點) | LINE69 | [5 empty] | 81 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | BE0 | 910BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.910BE | 910BE (非取樣點) | LINE69 | [5 empty] | 82 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | ES2 | 732E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0426 | 427 | 0035 | 1-3A-10 | 1-3A-11 | 1-23 | 732 ES | ES ON | 學甲佳里一路 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.732E_ES | 732E(學甲佳里一路) ES | LINE69 |  |  |  |  | CDC | 83 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | LE0 | 730LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.730LE | 730LE (非取樣點) | LINE69 | [5 empty] | 84 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | BE0 | 730BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.730BE | 730BE (非取樣點) | LINE69 | [5 empty] | 85 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F1 PH RY | PHA | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_PHA | 11KV學平線(VD21) 相間RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F1 GD RY | GDA | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_GDA | 11KV學平線(VD21) 接地RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | F1 CB | 79 U/L | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_79UL | 11KV學平線(VD21) 79RY U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_ADJ | 11KV學平線(VD21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | F2 PH RY | PHA | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_PHA | 11KV信義線(VD22) 相間RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F2 GD RY | GDA | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_GDA | 11KV信義線(VD22) 接地RY | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | F2 CB | 79 U/L | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_79UL | 11KV信義線(VD22) 79RY U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_ADJ | 11KV信義線(VD22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F3 PH RY | PHA | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_PHA | 11KV中洲線(VD23) 相間RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | F3 GD RY | GDA | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_GDA | 11KV中洲線(VD23) 接地RY | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | F3 CB | 79 U/L | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_79UL | 11KV中洲線(VD23) 79RY U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_ADJ | 11KV中洲線(VD23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | F4 PH RY | PHA | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_PHA | 11KV宅港線(VD24) 相間RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | F4 GD RY | GDA | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_GDA | 11KV宅港線(VD24) 接地RY | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | F4 CB | 79 U/L | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_79UL | 11KV宅港線(VD24) 79RY U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_ADJ | 11KV宅港線(VD24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | F5 PH RY | PHA | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_PHA | 11KV文化線(VD25) 相間RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | F5 GD RY | GDA | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_GDA | 11KV文化線(VD25) 接地RY | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | F5 CB | 79 U/L | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_79UL | 11KV文化線(VD25) 79RY U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_ADJ | 11KV文化線(VD25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | F6 PH RY | PHA | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_PHA | 11KV竹埔線(VD26) 相間RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | F6 GD RY | GDA | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_GDA | 11KV竹埔線(VD26) 接地RY | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | F6 CB | 79 U/L | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_79UL | 11KV竹埔線(VD26) 79RY U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | F6 LCO | ADJ(U/L) | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_ADJ | 11KV竹埔線(VD26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F7 PH RY | PHA | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_PHA | 11KV美豐線(VD27) 相間RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F7 GD RY | GDA | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_GDA | 11KV美豐線(VD27) 接地RY | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | F7 CB | 79 U/L | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_79UL | 11KV美豐線(VD27) 79RY U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | F7 LCO | ADJ(U/L) | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_ADJ | 11KV美豐線(VD27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | F8 PH RY | PHA | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_PHA | 11KV學工線(VD28) 相間RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F8 GD RY | GDA | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_GDA | 11KV學工線(VD28) 接地RY | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | F8 CB | 79 U/L | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_79UL | 11KV學工線(VD28) 79RY U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | F8 LCO | ADJ(U/L) | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_ADJ | 11KV學工線(VD28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F9 PH RY | PHA | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_PHA | 11KV學興線(VD29) 相間RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | F9 GD RY | GDA | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_GDA | 11KV學興線(VD29) 接地RY | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | F9 CB | 79 U/L | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_79UL | 11KV學興線(VD29) 79RY U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | F9 LCO | ADJ(U/L) | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_ADJ | 11KV學興線(VD29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F10 PH RY | PHA | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_PHA | 11KV學甲線(VD30) 相間RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F10 GD RY | GDA | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_GDA | 11KV學甲線(VD30) 接地RY | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | F10 CB | 79 U/L | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_79UL | 11KV學甲線(VD30) 79RY U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | F10 LCO | ADJ(U/L) | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_ADJ | 11KV學甲線(VD30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | F11 PH RY | PHA | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_PHA | 11KV新生線(VD31) 相間RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | F11 GD RY | GDA | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_GDA | 11KV新生線(VD31) 接地RY | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0100 | 1-35-07 |  | 1-64 | F11 CB | 79 U/L | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_79UL | 11KV新生線(VD31) 79RY U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | F11 LCO | ADJ(U/L) | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_ADJ | 11KV新生線(VD31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F12 PH RY | PHA | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_PHA | 11KV錦湖線(VD32) 相間RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F12 GD RY | GDA | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_GDA | 11KV錦湖線(VD32) 接地RY | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0101 | 1-35-08 |  | 1-65 | F12 CB | 79 U/L | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_79UL | 11KV錦湖線(VD32) 79RY U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | F12 LCO | ADJ(U/L) | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_ADJ | 11KV錦湖線(VD32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | F13 PH RY | PHA | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_PHA | 11KV達明線(VD33) 相間RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F13 GD RY | GDA | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_GDA | 11KV達明線(VD33) 接地RY | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0102 | 1-35-09 |  | 1-66 | F13 CB | 79 U/L | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_79UL | 11KV達明線(VD33) 79RY U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | F13 LCO | ADJ(U/L) | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_ADJ | 11KV達明線(VD33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F14 PH RY | PHA | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_PHA | 11KV三慈線(VD34) 相間RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | F14 GD RY | GDA | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_GDA | 11KV三慈線(VD34) 接地RY | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0103 | 1-35-10 |  | 1-67 | F14 CB | 79 U/L | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_79UL | 11KV三慈線(VD34) 79RY U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | F14 LCO | ADJ(U/L) | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_ADJ | 11KV三慈線(VD34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F15 PH RY | PHA | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_PHA | 11KV山寮線(VD35) 相間RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F15 GD RY | GDA | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_GDA | 11KV山寮線(VD35) 接地RY | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0104 | 1-35-11 |  | 1-68 | F15 CB | 79 U/L | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_79UL | 11KV山寮線(VD35) 79RY U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | F15 LCO | ADJ(U/L) | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_ADJ | 11KV山寮線(VD35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VD21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | F1 CB | CB ON/OFF | 學平線 |  | aaab | B2/S43_D1 | [8 empty] | 學甲SS.VD21_CB | VD21(11KV學平線) CB | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD21_ES | VD21_ES (非取樣點) | FEEDER | [5 empty] | 147 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VD22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | F2 CB | CB ON/OFF | 信義線 |  | aabb | B2/S43_D1 | [8 empty] | 學甲SS.VD22_CB | VD22(11KV信義線) CB | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD22_ES | VD22_ES (非取樣點) | FEEDER | [5 empty] | 149 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VD23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F3 CB | CB ON/OFF | 中洲線 |  | aacb | B2/S43_D1 | [8 empty] | 學甲SS.VD23_CB | VD23(11KV中洲線) CB | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD23_ES | VD23_ES (非取樣點) | FEEDER | [5 empty] | 151 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VD24/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | F4 CB | CB ON/OFF | 宅港線 |  | aaeb | B2/S43_D1 | [8 empty] | 學甲SS.VD24_CB | VD24(11KV宅港線) CB | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD24_ES | VD24_ES (非取樣點) | FEEDER | [5 empty] | 153 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VD25/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | F5 CB | CB ON/OFF | 文化線 |  | aafb | B2/S43_D1 | [8 empty] | 學甲SS.VD25_CB | VD25(11KV文化線) CB | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD25_ES | VD25_ES (非取樣點) | FEEDER | [5 empty] | 155 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VD26/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | F6 CB | CB ON/OFF | 竹埔線 |  | abab | B2/S43_D1 | [8 empty] | 學甲SS.VD26_CB | VD26(11KV竹埔線) CB | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD26_ES | VD26_ES (非取樣點) | FEEDER | [5 empty] | 157 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VD27/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | F7 CB | CB ON/OFF | 美豐線 |  | abbb | B2/S43_D1 | [8 empty] | 學甲SS.VD27_CB | VD27(11KV美豐線) CB | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD27_ES | VD27_ES (非取樣點) | FEEDER | [5 empty] | 159 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VD28/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | F8 CB | CB ON/OFF | 學工線 |  | abdb | B2/S43_D1 | [8 empty] | 學甲SS.VD28_CB | VD28(11KV學工線) CB | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD28_ES | VD28_ES (非取樣點) | FEEDER | [5 empty] | 161 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBUS | L/VD29/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | F9 CB | CB ON/OFF | 學興線 |  | acab | B2/S43_D1 | [8 empty] | 學甲SS.VD29_CB | VD29(11KV學興線) CB | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD29_ES | VD29_ES (非取樣點) | FEEDER | [5 empty] | 163 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBUS | L/VD30/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | F10 CB | CB ON/OFF | 學甲線 |  | accb | B2/S43_D1 | [8 empty] | 學甲SS.VD30_CB | VD30(11KV學甲線) CB | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD30_ES | VD30_ES (非取樣點) | FEEDER | [5 empty] | 165 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VD31/T1 |  |  | 0140 |  | 0092 | 1-11-04 |  | 1-5C | F11 CB | CB ON/OFF | 新生線 |  | adab | B2/S43_D1 | [8 empty] | 學甲SS.VD31_CB | VD31(11KV新生線) CB | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD31_ES | VD31_ES (非取樣點) | FEEDER | [5 empty] | 167 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VD32/T1 |  |  | 0141 |  | 0093 | 1-11-05 |  | 1-5D | F12 CB | CB ON/OFF | 錦湖線 |  | adbb | B2/S43_D1 | [8 empty] | 學甲SS.VD32_CB | VD32(11KV錦湖線) CB | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD32_ES | VD32_ES (非取樣點) | FEEDER | [5 empty] | 169 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VD33/T1 |  |  | 0142 |  | 0094 | 1-11-06 |  | 1-5E | F13 CB | CB ON/OFF | 達明線 |  | addb | B2/S43_D1 | [8 empty] | 學甲SS.VD33_CB | VD33(11KV達明線) CB | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD33_ES | VD33_ES (非取樣點) | FEEDER | [5 empty] | 171 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VD34/T1 |  |  | 0143 |  | 0095 | 1-11-07 |  | 1-5F | F14 CB | CB ON/OFF | 三慈線 |  | adeb | B2/S43_D1 | [8 empty] | 學甲SS.VD34_CB | VD34(11KV三慈線) CB | FEEDER |  |  |  |  | CDC | 172 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD34_ES | VD34_ES (非取樣點) | FEEDER | [5 empty] | 173 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VD35/T1 |  |  | 0144 |  | 0096 | 1-12-00 |  | 1-60 | F15 CB | CB ON/OFF | 山寮線 |  | adfb | B2/S43_D1 | [8 empty] | 學甲SS.VD35_CB | VD35(11KV山寮線) CB | FEEDER |  |  |  |  | CDC | 174 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD35_ES | VD35_ES (非取樣點) | FEEDER | [5 empty] | 175 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1 TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 176 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1 TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 177 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1 TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 178 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2 TIE R相電流 | A1 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 179 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2 TIE S相電流 | A2 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 180 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2 TIE T相電流 | A3 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 181 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2ABUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | zzzz | B2/S43_D1 | [8 empty] | 學甲SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 182 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIE PH RY | PHA | #1 TIE CB |  |  | B2/S43_D1 | [8 empty] | 學甲SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 183 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1 TIE GD RY | GDA | #1 TIE CB |  |  | B2/S43_D1 | [8 empty] | 學甲SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 184 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BBUS | B/3BUS |  |  | 0123 |  | 0071 | 1-0F-03 |  | 1-47 | #2 TIE CB | CB ON/OFF | #2 TIE CB |  | zzzz | B2/S43_D1 | [8 empty] | 學甲SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 185 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2 TIEPH RY | PHA | #2 TIE CB |  |  | B2/S43_D1 | [8 empty] | 學甲SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 186 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #2 TIEGD RY | GDA | #2 TIE CB |  |  | B2/S43_D1 | [8 empty] | 學甲SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 187 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.TIE1DS | TIE1DS (非取樣點) | TIE | [5 empty] | 188 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.TIE2DS | TIE2DS (非取樣點) | TIE | [5 empty] | 189 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | TIE1DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.TIE1DS2 | TIE1DS2 (非取樣點) | TIE | [5 empty] | 190 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | TIE2DS(非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.TIE2DS2 | TIE2DS2 (非取樣點) | TIE | [5 empty] | 191 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 192 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 193 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 194 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 195 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 196 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 MTR | MW | 二號主變 | MW_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 197 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 MTR | MVAR | 二號主變 | MVAR_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 198 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 MTR R電流 | A1 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 199 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 MTR S電流 | A2 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 200 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 MTR T電流 | A3 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 201 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 MTR | MW | 三號主變 | MW_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 202 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 MTR | MVAR | 三號主變 | MVAR_-36_36(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 203 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 MTR R電流 | A1 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 204 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 MTR S電流 | A2 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 205 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 MTR T電流 | A3 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 206 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 207 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 208 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 209 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH | 一號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 210 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 211 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 212 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 213 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 214 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2TR | MWH | 二號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 215 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2TR | MVARH(+) | 二號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 216 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 217 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 218 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 MTR | TAP | 三號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 219 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3TR | MWH | 三號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 220 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3TR | MVARH(+) | 三號主變 |  |  | B1/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 221 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aabb | B3/S43_D1 | [8 empty] | 學甲SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 222 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 223 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 224 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aafb | B3/S43_D1 | [8 empty] | 學甲SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 225 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 226 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 227 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aahb | B3/S43_D1 | [8 empty] | 學甲SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 228 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 229 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S43_D1 | [8 empty] | 學甲SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 230 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1 MTR | CB ON/OFF | 一號主變二次側 |  | aada | B2/S43_D1 | [8 empty] | 學甲SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 231 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | CB | 2MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2ABUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2 MTR A | CB ON/OFF | 二號主變二次側(A) |  | abca | B2/S43_D1 | [8 empty] | 學甲SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 232 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | CB | 2MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BBUS | T/2MTR |  |  | 0012 |  | 0070 | 1-01-04 |  | 1-46 | #2 MTR B | CB ON/OFF | 二號主變二次側(B) |  | acba | B2/S43_D1 | [8 empty] | 學甲SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 233 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BUS | T/3MTR |  |  | 0023 |  | 0089 | 1-02-07 |  | 1-59 | #3 MTR | CB ON/OFF | 三號主變二次側(A) |  | adca | B2/S43_D1 | [8 empty] | 學甲SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 234 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 235 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 236 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1 MTR | 51ZA | 一號主變 51Z RY |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 237 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 238 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1 MTR | 87 LS | 一號 主變87 RY使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 239 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 240 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 241 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 242 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 243 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2 MTR | 87 LS | 二號 主變87 RY使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 244 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 770 | PHA | 三號主變 51 RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 245 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 770 | GDA | 三號主變 51N RY |  |  | B3/S43_D1 | [8 empty] | 學甲SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 246 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3 MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 247 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3MTR | 87A | 三號主變差動電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 248 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3 MTR | 87 LS | 三號 主變87 RY使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 249 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1 MTR | PHA | 一號主變二次側 51 RY |  |  | B2/S43_D1 | [8 empty] | 學甲SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 250 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1 MTR | TRA | 一號主變重故障 |  | a | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 251 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1 MTR | TRF | 一號主變輕故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 252 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1 MTR | S/L | 一號主變 OLTC(中心/現場) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 253 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1 MTR | A/M | 一號主變 OLTC(自動/手動) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 254 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2 MTR A | PHA | 二號主變二次(A)51 RY |  |  | B2/S43_D1 | [8 empty] | 學甲SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 255 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2 MTR B | PHA | 二號主變二次(B)51 RY |  |  | B2/S43_D1 | [8 empty] | 學甲SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 256 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-34-00 |  |  | #2 MTR | TRA | 二號主變重故障 |  | a | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 257 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2 MTR | TRF | 二號主變輕故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 258 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2 MTR | S/L | 二號主變 OLTC(中心/現場) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 259 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2 MTR | A/M | 二號主變 OLTC(自動/手動) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 260 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3 MTR | PHA | 三號主變二次(A)51 RY |  |  | B2/S43_D1 | [8 empty] | 學甲SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 261 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0336 |  |  | 1-35-00 |  |  | #3 MTR | 3TRA | 三號主變重故障 |  | a | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 262 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3 MTR | 3TRF | 三號主變輕故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 263 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3 MTR | S/L | 三號主變 OLTC(中心/現場) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 264 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3 MTR | A/M | 三號主變 OLTC(自動/手動) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 265 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | 一號主變 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 266 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | 二號主變 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 267 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0044 | 1-38-04 | 1-38-05 | 1-2C | 771 | ABS ON | 三號主變 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 268 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1 MTR | 96A | 一號主變 96PA 電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 269 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1 MTR | TAPA | 一號主變TAP遲滯 (48TX) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 270 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1 MTR | 1ACF | 一號主變AC電源失效 (27欠壓) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 271 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2 MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 272 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2 MTR | TAPA | 二號主變TAP遲滯 (48TX) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 273 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2MTR | 2ACF | 二號主變AC電源失效(27欠壓) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 274 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3MTR | 96A | 三號主變 96D,63A RY |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 275 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3 MTR | TAPA | 三號主變TAP遲滯 (48TX) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 276 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | #3 MTR | #3ACF | 三號主變AC電源失效(27欠壓) |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 277 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | SC 69KV |  | aaaa | B2/S43_A1 | [8 empty] | 學甲SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 278 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 279 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | aagb | B2/S43_D1 | [8 empty] | 學甲SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 280 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1 SC | A/M | 一號SC 乏控器(自動/手動) |  |  | B2/S43_D1 | [8 empty] | 學甲SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 281 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 282 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BBUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC | CB ON/OFF | #2 11KV SC |  | acdb | B2/S43_D1 | [8 empty] | 學甲SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 283 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2 SC | A/M | 二號 SC乏控器(自動/手動) |  |  | B2/S43_D1 | [8 empty] | 學甲SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 284 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.220ES | 220ES (非取樣點) | SC | [5 empty] | 285 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BUS | C/3SC |  |  | 0139 |  | 0091 | 1-11-03 |  | 1-5B | #3 11KV SC | CB ON/OFF | #3 11KV SC |  | adgb | B2/S43_D1 | [8 empty] | 學甲SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 286 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0099 | 1-35-06 |  | 1-63 | #3 SC | A/M | 三號 SC乏控器(自動/手動) |  |  | B2/S43_D1 | [8 empty] | 學甲SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 287 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.230ES | 230ES (非取樣點) | SC | [5 empty] | 288 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0390 | 391 | 0039 | 1-38-06 | 1-38-07 | 1-27 | 811 | ABS ON | 69KVSC |  |  | B2/S43_A1 | [8 empty] | 學甲SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 289 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 810 | PHA GDA | SC 69KV 51 51N RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 290 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 810 | UVA OVA | SC 69KV 27 59N RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 291 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.810LE | 810LE (非取樣點) | SC | [5 empty] | 292 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1 SC5151NRY | SCA | #1 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 293 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1 SC2759RY | UVA | #1 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 294 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2 SC5151NRY | SCA | #2 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 295 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2 SC2759RY | UVA | #2 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 296 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | #3SC5151NRY | SCA | #3 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 297 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #3SC2759RY | UVA | #3 11KV SC |  |  | B2/S43_D1 | [8 empty] | 學甲SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 298 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 11KV(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11KV_#1SCDS | 11KV_#1SCDS (非取樣點) | SC | [5 empty] | 299 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 11KV(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11KV_#2SCDS | 11KV_#2SCDS (非取樣點) | SC | [5 empty] | 300 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 11KV(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11KV_#3SCDS | 11KV_#3SCDS (非取樣點) | SC | [5 empty] | 301 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 302 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 303 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 304 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 305 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 306 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 307 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 學甲SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 308 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 309 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 其他重故障 |  | 其他重故障 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 310 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  | 其他輕故障 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 311 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池警報 |  | 洩油池警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 開關場 |  | 水氣霧釋放 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化門禁(1) | 水氣霧釋放 | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 控制室旁 |  | 所内淹水高水位 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化門禁(2) | 所內淹水高水位 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 控制室旁 |  | 所内淹水低水位 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化門禁(3) | 所內淹水低水位 | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | 開關場 |  | 水氣霧警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化防盜(1) | 水氣霧警報 | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | 開關場 |  | 水氣霧故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化防盜(2) | 水氣霧故障 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | MCSG |  | MCSG偵煙警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.無人化防盜(3) | MCSG偵煙警報 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場照明(A) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S43_D1 | [8 empty] | 學甲SS.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明(B) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S43_D1 | [8 empty] | 學甲SS.開關場照明(B) | 開關場照明(B) | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 控制室 |  | CO2 警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.火災警報(1) | CO2警報 | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 控制室 |  | CO2 故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.火災警報(2) | CO2故障 | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.火災警報(3) | 火災警報(3) | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內電源欠壓 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 | DCA | NFB跳脫監視 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.直流電源DCA | NFB跳脫監視 | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCE | 直流電源接地故障 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S43_D1 | [8 empty] | 學甲SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS 89A | ABS NFB跳脫警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | SCA | SC警報 | Element | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV SC | 69KVSC AL | 69KVSC警報 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KV_SC警報 | 69KV SC警報 | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | Door |  |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.門禁 | 門禁 | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0380 |  |  | 1-37-12 |  |  | 910 | 87RYFA | 910數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.910_RYFA | 新營學甲一路(910)數位電驛故障 | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0382 |  |  | 1-37-14 |  |  | 730 | 87RYFA | 730數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.730_RYFA | 學甲佳里一路(730)數位電驛故障 | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87CFA |  | B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0381 |  |  | 1-37-13 |  |  | 910 | 87CFA | 910通訊故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.910_87CFA | 新營學甲一路(910)87RY通訊故障 | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 730 | 730 |  | 87CFA |  | B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0383 |  |  | 1-37-15 |  |  | 730 | 87CFA | 730通訊故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.730_87CFA | 學甲佳里一路(730)87RY通訊故障 | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 乏 | VAR | 三慈線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.三慈線KVAR | 11KV三慈線 KVAR | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 R相電流 | A1 | 三慈線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.三慈線A1 | 11KV三慈線 R相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F14 S相電流 | A2 | 三慈線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.三慈線A2 | 11KV三慈線 S相AMP | FEEDER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F14 T相電流 | A3 | 三慈線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.三慈線A3 | 11KV三慈線 T相AMP | FEEDER |  |  |  |  | CDC | 343 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F14 N相電流 | AMP | 三慈線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.三慈線A0 | 11KV三慈線 N相AMP | FEEDER |  |  |  |  | CDC | 344 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 乏 | VAR | 山寮線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.山寮線KVAR | 11KV山寮線 KVAR | FEEDER |  |  |  |  | CDC | 345 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 R相電流 | A1 | 山寮線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.山寮線A1 | 11KV山寮線 R相AMP | FEEDER |  |  |  |  | CDC | 346 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 S相電流 | A2 | 山寮線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.山寮線A2 | 11KV山寮線 S相AMP | FEEDER |  |  |  |  | CDC | 347 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F15 T相電流 | A3 | 山寮線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.山寮線A3 | 11KV山寮線 T相AMP | FEEDER |  |  |  |  | CDC | 348 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F15 N相電流 | AMP | 山寮線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.山寮線A0 | 11KV山寮線 N相AMP | FEEDER |  |  |  |  | CDC | 349 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 中洲線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.中洲線KVAR | 11KV中洲線 KVAR | FEEDER |  |  |  |  | CDC | 350 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 中洲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.中洲線A1 | 11KV中洲線 R相AMP | FEEDER |  |  |  |  | CDC | 351 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 中洲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.中洲線A2 | 11KV中洲線 S相AMP | FEEDER |  |  |  |  | CDC | 352 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 中洲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.中洲線A3 | 11KV中洲線 T相AMP | FEEDER |  |  |  |  | CDC | 353 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 中洲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.中洲線A0 | 11KV中洲線 N相AMP | FEEDER |  |  |  |  | CDC | 354 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 文化線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.文化線KVAR | 11KV文化線 KVAR | FEEDER |  |  |  |  | CDC | 355 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 文化線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.文化線A1 | 11KV文化線 R相AMP | FEEDER |  |  |  |  | CDC | 356 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 文化線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.文化線A2 | 11KV文化線 S相AMP | FEEDER |  |  |  |  | CDC | 357 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 文化線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.文化線A3 | 11KV文化線 T相AMP | FEEDER |  |  |  |  | CDC | 358 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 文化線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.文化線A0 | 11KV文化線 N相AMP | FEEDER |  |  |  |  | CDC | 359 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 宅港線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.宅港線KVAR | 11KV宅港線 KVAR | FEEDER |  |  |  |  | CDC | 360 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 宅港線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.宅港線A1 | 11KV宅港線 R相AMP | FEEDER |  |  |  |  | CDC | 361 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 宅港線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.宅港線A2 | 11KV宅港線 S相AMP | FEEDER |  |  |  |  | CDC | 362 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 宅港線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.宅港線A3 | 11KV宅港線 T相AMP | FEEDER |  |  |  |  | CDC | 363 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 宅港線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.宅港線A0 | 11KV宅港線 N相AMP | FEEDER |  |  |  |  | CDC | 364 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 乏 | VAR | 竹埔線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.竹埔線KVAR | 11KV竹埔線 KVAR | FEEDER |  |  |  |  | CDC | 365 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F6 R相電流 | A1 | 竹埔線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.竹埔線A1 | 11KV竹埔線 R相AMP | FEEDER |  |  |  |  | CDC | 366 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F6 S相電流 | A2 | 竹埔線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.竹埔線A2 | 11KV竹埔線 S相AMP | FEEDER |  |  |  |  | CDC | 367 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F6 T相電流 | A3 | 竹埔線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.竹埔線A3 | 11KV竹埔線 T相AMP | FEEDER |  |  |  |  | CDC | 368 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | F6 N相電流 | AMP | 竹埔線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.竹埔線A0 | 11KV竹埔線 N相AMP | FEEDER |  |  |  |  | CDC | 369 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 信義線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.信義線KVAR | 11KV信義線 KVAR | FEEDER |  |  |  |  | CDC | 370 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 信義線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.信義線A1 | 11KV信義線 R相AMP | FEEDER |  |  |  |  | CDC | 371 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 信義線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.信義線A2 | 11KV信義線 S相AMP | FEEDER |  |  |  |  | CDC | 372 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 信義線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.信義線A3 | 11KV信義線 T相AMP | FEEDER |  |  |  |  | CDC | 373 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 信義線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.信義線A0 | 11KV信義線 N相AMP | FEEDER |  |  |  |  | CDC | 374 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 乏 | VAR | 美豐線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.美豐線KVAR | 11KV美豐線 KVAR | FEEDER |  |  |  |  | CDC | 375 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 R相電流 | A1 | 美豐線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.美豐線A1 | 11KV美豐線 R相AMP | FEEDER |  |  |  |  | CDC | 376 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 S相電流 | A2 | 美豐線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.美豐線A2 | 11KV美豐線 S相AMP | FEEDER |  |  |  |  | CDC | 377 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F7 T相電流 | A3 | 美豐線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.美豐線A3 | 11KV美豐線 T相AMP | FEEDER |  |  |  |  | CDC | 378 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F7 N相電流 | AMP | 美豐線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.美豐線A0 | 11KV美豐線 N相AMP | FEEDER |  |  |  |  | CDC | 379 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 乏 | VAR | 新生線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.新生線KVAR | 11KV新生線 KVAR | FEEDER |  |  |  |  | CDC | 380 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 R相電流 | A1 | 新生線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.新生線A1 | 11KV新生線 R相AMP | FEEDER |  |  |  |  | CDC | 381 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F11 S相電流 | A2 | 新生線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.新生線A2 | 11KV新生線 S相AMP | FEEDER |  |  |  |  | CDC | 382 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F11 T相電流 | A3 | 新生線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.新生線A3 | 11KV新生線 T相AMP | FEEDER |  |  |  |  | CDC | 383 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F11 N相電流 | AMP | 新生線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.新生線A0 | 11KV新生線 N相AMP | FEEDER |  |  |  |  | CDC | 384 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 乏 | VAR | 達明線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.達明線KVAR | 11KV達明線 KVAR | FEEDER |  |  |  |  | CDC | 385 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 R相電流 | A1 | 達明線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.達明線A1 | 11KV達明線 R相AMP | FEEDER |  |  |  |  | CDC | 386 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 S相電流 | A2 | 達明線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.達明線A2 | 11KV達明線 S相AMP | FEEDER |  |  |  |  | CDC | 387 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 T相電流 | A3 | 達明線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.達明線A3 | 11KV達明線 T相AMP | FEEDER |  |  |  |  | CDC | 388 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F13 N相電流 | AMP | 達明線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.達明線A0 | 11KV達明線 N相AMP | FEEDER |  |  |  |  | CDC | 389 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 乏 | VAR | 學工線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學工線KVAR | 11KV學工線 KVAR | FEEDER |  |  |  |  | CDC | 390 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 R相電流 | A1 | 學工線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學工線A1 | 11KV學工線 R相AMP | FEEDER |  |  |  |  | CDC | 391 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 S相電流 | A2 | 學工線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學工線A2 | 11KV學工線 S相AMP | FEEDER |  |  |  |  | CDC | 392 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 T相電流 | A3 | 學工線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學工線A3 | 11KV學工線 T相AMP | FEEDER |  |  |  |  | CDC | 393 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F8 N相電流 | AMP | 學工線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學工線A0 | 11KV學工線 N相AMP | FEEDER |  |  |  |  | CDC | 394 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F10 乏 | VAR | 學甲線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學甲線KVAR | 11KV學甲線 KVAR | FEEDER |  |  |  |  | CDC | 395 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 R相電流 | A1 | 學甲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學甲線A1 | 11KV學甲線 R相AMP | FEEDER |  |  |  |  | CDC | 396 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 S相電流 | A2 | 學甲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學甲線A2 | 11KV學甲線 S相AMP | FEEDER |  |  |  |  | CDC | 397 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 T相電流 | A3 | 學甲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學甲線A3 | 11KV學甲線 T相AMP | FEEDER |  |  |  |  | CDC | 398 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F10 N相電流 | AMP | 學甲線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學甲線A0 | 11KV學甲線 N相AMP | FEEDER |  |  |  |  | CDC | 399 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 乏 | VAR | 錦湖線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.錦湖線KVAR | 11KV錦湖線 KVAR | FEEDER |  |  |  |  | CDC | 400 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 R相電流 | A1 | 錦湖線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.錦湖線A1 | 11KV錦湖線 R相AMP | FEEDER |  |  |  |  | CDC | 401 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 S相電流 | A2 | 錦湖線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.錦湖線A2 | 11KV錦湖線 S相AMP | FEEDER |  |  |  |  | CDC | 402 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F12 T相電流 | A3 | 錦湖線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.錦湖線A3 | 11KV錦湖線 T相AMP | FEEDER |  |  |  |  | CDC | 403 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F12 N相電流 | AMP | 錦湖線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.錦湖線A0 | 11KV錦湖線 N相AMP | FEEDER |  |  |  |  | CDC | 404 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S43_D1 | [8 empty] | 學甲SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 405 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 學平線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學平線KVAR | 11KV學平線 KVAR | FEEDER |  |  |  |  | CDC | 406 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 學平線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學平線A1 | 11KV學平線 R相AMP | FEEDER |  |  |  |  | CDC | 407 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 學平線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學平線A2 | 11KV學平線 S相AMP | FEEDER |  |  |  |  | CDC | 408 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 學平線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學平線A3 | 11KV學平線 T相AMP | FEEDER |  |  |  |  | CDC | 409 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 學平線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學平線A0 | 11KV學平線 N相AMP | FEEDER |  |  |  |  | CDC | 410 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 乏 | VAR | 學興線 | KVAR_-9000_9000(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學興線KVAR | 11KV學興線 KVAR | FEEDER |  |  |  |  | CDC | 411 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 R相電流 | A1 | 學興線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學興線A1 | 11KV學興線 R相AMP | FEEDER |  |  |  |  | CDC | 412 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 S相電流 | A2 | 學興線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學興線A2 | 11KV學興線 S相AMP | FEEDER |  |  |  |  | CDC | 413 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 T相電流 | A3 | 學興線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學興線A3 | 11KV學興線 T相AMP | FEEDER |  |  |  |  | CDC | 414 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F9 N相電流 | AMP | 學興線 | A_-500_500(-2000_2000) |  | B2/S43_D1 | [8 empty] | 學甲SS.學興線A0 | 11KV學興線 N相AMP | FEEDER |  |  |  |  | CDC | 415 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0016 |  |  | 1-90 |  |  | 69KV BUS # 2 | KV | 69KV BUS2 PT | kV_-90_90(-2000_2000) | aba | B2/S43_A1 | [8 empty] | 學甲SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 416 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | I |  | INSERT | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 600 TIE | A | 600 TIE 電流 | A_-1200_1200(-2000_2000) |  | B2/S43_A1 | [8 empty] | 學甲SS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 417 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1MTR | #1 63Q | #1MTR ULTC保護 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | [5 empty] | 418 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #1MTR | #1 96B1 | #1MTR撲氣一段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 419 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #1MTR | #1 96B2 | #1MTR撲氣二段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | [5 empty] | 420 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1MTR | #1 96D | #1MTR放壓裝置 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | [5 empty] | 421 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1MTR | #1 96P | #1MTR突壓電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | [5 empty] | 422 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #2MTR | #2 63Q | #2MTR ULTC保護 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | [5 empty] | 423 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #2MTR | #2 96B1 | #2MTR撲氣一段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 424 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #2MTR | #2 96B2 | #2MTR撲氣二段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | [5 empty] | 425 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #2MTR | #2 96D | #2MTR放壓裝置 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | [5 empty] | 426 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2MTR | #2 96P | #2MTR突壓電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | [5 empty] | 427 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #3MTR | #3 63Q | #3MTR ULTC保護 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | [5 empty] | 428 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #3MTR | #3 96B1 | #3MTR撲氣一段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 429 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #3MTR | #3 96B2 | #3MTR撲氣二段 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | [5 empty] | 430 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #3MTR | #3 96D | #3MTR放壓裝置 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | [5 empty] | 431 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #3MTR | #3 96P | #3MTR突壓電驛 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | [5 empty] | 432 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0379 |  |  | 1-37-11 |  |  | 650 | 87CFA | 650通訊故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_87CFA | 新西學甲(650)87RY通訊故障 | OTHER | [5 empty] | 433 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0378 |  |  | 1-37-10 |  |  | 650 | 87RYFA | 650數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.650_RYFA | 新西學甲(650)數位電驛故障 | OTHER | [5 empty] | 434 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0377 |  |  | 1-37-09 |  |  | 630 | 87CFA | 630通訊故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_87CFA | 永華學甲(630)87RY通訊故障 | OTHER | [5 empty] | 435 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0376 |  |  | 1-37-08 |  |  | 630 | 87RYFA | 630數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.630_RYFA | 永華學甲(630)數位電驛故障 | OTHER | [5 empty] | 436 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV數位電驛故障 | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | IED | RYFA | 11KV IED 故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | [5 empty] | 437 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | PM | PMA | PowerMeter 故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.PMA | POWER METER故障 | OTHER | [5 empty] | 438 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1BUS | B/2BUS |  |  | 0038 |  | 0007 | 1-04-06 |  | 1-07 | 600 | CB ON/OFF | 600 TIE CB ON/OFF |  | zzzz | B2/S43_A1 | [8 empty] | 學甲SS.600_CB | 600(TIE) CB | TIE | [5 empty] | 439 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0428 | 429 | 0036 | 1-3A-12 | 1-3A-13 | 1-24 | 601 | DS ON | 601 DS-AS |  |  | B2/S43_A1 | [8 empty] | 學甲SS.601_DS | 601(TIE) DS | TIE | [5 empty] | 440 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0430 | 431 | 0037 | 1-3A-14 | 1-3A-15 | 1-25 | 602 | DS ON | 602 DS-AS |  |  | B2/S43_A1 | [8 empty] | 學甲SS.602_DS | 602(TIE) DS | TIE | [5 empty] | 441 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 600 | 87B1A | 600 TIE #1BUS 87 RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | [5 empty] | 442 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  | INSERT | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV #2BUS | UVA2 | 69KV BUS #2衡相監視 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 443 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 600 | 87B2A | 600 TIE #2BUS 87 RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | [5 empty] | 444 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | 87A | 69KV匯流排數位電驛故障 | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0470 |  |  | 1-3D-06 |  |  | 600 | 87BF | 69KV匯流排電驛故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KVBUS_BF | 69KV匯流排數位電驛故障 | OTHER | [5 empty] | 445 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0469 |  |  | 1-3D-05 |  |  | 600 | RYFA | 600 TIE 數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.600_RYFA | 600TIE數位電驛故障 | OTHER | [5 empty] | 446 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0464 |  | 0038 | 1-3D-00 |  | 1-26 | 600 | 87B1S | #1Bus 87 RY 使用/閉鎖 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69KV_87B1_U/L | 69KVBUS 87B1 U/L | OTHER | [5 empty] | 447 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0465 |  | 0040 | 1-3D-01 |  | 1-28 | 600 | 87B2S | #2Bus 87 RY 使用/閉鎖 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.69KV_87B2_U/L | 69KVBUS 87B2 U/L | OTHER | [5 empty] | 448 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | INSERT | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 600 | GDA | 600 TIE #1BUS 67N RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | OTHER | [5 empty] | 449 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | INSERT | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 600 | GDA | 600 TIE #2BUS 67N RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | OTHER | [5 empty] | 450 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | INSERT | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 600 | PHA | 600 TIE #1BUS 67 RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | OTHER | [5 empty] | 451 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | INSERT | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | 600 | PHA | 600 TIE #2BUS 67 RY |  |  | B2/S43_A1 | [8 empty] | 學甲SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | OTHER | [5 empty] | 452 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | ComPoint |  |  | 12B_CTFA |  | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0468 |  |  | 1-3D-04 |  |  | 600 | CTFA | 69KV BUS RY通訊故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.69KVBUS_CTFA | 69KVBUS CT故障 | OTHER | [5 empty] | 453 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0375 |  |  | 1-37-07 |  |  | 720 | 87CFA | 720通訊故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_87CFA | 新營學甲二路(720)87RY通訊故障 | OTHER | [5 empty] | 454 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0374 |  |  | 1-37-06 |  |  | 720 | 87RYFA | 720數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.720_RYFA | 新營學甲二路(720)數位電驛故障 | OTHER | [5 empty] | 455 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0373 |  |  | 1-37-05 |  |  | 620 | 87CFA | 620通訊故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_87CFA | 學甲佳里二路(620)87RY通訊故障 | OTHER | [5 empty] | 456 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0372 |  |  | 1-37-04 |  |  | 620 | 87RYFA | 620數位電驛故障 |  |  | B2/S43_A1 | [8 empty] | 學甲SS.620_RYFA | 學甲佳里二路(620)數位電驛故障 | OTHER | [5 empty] | 457 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0471 |  |  | 1-3D-07 |  |  | #1MTR IED | RYFA | #1MTR及饋線 IED 故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | [5 empty] | 458 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0475 |  |  | 1-3D-11 |  |  | #1MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 459 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0478 |  |  | 1-3D-14 |  |  | #1MTR 871S | 871S | #1MTR 87RY 1S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 460 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0479 |  |  | 1-3D-15 |  |  | #1MTR 872S | 872S | #1MTR 87RY 2S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 461 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0476 |  |  | 1-3D-12 |  |  | #2MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 462 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | #2MTR 871S | 871S | #2MTR 87RY 1S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 463 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | #2MTR 872S | 872S | #2MTR 87RY 2S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 464 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 2MTR | #2MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0472 |  |  | 1-3D-08 |  |  | #2MTR IED | RYFA | #2MTR及饋線 IED 故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | [5 empty] | 465 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0473 |  |  | 1-3D-09 |  |  | #3MTR IED | RYFA | #3MTR及饋線 IED 故障 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | [5 empty] | 466 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0477 |  |  | 1-3D-13 |  |  | #3MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 467 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | #3MTR 871S | 871S | #3MTR 87RY 1S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 468 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0303 |  |  | 1-32-15 |  |  | #3MTR 872S | 872S | #3MTR 87RY 2S使用/閉鎖 |  |  | B1/S43_D1 | [8 empty] | 學甲SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 469 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0180 |  | 0066 | 1-16-04 |  | 1-42 | #1 SSTR CB | CB ON/OFF | #1 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 470 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | #1 SSTR PH RY | PHA | #1 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 471 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | #1 SSTR GD RY | GDA | #1 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 472 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 490 | #3SSTR(490) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0183 |  | 0067 | 1-16-07 |  | 1-43 | #2 SSTR CB | CB ON/OFF | #2 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.490_CB | 490(#3SSTR) CB | OTHER | [5 empty] | 473 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 490 | #3SSTR(490) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | #2 SSTR PH RY | PHA | #2 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3SSTR_51A | #3SSTR 51RY | OTHER | [5 empty] | 474 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 490 | #3SSTR(490) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #2 SSTR GD RY | GDA | #2 SSTR |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | [5 empty] | 475 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  | 0065 | 1-14-00 |  | 1-41 | #1 TR 81 RY | 181A | #1 Main 81A |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MA_81A/S | #1MA 81RY | OTHER | [5 empty] | 476 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0107 | 1-33-13 |  | 1-6B | #1 MTR 81 RY | 81 U/L | #1 Main 81 使用/閉鎖 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | [5 empty] | 477 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  | 0086 | 1-14-01 |  | 1-56 | #2 TRA 81 RY | 2A81A | #2A Main 81A |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MA_81A/S | #2MA 81RY | OTHER | [5 empty] | 478 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0108 | 1-34-13 |  | 1-6C | #2 MTR A | 81 U/L | #2A Main 81 使用/閉鎖 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | [5 empty] | 479 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  | 0087 | 1-14-02 |  | 1-57 | #2 TRB 81 RY | 2B81A | #2B Main 81A |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MB_81A/S | #2MB 81RY | OTHER | [5 empty] | 480 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0334 |  | 0109 | 1-34-14 |  | 1-6D | #2 MTR B | 81 U/L | #2B Main 81 使用/閉鎖 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | [5 empty] | 481 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  | 0105 | 1-14-03 |  | 1-69 | #3 TR 81 RY | 381A | #3 Main 81A |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MA_81A/S | #3MA 81RY | OTHER | [5 empty] | 482 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0110 | 1-35-13 |  | 1-6E | #3 MTR | 81 U/L | #3 Main 81 使用/閉鎖 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | [5 empty] | 483 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS |  |  | 1GIS | #1GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1 GIS CB | CBA | #1 GIS斷路器重故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1GIS_CBA | #1GIS重故障 | OTHER | [5 empty] | 484 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 1GIS | #1GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1 GIS CB | CBF | #1 GIS斷路器輕故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#1GIS_CBF | #1GIS輕故障 | OTHER | [5 empty] | 485 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2GIS | #2GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2 GIS CB | CBA | #2 GIS斷路器重故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2GIS_CBA | #2GIS重故障 | OTHER | [5 empty] | 486 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 2GIS | #2GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2 GIS CB | CBF | #2 GIS斷路器輕故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#2GIS_CBF | #2GIS輕故障 | OTHER | [5 empty] | 487 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3GIS | #3GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3 GIS CB | CBA | #3 GIS斷路器重故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3GIS_CBA | #3GIS重故障 | OTHER | [5 empty] | 488 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS |  |  | 3GIS | #3GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3 GIS CB | CBF | #3 GIS斷路器輕故障 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.#3GIS_CBF | #3GIS輕故障 | OTHER | [5 empty] | 489 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 CB | KWH | 學平線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 490 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 CB | KWH | 信義線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 491 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 CB | KWH | 中洲線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 492 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 CB | KWH | 宅港線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 493 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 CB | KWH | 文化線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 494 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 CB | KWH | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 495 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 CB | KWH | 美豐線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 496 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 CB | KWH | 學工線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 497 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 CB | KWH | 學興線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 498 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 CB | KWH | 學甲線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 499 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F11 CB | KWH | 新生線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 500 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F12 CB | KWH | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 501 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F13 CB | KWH | 達明線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 502 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F14 CB | KWH | 三慈線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 503 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F15 CB | KWH | 山寮線 |  |  | B2/S43_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 504 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S43 | 學甲SS | 0 |  | ComPoint |  |  | 81_RYFA | [14 empty] | 0474 |  |  | 1-3D-10 |  |  | 81RY IED | RYFA | 81RY IED 故障 |  |  | B3/S43_D1 | [8 empty] | 學甲SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | F1 81 U/L | 81 U/L | F1 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_81U/L | 11KV學平線(VD21) 81RY U/L | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | F2 81 U/L | 81 U/L | F2 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_81U/L | 11KV信義線(VD22) 81RY U/L | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0490 |  |  | 1-3E-10 |  |  | F3 81 U/L | 81 U/L | F3 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_81U/L | 11KV中洲線(VD23) 81RY U/L | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0491 |  |  | 1-3E-11 |  |  | F4 81 U/L | 81 U/L | F4 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_81U/L | 11KV宅港線(VD24) 81RY U/L | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | F5 81 U/L | 81 U/L | F5 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_81U/L | 11KV文化線(VD25) 81RY U/L | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | F6 81 U/L | 81 U/L | F6 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_81U/L | 11KV竹埔線(VD26) 81RY U/L | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | F7 81 U/L | 81 U/L | F7 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_81U/L | 11KV美豐線(VD27) 81RY U/L | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | F8 81 U/L | 81 U/L | F8 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_81U/L | 11KV學工線(VD28) 81RY U/L | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | F9 81 U/L | 81 U/L | F9 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_81U/L | 11KV學興線(VD29) 81RY U/L | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | F10 81 U/L | 81 U/L | F10 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_81U/L | 11KV學甲線(VD30) 81RY U/L | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | F11 81 U/L | 81 U/L | F11 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_81U/L | 11KV新生線(VD31) 81RY U/L | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | F12 81 U/L | 81 U/L | F12 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_81U/L | 11KV錦湖線(VD32) 81RY U/L | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | F13 81 U/L | 81 U/L | F13 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_81U/L | 11KV達明線(VD33) 81RY U/L | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | F14 81 U/L | 81 U/L | F14 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_81U/L | 11KV三慈線(VD34) 81RY U/L | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | F15 81 U/L | 81 U/L | F15 81 U/L |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_81U/L | 11KV山寮線(VD35) 81RY U/L | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0448 |  |  | 1-3C-00 |  |  | F1 79 RY | 79LOA | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_79_LOA | 11KV學平線(VD21) 79LOA | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F1 81 RY | 81A | 學平線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD21_81A/S | 11KV學平線(VD21) 81RY | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0449 |  |  | 1-3C-01 |  |  | F2 79 RY | 79LOA | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_79_LOA | 11KV信義線(VD22) 79LOA | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F2 81 RY | 81A | 信義線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD22_81A/S | 11KV信義線(VD22) 81RY | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | F3 79 RY | 79LOA | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_79_LOA | 11KV中洲線(VD23) 79LOA | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F3 81 RY | 81A | 中洲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD23_81A/S | 11KV中洲線(VD23) 81RY | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0451 |  |  | 1-3C-03 |  |  | F4 79 RY | 79LOA | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_79_LOA | 11KV宅港線(VD24) 79LOA | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F4 81 RY | 81A | 宅港線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD24_81A/S | 11KV宅港線(VD24) 81RY | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0452 |  |  | 1-3C-04 |  |  | F5 79 RY | 79LOA | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_79_LOA | 11KV文化線(VD25) 79LOA | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | F5 81 RY | 81A | 文化線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD25_81A/S | 11KV文化線(VD25) 81RY | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0453 |  |  | 1-3C-05 |  |  | F6 79 RY | 79LOA | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_79_LOA | 11KV竹埔線(VD26) 79LOA | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | F6 81 RY | 81A | 竹埔線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD26_81A/S | 11KV竹埔線(VD26) 81RY | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0454 |  |  | 1-3C-06 |  |  | F7 79 RY | 79LOA | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_79_LOA | 11KV美豐線(VD27) 79LOA | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F7 81 RY | 81A | 美豐線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD27_81A/S | 11KV美豐線(VD27) 81RY | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0455 |  |  | 1-3C-07 |  |  | F8 79 RY | 79LOA | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_79_LOA | 11KV學工線(VD28) 79LOA | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F8 81 RY | 81A | 學工線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD28_81A/S | 11KV學工線(VD28) 81RY | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0456 |  |  | 1-3C-08 |  |  | F9 79 RY | 79LOA | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_79_LOA | 11KV學興線(VD29) 79LOA | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | F9 81 RY | 81A | 學興線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD29_81A/S | 11KV學興線(VD29) 81RY | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0457 |  |  | 1-3C-09 |  |  | F10 79 RY | 79LOA | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_79_LOA | 11KV學甲線(VD30) 79LOA | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F10 81 RY | 81A | 學甲線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD30_81A/S | 11KV學甲線(VD30) 81RY | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0458 |  |  | 1-3C-10 |  |  | F11 79 RY | 79LOA | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_79_LOA | 11KV新生線(VD31) 79LOA | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 81 RY | 81A | 新生線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD31_81A/S | 11KV新生線(VD31) 81RY | OTHER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0459 |  |  | 1-3C-11 |  |  | F12 79 RY | 79LOA | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_79_LOA | 11KV錦湖線(VD32) 79LOA | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | F12 81 RY | 81A | 錦湖線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD32_81A/S | 11KV錦湖線(VD32) 81RY | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0460 |  |  | 1-3C-12 |  |  | F13 79 RY | 79LOA | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_79_LOA | 11KV達明線(VD33) 79LOA | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 81 RY | 81A | 達明線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD33_81A/S | 11KV達明線(VD33) 81RY | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0461 |  |  | 1-3C-13 |  |  | F14 79 RY | 79LOA | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_79_LOA | 11KV三慈線(VD34) 79LOA | OTHER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F14 81 RY | 81A | 三慈線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD34_81A/S | 11KV三慈線(VD34) 81RY | OTHER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0462 |  |  | 1-3C-14 |  |  | F15 79 RY | 79LOA | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_79_LOA | 11KV山寮線(VD35) 79LOA | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | F15 81 RY | 81A | 山寮線 |  |  | B2/S43_D1 | [8 empty] | 學甲SS.VD35_81A/S | 11KV山寮線(VD35) 81RY | OTHER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | E1 | 2MA_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 552 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | E1 | 3M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.601E | 601E (非取樣點) | TIE | [5 empty] | 554 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.602E | 602E (非取樣點) | TIE | [5 empty] | 555 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | BE2 | 69B2E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_A1 | [8 empty] | 學甲SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 556 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391 (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 557 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 558 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 490 | #3SSTR(490) |  | D1 | 491 (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 559 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 490 | #3SSTR(490) |  | E1 | 491E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 560 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD21_DS | VD21_DS (非取樣點) | FEEDER | [5 empty] | 561 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD22_DS | VD22_DS (非取樣點) | FEEDER | [5 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD23_DS | VD23_DS (非取樣點) | FEEDER | [5 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD24_DS | VD24_DS (非取樣點) | FEEDER | [5 empty] | 564 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD25_DS | VD25_DS (非取樣點) | FEEDER | [5 empty] | 565 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD26_DS | VD26_DS (非取樣點) | FEEDER | [5 empty] | 566 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD27_DS | VD27_DS (非取樣點) | FEEDER | [5 empty] | 567 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD28_DS | VD28_DS (非取樣點) | FEEDER | [5 empty] | 568 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD29_DS | VD29_DS (非取樣點) | FEEDER | [5 empty] | 569 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD30_DS | VD30_DS (非取樣點) | FEEDER | [5 empty] | 570 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD31_DS | VD31_DS (非取樣點) | FEEDER | [5 empty] | 571 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD32_DS | VD32_DS (非取樣點) | FEEDER | [5 empty] | 572 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD33_DS | VD33_DS (非取樣點) | FEEDER | [5 empty] | 573 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD34_DS | VD34_DS (非取樣點) | FEEDER | [5 empty] | 574 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.VD35_DS | VD35_DS (非取樣點) | FEEDER | [5 empty] | 575 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | 101E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.101E | 101E (非取樣點) | TIE | [5 empty] | 576 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E2 | 102E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.102E | 102E (非取樣點) | TIE | [5 empty] | 577 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | 201E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.201E | 201E (非取樣點) | TIE | [5 empty] | 578 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | 202E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.202E | 202E (非取樣點) | TIE | [5 empty] | 579 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 580 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | D1 | 2MA_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 581 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | D1 | 2MB_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 582 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | E1 | 2MB_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 583 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | M3 | #3MTR(M3) |  | D1 | 3M_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 584 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 1BUS | #1BUS |  | BE1 | 11B1E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11B1E | 11B1E (非取樣點) | BUS | [5 empty] | 585 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 2BUS | #2BUS |  | BE2 | 11B2E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11B2E | 11B2E (非取樣點) | BUS | [5 empty] | 586 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 2BUS | #2BUS |  | BE0 | 11B2BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11B2BE | 11B2BE (非取樣點) | BUS | [5 empty] | 587 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 3BUS | #3BUS |  | BE3 | 11B3E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S43_D1 | [8 empty] | 學甲SS.11B3E | 11B3E (非取樣點) | BUS | [5 empty] | 588 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2 BUS | KV | 二號 BUS PT | kV_-9_9(-2000_2000) | aca | B2/S43_D1 | [8 empty] | 學甲SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S43 | 學甲SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S43_D1 | [12 empty] | 學甲SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S43/69/1BUS/V; OPRD2: S43/69/2BUS/V
S43 | 學甲SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S43_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S43/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S43 | 學甲SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S43_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_8 | OPRD1: S43/11/M1/MW; OPRD2: S43/11/M3/MW; OPRD3: S43/69/620/MW; OPRD4: S43/69/630/MW; OPRD5: S43/69/650/MW; OPRD6: S43/69/720/MW; OPRD7: S43/69/730/MW; OPRD8: S43/69/910/MW
S43 | 學甲SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S43_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S43/0/CalcPoint/OPRN2_MW
S43 | 學甲SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S43_D1 | [17 empty] | none
S43 | 學甲SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S43_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S43/0/CalcPoint/OPRN1; OPRD2: S43/0/CalcPoint/OPRN2; OPRD3: S43/0/CalcPoint/PRFL_UL
S43 | 學甲SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S43_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S43/11/M1/MW; OPRD2: S43/11/M1/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S43_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S43/11/M3/MW; OPRD2: S43/11/M3/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.620_AMP | 學甲佳里二路 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S43/69/620/MW; OPRD2: S43/69/620/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.630_AMP | 永華線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S43/69/630/MW; OPRD2: S43/69/630/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 650 | 新西～學甲線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.650_AMP | 新西線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S43/69/650/MW; OPRD2: S43/69/650/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.720_AMP | 新營學甲二路 AMP | LINE69 | AMP_CAL | C12R0831 | amp_cal | OPRD1: S43/69/720/MW; OPRD2: S43/69/720/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.730_AMP | 學甲佳里一路 AMP | LINE69 | AMP_CAL | C12R0831 | amp_cal | OPRD1: S43/69/730/MW; OPRD2: S43/69/730/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.910_AMP | 新營學甲一路 AMP | LINE69 | AMP_CAL | C12R0831 | amp_cal | OPRD1: S43/69/910/MW; OPRD2: S43/69/910/MVAR; OPRD3: S43/0/CalcPoint/Vbs2
S43 | 學甲SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S43_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S43/11/1BUS/V
S43 | 學甲SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S43_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S43/11/2BUS/V
S43 | 學甲SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S43_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S43/11/3BUS/V
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S43_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 學甲SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S43/11/M1/MW; OPRD2: S43/11/M1/MVAR
S43 | 學甲SS |  |  | 2MTR(A) | #2MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S43_D1 | LG_15 | 14.25 | 16.5 | 18.75 | 30 |  | -14.25 | -16.5 | -18.75 | -30 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S43/11/M2A/MW; OPRD2: S43/11/M2A/MVAR
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S43_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 學甲SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S43/11/M3/MW; OPRD2: S43/11/M3/MVAR
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S43_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S43//1MTR/MVA; OPRD2: 0
S43 | 學甲SS |  |  | 2MTR(A) | #2MTR(A) |  | LOAD | [9 empty] | B1/S43_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S43//2MTR(A)/MVA; OPRD2: 0
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S43_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S43//3MTR/MVA; OPRD2: 0
S43 | 學甲SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S43_D1 | [12 empty] | 學甲SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S43/11/M1/MW; OPRD2: S43/11/M1/MVAR
S43 | 學甲SS |  |  | 2MTR(A) | #2MTR(A) |  | PF | [9 empty] | B1/S43_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S43/11/M2A/MW; OPRD2: S43/11/M2A/MVAR
S43 | 學甲SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S43_D1 | [12 empty] | 學甲SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S43/11/M3/MW; OPRD2: S43/11/M3/MVAR
S43 | 學甲SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S43_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S43//1MTR/SupLocal; OPRD2: S43//1MTR/Tap Chan; OPRD3: NULL
S43 | 學甲SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S43_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S43//2MTR/SupLocal; OPRD2: S43//2MTR/Tap Chan; OPRD3: NULL
S43 | 學甲SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S43_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S43//3MTR/SupLocal; OPRD2: S43//3MTR/Tap Chan; OPRD3: NULL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/1BUS/V; OPRD2: S43/11/VD21/I_R; OPRD3: S43/11/VD21/I_S; OPRD4: S43/11/VD21/I_T
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/1BUS/V; OPRD2: S43/11/VD22/I_R; OPRD3: S43/11/VD22/I_S; OPRD4: S43/11/VD22/I_T
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/1BUS/V; OPRD2: S43/11/VD23/I_R; OPRD3: S43/11/VD23/I_S; OPRD4: S43/11/VD23/I_T
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/1BUS/V; OPRD2: S43/11/VD24/I_R; OPRD3: S43/11/VD24/I_S; OPRD4: S43/11/VD24/I_T
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/1BUS/V; OPRD2: S43/11/VD25/I_R; OPRD3: S43/11/VD25/I_S; OPRD4: S43/11/VD25/I_T
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S43/11/VD26/I_R; OPRD3: S43/11/VD26/I_S; OPRD4: S43/11/VD26/I_T
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S43/11/VD27/I_R; OPRD3: S43/11/VD27/I_S; OPRD4: S43/11/VD27/I_T
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S43/11/VD28/I_R; OPRD3: S43/11/VD28/I_S; OPRD4: S43/11/VD28/I_T
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S43/11/VD29/I_R; OPRD3: S43/11/VD29/I_S; OPRD4: S43/11/VD29/I_T
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S43/11/VD30/I_R; OPRD3: S43/11/VD30/I_S; OPRD4: S43/11/VD30/I_T
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/3BUS/V; OPRD2: S43/11/VD31/I_R; OPRD3: S43/11/VD31/I_S; OPRD4: S43/11/VD31/I_T
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/3BUS/V; OPRD2: S43/11/VD32/I_R; OPRD3: S43/11/VD32/I_S; OPRD4: S43/11/VD32/I_T
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/3BUS/V; OPRD2: S43/11/VD33/I_R; OPRD3: S43/11/VD33/I_S; OPRD4: S43/11/VD33/I_T
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/3BUS/V; OPRD2: S43/11/VD34/I_R; OPRD3: S43/11/VD34/I_S; OPRD4: S43/11/VD34/I_T
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S43/11/3BUS/V; OPRD2: S43/11/VD35/I_R; OPRD3: S43/11/VD35/I_S; OPRD4: S43/11/VD35/I_T
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD21/kVA; OPRD2: S43/11/VD21/KVAR
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD22/kVA; OPRD2: S43/11/VD22/KVAR
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD23/kVA; OPRD2: S43/11/VD23/KVAR
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD24/kVA; OPRD2: S43/11/VD24/KVAR
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD25/kVA; OPRD2: S43/11/VD25/KVAR
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD26/kVA; OPRD2: S43/11/VD26/KVAR
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD27/kVA; OPRD2: S43/11/VD27/KVAR
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD28/kVA; OPRD2: S43/11/VD28/KVAR
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD29/kVA; OPRD2: S43/11/VD29/KVAR
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD30/kVA; OPRD2: S43/11/VD30/KVAR
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD31/kVA; OPRD2: S43/11/VD31/KVAR
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD32/kVA; OPRD2: S43/11/VD32/KVAR
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD33/kVA; OPRD2: S43/11/VD33/KVAR
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD34/kVA; OPRD2: S43/11/VD34/KVAR
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S43_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S43/11/VD35/kVA; OPRD2: S43/11/VD35/KVAR
S43 | 學甲SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S43_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S43/11/M1/MW; OPRD2: S43/11/M3/MW
S43 | 學甲SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S43_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S43/11/M1/MVAR; OPRD2: S43/11/M3/MVAR
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S43_D1 | [12 empty] | 學甲SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S43/11/210/CB; OPRD2: 6.9; OPRD3: 0
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S43_D1 | [12 empty] | 學甲SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S43/11/220/CB; OPRD2: 6.9; OPRD3: 0
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S43_D1 | [12 empty] | 學甲SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S43/11/230/CB; OPRD2: 6.9; OPRD3: 0
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S43_A1 | [12 empty] | 學甲SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S43/69/810/CB; OPRD2: 69; OPRD3: 0
S43 | 學甲SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S43_D1 | [12 empty] | 學甲SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_26 | OPRD1: S43//1MTR/63Q; OPRD2: S43//1MTR/96PA; OPRD3: S43//1MTR/TRA; OPRD4: S43//1MTR/96D; OPRD5: S43//1MTR/96B2; OPRD6: S43//1MTR/96B1; OPRD7: S43//1MTR/87A; OPRD8: S43//1MTR/51ZA; OPRD9: S43//2MTR/63Q; OPRD10: S43//2MTR/TRA; OPRD11: S43//2MTR/96B1; OPRD12: S43//2MTR/96D; OPRD13: S43//2MTR/96B2; OPRD14: S43//2MTR/51ZA; OPRD15: S43//2MTR/96PA; OPRD16: S43//2MTR/87A; OPRD17: S43//3MTR/96B1; OPRD18: S43//3MTR/63Q; OPRD19: S43//3MTR/96D; OPRD20: S43//3MTR/96B2; OPRD21: S43//3MTR/96PA; OPRD22: S43//3MTR/87A; OPRD23: S43//3MTR/TRA; OPRD24: S43//3MTR/51ZA; OPRD25: S43/69/1BUS/87A; OPRD26: S43/69/2BUS/87A
S43 | 學甲SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S43_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S43//1MTR/TRF; OPRD2: S43//2MTR/TRF; OPRD3: S43//3MTR/TRF
S43 | 學甲SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S43_A1 | [17 empty] | lamp2CC | OPRD1: S43/0/RTU/RTU_R_L
S43 | 學甲SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S43_A1 | [17 empty] | lamp2CC | OPRD1: S43/0/StaDev/PSA
S43 | 學甲SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S43_A1 | [17 empty] | lamp2CC | OPRD1: S43/0/StaDev/PSF
S43 | 學甲SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S43_A1 | [17 empty] | lamp2CC | OPRD1: S43/0/StaDev/DCA
S43 | 學甲SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S43_A1 | [17 empty] | lamp2CC | OPRD1: S43/0/StaDev/DCE
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/CBA
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/CBF
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/ABS_89A
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | SCA | SC警報 |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/SCA
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | 87A | 69KV匯流排數位電驛故障 |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/87A
S43 | 學甲SS | 69 | 69kV | ComPoint_D1 |  |  | 12B_CTFA |  |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S43_D1 | [17 empty] | lamp2CC | OPRD1: S43/69/ComPoint/12B_CTFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S43 | 學甲SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 學甲SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S43/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.620_AMP | 學甲佳里二路 AMP | LINE69 | S43/69/620/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.630_AMP | 永華線 AMP | LINE69 | S43/69/630/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.650_AMP | 新西線 AMP | LINE69 | S43/69/650/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.720_AMP | 新營學甲二路 AMP | LINE69 | S43/69/720/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C12R0831 | 747.900024 | 747.900024 | 831.000000 | 1200.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 0 |  |  |  |  | 三慈線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.三慈線KVA | 11KV三慈線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 三慈線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.三慈線KW | 11KV三慈線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 山寮線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.山寮線KVA | 11KV山寮線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 山寮線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.山寮線KW | 11KV山寮線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 中洲線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.中洲線KVA | 11KV中洲線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 中洲線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.中洲線KW | 11KV中洲線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 文化線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.文化線KVA | 11KV文化線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 文化線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.文化線KW | 11KV文化線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 宅港線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.宅港線KVA | 11KV宅港線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 宅港線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.宅港線KW | 11KV宅港線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 竹埔線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.竹埔線KVA | 11KV竹埔線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 竹埔線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.竹埔線KW | 11KV竹埔線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 信義線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.信義線KVA | 11KV信義線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 信義線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.信義線KW | 11KV信義線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 美豐線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.美豐線KVA | 11KV美豐線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 美豐線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.美豐線KW | 11KV美豐線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 新生線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.新生線KVA | 11KV新生線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 新生線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.新生線KW | 11KV新生線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 達明線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.達明線KVA | 11KV達明線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 達明線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.達明線KW | 11KV達明線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學工線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學工線KVA | 11KV學工線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學工線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學工線KW | 11KV學工線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學甲線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學甲線KVA | 11KV學甲線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學甲線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學甲線KW | 11KV學甲線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 錦湖線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.錦湖線KVA | 11KV錦湖線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 錦湖線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.錦湖線KW | 11KV錦湖線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S43//1MTR/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_PF | #1MTR 功率因素 | DTR | S43//1MTR/PF |  | RPDC_PF_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S43//3MTR/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_PF | #3MTR 功率因素 | DTR | S43//3MTR/PF |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S43 | 學甲SS | 11 | 11kV | 210_SC | #1SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S43/11/210/MVAR |  | SC_CAL_11 |  |  | 39 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 11 | 11kV | 220_SC | #2SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S43/11/220/MVAR |  | SC_CAL_11 |  |  | 40 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 11 | 11kV | 230_SC | #3SC | 3 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S43/11/230/MVAR |  | SC_CAL_11 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S43/69/810/MVAR |  | SC_CAL_69 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學平線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學平線KVA | 11KV學平線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學平線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學平線KW | 11KV學平線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學興線KVA | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學興線KVA | 11KV學興線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 0 |  |  |  |  | 學興線KW | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.學興線KW | 11KV學興線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.730_AMP | 學甲佳里一路 AMP | LINE69 | S43/69/730/I |  | AMP_CAL |  |  | 47 | CalcAIPoint | [21 empty] | C12R0831 | 747.900024 | 747.900024 | 831.000000 | 1200.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | I | [25 empty] | ADCS_N | [8 empty] | 學甲SS.910_AMP | 新營學甲一路 AMP | LINE69 | S43/69/910/I |  | AMP_CAL |  |  | 48 | CalcAIPoint | [21 empty] | C12R0831 | 747.900024 | 747.900024 | 831.000000 | 1200.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S43 | 學甲SS | 69 | 69kV | 620_CB | 學甲佳里二路(620_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.620_CB_3 | 620(學甲佳里二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 49 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 630_CB | 永華線(630_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.630_CB_3 | 630(永華線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 50 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 650_CB | 新西線(650_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.650_CB_3 | 650(新西線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 51 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 720_CB | 新營學甲二路(720_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.720_CB_3 | 720(新營學甲二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 52 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.810_CB_3 | 810(69KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 53 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 學甲SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 54 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 學甲SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 55 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 學甲SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S43/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 57 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | STATION_FAULT_3 |  |  | 58 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620_AMP | 學甲佳里二路 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.620_AMP_A | 學甲佳里二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 620_AMP | 學甲佳里二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.620_AMP_3 | 學甲佳里二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 630_AMP | 永華線 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.630_AMP_A | 永華線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 630_AMP | 永華線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.630_AMP_3 | 永華線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 650_AMP | 新西線 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.650_AMP_A | 新西線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 650_AMP | 新西線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.650_AMP_3 | 新西線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 720_AMP | 新營學甲二路 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.720_AMP_A | 新營學甲二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 720_AMP | 新營學甲二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.720_AMP_3 | 新營學甲二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 66 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 1MTR_MVA | #1MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_MVA_3 | #1MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 68 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 2MTR_MVA | #2MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_MVA_3 | #2MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 69 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 70 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 3MTR_MVA | #3MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_MVA_3 | #3MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 71 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 730_CB | 學甲佳里一路(730_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.730_CB_3 | 730(學甲佳里一路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 73 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 910_CB | 新營學甲一路(910_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.910_CB_3 | 910(新營學甲一路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 730_AMP | 學甲佳里一路 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.730_AMP_A | 學甲佳里一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 730_AMP | 學甲佳里一路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.730_AMP_3 | 學甲佳里一路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 910_AMP | 新營學甲一路 | [27 empty] | ADCS_N | [8 empty] | 學甲SS.910_AMP_A | 新營學甲一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | 910_AMP | 新營學甲一路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.910_AMP_3 | 新營學甲一路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S43 | 學甲SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 學甲SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 79 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 600_CB | 600(600_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600_CB_3 | 600 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 600_RYFA | 600TIE數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600_RYFA_3 | 600TIE數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 81 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | BUS_BF | 匯流排數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KVBUS_BF_3 | 69KV匯流排數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 82 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600GDA(1) | #1BUS |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600GDA(1)_3 | 69KV #1BUS TIE(600) 67NA (D3) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 83 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600GDA(2) | #2BUS |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600GDA(2)_3 | 69KV #2BUS TIE(600) 67NA (D3) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 84 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600PHA(1) | #1BUS |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600PHA(1)_3 | 69KV #1BUS TIE(600) 67A (D3) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 85 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600PHA(2) | #2BUS |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.600PHA(2)_3 | 69KV #2BUS TIE(600) 67A (D3) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 86 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | BUS_CTFA | BUS CT故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KVBUS_CTFA_3 | 69KVBUS CT故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 87 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 630_87CFA | 永華學甲(630)87RY通訊故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.630_87CFA_3 | 永華學甲(630)87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 630_RYFA | 永華學甲(630)數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.630_RYFA_3 | 永華學甲(630)數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 650_87CFA | 新西學甲(650)87RY通訊故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.650_87CFA_3 | 新西學甲(650)87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 90 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 650_RYFA | 新西學甲(650)數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.650_RYFA_3 | 新西學甲(650)數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 91 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | _SC警報 | SC警報 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KV_SC警報_3 | 69KV SC警報 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 92 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 720_87CFA | 新營學甲二路87RY通訊故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.720_87CFA_3 | 新營學甲二路87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 93 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 720_RYFA | 新營學甲二路數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.720_RYFA_3 | 新營學甲二路數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 94 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 620_87CFA | 學甲佳里二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.620_87CFA_3 | 學甲佳里二路 87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 95 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 620_RYFA | 學甲佳里二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.620_RYFA_3 | 學甲佳里二路 數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 96 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S43/0/RTU/ADCH1 |  |  |  | CDC | 97 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S43/0/RTU/ADCH2 |  |  |  | CDC | 98 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S43/0/RTU/ADCH3 |  |  |  | CDC | 99 | GENERICAIPoint | SS303_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S43/0/RTU/ADCL1 |  |  |  | CDC | 100 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S43/0/RTU/ADCL2 |  |  |  | CDC | 101 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S43/0/RTU/ADCL3 |  |  |  | CDC | 102 | GENERICAIPoint | SS303_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S43/69/1BUS/V |  |  |  | CDC | 103 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S43 | 學甲SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S43/11/1BUS/V |  |  |  | CDC | 104 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S43/11/2BUS/V |  |  |  | CDC | 105 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S43/11/3BUS/V |  |  |  | CDC | 106 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.620_MW | 學甲佳里二路 MW | LINE69 | S43/69/620/MW |  |  |  | CDC | 107 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.620_MVAR | 學甲佳里二路 MVAR | LINE69 | S43/69/620/MVAR |  |  |  | CDC | 108 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.630_MW | 永華線 MW | LINE69 | S43/69/630/MW |  |  |  | CDC | 109 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.630_MVAR | 永華線 MVAR | LINE69 | S43/69/630/MVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.650_MW | 新西線 MW | LINE69 | S43/69/650/MW |  |  |  | CDC | 111 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.650_MVAR | 新西線 MVAR | LINE69 | S43/69/650/MVAR |  |  |  | CDC | 112 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.720_MW | 新營學甲二路 MW | LINE69 | S43/69/720/MW |  |  |  | CDC | 113 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.720_MVAR | 新營學甲二路 MVAR | LINE69 | S43/69/720/MVAR |  |  |  | CDC | 114 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 三慈線 | 三慈線 |  | 三慈線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.三慈線KVAR | 11KV三慈線 KVAR | FEEDER | S43/11/VD34/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 三慈線 | 三慈線 |  | 三慈線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.三慈線A1 | 11KV三慈線 R相AMP | FEEDER | S43/11/VD34/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 三慈線 | 三慈線 |  | 三慈線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.三慈線A2 | 11KV三慈線 S相AMP | FEEDER | S43/11/VD34/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 三慈線 | 三慈線 |  | 三慈線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.三慈線A3 | 11KV三慈線 T相AMP | FEEDER | S43/11/VD34/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 三慈線 | 三慈線 |  | 三慈線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.三慈線A0 | 11KV三慈線 N相AMP | FEEDER | S43/11/VD34/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 山寮線 | 山寮線 |  | 山寮線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.山寮線KVAR | 11KV山寮線 KVAR | FEEDER | S43/11/VD35/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 山寮線 | 山寮線 |  | 山寮線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.山寮線A1 | 11KV山寮線 R相AMP | FEEDER | S43/11/VD35/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 山寮線 | 山寮線 |  | 山寮線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.山寮線A2 | 11KV山寮線 S相AMP | FEEDER | S43/11/VD35/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 山寮線 | 山寮線 |  | 山寮線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.山寮線A3 | 11KV山寮線 T相AMP | FEEDER | S43/11/VD35/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 山寮線 | 山寮線 |  | 山寮線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.山寮線A0 | 11KV山寮線 N相AMP | FEEDER | S43/11/VD35/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.中洲線KVAR | 11KV中洲線 KVAR | FEEDER | S43/11/VD23/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.中洲線A1 | 11KV中洲線 R相AMP | FEEDER | S43/11/VD23/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.中洲線A2 | 11KV中洲線 S相AMP | FEEDER | S43/11/VD23/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.中洲線A3 | 11KV中洲線 T相AMP | FEEDER | S43/11/VD23/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.中洲線A0 | 11KV中洲線 N相AMP | FEEDER | S43/11/VD23/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.文化線KVAR | 11KV文化線 KVAR | FEEDER | S43/11/VD25/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.文化線A1 | 11KV文化線 R相AMP | FEEDER | S43/11/VD25/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.文化線A2 | 11KV文化線 S相AMP | FEEDER | S43/11/VD25/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.文化線A3 | 11KV文化線 T相AMP | FEEDER | S43/11/VD25/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.文化線A0 | 11KV文化線 N相AMP | FEEDER | S43/11/VD25/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 宅港線 | 宅港線 |  | 宅港線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.宅港線KVAR | 11KV宅港線 KVAR | FEEDER | S43/11/VD24/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 宅港線 | 宅港線 |  | 宅港線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.宅港線A1 | 11KV宅港線 R相AMP | FEEDER | S43/11/VD24/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 宅港線 | 宅港線 |  | 宅港線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.宅港線A2 | 11KV宅港線 S相AMP | FEEDER | S43/11/VD24/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 宅港線 | 宅港線 |  | 宅港線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.宅港線A3 | 11KV宅港線 T相AMP | FEEDER | S43/11/VD24/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 宅港線 | 宅港線 |  | 宅港線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.宅港線A0 | 11KV宅港線 N相AMP | FEEDER | S43/11/VD24/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 竹埔線 | 竹埔線 |  | 竹埔線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.竹埔線KVAR | 11KV竹埔線 KVAR | FEEDER | S43/11/VD26/KVAR |  |  |  | CDC | 140 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 竹埔線 | 竹埔線 |  | 竹埔線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.竹埔線A1 | 11KV竹埔線 R相AMP | FEEDER | S43/11/VD26/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 竹埔線 | 竹埔線 |  | 竹埔線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.竹埔線A2 | 11KV竹埔線 S相AMP | FEEDER | S43/11/VD26/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 竹埔線 | 竹埔線 |  | 竹埔線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.竹埔線A3 | 11KV竹埔線 T相AMP | FEEDER | S43/11/VD26/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 竹埔線 | 竹埔線 |  | 竹埔線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.竹埔線A0 | 11KV竹埔線 N相AMP | FEEDER | S43/11/VD26/I_N |  |  |  | CDC | 144 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 信義線 | 信義線 |  | 信義線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.信義線KVAR | 11KV信義線 KVAR | FEEDER | S43/11/VD22/KVAR |  |  |  | CDC | 145 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 信義線 | 信義線 |  | 信義線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.信義線A1 | 11KV信義線 R相AMP | FEEDER | S43/11/VD22/I_R |  |  |  | CDC | 146 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 信義線 | 信義線 |  | 信義線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.信義線A2 | 11KV信義線 S相AMP | FEEDER | S43/11/VD22/I_S |  |  |  | CDC | 147 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 信義線 | 信義線 |  | 信義線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.信義線A3 | 11KV信義線 T相AMP | FEEDER | S43/11/VD22/I_T |  |  |  | CDC | 148 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 信義線 | 信義線 |  | 信義線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.信義線A0 | 11KV信義線 N相AMP | FEEDER | S43/11/VD22/I_N |  |  |  | CDC | 149 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 美豐線 | 美豐線 |  | 美豐線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.美豐線KVAR | 11KV美豐線 KVAR | FEEDER | S43/11/VD27/KVAR |  |  |  | CDC | 150 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 美豐線 | 美豐線 |  | 美豐線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.美豐線A1 | 11KV美豐線 R相AMP | FEEDER | S43/11/VD27/I_R |  |  |  | CDC | 151 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 美豐線 | 美豐線 |  | 美豐線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.美豐線A2 | 11KV美豐線 S相AMP | FEEDER | S43/11/VD27/I_S |  |  |  | CDC | 152 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 美豐線 | 美豐線 |  | 美豐線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.美豐線A3 | 11KV美豐線 T相AMP | FEEDER | S43/11/VD27/I_T |  |  |  | CDC | 153 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 美豐線 | 美豐線 |  | 美豐線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.美豐線A0 | 11KV美豐線 N相AMP | FEEDER | S43/11/VD27/I_N |  |  |  | CDC | 154 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.新生線KVAR | 11KV新生線 KVAR | FEEDER | S43/11/VD31/KVAR |  |  |  | CDC | 155 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.新生線A1 | 11KV新生線 R相AMP | FEEDER | S43/11/VD31/I_R |  |  |  | CDC | 156 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.新生線A2 | 11KV新生線 S相AMP | FEEDER | S43/11/VD31/I_S |  |  |  | CDC | 157 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.新生線A3 | 11KV新生線 T相AMP | FEEDER | S43/11/VD31/I_T |  |  |  | CDC | 158 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.新生線A0 | 11KV新生線 N相AMP | FEEDER | S43/11/VD31/I_N |  |  |  | CDC | 159 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 達明線 | 達明線 |  | 達明線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.達明線KVAR | 11KV達明線 KVAR | FEEDER | S43/11/VD33/KVAR |  |  |  | CDC | 160 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 達明線 | 達明線 |  | 達明線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.達明線A1 | 11KV達明線 R相AMP | FEEDER | S43/11/VD33/I_R |  |  |  | CDC | 161 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 達明線 | 達明線 |  | 達明線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.達明線A2 | 11KV達明線 S相AMP | FEEDER | S43/11/VD33/I_S |  |  |  | CDC | 162 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 達明線 | 達明線 |  | 達明線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.達明線A3 | 11KV達明線 T相AMP | FEEDER | S43/11/VD33/I_T |  |  |  | CDC | 163 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 達明線 | 達明線 |  | 達明線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.達明線A0 | 11KV達明線 N相AMP | FEEDER | S43/11/VD33/I_N |  |  |  | CDC | 164 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學工線 | 學工線 |  | 學工線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學工線KVAR | 11KV學工線 KVAR | FEEDER | S43/11/VD28/KVAR |  |  |  | CDC | 165 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學工線 | 學工線 |  | 學工線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學工線A1 | 11KV學工線 R相AMP | FEEDER | S43/11/VD28/I_R |  |  |  | CDC | 166 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學工線 | 學工線 |  | 學工線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學工線A2 | 11KV學工線 S相AMP | FEEDER | S43/11/VD28/I_S |  |  |  | CDC | 167 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學工線 | 學工線 |  | 學工線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學工線A3 | 11KV學工線 T相AMP | FEEDER | S43/11/VD28/I_T |  |  |  | CDC | 168 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學工線 | 學工線 |  | 學工線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學工線A0 | 11KV學工線 N相AMP | FEEDER | S43/11/VD28/I_N |  |  |  | CDC | 169 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學甲線 | 學甲線 |  | 學甲線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學甲線KVAR | 11KV學甲線 KVAR | FEEDER | S43/11/VD30/KVAR |  |  |  | CDC | 170 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學甲線 | 學甲線 |  | 學甲線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學甲線A1 | 11KV學甲線 R相AMP | FEEDER | S43/11/VD30/I_R |  |  |  | CDC | 171 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學甲線 | 學甲線 |  | 學甲線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學甲線A2 | 11KV學甲線 S相AMP | FEEDER | S43/11/VD30/I_S |  |  |  | CDC | 172 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學甲線 | 學甲線 |  | 學甲線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學甲線A3 | 11KV學甲線 T相AMP | FEEDER | S43/11/VD30/I_T |  |  |  | CDC | 173 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學甲線 | 學甲線 |  | 學甲線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學甲線A0 | 11KV學甲線 N相AMP | FEEDER | S43/11/VD30/I_N |  |  |  | CDC | 174 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 錦湖線 | 錦湖線 |  | 錦湖線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.錦湖線KVAR | 11KV錦湖線 KVAR | FEEDER | S43/11/VD32/KVAR |  |  |  | CDC | 175 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 錦湖線 | 錦湖線 |  | 錦湖線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.錦湖線A1 | 11KV錦湖線 R相AMP | FEEDER | S43/11/VD32/I_R |  |  |  | CDC | 176 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 錦湖線 | 錦湖線 |  | 錦湖線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.錦湖線A2 | 11KV錦湖線 S相AMP | FEEDER | S43/11/VD32/I_S |  |  |  | CDC | 177 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 錦湖線 | 錦湖線 |  | 錦湖線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.錦湖線A3 | 11KV錦湖線 T相AMP | FEEDER | S43/11/VD32/I_T |  |  |  | CDC | 178 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 錦湖線 | 錦湖線 |  | 錦湖線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.錦湖線A0 | 11KV錦湖線 N相AMP | FEEDER | S43/11/VD32/I_N |  |  |  | CDC | 179 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S43/11/TIE1/I_R |  |  |  | CDC | 180 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S43/11/TIE1/I_S |  |  |  | CDC | 181 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S43/11/TIE1/I_T |  |  |  | CDC | 182 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S43/11/TIE2/I_R |  |  |  | CDC | 183 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S43/11/TIE2/I_S |  |  |  | CDC | 184 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S43/11/TIE2/I_T |  |  |  | CDC | 185 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_MW | #1MTR二次側 MW | DTR | S43/11/M1/MW |  |  |  | CDC | 186 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S43/11/M1/MVAR |  |  |  | CDC | 187 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S43/11/M1/I_R |  |  |  | CDC | 188 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S43/11/M1/I_S |  |  |  | CDC | 189 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S43/11/M1/I_T |  |  |  | CDC | 190 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_OIL | #1MTR 油溫 | DTR | S43//1MTR/OilTemp |  |  |  | CDC | 191 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_COIL | #1MTR 線溫 | DTR | S43//1MTR/CoilTemp |  |  |  | CDC | 192 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S43//1MTR/TapPosMv |  |  |  | CDC | 193 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_MW | #2MTR二次側 MW | DTR | S43/11/M2A/MW |  |  |  | CDC | 194 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S43/11/M2A/MVAR |  |  |  | CDC | 195 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S43/11/M2A/I_R |  |  |  | CDC | 196 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S43/11/M2A/I_S |  |  |  | CDC | 197 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S43/11/M2A/I_T |  |  |  | CDC | 198 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_OIL | #2MTR 油溫 | DTR | S43//2MTR/OilTemp |  |  |  | CDC | 199 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_COIL | #2MTR 線溫 | DTR | S43//2MTR/CoilTemp |  |  |  | CDC | 200 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S43//2MTR/TapPosMv |  |  |  | CDC | 201 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_MW | #3MTR二次側 MW | DTR | S43/11/M3/MW |  |  |  | CDC | 202 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S43/11/M3/MVAR |  |  |  | CDC | 203 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S43/11/M3/I_R |  |  |  | CDC | 204 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S43/11/M3/I_S |  |  |  | CDC | 205 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S43/11/M3/I_T |  |  |  | CDC | 206 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_OIL | #3MTR 油溫 | DTR | S43//3MTR/OilTemp |  |  |  | CDC | 207 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_COIL | #3MTR 線溫 | DTR | S43//3MTR/CoilTemp |  |  |  | CDC | 208 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S43//3MTR/TapPosMv |  |  |  | CDC | 209 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S43 | 學甲SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.直流電源電壓 | 直流電源電壓 | OTHER | S43/0/StaDev/DCV |  |  |  | CDC | 210 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學平線 | 學平線 |  | 學平線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學平線KVAR | 11KV學平線 KVAR | FEEDER | S43/11/VD21/KVAR |  |  |  | CDC | 211 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學平線 | 學平線 |  | 學平線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學平線A1 | 11KV學平線 R相AMP | FEEDER | S43/11/VD21/I_R |  |  |  | CDC | 212 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學平線 | 學平線 |  | 學平線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學平線A2 | 11KV學平線 S相AMP | FEEDER | S43/11/VD21/I_S |  |  |  | CDC | 213 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學平線 | 學平線 |  | 學平線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學平線A3 | 11KV學平線 T相AMP | FEEDER | S43/11/VD21/I_T |  |  |  | CDC | 214 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學平線 | 學平線 |  | 學平線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學平線A0 | 11KV學平線 N相AMP | FEEDER | S43/11/VD21/I_N |  |  |  | CDC | 215 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學興線 | 學興線 |  | 學興線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學興線KVAR | 11KV學興線 KVAR | FEEDER | S43/11/VD29/KVAR |  |  |  | CDC | 216 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學興線 | 學興線 |  | 學興線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學興線A1 | 11KV學興線 R相AMP | FEEDER | S43/11/VD29/I_R |  |  |  | CDC | 217 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學興線 | 學興線 |  | 學興線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學興線A2 | 11KV學興線 S相AMP | FEEDER | S43/11/VD29/I_S |  |  |  | CDC | 218 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學興線 | 學興線 |  | 學興線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學興線A3 | 11KV學興線 T相AMP | FEEDER | S43/11/VD29/I_T |  |  |  | CDC | 219 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 11 | 11kV | 學興線 | 學興線 |  | 學興線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 學甲SS.學興線A0 | 11KV學興線 N相AMP | FEEDER | S43/11/VD29/I_N |  |  |  | CDC | 220 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.730_MW | 學甲佳里一路 MW | LINE69 | S43/69/730/MW |  |  |  | CDC | 221 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.730_MVAR | 學甲佳里一路 MVAR | LINE69 | S43/69/730/MVAR |  |  |  | CDC | 222 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.910_MW | 新營學甲一路 MW | LINE69 | S43/69/910/MW |  |  |  | CDC | 223 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.910_MVAR | 新營學甲一路 MVAR | LINE69 | S43/69/910/MVAR |  |  |  | CDC | 224 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-90 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S43/69/2BUS/V |  |  |  | CDC | 225 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S43 | 學甲SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-91 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 學甲SS.600TIE_AMP | 600TIE AMP | TIE | S43/69/600/I |  |  |  | CDC | 226 | GENERICAIPoint | SS303_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.620_PHA | 學甲佳里二路(620) 相間RY | LINE69 | S43/69/620/PHA |  |  |  | CDC | 227 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.620_GDA | 學甲佳里二路(620) 接地RY | LINE69 | S43/69/620/GDA |  |  |  | CDC | 228 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.620_CB | 620(學甲佳里二路) CB | LINE69 | S43/69/620/CB |  |  |  | CDC | 229 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | ABS1 | 621 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.621_ABS | 621(學甲佳里二路) ABS | LINE69 | S43/69/620/ABS1 |  |  |  | CDC | 230 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | ABS2 | 622 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.622_ABS | 622(學甲佳里二路) ABS | LINE69 | S43/69/620/ABS2 |  |  |  | CDC | 231 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | E2 | 622E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.622E_ES | 622E(學甲佳里二路) ES | LINE69 | S43/69/620/ES2 |  |  |  | CDC | 232 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.630_PHA | 永華線(630) 相間RY | LINE69 | S43/69/630/PHA |  |  |  | CDC | 233 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.630_GDA | 永華線(630) 接地RY | LINE69 | S43/69/630/GDA |  |  |  | CDC | 234 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.630_CB | 630(永華線) CB | LINE69 | S43/69/630/CB |  |  |  | CDC | 235 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | ABS1 | 631 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.631_ABS | 631(永華線) ABS | LINE69 | S43/69/630/ABS1 |  |  |  | CDC | 236 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | ABS2 | 632 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.632_ABS | 632(永華線) ABS | LINE69 | S43/69/630/ABS2 |  |  |  | CDC | 237 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | E2 | 632E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 學甲SS.632E_ES | 632E(永華線) ES | LINE69 | S43/69/630/ES2 |  |  |  | CDC | 238 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.650_PHA | 新西線(650) 相間RY | LINE69 | S43/69/650/PHA |  |  |  | CDC | 239 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.650_GDA | 新西線(650) 接地RY | LINE69 | S43/69/650/GDA |  |  |  | CDC | 240 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.650_CB | 650(新西線) CB | LINE69 | S43/69/650/CB |  |  |  | CDC | 241 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | ABS1 | 651 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 學甲SS.651_ABS | 651(新西線) ABS | LINE69 | S43/69/650/ABS1 |  |  |  | CDC | 242 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | ABS2 | 652 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 學甲SS.652_ABS | 652(新西線) ABS | LINE69 | S43/69/650/ABS2 |  |  |  | CDC | 243 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | E2 | 652E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 學甲SS.652E_ES | 652E(新西線) ES | LINE69 | S43/69/650/ES2 |  |  |  | CDC | 244 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.720_PHA | 新營學甲二路(720) 相間RY | LINE69 | S43/69/720/PHA |  |  |  | CDC | 245 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.720_GDA | 新營學甲二路(720) 接地RY | LINE69 | S43/69/720/GDA |  |  |  | CDC | 246 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.720_CB | 720(新營學甲二路) CB | LINE69 | S43/69/720/CB |  |  |  | CDC | 247 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | ABS1 | 721 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.721_ABS | 721(新營學甲二路) ABS | LINE69 | S43/69/720/ABS1 |  |  |  | CDC | 248 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | ABS2 | 722 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.722_ABS | 722(新營學甲二路) ABS | LINE69 | S43/69/720/ABS2 |  |  |  | CDC | 249 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | E2 | 722E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.722E_ES | 722E(新營學甲二路) ES | LINE69 | S43/69/720/ES2 |  |  |  | CDC | 250 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_PHA | 11KV學平線(VD21) 相間RY | FEEDER | S43/11/VD21/PHA |  |  |  | CDC | 251 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_GDA | 11KV學平線(VD21) 接地RY | FEEDER | S43/11/VD21/GDA |  |  |  | CDC | 252 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_79UL | 11KV學平線(VD21) 79RY U/L | FEEDER | S43/11/VD21/79UL |  |  |  | CDC | 253 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_ADJ | 11KV學平線(VD21) LCO分流器 U/L | FEEDER | S43/11/VD21/ADJ |  |  |  | CDC | 254 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD21 | VD21(11KV學平線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_CB | VD21(11KV學平線) CB | FEEDER | S43/11/VD21/CB |  |  |  | CDC | 255 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_PHA | 11KV信義線(VD22) 相間RY | FEEDER | S43/11/VD22/PHA |  |  |  | CDC | 256 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_GDA | 11KV信義線(VD22) 接地RY | FEEDER | S43/11/VD22/GDA |  |  |  | CDC | 257 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_79UL | 11KV信義線(VD22) 79RY U/L | FEEDER | S43/11/VD22/79UL |  |  |  | CDC | 258 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_ADJ | 11KV信義線(VD22) LCO分流器 U/L | FEEDER | S43/11/VD22/ADJ |  |  |  | CDC | 259 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD22 | VD22(11KV信義線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_CB | VD22(11KV信義線) CB | FEEDER | S43/11/VD22/CB |  |  |  | CDC | 260 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_PHA | 11KV中洲線(VD23) 相間RY | FEEDER | S43/11/VD23/PHA |  |  |  | CDC | 261 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_GDA | 11KV中洲線(VD23) 接地RY | FEEDER | S43/11/VD23/GDA |  |  |  | CDC | 262 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_79UL | 11KV中洲線(VD23) 79RY U/L | FEEDER | S43/11/VD23/79UL |  |  |  | CDC | 263 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_ADJ | 11KV中洲線(VD23) LCO分流器 U/L | FEEDER | S43/11/VD23/ADJ |  |  |  | CDC | 264 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD23 | VD23(11KV中洲線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_CB | VD23(11KV中洲線) CB | FEEDER | S43/11/VD23/CB |  |  |  | CDC | 265 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_PHA | 11KV宅港線(VD24) 相間RY | FEEDER | S43/11/VD24/PHA |  |  |  | CDC | 266 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_GDA | 11KV宅港線(VD24) 接地RY | FEEDER | S43/11/VD24/GDA |  |  |  | CDC | 267 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_79UL | 11KV宅港線(VD24) 79RY U/L | FEEDER | S43/11/VD24/79UL |  |  |  | CDC | 268 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_ADJ | 11KV宅港線(VD24) LCO分流器 U/L | FEEDER | S43/11/VD24/ADJ |  |  |  | CDC | 269 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD24 | VD24(11KV宅港線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_CB | VD24(11KV宅港線) CB | FEEDER | S43/11/VD24/CB |  |  |  | CDC | 270 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_PHA | 11KV文化線(VD25) 相間RY | FEEDER | S43/11/VD25/PHA |  |  |  | CDC | 271 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_GDA | 11KV文化線(VD25) 接地RY | FEEDER | S43/11/VD25/GDA |  |  |  | CDC | 272 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_79UL | 11KV文化線(VD25) 79RY U/L | FEEDER | S43/11/VD25/79UL |  |  |  | CDC | 273 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_ADJ | 11KV文化線(VD25) LCO分流器 U/L | FEEDER | S43/11/VD25/ADJ |  |  |  | CDC | 274 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD25 | VD25(11KV文化線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_CB | VD25(11KV文化線) CB | FEEDER | S43/11/VD25/CB |  |  |  | CDC | 275 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_PHA | 11KV竹埔線(VD26) 相間RY | FEEDER | S43/11/VD26/PHA |  |  |  | CDC | 276 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_GDA | 11KV竹埔線(VD26) 接地RY | FEEDER | S43/11/VD26/GDA |  |  |  | CDC | 277 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_79UL | 11KV竹埔線(VD26) 79RY U/L | FEEDER | S43/11/VD26/79UL |  |  |  | CDC | 278 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_ADJ | 11KV竹埔線(VD26) LCO分流器 U/L | FEEDER | S43/11/VD26/ADJ |  |  |  | CDC | 279 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD26 | VD26(11KV竹埔線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_CB | VD26(11KV竹埔線) CB | FEEDER | S43/11/VD26/CB |  |  |  | CDC | 280 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_PHA | 11KV美豐線(VD27) 相間RY | FEEDER | S43/11/VD27/PHA |  |  |  | CDC | 281 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_GDA | 11KV美豐線(VD27) 接地RY | FEEDER | S43/11/VD27/GDA |  |  |  | CDC | 282 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_79UL | 11KV美豐線(VD27) 79RY U/L | FEEDER | S43/11/VD27/79UL |  |  |  | CDC | 283 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_ADJ | 11KV美豐線(VD27) LCO分流器 U/L | FEEDER | S43/11/VD27/ADJ |  |  |  | CDC | 284 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD27 | VD27(11KV美豐線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_CB | VD27(11KV美豐線) CB | FEEDER | S43/11/VD27/CB |  |  |  | CDC | 285 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_PHA | 11KV學工線(VD28) 相間RY | FEEDER | S43/11/VD28/PHA |  |  |  | CDC | 286 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_GDA | 11KV學工線(VD28) 接地RY | FEEDER | S43/11/VD28/GDA |  |  |  | CDC | 287 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_79UL | 11KV學工線(VD28) 79RY U/L | FEEDER | S43/11/VD28/79UL |  |  |  | CDC | 288 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_ADJ | 11KV學工線(VD28) LCO分流器 U/L | FEEDER | S43/11/VD28/ADJ |  |  |  | CDC | 289 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD28 | VD28(11KV學工線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_CB | VD28(11KV學工線) CB | FEEDER | S43/11/VD28/CB |  |  |  | CDC | 290 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_PHA | 11KV學興線(VD29) 相間RY | FEEDER | S43/11/VD29/PHA |  |  |  | CDC | 291 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_GDA | 11KV學興線(VD29) 接地RY | FEEDER | S43/11/VD29/GDA |  |  |  | CDC | 292 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_79UL | 11KV學興線(VD29) 79RY U/L | FEEDER | S43/11/VD29/79UL |  |  |  | CDC | 293 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_ADJ | 11KV學興線(VD29) LCO分流器 U/L | FEEDER | S43/11/VD29/ADJ |  |  |  | CDC | 294 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD29 | VD29(11KV學興線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_CB | VD29(11KV學興線) CB | FEEDER | S43/11/VD29/CB |  |  |  | CDC | 295 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_PHA | 11KV學甲線(VD30) 相間RY | FEEDER | S43/11/VD30/PHA |  |  |  | CDC | 296 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_GDA | 11KV學甲線(VD30) 接地RY | FEEDER | S43/11/VD30/GDA |  |  |  | CDC | 297 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_79UL | 11KV學甲線(VD30) 79RY U/L | FEEDER | S43/11/VD30/79UL |  |  |  | CDC | 298 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_ADJ | 11KV學甲線(VD30) LCO分流器 U/L | FEEDER | S43/11/VD30/ADJ |  |  |  | CDC | 299 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD30 | VD30(11KV學甲線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_CB | VD30(11KV學甲線) CB | FEEDER | S43/11/VD30/CB |  |  |  | CDC | 300 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_PHA | 11KV新生線(VD31) 相間RY | FEEDER | S43/11/VD31/PHA |  |  |  | CDC | 301 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_GDA | 11KV新生線(VD31) 接地RY | FEEDER | S43/11/VD31/GDA |  |  |  | CDC | 302 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_79UL | 11KV新生線(VD31) 79RY U/L | FEEDER | S43/11/VD31/79UL |  |  |  | CDC | 303 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_ADJ | 11KV新生線(VD31) LCO分流器 U/L | FEEDER | S43/11/VD31/ADJ |  |  |  | CDC | 304 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD31 | VD31(11KV新生線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_CB | VD31(11KV新生線) CB | FEEDER | S43/11/VD31/CB |  |  |  | CDC | 305 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_PHA | 11KV錦湖線(VD32) 相間RY | FEEDER | S43/11/VD32/PHA |  |  |  | CDC | 306 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_GDA | 11KV錦湖線(VD32) 接地RY | FEEDER | S43/11/VD32/GDA |  |  |  | CDC | 307 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_79UL | 11KV錦湖線(VD32) 79RY U/L | FEEDER | S43/11/VD32/79UL |  |  |  | CDC | 308 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_ADJ | 11KV錦湖線(VD32) LCO分流器 U/L | FEEDER | S43/11/VD32/ADJ |  |  |  | CDC | 309 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD32 | VD32(11KV錦湖線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_CB | VD32(11KV錦湖線) CB | FEEDER | S43/11/VD32/CB |  |  |  | CDC | 310 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_PHA | 11KV達明線(VD33) 相間RY | FEEDER | S43/11/VD33/PHA |  |  |  | CDC | 311 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_GDA | 11KV達明線(VD33) 接地RY | FEEDER | S43/11/VD33/GDA |  |  |  | CDC | 312 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_79UL | 11KV達明線(VD33) 79RY U/L | FEEDER | S43/11/VD33/79UL |  |  |  | CDC | 313 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_ADJ | 11KV達明線(VD33) LCO分流器 U/L | FEEDER | S43/11/VD33/ADJ |  |  |  | CDC | 314 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD33 | VD33(11KV達明線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_CB | VD33(11KV達明線) CB | FEEDER | S43/11/VD33/CB |  |  |  | CDC | 315 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_PHA | 11KV三慈線(VD34) 相間RY | FEEDER | S43/11/VD34/PHA |  |  |  | CDC | 316 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_GDA | 11KV三慈線(VD34) 接地RY | FEEDER | S43/11/VD34/GDA |  |  |  | CDC | 317 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_79UL | 11KV三慈線(VD34) 79RY U/L | FEEDER | S43/11/VD34/79UL |  |  |  | CDC | 318 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_ADJ | 11KV三慈線(VD34) LCO分流器 U/L | FEEDER | S43/11/VD34/ADJ |  |  |  | CDC | 319 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD34 | VD34(11KV三慈線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_CB | VD34(11KV三慈線) CB | FEEDER | S43/11/VD34/CB |  |  |  | CDC | 320 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_PHA | 11KV山寮線(VD35) 相間RY | FEEDER | S43/11/VD35/PHA |  |  |  | CDC | 321 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_GDA | 11KV山寮線(VD35) 接地RY | FEEDER | S43/11/VD35/GDA |  |  |  | CDC | 322 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_79UL | 11KV山寮線(VD35) 79RY U/L | FEEDER | S43/11/VD35/79UL |  |  |  | CDC | 323 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_ADJ | 11KV山寮線(VD35) LCO分流器 U/L | FEEDER | S43/11/VD35/ADJ |  |  |  | CDC | 324 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S43 | 學甲SS | 11 | 11kV | VD35 | VD35(11KV山寮線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_CB | VD35(11KV山寮線) CB | FEEDER | S43/11/VD35/CB |  |  |  | CDC | 325 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE1_CB | 11KV TIE1 CB | TIE | S43/11/TIE1/CB |  |  |  | CDC | 326 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE1_51A | 11KV TIE1 51RY | TIE | S43/11/TIE1/51A |  |  |  | CDC | 327 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S43/11/TIE1/51NA |  |  |  | CDC | 328 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE2_CB | 11KV TIE2 CB | TIE | S43/11/TIE2/CB |  |  |  | CDC | 329 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE2_51A | 11KV TIE2 51RY | TIE | S43/11/TIE2/51A |  |  |  | CDC | 330 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S43/11/TIE2/51NA |  |  |  | CDC | 331 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.750_CB | 750(#1MTR) CB | DTR | S43/69/750/CB |  |  |  | CDC | 332 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.1M_CB | 1M(#1MTR) CB | DTR | S43/11/M1/CB |  |  |  | CDC | 333 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_51A | #1MTR 51RY | DTR | S43/69/750/51A |  |  |  | CDC | 334 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_51NA | #1MTR 51N RY | DTR | S43/69/750/51NA |  |  |  | CDC | 335 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S43//1MTR/51ZA |  |  |  | CDC | 336 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_87A | #1MTR 87RY | DTR | S43//1MTR/87A |  |  |  | CDC | 337 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S43//1MTR/87UL |  |  |  | CDC | 338 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S43/11/M1/51A |  |  |  | CDC | 339 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_TRA | #1MTR 重故障 | DTR | S43//1MTR/TRA |  |  |  | CDC | 340 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S43//1MTR/TRF |  |  |  | CDC | 341 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S43//1MTR/SupLocal |  |  |  | CDC | 342 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S43//1MTR/Tap Chan |  |  |  | CDC | 343 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.751_ABS | 751(#1MTR) ABS | DTR | S43/69/750/ABS1 |  |  |  | CDC | 344 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_96A | #1MTR 96P RY | DTR | S43//1MTR/96PA |  |  |  | CDC | 345 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S43//1MTR/OLTC_DLY |  |  |  | CDC | 346 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S43//1MTR/AC_Fault |  |  |  | CDC | 347 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.760_CB | 760(#2MTR) CB | DTR | S43/69/760/CB |  |  |  | CDC | 348 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MA_CB | 2MA(#2MTR) CB | DTR | S43/11/M2A/CB |  |  |  | CDC | 349 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-46 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MB_CB | 2MB(#2MTR) CB | DTR | S43/11/M2B/CB |  |  |  | CDC | 350 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_51A | #2MTR 51RY | DTR | S43/69/760/51A |  |  |  | CDC | 351 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_51NA | #2MTR 51N RY | DTR | S43/69/760/51NA |  |  |  | CDC | 352 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S43//2MTR/51ZA |  |  |  | CDC | 353 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_87A | #2MTR 87RY | DTR | S43//2MTR/87A |  |  |  | CDC | 354 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S43//2MTR/87UL |  |  |  | CDC | 355 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S43/11/M2A/51A |  |  |  | CDC | 356 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S43/11/M2B/51A |  |  |  | CDC | 357 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_TRA | #2MTR 重故障 | DTR | S43//2MTR/TRA |  |  |  | CDC | 358 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S43//2MTR/TRF |  |  |  | CDC | 359 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S43//2MTR/SupLocal |  |  |  | CDC | 360 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S43//2MTR/Tap Chan |  |  |  | CDC | 361 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.761_ABS | 761(#2MTR) ABS | DTR | S43/69/760/ABS1 |  |  |  | CDC | 362 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_96A | #2MTR 96P RY | DTR | S43//2MTR/96PA |  |  |  | CDC | 363 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S43//2MTR/OLTC_DLY |  |  |  | CDC | 364 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S43//2MTR/AC_Fault |  |  |  | CDC | 365 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.770_CB | 770(#3MTR) CB | DTR | S43/69/770/CB |  |  |  | CDC | 366 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.3M_CB | 3M(#3MTR) CB | DTR | S43/11/M3/CB |  |  |  | CDC | 367 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_51A | #3MTR 51RY | DTR | S43/69/770/51A |  |  |  | CDC | 368 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_51NA | #3MTR 51N RY | DTR | S43/69/770/51NA |  |  |  | CDC | 369 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S43//3MTR/51ZA |  |  |  | CDC | 370 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_87A | #3MTR 87RY | DTR | S43//3MTR/87A |  |  |  | CDC | 371 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S43//3MTR/87UL |  |  |  | CDC | 372 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S43/11/M3/51A |  |  |  | CDC | 373 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_TRA | #3MTR 重故障 | DTR | S43//3MTR/TRA |  |  |  | CDC | 374 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S43//3MTR/TRF |  |  |  | CDC | 375 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S43//3MTR/SupLocal |  |  |  | CDC | 376 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S43//3MTR/Tap Chan |  |  |  | CDC | 377 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.771_ABS | 771(#3MTR) ABS | DTR | S43/69/770/ABS1 |  |  |  | CDC | 378 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_96A | #3MTR 96P RY | DTR | S43//3MTR/96PA |  |  |  | CDC | 379 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S43//3MTR/OLTC_DLY |  |  |  | CDC | 380 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S43//3MTR/AC_Fault |  |  |  | CDC | 381 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_CB | 210(11KV #1SC) CB | SC | S43/11/210/CB |  |  |  | CDC | 382 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S43/11/210/Tap Chan |  |  |  | CDC | 383 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_SCA | 11KV #1SC 51,51N RY | SC | S43/11/210/SCA |  |  |  | CDC | 384 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S43/11/210/UVA |  |  |  | CDC | 385 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_CB | 220(11KV #2SC) CB | SC | S43/11/220/CB |  |  |  | CDC | 386 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S43/11/220/Tap Chan |  |  |  | CDC | 387 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_SCA | 11KV #2SC 51,51N RY | SC | S43/11/220/SCA |  |  |  | CDC | 388 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S43/11/220/UVA |  |  |  | CDC | 389 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_CB | 230(11KV #3SC) CB | SC | S43/11/230/CB |  |  |  | CDC | 390 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S43/11/230/Tap Chan |  |  |  | CDC | 391 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_SCA | 11KV #3SC 51,51N RY | SC | S43/11/230/SCA |  |  |  | CDC | 392 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S43/11/230/UVA |  |  |  | CDC | 393 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.810_CB | 810(69KV #1SC) CB | SC | S43/69/810/CB |  |  |  | CDC | 394 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.811_ABS | 811(69KV #1SC) ABS | SC | S43/69/810/ABS1 |  |  |  | CDC | 395 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.810_SCA | 69KV #1SC 51,51N RY | SC | S43/69/810/SCA |  |  |  | CDC | 396 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.810_OUVA | 69KV #1SC 27,59RY | SC | S43/69/810/UVA |  |  |  | CDC | 397 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S43/69/1BUS/BUS_VUA |  |  |  | CDC | 398 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S43/11/ComPoint/CBA |  |  |  | CDC | 399 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S43/11/ComPoint/CBF |  |  |  | CDC | 400 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S43/69/ComPoint/ABS_89A |  |  |  | CDC | 401 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S43/69/ComPoint/CBA |  |  |  | CDC | 402 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S43/69/ComPoint/CBF |  |  |  | CDC | 403 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S43/0/RTU/RTU_R_L |  |  |  | CDC | 404 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S43 | 學甲SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.TEST_CB | TEST CB | OTHER | S43/0/RTU/Test_CB |  |  |  | CDC | 405 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-31-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.火災警報(1) | CO2警報 | OTHER | S43/0/StaDev/Fire1 |  |  |  | CDC | 406 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.火災警報(2) | CO2故障 | OTHER | S43/0/StaDev/Fire2 |  |  |  | CDC | 407 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-30-10 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.火災警報(3) | 火災警報(3) | OTHER | S43/0/StaDev/Fire3 |  |  |  | CDC | 408 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.其他重故障 | 變電所內其他重故障 | OTHER | S43/0/StaDev/PSA |  |  |  | CDC | 409 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S43/0/StaDev/PSF |  |  |  | CDC | 410 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S43/0/StaDev/STUV |  |  |  | CDC | 411 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S43/0/StaDev/CHG1 |  |  |  | CDC | 412 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.直流電源DCA | NFB跳脫監視 | OTHER | S43/0/StaDev/DCA |  |  |  | CDC | 413 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S43/0/StaDev/DCE |  |  |  | CDC | 414 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S43/0/StaDev/OilLeak |  |  |  | CDC | 415 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S43/0/StaDev/CHG2 |  |  |  | CDC | 416 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化防盜(1) | 水氣霧警報 | OTHER | S43/0/StaDev/Burglar1 |  |  |  | CDC | 417 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化防盜(2) | 水氣霧故障 | OTHER | S43/0/StaDev/Burglar2 |  |  |  | CDC | 418 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化防盜(3) | MCSG偵煙警報 | OTHER | S43/0/StaDev/Burglar3 |  |  |  | CDC | 419 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化門禁(1) | 水氣霧釋放 | OTHER | S43/0/StaDev/Door1 |  |  |  | CDC | 420 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化門禁(2) | 所內淹水高水位 | OTHER | S43/0/StaDev/Door2 |  |  |  | CDC | 421 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.無人化門禁(3) | 所內淹水低水位 | OTHER | S43/0/StaDev/Door3 |  |  |  | CDC | 422 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.開關場照明(A) | 開關場照明(A) | OTHER | S43/0/StaDev/Lights1 |  |  |  | CDC | 423 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S43 | 學甲SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.開關場照明(B) | 開關場照明(B) | OTHER | S43/0/StaDev/Lights2 |  |  |  | CDC | 424 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S43 | 學甲SS | 69 | 69kV |  |  |  | SC警報 | [17 empty] | 1-31-08 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.69KV_SC警報 | 69KV SC警報 | OTHER | S43/69/ComPoint/SCA |  |  |  | CDC | 425 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.門禁 | 門禁 | OTHER | S43/0/StaDev/Door |  |  |  | CDC | 426 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | PHA | [17 empty] | 1-0A-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.730_PHA | 學甲佳里一路(730) 相間RY | LINE69 | S43/69/730/PHA |  |  |  | CDC | 427 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | GDA | [17 empty] | 1-0A-07 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.730_GDA | 學甲佳里一路(730) 接地RY | LINE69 | S43/69/730/GDA |  |  |  | CDC | 428 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | 87A | [17 empty] | 1-0A-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.730_87A | 學甲佳里一路(730) 87RY | LINE69 | S43/69/730/87A |  |  |  | CDC | 429 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | 87UL | [17 empty] | 1-32-10 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 學甲SS.730_87UL | 學甲佳里一路(730) 87RY U/L | LINE69 | S43/69/730/87UL |  |  |  | CDC | 430 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | CB | [17 empty] | 1-0A-04 |  | 1-06 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.730_CB | 730(學甲佳里一路) CB | LINE69 | S43/69/730/CB |  |  |  | CDC | 431 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | E2 | 732E | [16 empty] | 1-3A-10 | 1-3A-11 | 1-23 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.732E_ES | 732E(學甲佳里一路) ES | LINE69 | S43/69/730/ES2 |  |  |  | CDC | 432 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.910_PHA | 新營學甲一路(910) 相間RY | LINE69 | S43/69/910/PHA |  |  |  | CDC | 433 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.910_GDA | 新營學甲一路(910) 接地RY | LINE69 | S43/69/910/GDA |  |  |  | CDC | 434 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.910_87A | 新營學甲一路(910) 87RY | LINE69 | S43/69/910/87A |  |  |  | CDC | 435 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 學甲SS.910_87UL | 新營學甲一路(910) 87RY U/L | LINE69 | S43/69/910/87UL |  |  |  | CDC | 436 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | CB | [17 empty] | 1-0A-00 |  | 1-05 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.910_CB | 910(新營學甲一路) CB | LINE69 | S43/69/910/CB |  |  |  | CDC | 437 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | E2 | 912E | [16 empty] | 1-3A-04 | 1-3A-05 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.912E_ES | 912E(新營學甲一路) ES | LINE69 | S43/69/910/ES2 |  |  |  | CDC | 438 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S43 | 學甲SS | 0 |  | 730 | 學甲佳里一路(730) |  | 87CFA | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.730_87CFA | 學甲佳里一路(730)87RY通訊故障 | OTHER | S43/0/730/87CFA |  |  |  | CDC | 439 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 730 | 學甲佳里一路(730) |  | RYFA | [17 empty] | 1-37-14 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.730_RYFA | 學甲佳里一路(730)數位電驛故障 | OTHER | S43/69/730/RYFA |  |  |  | CDC | 440 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 910 | 新營學甲一路(910) |  | 87CFA | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.910_87CFA | 新營學甲一路(910)87RY通訊故障 | OTHER | S43/0/910/87CFA |  |  |  | CDC | 441 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 910 | 新營學甲一路(910) |  | RYFA | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.910_RYFA | 新營學甲一路(910)數位電驛故障 | OTHER | S43/69/910/RYFA |  |  |  | CDC | 442 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-06-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | S43//1MTR/63Q |  |  |  | CDC | 443 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-05-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | S43//1MTR/96B1 |  |  |  | CDC | 444 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-05-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | S43//1MTR/96B2 |  |  |  | CDC | 445 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-05-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | S43//1MTR/96D |  |  |  | CDC | 446 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-05-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | S43//1MTR/96P |  |  |  | CDC | 447 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-06-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | S43//2MTR/63Q |  |  |  | CDC | 448 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-06-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | S43//2MTR/96B1 |  |  |  | CDC | 449 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-06-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | S43//2MTR/96B2 |  |  |  | CDC | 450 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-06-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | S43//2MTR/96D |  |  |  | CDC | 451 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-06-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | S43//2MTR/96P |  |  |  | CDC | 452 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-07-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | S43//3MTR/63Q |  |  |  | CDC | 453 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-06-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | S43//3MTR/96B1 |  |  |  | CDC | 454 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-06-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | S43//3MTR/96B2 |  |  |  | CDC | 455 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-07-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | S43//3MTR/96D |  |  |  | CDC | 456 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-07-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | S43//3MTR/96P |  |  |  | CDC | 457 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.650_87A | 新西線(650) 87RY | LINE69 | S43/69/650/87A |  |  |  | CDC | 458 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 學甲SS.650_87UL | 新西線(650) 87RY U/L | LINE69 | S43/69/650/87UL |  |  |  | CDC | 459 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 650 | #1MTR(650) |  | 87CFA | [17 empty] | 1-37-11 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.650_87CFA | 新西學甲(650)87RY通訊故障 | OTHER | S43/69/650/87CFA |  |  |  | CDC | 460 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 650 | #1MTR(650) |  | RYFA | [17 empty] | 1-37-10 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.650_RYFA | 新西學甲(650)數位電驛故障 | OTHER | S43/69/650/RYFA |  |  |  | CDC | 461 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.630_87A | 永華線(630) 87RY | LINE69 | S43/69/630/87A |  |  |  | CDC | 462 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 學甲SS.630_87UL | 永華線(630) 87RY U/L | LINE69 | S43/69/630/87UL |  |  |  | CDC | 463 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 630 | 永華線(630) |  | 87CFA | [17 empty] | 1-37-09 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.630_87CFA | 永華學甲(630)87RY通訊故障 | OTHER | S43/69/630/87CFA |  |  |  | CDC | 464 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 630 | 永華線(630) |  | RYFA | [17 empty] | 1-37-08 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.630_RYFA | 永華學甲(630)數位電驛故障 | OTHER | S43/69/630/RYFA |  |  |  | CDC | 465 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV |  |  |  | RYFA | [17 empty] | 1-33-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | S43/11/ComPoint/IRFA |  |  |  | CDC | 466 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-33-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.PMA | POWER METER故障 | OTHER | S43/0/ComPoint/PMA |  |  |  | CDC | 467 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-06 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.600_CB | 600(TIE) CB | TIE | S43/69/600/CB |  |  |  | CDC | 468 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-24 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.601_DS | 601(TIE) DS | TIE | S43/69/600/DS1 |  |  |  | CDC | 469 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3A-14 | 1-3A-15 | 1-25 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.602_DS | 602(TIE) DS | TIE | S43/69/600/DS2 |  |  |  | CDC | 470 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-07 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S43/69/1BUS/87A |  |  |  | CDC | 471 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 學甲SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S43/69/2BUS/BUS_VUA |  |  |  | CDC | 472 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S43/69/2BUS/87A |  |  |  | CDC | 473 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | BUS | BUS |  | BF | [17 empty] | 1-3D-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.69KVBUS_BF | 69KV匯流排數位電驛故障 | OTHER | S43/69/ComPoint/87A |  |  |  | CDC | 474 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | DS1 | 731 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.731_DS | 731(學甲佳里一路) DS | LINE69 | S43/69/730/ABS1 |  |  |  | CDC | 475 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | DS2 | 732 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-22 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.732_DS | 732(學甲佳里一路) DS | LINE69 | S43/69/730/ABS2 |  |  |  | CDC | 476 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | DS1 | 911 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 學甲SS.911_DS | 911(新營學甲一路) DS | LINE69 | S43/69/910/ABS1 |  |  |  | CDC | 477 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | DS2 | 912 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 學甲SS.912_DS | 912(新營學甲一路) DS | LINE69 | S43/69/910/ABS2 |  |  |  | CDC | 478 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S43 | 學甲SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-3D-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.600_RYFA | 600TIE數位電驛故障 | OTHER | S43/69/600/RYFA |  |  |  | CDC | 479 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | _87B1 | BUS 87B1 |  | U/L | [17 empty] | 1-3D-00 |  | 1-26 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.69KV_87B1_U/L | 69KVBUS 87B1 U/L | OTHER | S43/69/1BUS/87UL |  |  |  | CDC | 480 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | _87B2 | BUS 87B2 |  | U/L | [17 empty] | 1-3D-01 |  | 1-28 | [5 empty] | 69KV_N | [8 empty] | 學甲SS.69KV_87B2_U/L | 69KVBUS 87B2 U/L | OTHER | S43/69/2BUS/87UL |  |  |  | CDC | 481 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | 600GDA(1) | [17 empty] | 1-05-03 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | OTHER | S43/69/600/GDA1 |  |  |  | CDC | 482 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | 600GDA(2) | [17 empty] | 1-07-04 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | OTHER | S43/69/600/GDA2 |  |  |  | CDC | 483 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 1BUS | #1BUS |  | 600PHA(1) | [17 empty] | 1-05-02 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | OTHER | S43/69/600/PHA1 |  |  |  | CDC | 484 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 2BUS | #2BUS |  | 600PHA(2) | [17 empty] | 1-07-03 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | OTHER | S43/69/600/PHA2 |  |  |  | CDC | 485 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | BUS | BUS |  | 87CTFA | [17 empty] | 1-3D-04 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.69KVBUS_CTFA | 69KVBUS CT故障 | OTHER | S43/69/ComPoint/12B_CTFA |  |  |  | CDC | 486 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.720_87A | 新營學甲二路(720) 87RY | LINE69 | S43/69/720/87A |  |  |  | CDC | 487 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 學甲SS.720_87UL | 新營學甲二路(720) 87RY U/L | LINE69 | S43/69/720/87UL |  |  |  | CDC | 488 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 720 | 新營學甲二路(720) |  | 87CFA | [17 empty] | 1-37-07 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.720_87CFA | 新營學甲二路(720)87RY通訊故障 | OTHER | S43/69/720/87CFA |  |  |  | CDC | 489 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 720 | 新營學甲二路(720) |  | RYFA | [17 empty] | 1-37-06 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.720_RYFA | 新營學甲二路(720)數位電驛故障 | OTHER | S43/69/720/RYFA |  |  |  | CDC | 490 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.620_87A | 學甲佳里二路(620) 87RY | LINE69 | S43/69/620/87A |  |  |  | CDC | 491 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 學甲SS.620_87UL | 學甲佳里二路(620) 87RY U/L | LINE69 | S43/69/620/87UL |  |  |  | CDC | 492 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 620 | 外港線(620) |  | 87CFA | [17 empty] | 1-37-05 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.620_87CFA | 學甲佳里二路(620)87RY通訊故障 | OTHER | S43/69/620/87CFA |  |  |  | CDC | 493 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 620 | 外港線(620) |  | RYFA | [17 empty] | 1-37-04 | [7 empty] | 69KV_N | [8 empty] | 學甲SS.620_RYFA | 學甲佳里二路(620)數位電驛故障 | OTHER | S43/69/620/RYFA |  |  |  | CDC | 494 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 81RY | 81RY |  | RYFA | [17 empty] | 1-3D-10 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | S43/0/ComPoint/81_RYFA |  |  |  | CDC | 495 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-3D-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | S43//1MTR/RYFA |  |  |  | CDC | 496 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-3D-11 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | S43//1MTR/MTR_86A |  |  |  | CDC | 497 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 871S | [17 empty] | 1-3D-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | S43//1MTR/1_87UL1 |  |  |  | CDC | 498 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 1MTR | #1MTR |  | 872S | [17 empty] | 1-3D-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | S43//1MTR/1_87UL2 |  |  |  | CDC | 499 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-3D-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | S43//2MTR/MTR_86A |  |  |  | CDC | 500 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 871S | [17 empty] | 1-32-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | S43//2MTR/1_87UL1 |  |  |  | CDC | 501 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | 872S | [17 empty] | 1-32-13 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | S43//2MTR/1_87UL2 |  |  |  | CDC | 502 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-3D-08 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | S43//2MTR/RYFA |  |  |  | CDC | 503 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 1-3D-09 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | S43//3MTR/RYFA |  |  |  | CDC | 504 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-3D-13 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | S43//3MTR/MTR_86A |  |  |  | CDC | 505 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 871S | [17 empty] | 1-32-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | S43//3MTR/1_87UL1 |  |  |  | CDC | 506 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 3MTR | #3MTR |  | 872S | [17 empty] | 1-32-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | S43//3MTR/1_87UL2 |  |  |  | CDC | 507 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-16-04 |  | 1-42 | [5 empty] | 161KV_N | [8 empty] | 學甲SS.390_CB | 390(#1SSTR) CB | OTHER | S43/11/390/CB |  |  |  | CDC | 508 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-16-05 | [7 empty] | 161KV_N | [8 empty] | 學甲SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S43/11/390/51A |  |  |  | CDC | 509 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-16-06 | [7 empty] | 161KV_N | [8 empty] | 學甲SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S43/11/390/51NA |  |  |  | CDC | 510 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 490 | #3SSTR(490) |  | CB | [17 empty] | 1-16-07 |  | 1-43 | [5 empty] | 161KV_N | [8 empty] | 學甲SS.490_CB | 490(#3SSTR) CB | OTHER | S43/11/490/CB |  |  |  | CDC | 511 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-17-00 | [7 empty] | 161KV_N | [8 empty] | 學甲SS.#3SSTR_51A | #3SSTR 51RY | OTHER | S43/11/490/51A |  |  |  | CDC | 512 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-17-01 | [7 empty] | 161KV_N | [8 empty] | 學甲SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | S43/11/490/51NA |  |  |  | CDC | 513 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1MA | #1MA |  | 81AS | [17 empty] | 1-14-00 |  | 1-41 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MA_81A/S | #1MA 81RY | OTHER | S43/11/M1/81AS |  |  |  | CDC | 514 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S43 | 學甲SS | 0 |  | 1MA | #1MA |  | 81UL | [17 empty] | 1-33-13 |  | 1-6B | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | S43/11/M1/81UL |  |  |  | CDC | 515 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MA | #2MA |  | 81AS | [17 empty] | 1-14-01 |  | 1-56 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MA_81A/S | #2MA 81RY | OTHER | S43/11/M2A/81AS |  |  |  | CDC | 516 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S43 | 學甲SS | 0 |  | 2MA | #2MA |  | 81UL | [17 empty] | 1-34-13 |  | 1-6C | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | S43/11/M2A/81UL |  |  |  | CDC | 517 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 2MB | #2MB |  | 81AS | [17 empty] | 1-14-02 |  | 1-57 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MB_81A/S | #2MB 81RY | OTHER | S43/11/M2B/81AS |  |  |  | CDC | 518 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S43 | 學甲SS | 0 |  | 2MB | #2MB |  | 81UL | [17 empty] | 1-34-14 |  | 1-6D | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | S43/11/M2B/81UL |  |  |  | CDC | 519 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 3MA | #3MA |  | 81AS | [17 empty] | 1-14-03 |  | 1-69 | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MA_81A/S | #3MA 81RY | OTHER | S43/11/M3/81AS |  |  |  | CDC | 520 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S43 | 學甲SS | 0 |  | 3MA | #3MA |  | 81UL | [17 empty] | 1-35-13 |  | 1-6E | [5 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | S43/11/M3/81UL |  |  |  | CDC | 521 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 0 |  | 1GIS | #1GIS |  | CBA | [17 empty] | 1-3E-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1GIS_CBA | #1GIS重故障 | OTHER | S43/11/1GIS/CBA |  |  |  | CDC | 522 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 1GIS | #1GIS |  | CBF | [17 empty] | 1-3E-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#1GIS_CBF | #1GIS輕故障 | OTHER | S43/11/1GIS/CBF |  |  |  | CDC | 523 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2GIS | #2GIS |  | CBA | [17 empty] | 1-3E-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2GIS_CBA | #2GIS重故障 | OTHER | S43/11/2GIS/CBA |  |  |  | CDC | 524 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 2GIS | #2GIS |  | CBF | [17 empty] | 1-3E-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#2GIS_CBF | #2GIS輕故障 | OTHER | S43/11/2GIS/CBF |  |  |  | CDC | 525 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3GIS | #3GIS |  | CBA | [17 empty] | 1-3E-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3GIS_CBA | #3GIS重故障 | OTHER | S43/11/3GIS/CBA |  |  |  | CDC | 526 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 0 |  | 3GIS | #3GIS |  | CBF | [17 empty] | 1-3E-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.#3GIS_CBF | #3GIS輕故障 | OTHER | S43/11/3GIS/CBF |  |  |  | CDC | 527 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) 81RY |  | 81UL | [17 empty] | 1-3E-08 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_81U/L | 11KV學平線(VD21) 81RY U/L | OTHER | S43/11/VD21/81UL |  |  |  | CDC | 528 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) 81RY |  | 81UL | [17 empty] | 1-3E-09 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_81U/L | 11KV信義線(VD22) 81RY U/L | OTHER | S43/11/VD22/81UL |  |  |  | CDC | 529 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) 81RY |  | 81UL | [17 empty] | 1-3E-10 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_81U/L | 11KV中洲線(VD23) 81RY U/L | OTHER | S43/11/VD23/81UL |  |  |  | CDC | 530 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) 81RY |  | 81UL | [17 empty] | 1-3E-11 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_81U/L | 11KV宅港線(VD24) 81RY U/L | OTHER | S43/11/VD24/81UL |  |  |  | CDC | 531 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) 81RY |  | 81UL | [17 empty] | 1-3E-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_81U/L | 11KV文化線(VD25) 81RY U/L | OTHER | S43/11/VD25/81UL |  |  |  | CDC | 532 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) 81RY |  | 81UL | [17 empty] | 1-3E-13 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_81U/L | 11KV竹埔線(VD26) 81RY U/L | OTHER | S43/11/VD26/81UL |  |  |  | CDC | 533 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) 81RY |  | 81UL | [17 empty] | 1-3E-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_81U/L | 11KV美豐線(VD27) 81RY U/L | OTHER | S43/11/VD27/81UL |  |  |  | CDC | 534 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) 81RY |  | 81UL | [17 empty] | 1-3E-15 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_81U/L | 11KV學工線(VD28) 81RY U/L | OTHER | S43/11/VD28/81UL |  |  |  | CDC | 535 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) 81RY |  | 81UL | [17 empty] | 1-3F-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_81U/L | 11KV學興線(VD29) 81RY U/L | OTHER | S43/11/VD29/81UL |  |  |  | CDC | 536 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) 81RY |  | 81UL | [17 empty] | 1-3F-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_81U/L | 11KV學甲線(VD30) 81RY U/L | OTHER | S43/11/VD30/81UL |  |  |  | CDC | 537 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) 81RY |  | 81UL | [17 empty] | 1-3F-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_81U/L | 11KV新生線(VD31) 81RY U/L | OTHER | S43/11/VD31/81UL |  |  |  | CDC | 538 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) 81RY |  | 81UL | [17 empty] | 1-3F-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_81U/L | 11KV錦湖線(VD32) 81RY U/L | OTHER | S43/11/VD32/81UL |  |  |  | CDC | 539 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) 81RY |  | 81UL | [17 empty] | 1-3F-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_81U/L | 11KV達明線(VD33) 81RY U/L | OTHER | S43/11/VD33/81UL |  |  |  | CDC | 540 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) 81RY |  | 81UL | [17 empty] | 1-3F-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_81U/L | 11KV三慈線(VD34) 81RY U/L | OTHER | S43/11/VD34/81UL |  |  |  | CDC | 541 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) 81RY |  | 81UL | [17 empty] | 1-3F-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_81U/L | 11KV山寮線(VD35) 81RY U/L | OTHER | S43/11/VD35/81UL |  |  |  | CDC | 542 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S43 | 學甲SS | 11 | 11kV | VD21_79 | 學平線(VD21) |  | LOA | [17 empty] | 1-3C-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_79_LOA | 11KV學平線(VD21) 79LOA | OTHER | S43/11/VD21/LOA |  |  |  | CDC | 543 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD21 | 學平線(VD21) |  | 81AS | [17 empty] | 1-14-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_81A/S | 11KV學平線(VD21) 81RY | OTHER | S43/11/VD21/81AS |  |  |  | CDC | 544 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22_79 | 信義線(VD22) |  | LOA | [17 empty] | 1-3C-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_79_LOA | 11KV信義線(VD22) 79LOA | OTHER | S43/11/VD22/LOA |  |  |  | CDC | 545 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD22 | 信義線(VD22) |  | 81AS | [17 empty] | 1-14-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_81A/S | 11KV信義線(VD22) 81RY | OTHER | S43/11/VD22/81AS |  |  |  | CDC | 546 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23_79 | 中洲線(VD23) |  | LOA | [17 empty] | 1-3C-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_79_LOA | 11KV中洲線(VD23) 79LOA | OTHER | S43/11/VD23/LOA |  |  |  | CDC | 547 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD23 | 中洲線(VD23) |  | 81AS | [17 empty] | 1-14-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_81A/S | 11KV中洲線(VD23) 81RY | OTHER | S43/11/VD23/81AS |  |  |  | CDC | 548 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24_79 | 宅港線(VD24) |  | LOA | [17 empty] | 1-3C-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_79_LOA | 11KV宅港線(VD24) 79LOA | OTHER | S43/11/VD24/LOA |  |  |  | CDC | 549 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD24 | 宅港線(VD24) |  | 81AS | [17 empty] | 1-15-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_81A/S | 11KV宅港線(VD24) 81RY | OTHER | S43/11/VD24/81AS |  |  |  | CDC | 550 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25_79 | 文化線(VD25) |  | LOA | [17 empty] | 1-3C-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_79_LOA | 11KV文化線(VD25) 79LOA | OTHER | S43/11/VD25/LOA |  |  |  | CDC | 551 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD25 | 文化線(VD25) |  | 81AS | [17 empty] | 1-15-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_81A/S | 11KV文化線(VD25) 81RY | OTHER | S43/11/VD25/81AS |  |  |  | CDC | 552 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26_79 | 竹埔線(VD26) |  | LOA | [17 empty] | 1-3C-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_79_LOA | 11KV竹埔線(VD26) 79LOA | OTHER | S43/11/VD26/LOA |  |  |  | CDC | 553 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD26 | 竹埔線(VD26) |  | 81AS | [17 empty] | 1-15-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_81A/S | 11KV竹埔線(VD26) 81RY | OTHER | S43/11/VD26/81AS |  |  |  | CDC | 554 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27_79 | 美豐線(VD27) |  | LOA | [17 empty] | 1-3C-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_79_LOA | 11KV美豐線(VD27) 79LOA | OTHER | S43/11/VD27/LOA |  |  |  | CDC | 555 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD27 | 美豐線(VD27) |  | 81AS | [17 empty] | 1-15-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_81A/S | 11KV美豐線(VD27) 81RY | OTHER | S43/11/VD27/81AS |  |  |  | CDC | 556 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28_79 | 學工線(VD28) |  | LOA | [17 empty] | 1-3C-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_79_LOA | 11KV學工線(VD28) 79LOA | OTHER | S43/11/VD28/LOA |  |  |  | CDC | 557 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD28 | 學工線(VD28) |  | 81AS | [17 empty] | 1-15-04 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_81A/S | 11KV學工線(VD28) 81RY | OTHER | S43/11/VD28/81AS |  |  |  | CDC | 558 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29_79 | 學興線(VD29) |  | LOA | [17 empty] | 1-3C-08 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_79_LOA | 11KV學興線(VD29) 79LOA | OTHER | S43/11/VD29/LOA |  |  |  | CDC | 559 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD29 | 學興線(VD29) |  | 81AS | [17 empty] | 1-15-05 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_81A/S | 11KV學興線(VD29) 81RY | OTHER | S43/11/VD29/81AS |  |  |  | CDC | 560 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30_79 | 學甲線(VD30) |  | LOA | [17 empty] | 1-3C-09 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_79_LOA | 11KV學甲線(VD30) 79LOA | OTHER | S43/11/VD30/LOA |  |  |  | CDC | 561 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD30 | 學甲線(VD30) |  | 81AS | [17 empty] | 1-15-06 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_81A/S | 11KV學甲線(VD30) 81RY | OTHER | S43/11/VD30/81AS |  |  |  | CDC | 562 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31_79 | 新生線(VD31) |  | LOA | [17 empty] | 1-3C-10 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_79_LOA | 11KV新生線(VD31) 79LOA | OTHER | S43/11/VD31/LOA |  |  |  | CDC | 563 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD31 | 新生線(VD31) |  | 81AS | [17 empty] | 1-15-07 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_81A/S | 11KV新生線(VD31) 81RY | OTHER | S43/11/VD31/81AS |  |  |  | CDC | 564 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32_79 | 錦湖線(VD32) |  | LOA | [17 empty] | 1-3C-11 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_79_LOA | 11KV錦湖線(VD32) 79LOA | OTHER | S43/11/VD32/LOA |  |  |  | CDC | 565 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD32 | 錦湖線(VD32) |  | 81AS | [17 empty] | 1-16-00 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_81A/S | 11KV錦湖線(VD32) 81RY | OTHER | S43/11/VD32/81AS |  |  |  | CDC | 566 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33_79 | 達明線(VD33) |  | LOA | [17 empty] | 1-3C-12 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_79_LOA | 11KV達明線(VD33) 79LOA | OTHER | S43/11/VD33/LOA |  |  |  | CDC | 567 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD33 | 達明線(VD33) |  | 81AS | [17 empty] | 1-16-01 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_81A/S | 11KV達明線(VD33) 81RY | OTHER | S43/11/VD33/81AS |  |  |  | CDC | 568 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34_79 | 三慈線(VD34) |  | LOA | [17 empty] | 1-3C-13 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_79_LOA | 11KV三慈線(VD34) 79LOA | OTHER | S43/11/VD34/LOA |  |  |  | CDC | 569 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD34 | 三慈線(VD34) |  | 81AS | [17 empty] | 1-16-02 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_81A/S | 11KV三慈線(VD34) 81RY | OTHER | S43/11/VD34/81AS |  |  |  | CDC | 570 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35_79 | 山寮線(VD35) |  | LOA | [17 empty] | 1-3C-14 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_79_LOA | 11KV山寮線(VD35) 79LOA | OTHER | S43/11/VD35/LOA |  |  |  | CDC | 571 | GENERICDIPoint | SS303_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | VD35 | 山寮線(VD35) |  | 81AS | [17 empty] | 1-16-03 | [7 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_81A/S | 11KV山寮線(VD35) 81RY | OTHER | S43/11/VD35/81AS |  |  |  | CDC | 572 | GENERICDIPoint | SS303_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S43 | 學甲SS | 11 | 11kV | 210_SC | #1SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 573 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 11 | 11kV | 220_SC | #2SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 574 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 11 | 11kV | 230_SC | #3SC | 3 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 575 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 學甲SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 576 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S43 | 學甲SS | 69 | 69kV | 620 | 外港線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.620BE | 620BE (非取樣點) | LINE69 | S43/69/620/BE0 |  |  |  |  | 577 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 630 | 永華線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.630BE | 630BE (非取樣點) | LINE69 | S43/69/630/BE0 |  |  |  |  | 578 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 650 | #1MTR(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.650BE | 650BE (非取樣點) | LINE69 | S43/69/650/BE0 |  |  |  |  | 579 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 720 | 新營學甲二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.720BE | 720BE (非取樣點) | LINE69 | S43/69/720/BE0 |  |  |  |  | 580 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD21 | VD21_ES |  | LE0 | VD21_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_ES | VD21_ES (非取樣點) | FEEDER | S43/11/VD21/ES |  |  |  |  | 581 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD22 | VD22_ES |  | LE0 | VD22_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_ES | VD22_ES (非取樣點) | FEEDER | S43/11/VD22/ES |  |  |  |  | 582 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD23 | VD23_ES |  | LE0 | VD23_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_ES | VD23_ES (非取樣點) | FEEDER | S43/11/VD23/ES |  |  |  |  | 583 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD24 | VD24_ES |  | LE0 | VD24_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_ES | VD24_ES (非取樣點) | FEEDER | S43/11/VD24/ES |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD25 | VD25_ES |  | LE0 | VD25_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_ES | VD25_ES (非取樣點) | FEEDER | S43/11/VD25/ES |  |  |  |  | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD26 | VD26_ES |  | LE0 | VD26_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_ES | VD26_ES (非取樣點) | FEEDER | S43/11/VD26/ES |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD27 | VD27_ES |  | LE0 | VD27_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_ES | VD27_ES (非取樣點) | FEEDER | S43/11/VD27/ES |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD28 | VD28_ES |  | LE0 | VD28_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_ES | VD28_ES (非取樣點) | FEEDER | S43/11/VD28/ES |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD29 | VD29_ES |  | LE0 | VD29_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_ES | VD29_ES (非取樣點) | FEEDER | S43/11/VD29/ES |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD30 | VD30_ES |  | LE0 | VD30_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_ES | VD30_ES (非取樣點) | FEEDER | S43/11/VD30/ES |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD31 | VD31_ES |  | LE0 | VD31_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_ES | VD31_ES (非取樣點) | FEEDER | S43/11/VD31/ES |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD32 | VD32_ES |  | LE0 | VD32_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_ES | VD32_ES (非取樣點) | FEEDER | S43/11/VD32/ES |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD33 | VD33_ES |  | LE0 | VD33_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_ES | VD33_ES (非取樣點) | FEEDER | S43/11/VD33/ES |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD34 | VD34_ES |  | LE0 | VD34_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_ES | VD34_ES (非取樣點) | FEEDER | S43/11/VD34/ES |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD35 | VD35_ES |  | LE0 | VD35_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_ES | VD35_ES (非取樣點) | FEEDER | S43/11/VD35/ES |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | TIE1DS | TIE1DS |  | TIE1DS | TIE1DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE1DS | TIE1DS (非取樣點) | TIE | S43/11/TIE1/D1 |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | TIE2DS | TIE2DS |  | TIE2DS | TIE2DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE2DS | TIE2DS (非取樣點) | TIE | S43/11/TIE2/D1 |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.750TE | 750TE (非取樣點) | DTR | S43/69/750/TE0 |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.750BE | 750BE (非取樣點) | DTR | S43/69/750/BE0 |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.1M_ES | 1M_ES (非取樣點) | DTR | S43/11/M1/ES |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.760TE | 760TE (非取樣點) | DTR | S43/69/760/TE0 |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.760BE | 760BE (非取樣點) | DTR | S43/69/760/BE0 |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.2M_ES | 2M_ES (非取樣點) | DTR | S43/11/M2/ES |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.770TE | 770TE (非取樣點) | DTR | S43/69/770/TE0 |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.770BE | 770BE (非取樣點) | DTR | S43/69/770/BE0 |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.3M_ES | 3M_ES (非取樣點) | DTR | S43/11/M3/ES |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.210ES | 210ES (非取樣點) | SC | S43/11/210/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | _1SCDS | _#1SCDS |  | #1SCDS | 11KV_#1SCDS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_#1SCDS | 11KV_#1SCDS (非取樣點) | SC | S43/11/210/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 220ES | 220ES |  | 220ES | 220ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.220ES | 220ES (非取樣點) | SC | S43/11/220/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | _2SCDS | _#2SCDS |  | #2SCDS | 11KV_#2SCDS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_#2SCDS | 11KV_#2SCDS (非取樣點) | SC | S43/11/220/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 230ES | 230ES |  | 230ES | 230ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.230ES | 230ES (非取樣點) | SC | S43/11/230/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 11 | 11kV | _3SCDS | _#3SCDS |  | #3SCDS | 11KV_#3SCDS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.11KV_#3SCDS | 11KV_#3SCDS (非取樣點) | SC | S43/11/230/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.810BE | 810BE (非取樣點) | SC | S43/69/810/BE0 |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 810LE | 810LE |  | 810LE | 810LE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.810LE | 810LE (非取樣點) | SC | S43/69/810/LE0 |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.69B1E | 69B1E (非取樣點) | BUS | S43/69/1BUS/BE1 |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 616 | NotelDIPoint | [38 empty] | START/STOP | STOP
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | BE0 | 730BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.730BE | 730BE (非取樣點) | LINE69 | S43/69/730/BE0 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | BE0 | 910BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.910BE | 910BE (非取樣點) | LINE69 | S43/69/910/BE0 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | LE0 | 730LE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.730LE | 730LE (非取樣點) | LINE69 | S43/69/730/LE0 |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 910 | 新營學甲一路(910) |  | LE0 | 910LE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.910LE | 910LE (非取樣點) | LINE69 | S43/69/910/LE0 |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.601E | 601E (非取樣點) | TIE | S43/69/600/E1 |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.602E | 602E (非取樣點) | TIE | S43/69/600/E2 |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.69B2E | 69B2E (非取樣點) | BUS | S43/69/2BUS/BE2 |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 學甲SS.391 | 391 (非取樣點) | OTHER | S43/11/390/D1 |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.391E | 391E (非取樣點) | OTHER | S43/11/390/E1 |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 學甲SS.491 | 491 (非取樣點) | OTHER | S43/11/490/D1 |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.491E | 491E (非取樣點) | OTHER | S43/11/490/E1 |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | VD21 | VD21_DS |  | DS1 | VD21_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD21_DS | VD21_DS (非取樣點) | FEEDER | S43/11/VD21/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD22 | VD22_DS |  | DS1 | VD22_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD22_DS | VD22_DS (非取樣點) | FEEDER | S43/11/VD22/DS |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD23 | VD23_DS |  | DS1 | VD23_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD23_DS | VD23_DS (非取樣點) | FEEDER | S43/11/VD23/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD24 | VD24_DS |  | DS1 | VD24_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD24_DS | VD24_DS (非取樣點) | FEEDER | S43/11/VD24/DS |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD25 | VD25_DS |  | DS1 | VD25_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD25_DS | VD25_DS (非取樣點) | FEEDER | S43/11/VD25/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD26 | VD26_DS |  | DS1 | VD26_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD26_DS | VD26_DS (非取樣點) | FEEDER | S43/11/VD26/DS |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD27 | VD27_DS |  | DS1 | VD27_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD27_DS | VD27_DS (非取樣點) | FEEDER | S43/11/VD27/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD28 | VD28_DS |  | DS1 | VD28_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD28_DS | VD28_DS (非取樣點) | FEEDER | S43/11/VD28/DS |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD29 | VD29_DS |  | DS1 | VD29_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD29_DS | VD29_DS (非取樣點) | FEEDER | S43/11/VD29/DS |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD30 | VD30_DS |  | DS1 | VD30_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD30_DS | VD30_DS (非取樣點) | FEEDER | S43/11/VD30/DS |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD31 | VD31_DS |  | DS1 | VD31_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD31_DS | VD31_DS (非取樣點) | FEEDER | S43/11/VD31/DS |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD32 | VD32_DS |  | DS1 | VD32_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD32_DS | VD32_DS (非取樣點) | FEEDER | S43/11/VD32/DS |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD33 | VD33_DS |  | DS1 | VD33_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD33_DS | VD33_DS (非取樣點) | FEEDER | S43/11/VD33/DS |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD34 | VD34_DS |  | DS1 | VD34_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD34_DS | VD34_DS (非取樣點) | FEEDER | S43/11/VD34/DS |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | VD35 | VD35_DS |  | DS1 | VD35_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.VD35_DS | VD35_DS (非取樣點) | FEEDER | S43/11/VD35/DS |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | TIE1DS2 | TIE1DS2 |  | TIE1DS2 | TIE1DS2 | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE1DS2 | TIE1DS2 (非取樣點) | TIE | S43/11/TIE1/D2 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | TIE2DS2 | TIE2DS2 |  | TIE2DS2 | TIE2DS2 | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.TIE2DS2 | TIE2DS2 (非取樣點) | TIE | S43/11/TIE2/D2 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.101E | 101E (非取樣點) | TIE | S43/11/TIE1/E1 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.102E | 102E (非取樣點) | TIE | S43/11/TIE1/E2 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 200 | 200 |  | E1 | 201E | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.201E | 201E (非取樣點) | TIE | S43/11/TIE2/E1 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 200 | 200 |  | E2 | 202E | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.202E | 202E (非取樣點) | TIE | S43/11/TIE2/E2 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.1M_DS | 1M_DS (非取樣點) | DTR | S43/11/M1/DS |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S43/11/M2A/DS |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S43/11/M2B/DS |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S43/11/M2B/ES |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS3_2 | [8 empty] | 學甲SS.3M_DS | 3M_DS (非取樣點) | DTR | S43/11/M3/DS |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S43 | 學甲SS | 0 |  | 11B1E | 11B1E |  | BE1 | 11B1E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.11B1E | 11B1E (非取樣點) | BUS | S43/11/1BUS/BE1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 11B2E | 11B2E |  | BE2 | 11B2E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.11B2E | 11B2E (非取樣點) | BUS | S43/11/2BUS/BE2 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 11B2BE | 11B2BE |  | B2BE0 | 11B2BE | [24 empty] | ADCS_N | [8 empty] | 學甲SS.11B2BE | 11B2BE (非取樣點) | BUS | S43/11/2BUS/BE0 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S43 | 學甲SS | 0 |  | 11B3E | 11B3E |  | BE3 | 11B3E | [24 empty] | ADCS_N | [8 empty] | 學甲SS.11B3E | 11B3E (非取樣點) | BUS | S43/11/3BUS/BE3 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo