## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S45 | 新東SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KVBUS | KV | 69KVBUS PT | kV_-90_90(-2000_2000) | aaa | B2/S45_A1 | [8 empty] | 新東SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S45 | 新東SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV #1 BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S45_D1 | [8 empty] | 新東SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2A BUS | KV | #2A BUS PT | kV_-9_9(-2000_2000) | aba | B2/S45_D1 | [8 empty] | 新東SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | 11KV #3 BUS | KV | 三號 BUS PT | kV_-9_9(-2000_2000) | ada | B2/S45_D1 | [8 empty] | 新東SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S45_A1 | [8 empty] | 新東SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA | 衡相監視 |  |  | B2/S45_A1 | [8 empty] | 新東SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 620 | MW | 新營新東線 | MW_-144_144(-2000_2000) |  | B2/S45_A1 | [8 empty] | 新東SS.620_MW | 新營新東線 MW | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 620 | MVAR | 新營新東線 | MVAR_-144_144(-2000_2000) |  | B2/S45_A1 | [8 empty] | 新東SS.620_MVAR | 新營新東線 MVAR | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 620 | MWH(+) | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 10 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 650 | MW | 新東白河線 | MW_-96_96(-2000_2000) |  | B2/S45_A1 | [8 empty] | 新東SS.650_MW | 白河線 MW | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 650 | MVAR | 新東白河線 | MVAR_-96_96(-2000_2000) |  | B2/S45_A1 | [8 empty] | 新東SS.650_MVAR | 白河線 MVAR | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 650 | MWH(+) | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 13 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 620 | PHA | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_PHA | 新營新東線(620) 相間RY | LINE69 |  |  |  |  | CDC | 14 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 620 | GDA | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_GDA | 新營新東線(620) 接地RY | LINE69 |  |  |  |  | CDC | 15 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 620 | 87A | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_87A | 新營新東線(620) 87RY | LINE69 |  |  |  |  | CDC | 16 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 650 | PHA | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_PHA | 白河線(650) 相間RY | LINE69 |  |  |  |  | CDC | 17 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 650 | GDA | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_GDA | 白河線(650) 接地RY | LINE69 |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 650 | 87A | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_87A | 白河線(650) 87RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | Locate Empty |  |  |  |  | B2/S45_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 20 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87UL |  | Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 620 | 87 U/L | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_87UL | 新營新東線(620) 87RY U/L | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 650 | 87 U/L | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_87UL | 白河線(650) 87RY U/L | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0018 | 1-38-08 | 1-38-09 | 1-12 | 621 | ABS ON | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.621_ABS | 621(新營新東線) ABS | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0019 | 1-38-10 | 1-38-11 | 1-13 | 622 | ABS ON | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.622_ABS | 622(新營新東線) ABS | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | ABS1 | 651 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0021 | 1-38-14 | 1-38-15 | 1-15 | 651 | ABS ON | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.651_ABS | 651(白河線) ABS | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | ABS2 | 652 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0022 | 1-39-00 | 1-39-01 | 1-16 | 652 | ABS ON | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.652_ABS | 652(白河線) ABS | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0396 | 397 | 0020 | 1-38-12 | 1-38-13 | 1-14 | 622E | ABS ON | 新營新東線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.622E_ES | 622E(新營新東線) ES | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | BE0 | 620BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_A1 | [8 empty] | 新東SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 28 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | ES2 | 652E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0402 | 403 | 0023 | 1-39-02 | 1-39-03 | 1-17 | 652E | ABS ON | 新東白河線 |  |  | B2/S45_A1 | [8 empty] | 新東SS.652E_ES | 652E(白河線) ES | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | BE0 | 650BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_A1 | [8 empty] | 新東SS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 30 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F1 PH RY | PHA | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_PHA | 11KV東一線(VE21) 相間RY | FEEDER |  |  |  |  | CDC | 31 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F1 GD RY | GDA | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_GDA | 11KV東一線(VE21) 接地RY | FEEDER |  |  |  |  | CDC | 32 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | F1 CB | 79 U/L | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_79UL | 11KV東一線(VE21) 79RY U/L | FEEDER |  |  |  |  | CDC | 33 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_ADJ | 11KV東一線(VE21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 34 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | F2 PH RY | PHA | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_PHA | 11KV東二線(VE22) 相間RY | FEEDER |  |  |  |  | CDC | 35 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F2 GD RY | GDA | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_GDA | 11KV東二線(VE22) 接地RY | FEEDER |  |  |  |  | CDC | 36 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | F2 CB | 79 U/L | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_79UL | 11KV東二線(VE22) 79RY U/L | FEEDER |  |  |  |  | CDC | 37 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_ADJ | 11KV東二線(VE22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 38 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F3 PH RY | PHA | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_PHA | 11KV東三線(VE23) 相間RY | FEEDER |  |  |  |  | CDC | 39 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | F3 GD RY | GDA | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_GDA | 11KV東三線(VE23) 接地RY | FEEDER |  |  |  |  | CDC | 40 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | F3 CB | 79 U/L | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_79UL | 11KV東三線(VE23) 79RY U/L | FEEDER |  |  |  |  | CDC | 41 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_ADJ | 11KV東三線(VE23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 42 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | F4 PH RY | PHA | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_PHA | 11KV東正線(VE24) 相間RY | FEEDER |  |  |  |  | CDC | 43 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | F4 GD RY | GDA | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_GDA | 11KV東正線(VE24) 接地RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | F4 CB | 79 U/L | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_79UL | 11KV東正線(VE24) 79RY U/L | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_ADJ | 11KV東正線(VE24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | F5 PH RY | PHA | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_PHA | 11KV東五線(VE25) 相間RY | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | F5 GD RY | GDA | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_GDA | 11KV東五線(VE25) 接地RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | F5 CB | 79 U/L | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_79UL | 11KV東五線(VE25) 79RY U/L | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_ADJ | 11KV東五線(VE25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | F6 PH RY | PHA | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_PHA | 11KV東六線(VE26) 相間RY | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | F6 GD RY | GDA | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_GDA | 11KV東六線(VE26) 接地RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | F6 CB | 79 U/L | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_79UL | 11KV東六線(VE26) 79RY U/L | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | F6 LCO | ADJ(U/L) | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_ADJ | 11KV東六線(VE26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F7 PH RY | PHA | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_PHA | 11KV東七線(VE27) 相間RY | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F7 GD RY | GDA | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_GDA | 11KV東七線(VE27) 接地RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | F7 CB | 79 U/L | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_79UL | 11KV東七線(VE27) 79RY U/L | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | F7 LCO | ADJ(U/L) | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_ADJ | 11KV東七線(VE27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | F8 PH RY | PHA | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_PHA | 11KV東八線(VE28) 相間RY | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F8 GD RY | GDA | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_GDA | 11KV東八線(VE28) 接地RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | F8 CB | 79 U/L | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_79UL | 11KV東八線(VE28) 79RY U/L | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | F8 LCO | ADJ(U/L) | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_ADJ | 11KV東八線(VE28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F9 PH RY | PHA | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_PHA | 11KV東九線(VE29) 相間RY | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | F9 GD RY | GDA | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_GDA | 11KV東九線(VE29) 接地RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | F9 CB | 79 U/L | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_79UL | 11KV東九線(VE29) 79RY U/L | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | F9 LCO | ADJ(U/L) | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_ADJ | 11KV東九線(VE29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F10 PH RY | PHA | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_PHA | 11KV東十線(VE30) 相間RY | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F10 GD RY | GDA | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_GDA | 11KV東十線(VE30) 接地RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | F10 CB | 79 U/L | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_79UL | 11KV東十線(VE30) 79RY U/L | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | F10 LCO | ADJ(U/L) | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_ADJ | 11KV東十線(VE30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | F11 PH RY | PHA | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_PHA | 11KV東忠線(VE31) 相間RY | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | F11 GD RY | GDA | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_GDA | 11KV東忠線(VE31) 接地RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0100 | 1-35-07 |  | 1-64 | F11 CB | 79 U/L | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_79UL | 11KV東忠線(VE31) 79RY U/L | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | F11 LCO | ADJ(U/L) | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_ADJ | 11KV東忠線(VE31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F12 PH RY | PHA | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_PHA | 11KV東孝線(VE32) 相間RY | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F12 GD RY | GDA | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_GDA | 11KV東孝線(VE32) 接地RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0101 | 1-35-08 |  | 1-65 | F12 CB | 79 U/L | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_79UL | 11KV東孝線(VE32) 79RY U/L | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | F12 LCO | ADJ(U/L) | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_ADJ | 11KV東孝線(VE32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | F13 PH RY | PHA | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_PHA | 11KV東仁線(VE33) 相間RY | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F13 GD RY | GDA | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_GDA | 11KV東仁線(VE33) 接地RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0102 | 1-35-09 |  | 1-66 | F13 CB | 79 U/L | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_79UL | 11KV東仁線(VE33) 79RY U/L | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | F13 LCO | ADJ(U/L) | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_ADJ | 11KV東仁線(VE33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F14 PH RY | PHA | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_PHA | 11KV東愛線(VE34) 相間RY | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | F14 GD RY | GDA | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_GDA | 11KV東愛線(VE34) 接地RY | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0103 | 1-35-10 |  | 1-67 | F14 CB | 79 U/L | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_79UL | 11KV東愛線(VE34) 79RY U/L | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | F14 LCO | ADJ(U/L) | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_ADJ | 11KV東愛線(VE34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F15 PH RY | PHA | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_PHA | 11KV東信線(VE35) 相間RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F15 GD RY | GDA | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_GDA | 11KV東信線(VE35) 接地RY | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0104 | 1-35-11 |  | 1-68 | F15 CB | 79 U/L | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_79UL | 11KV東信線(VE35) 79RY U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | F15 LCO | ADJ(U/L) | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_ADJ | 11KV東信線(VE35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VE21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | F1 CB | CB ON/OFF | 東一線 |  | aaab | B2/S45_D1 | [8 empty] | 新東SS.VE21_CB | VE21(11KV東一線) CB | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE21_ES | VE21_ES (非取樣點) | FEEDER | [5 empty] | 92 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VE22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | F2 CB | CB ON/OFF | 東二線 |  | aabb | B2/S45_D1 | [8 empty] | 新東SS.VE22_CB | VE22(11KV東二線) CB | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE22_ES | VE22_ES (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VE23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F3 CB | CB ON/OFF | 東三線 |  | aacb | B2/S45_D1 | [8 empty] | 新東SS.VE23_CB | VE23(11KV東三線) CB | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE23_ES | VE23_ES (非取樣點) | FEEDER | [5 empty] | 96 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VE24/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | F4 CB | CB ON/OFF | 東正線 |  | aaeb | B2/S45_D1 | [8 empty] | 新東SS.VE24_CB | VE24(11KV東正線) CB | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE24_ES | VE24_ES (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BUS | L/VE25/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | F5 CB | CB ON/OFF | 東五線 |  | aagb | B2/S45_D1 | [8 empty] | 新東SS.VE25_CB | VE25(11KV東五線) CB | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE25_ES | VE25_ES (非取樣點) | FEEDER | [5 empty] | 100 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VE26/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | F6 CB | CB ON/OFF | 東六線 |  | abbb | B2/S45_D1 | [8 empty] | 新東SS.VE26_CB | VE26(11KV東六線) CB | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE26_ES | VE26_ES (非取樣點) | FEEDER | [5 empty] | 102 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VE27/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | F7 CB | CB ON/OFF | 東七線 |  | abdb | B2/S45_D1 | [8 empty] | 新東SS.VE27_CB | VE27(11KV東七線) CB | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE27_ES | VE27_ES (非取樣點) | FEEDER | [5 empty] | 104 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABUS | L/VE28/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | F8 CB | CB ON/OFF | 東八線 |  | abeb | B2/S45_D1 | [8 empty] | 新東SS.VE28_CB | VE28(11KV東八線) CB | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE28_ES | VE28_ES (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBUS | L/VE29/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | F9 CB | CB ON/OFF | 東九線 |  | acab | B2/S45_D1 | [8 empty] | 新東SS.VE29_CB | VE29(11KV東九線) CB | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE29_ES | VE29_ES (非取樣點) | FEEDER | [5 empty] | 108 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBUS | L/VE30/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | F10 CB | CB ON/OFF | 東十線 |  | accb | B2/S45_D1 | [8 empty] | 新東SS.VE30_CB | VE30(11KV東十線) CB | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE30_ES | VE30_ES (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VE31/T1 |  |  | 0140 |  | 0092 | 1-11-04 |  | 1-5C | F11 CB | CB ON/OFF | 東忠線 |  | adab | B2/S45_D1 | [8 empty] | 新東SS.VE31_CB | VE31(11KV東忠線) CB | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE31_ES | VE31_ES (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VE32/T1 |  |  | 0141 |  | 0093 | 1-11-05 |  | 1-5D | F12 CB | CB ON/OFF | 東孝線 |  | adbb | B2/S45_D1 | [8 empty] | 新東SS.VE32_CB | VE32(11KV東孝線) CB | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE32_ES | VE32_ES (非取樣點) | FEEDER | [5 empty] | 114 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VE33/T1 |  |  | 0142 |  | 0094 | 1-11-06 |  | 1-5E | F13 CB | CB ON/OFF | 東仁線 |  | addb | B2/S45_D1 | [8 empty] | 新東SS.VE33_CB | VE33(11KV東仁線) CB | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE33_ES | VE33_ES (非取樣點) | FEEDER | [5 empty] | 116 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VE34/T1 |  |  | 0143 |  | 0095 | 1-11-07 |  | 1-5F | F14 CB | CB ON/OFF | 東愛線 |  | adeb | B2/S45_D1 | [8 empty] | 新東SS.VE34_CB | VE34(11KV東愛線) CB | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE34_ES | VE34_ES (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VE35/T1 |  |  | 0144 |  | 0096 | 1-12-00 |  | 1-60 | F15 CB | CB ON/OFF | 東信線 |  | adfb | B2/S45_D1 | [8 empty] | 新東SS.VE35_CB | VE35(11KV東信線) CB | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE35_ES | VE35_ES (非取樣點) | FEEDER | [5 empty] | 120 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1 TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 121 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1 TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 122 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1 TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 123 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2 TIE R相電流 | A1 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 124 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2 TIE S相電流 | A2 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 125 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2 TIE T相電流 | A3 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 126 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1450 | 1377.5 | 1450 | 1595 | 1783.5 | 2.27 | -1377.5 | -1450 | -1595 | -1783.5 | 1 | 0.01 | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BUS | B/2ABUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | zzzz | B2/S45_D1 | [8 empty] | 新東SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 127 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIE PH RY | PHA | #1 TIE CB |  |  | B2/S45_D1 | [8 empty] | 新東SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 128 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1 TIE GD RY | GDA | #1 TIE CB |  |  | B2/S45_D1 | [8 empty] | 新東SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 129 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBUS | B/3BUS |  |  | 0123 |  | 0071 | 1-0F-03 |  | 1-47 | #2 TIE CB | CB ON/OFF | #2 TIE CB |  | zzzz | B2/S45_D1 | [8 empty] | 新東SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 130 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2 TIEPH RY | PHA | #2 TIE CB |  |  | B2/S45_D1 | [8 empty] | 新東SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 131 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #2 TIEGD RY | GDA | #2 TIE CB |  |  | B2/S45_D1 | [8 empty] | 新東SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 132 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 133 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 134 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | (非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | [5 empty] | 135 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | (非取樣點) | ADD | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | [5 empty] | 136 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 137 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 138 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 139 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 140 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 141 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 MTR | MW | 二號主變 | MW_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 142 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 MTR | MVAR | 二號主變 | MVAR_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 143 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 MTR R電流 | A1 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 144 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 MTR S電流 | A2 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 145 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 MTR T電流 | A3 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 146 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 MTR | MW | 三號主變 | MW_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 147 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 MTR | MVAR | 三號主變 | MVAR_-36_36(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 148 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 MTR R電流 | A1 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 149 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 MTR S電流 | A2 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 150 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 MTR T電流 | A3 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 151 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 152 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 153 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 154 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH(+) | 一號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 155 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 156 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 157 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 158 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 159 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2TR | MWH(+) | 二號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 160 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2TR | MVARH(+) | 二號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 161 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 162 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 163 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 MTR | TAP | 三號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 164 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3TR | MWH(+) | 三號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 165 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3TR | MVARH(+) | 三號主變 |  |  | B1/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 166 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | 750 | CB ON/OFF | 一號主變一次側 |  | aaab | B3/S45_D1 | [8 empty] | 新東SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 167 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 168 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 169 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aacb | B3/S45_D1 | [8 empty] | 新東SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 170 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 171 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 172 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aafb | B3/S45_D1 | [8 empty] | 新東SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 173 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 174 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S45_D1 | [8 empty] | 新東SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 175 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1 MTR | CB ON/OFF | 一號主變二次側 |  | aada | B2/S45_D1 | [8 empty] | 新東SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 176 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | CB | 2MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2 MTR A | CB ON/OFF | 二號主變二次側(A) |  | abca | B2/S45_D1 | [8 empty] | 新東SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 177 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | CB | 2MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBUS | T/2MTR |  |  | 0012 |  | 0070 | 1-01-04 |  | 1-46 | #2 MTR B | CB ON/OFF | 二號主變二次側(B) |  | acba | B2/S45_D1 | [8 empty] | 新東SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 178 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0023 |  | 0089 | 1-02-07 |  | 1-59 | #3 MTR | CB ON/OFF | 三號主變二次側(A) |  | adca | B2/S45_D1 | [8 empty] | 新東SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 179 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 180 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 181 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1 MTR | 51ZA | 一號主變 51Z RY |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 182 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 183 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1 MTR | 87 LS | 一號主變87 RY使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 184 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 186 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 187 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 188 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2 MTR | 87 LS | 二號 主變87 RY使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 189 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 770 | PHA | 三號主變 51 RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 190 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 770 | GDA | 三號主變 51N RY |  |  | B3/S45_D1 | [8 empty] | 新東SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 191 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3 MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 192 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3MTR | 87A | 三號主變差動電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 193 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3 MTR | 87 LS | 三號 主變87 RY使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 194 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1 MTR | PHA | 一號主變二次側 51 RY |  |  | B2/S45_D1 | [8 empty] | 新東SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 195 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1 MTR | TRA | 一號主變重故障 |  | a | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 196 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1 MTR | TRF | 一號主變輕故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 197 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1 MTR | S/L | 一號主變 OLTC(中心/現場) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 198 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1 MTR | A/M | 一號主變 OLTC(自動/手動) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 199 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2 MTR A | PHA | 二號主變二次(A)51 RY |  |  | B2/S45_D1 | [8 empty] | 新東SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 200 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2 MTR B | PHA | 二號主變二次(B)51 RY |  |  | B2/S45_D1 | [8 empty] | 新東SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 201 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-34-00 |  |  | #2 MTR | TRA | 二號主變重故障 |  | a | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 202 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2 MTR | TRF | 二號主變輕故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 203 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2 MTR | S/L | 二號主變 OLTC(中心/現場) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 204 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2 MTR | A/M | 二號主變 OLTC(自動/手動) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 205 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3 MTR | PHA | 三號主變二次51 RY |  |  | B2/S45_D1 | [8 empty] | 新東SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 206 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0336 |  |  | 1-35-00 |  |  | #3 MTR | 3TRA | 三號主變重故障 |  | a | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 207 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3 MTR | 3TRF | 三號主變輕故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 208 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3 MTR | S/L | 三號主變 OLTC(中心/現場) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 209 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3 MTR | A/M | 三號主變 OLTC(自動/手動) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 210 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | 751 | ABS ON | 一號主變 |  |  | B3/S45_D1 | [8 empty] | 新東SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 211 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | 761 | ABS ON | 二號主變 |  |  | B3/S45_D1 | [8 empty] | 新東SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 212 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0044 | 1-38-04 | 1-38-05 | 1-2C | 771 | ABS ON | 三號主變 |  |  | B3/S45_D1 | [8 empty] | 新東SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 213 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1 MTR | 96A | 一號主變 96PA 電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 214 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1 MTR | TAPA | 一號主變TAP遲滯 (48TX) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 215 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1 MTR | 1ACF | 一號主變AC電源失效(27欠壓) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 216 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2 MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 217 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2 MTR | TAPA | 二號主變TAP遲滯 (48TX) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 218 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2MTR | 2ACF | 二號主變AC電源失效 (27欠壓) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 219 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3MTR | 96A | 三號主變 96D,63A RY |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 220 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3 MTR | TAPA | 三號主變TAP遲滯 (48TX) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 221 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | #3 MTR | #3ACF | 三號主變AC電源失效(27欠壓) |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 222 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | SC 69KV |  | aaea | B2/S45_A1 | [8 empty] | 新東SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 223 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_A1 | [8 empty] | 新東SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 224 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | aahb | B2/S45_D1 | [8 empty] | 新東SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 225 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1 SC | A/M | 一號SC 乏控器(自動/手動) |  |  | B2/S45_D1 | [8 empty] | 新東SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 226 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 227 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC | CB ON/OFF | #2 11KV SC |  | acdb | B2/S45_D1 | [8 empty] | 新東SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 228 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2 SC | A/M | 二號SC 乏控器(自動/手動) |  |  | B2/S45_D1 | [8 empty] | 新東SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 229 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.220ES | 220ES (非取樣點) | SC | [5 empty] | 230 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BUS | C/3SC |  |  | 0139 |  | 0091 | 1-11-03 |  | 1-5B | #3 11KV SC | CB ON/OFF | #3 11KV SC |  | adgb | B2/S45_D1 | [8 empty] | 新東SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 231 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0099 | 1-35-06 |  | 1-63 | #3 SC | A/M | 三號SC乏控器(自動/手動) |  |  | B2/S45_D1 | [8 empty] | 新東SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 232 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.230ES | 230ES (非取樣點) | SC | [5 empty] | 233 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0390 | 391 | 0039 | 1-38-06 | 1-38-07 | 1-27 | 811 | ABS ON | 69KVSC |  |  | B2/S45_A1 | [8 empty] | 新東SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 234 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 810 | PHA GDA | SC 69KV 51 51N RY |  |  | B2/S45_A1 | [8 empty] | 新東SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 235 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 810 | UVA OVA | SC 69KV 27 59N RY |  |  | B2/S45_A1 | [8 empty] | 新東SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 236 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_A1 | [8 empty] | 新東SS.810LE | 810LE (非取樣點) | SC | [5 empty] | 237 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1 SC5151NRY | SCA | #1 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 238 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1 SC2759RY | UVA | #1 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 239 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2 SC5151NRY | SCA | #2 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 240 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2 SC2759RY | UVA | #2 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 241 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | #3SC5151NRY | SCA | #3 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 242 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #3SC2759RY | UVA | #3 11KV SC |  |  | B2/S45_D1 | [8 empty] | 新東SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 243 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S45_D1 | [8 empty] | 新東SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 244 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S45_D1 | [8 empty] | 新東SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 245 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S45_D1 | [8 empty] | 新東SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 246 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S45_D1 | [8 empty] | 新東SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 247 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 新東SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 其他重故障 |  | 其他重故障 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  | 其他輕故障 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.直流充電機故障 | 變電所直流充電機故障 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池警報 |  | 洩油池警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 開關場 |  | 水氣霧釋放 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化門禁(1) | 水氣霧釋放 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 控制室旁 |  | 所内淹水高水位 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化門禁(2) | 所內淹水高水位 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 控制室旁 |  | 所内淹水低水位 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化門禁(3) | 所內淹水低水位 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | 開關場 |  | 水氣霧警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化防盜(1) | 水氣霧警報 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | 開關場 |  | 水氣霧故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化防盜(2) | 水氣霧故障 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | MCSG |  | MCSG偵煙警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.無人化防盜(3) | MCSG偵煙警報 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場照明(A) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S45_D1 | [8 empty] | 新東SS.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明(B) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S45_D1 | [8 empty] | 新東SS.開關場照明(B) | 開關場照明(B) | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | 81AS1 | 81RY_A/S(1) | Element | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0065 | 1-0C-06 |  | 1-41 | Locate Empty |  |  |  |  | B3/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 263 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | 81AS2 | 81RY_A/S(2) | Element | Status | 81RY A/S(2) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  | 0086 | 1-0F-04 |  | 1-56 | Locate Empty |  |  |  |  | B3/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 264 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 控制室 |  | CO2 警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.火災警報(1) | CO2警報 | OTHER |  |  |  |  | CDC | 265 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 控制室 |  | CO2 故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.火災警報(2) | CO2故障 | OTHER |  |  |  |  | CDC | 266 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.火災警報(3) | 火災警報(3) | OTHER |  |  |  |  | CDC | 267 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內電源欠壓 |  |  | B3/S45_D1 | [8 empty] | 新東SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 268 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 | DCA | NFB跳脫監視 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.直流電源DCA | NFB跳脫監視 | OTHER |  |  |  |  | CDC | 269 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCE | 直流電源接地故障 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 270 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 271 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 272 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 273 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S45_D1 | [8 empty] | 新東SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 274 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS 89A | ABS NFB跳脫警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 275 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | ComPoint |  |  | SCA | SC警報 | Element | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV SC | 69KVSC AL | 69KVSC警報 |  |  | B3/S45_D1 | [8 empty] | 新東SS.69KV_SC警報 | 69KV SC警報 | OTHER |  |  |  |  | CDC | 276 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | Door |  |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S45_D1 | [8 empty] | 新東SS.門禁 | 門禁 | OTHER |  |  |  |  | CDC | 277 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0372 |  |  | 1-37-04 |  |  | 620 | 87RYFA | 620數位電驛故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_87RYFA | 新營新東線(620)數位電驛故障 | OTHER |  |  |  |  | CDC | 278 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0373 |  |  | 1-37-05 |  |  | 620 | 87CFA | 620通訊故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.620_87CFA | 新營新東線(620)87RY通訊故障 | OTHER |  |  |  |  | CDC | 279 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 東一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東一線KVAR | 11KV東一線 KVAR | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 東一線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東一線A1 | 11KV東一線 R相AMP | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 東一線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東一線A2 | 11KV東一線 S相AMP | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 東一線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東一線A3 | 11KV東一線 T相AMP | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 東一線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東一線A0 | 11KV東一線 N相AMP | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 乏 | VAR | 東七線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東七線KVAR | 11KV東七線 KVAR | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 R相電流 | A1 | 東七線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東七線A1 | 11KV東七線 R相AMP | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 S相電流 | A2 | 東七線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東七線A2 | 11KV東七線 S相AMP | FEEDER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F7 T相電流 | A3 | 東七線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東七線A3 | 11KV東七線 T相AMP | FEEDER |  |  |  |  | CDC | 288 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F7 N相電流 | AMP | 東七線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東七線A0 | 11KV東七線 N相AMP | FEEDER |  |  |  |  | CDC | 289 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 乏 | VAR | 東九線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東九線KVAR | 11KV東九線 KVAR | FEEDER |  |  |  |  | CDC | 290 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 R相電流 | A1 | 東九線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東九線A1 | 11KV東九線 R相AMP | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 S相電流 | A2 | 東九線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東九線A2 | 11KV東九線 S相AMP | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 T相電流 | A3 | 東九線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東九線A3 | 11KV東九線 T相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F9 N相電流 | AMP | 東九線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東九線A0 | 11KV東九線 N相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 東二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東二線KVAR | 11KV東二線 KVAR | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 東二線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東二線A1 | 11KV東二線 R相AMP | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 東二線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東二線A2 | 11KV東二線 S相AMP | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 東二線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東二線A3 | 11KV東二線 T相AMP | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 東二線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東二線A0 | 11KV東二線 N相AMP | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 乏 | VAR | 東八線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東八線KVAR | 11KV東八線 KVAR | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 R相電流 | A1 | 東八線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東八線A1 | 11KV東八線 R相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 S相電流 | A2 | 東八線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東八線A2 | 11KV東八線 S相AMP | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 T相電流 | A3 | 東八線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東八線A3 | 11KV東八線 T相AMP | FEEDER |  |  |  |  | CDC | 303 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F8 N相電流 | AMP | 東八線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東八線A0 | 11KV東八線 N相AMP | FEEDER |  |  |  |  | CDC | 304 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F10 乏 | VAR | 東十線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東十線KVAR | 11KV東十線 KVAR | FEEDER |  |  |  |  | CDC | 305 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 R相電流 | A1 | 東十線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東十線A1 | 11KV東十線 R相AMP | FEEDER |  |  |  |  | CDC | 306 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 S相電流 | A2 | 東十線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東十線A2 | 11KV東十線 S相AMP | FEEDER |  |  |  |  | CDC | 307 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 T相電流 | A3 | 東十線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東十線A3 | 11KV東十線 T相AMP | FEEDER |  |  |  |  | CDC | 308 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F10 N相電流 | AMP | 東十線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東十線A0 | 11KV東十線 N相AMP | FEEDER |  |  |  |  | CDC | 309 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 東三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東三線KVAR | 11KV東三線 KVAR | FEEDER |  |  |  |  | CDC | 310 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 東三線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東三線A1 | 11KV東三線 R相AMP | FEEDER |  |  |  |  | CDC | 311 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 東三線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東三線A2 | 11KV東三線 S相AMP | FEEDER |  |  |  |  | CDC | 312 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 東三線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東三線A3 | 11KV東三線 T相AMP | FEEDER |  |  |  |  | CDC | 313 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 東三線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東三線A0 | 11KV東三線 N相AMP | FEEDER |  |  |  |  | CDC | 314 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 東五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東五線KVAR | 11KV東五線 KVAR | FEEDER |  |  |  |  | CDC | 315 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 東五線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東五線A1 | 11KV東五線 R相AMP | FEEDER |  |  |  |  | CDC | 316 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 東五線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東五線A2 | 11KV東五線 S相AMP | FEEDER |  |  |  |  | CDC | 317 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 東五線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東五線A3 | 11KV東五線 T相AMP | FEEDER |  |  |  |  | CDC | 318 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 東五線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東五線A0 | 11KV東五線 N相AMP | FEEDER |  |  |  |  | CDC | 319 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 乏 | VAR | 東仁線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東仁線KVAR | 11KV東仁線 KVAR | FEEDER |  |  |  |  | CDC | 320 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 R相電流 | A1 | 東仁線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東仁線A1 | 11KV東仁線 R相AMP | FEEDER |  |  |  |  | CDC | 321 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 S相電流 | A2 | 東仁線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東仁線A2 | 11KV東仁線 S相AMP | FEEDER |  |  |  |  | CDC | 322 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 T相電流 | A3 | 東仁線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東仁線A3 | 11KV東仁線 T相AMP | FEEDER |  |  |  |  | CDC | 323 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F13 N相電流 | AMP | 東仁線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東仁線A0 | 11KV東仁線 N相AMP | FEEDER |  |  |  |  | CDC | 324 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 乏 | VAR | 東六線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東六線KVAR | 11KV東六線 KVAR | FEEDER |  |  |  |  | CDC | 325 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F6 R相電流 | A1 | 東六線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東六線A1 | 11KV東六線 R相AMP | FEEDER |  |  |  |  | CDC | 326 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F6 S相電流 | A2 | 東六線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東六線A2 | 11KV東六線 S相AMP | FEEDER |  |  |  |  | CDC | 327 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F6 T相電流 | A3 | 東六線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東六線A3 | 11KV東六線 T相AMP | FEEDER |  |  |  |  | CDC | 328 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | F6 N相電流 | AMP | 東六線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東六線A0 | 11KV東六線 N相AMP | FEEDER |  |  |  |  | CDC | 329 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 東正線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東正線KVAR | 11KV東正線 KVAR | FEEDER |  |  |  |  | CDC | 330 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 東正線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東正線A1 | 11KV東正線 R相AMP | FEEDER |  |  |  |  | CDC | 331 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 東正線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東正線A2 | 11KV東正線 S相AMP | FEEDER |  |  |  |  | CDC | 332 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 東正線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東正線A3 | 11KV東正線 T相AMP | FEEDER |  |  |  |  | CDC | 333 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 東正線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東正線A0 | 11KV東正線 N相AMP | FEEDER |  |  |  |  | CDC | 334 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 乏 | VAR | 東孝線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東孝線KVAR | 11KV東孝線 KVAR | FEEDER |  |  |  |  | CDC | 335 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 R相電流 | A1 | 東孝線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東孝線A1 | 11KV東孝線 R相AMP | FEEDER |  |  |  |  | CDC | 336 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 S相電流 | A2 | 東孝線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東孝線A2 | 11KV東孝線 S相AMP | FEEDER |  |  |  |  | CDC | 337 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F12 T相電流 | A3 | 東孝線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東孝線A3 | 11KV東孝線 T相AMP | FEEDER |  |  |  |  | CDC | 338 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F12 N相電流 | AMP | 東孝線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東孝線A0 | 11KV東孝線 N相AMP | FEEDER |  |  |  |  | CDC | 339 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 乏 | VAR | 東忠線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東忠線KVAR | 11KV東忠線 KVAR | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 R相電流 | A1 | 東忠線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東忠線A1 | 11KV東忠線 R相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F11 S相電流 | A2 | 東忠線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東忠線A2 | 11KV東忠線 S相AMP | FEEDER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F11 T相電流 | A3 | 東忠線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東忠線A3 | 11KV東忠線 T相AMP | FEEDER |  |  |  |  | CDC | 343 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F11 N相電流 | AMP | 東忠線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東忠線A0 | 11KV東忠線 N相AMP | FEEDER |  |  |  |  | CDC | 344 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 乏 | VAR | 東信線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東信線KVAR | 11KV東信線 KVAR | FEEDER |  |  |  |  | CDC | 345 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 R相電流 | A1 | 東信線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東信線A1 | 11KV東信線 R相AMP | FEEDER |  |  |  |  | CDC | 346 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 S相電流 | A2 | 東信線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東信線A2 | 11KV東信線 S相AMP | FEEDER |  |  |  |  | CDC | 347 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F15 T相電流 | A3 | 東信線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東信線A3 | 11KV東信線 T相AMP | FEEDER |  |  |  |  | CDC | 348 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F15 N相電流 | AMP | 東信線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東信線A0 | 11KV東信線 N相AMP | FEEDER |  |  |  |  | CDC | 349 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 乏 | VAR | 東愛線 | KVAR_-9000_9000(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東愛線KVAR | 11KV東愛線 KVAR | FEEDER |  |  |  |  | CDC | 350 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 R相電流 | A1 | 東愛線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東愛線A1 | 11KV東愛線 R相AMP | FEEDER |  |  |  |  | CDC | 351 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F14 S相電流 | A2 | 東愛線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東愛線A2 | 11KV東愛線 S相AMP | FEEDER |  |  |  |  | CDC | 352 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F14 T相電流 | A3 | 東愛線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東愛線A3 | 11KV東愛線 T相AMP | FEEDER |  |  |  |  | CDC | 353 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F14 N相電流 | AMP | 東愛線 | A_-500_500(-2000_2000) |  | B2/S45_D1 | [8 empty] | 新東SS.東愛線A0 | 11KV東愛線 N相AMP | FEEDER |  |  |  |  | CDC | 354 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC電壓 | DCV | 直流電源電壓 | DCVolt_-50_50(-2000_2000) |  | B3/S45_D1 | [8 empty] | 新東SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 355 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 620 | CB ON/OFF | 新營新東線 |  | aaba | B2/S45_A1 | [8 empty] | 新東SS.620_CB | 620(新營新東線) CB | LINE69 |  |  |  |  | CDC | 356 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 650 | CB ON/OFF | 新東白河線 |  | aada | B2/S45_A1 | [8 empty] | 新東SS.650_CB | 650(白河線) CB | LINE69 |  |  |  |  | CDC | 357 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0375 |  |  | 1-37-07 |  |  | 650 | 87CFA | 650通訊故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_87CFA | 650 87RY通訊故障 | OTHER | [5 empty] | 358 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0374 |  |  | 1-37-06 |  |  | 650 | 87RYFA | 650數位電驛故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.650_87RYFA | 650 數位電驛故障 | OTHER | [5 empty] | 359 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0383 |  |  | 1-37-15 |  |  | 810 | 87CFA | 810通訊故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.810_CFA | 810 RY通訊故障 | OTHER | [5 empty] | 360 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0382 |  |  | 1-37-14 |  |  | 810 | 87RYFA | 810數位電驛故障 |  |  | B2/S45_A1 | [8 empty] | 新東SS.810_RYFA | 810 數位電驛故障 | OTHER | [5 empty] | 361 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1MTR | #1 63Q | #1MTR ULTC保護 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | [5 empty] | 362 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #1MTR | #1 96B1 | #1MTR撲氣一段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 363 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #1MTR | #1 96B2 | #1MTR撲氣二段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | [5 empty] | 364 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1MTR | #1 96D | #1MTR放壓裝置 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | [5 empty] | 365 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1MTR | #1 96P | #1MTR突壓電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | [5 empty] | 366 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #2MTR | #2 63Q | #2MTR ULTC保護 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | [5 empty] | 367 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #2MTR | #2 96B1 | #2MTR撲氣一段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 368 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #2MTR | #2 96B2 | #2MTR撲氣二段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | [5 empty] | 369 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #2MTR | #2 96D | #2MTR放壓裝置 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | [5 empty] | 370 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2MTR | #2 96P | #2MTR突壓電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | [5 empty] | 371 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #3MTR | #3 63Q | #3MTR ULTC保護 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | [5 empty] | 372 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #3MTR | #3 96B1 | #3MTR撲氣一段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 373 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #3MTR | #3 96B2 | #3MTR撲氣二段 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | [5 empty] | 374 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #3MTR | #3 96D | #3MTR放壓裝置 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | [5 empty] | 375 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #3MTR | #3 96P | #3MTR突壓電驛 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | [5 empty] | 376 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | ComPoint |  |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | IED | RYFA | 11KV IED 故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | [5 empty] | 377 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | ComPoint |  |  | PMA |  | INSERT | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | PM | PMA | PowerMeter 故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.PMA | POWER METER故障 | OTHER | [5 empty] | 378 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0180 |  | 0066 | 1-16-04 |  | 1-42 | #1 SSTR CB | CB ON/OFF | #1 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 379 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | #1 SSTR PH RY | PHA | #1 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 380 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 390 | #1SSTR(390) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | #1 SSTR GD RY | GDA | #1 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 381 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 490 | #3SSTR(490) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0183 |  | 0067 | 1-16-07 |  | 1-43 | #2 SSTR CB | CB ON/OFF | #2 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.490_CB | 490(#3SSTR) CB | OTHER | [5 empty] | 382 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 490 | #3SSTR(490) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | #2 SSTR PH RY | PHA | #2 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3SSTR_51A | #3SSTR 51RY | OTHER | [5 empty] | 383 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 490 | #3SSTR(490) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #2 SSTR GD RY | GDA | #2 SSTR |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | [5 empty] | 384 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | #1 TR 81 RY | 81A | #1 Main |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1MA_81A/S | #1MA 81RY | OTHER | [5 empty] | 385 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0317 |  | 0107 | 1-33-13 |  | 1-6B | #1 MTR 81 RY | 81 U/L | #1 Main 使用/閉鎖 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | [5 empty] | 386 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | #2 TRA 81 RY | 81A | #2A Main |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2MA_81A/S | #2MA 81RY | OTHER | [5 empty] | 387 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0108 | 1-34-13 |  | 1-6C | #2 MTR A | 81 U/L | #2A Main 使用/閉鎖 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | [5 empty] | 388 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  | 0087 | 1-14-02 |  | 1-57 | #2 TRB 81 RY | 81A | #2B Main |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2MB_81A/S | #2MB 81RY | OTHER | [5 empty] | 389 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0334 |  | 0109 | 1-34-14 |  | 1-6D | #2 MTR B | 81 U/L | #2B Main 使用/閉鎖 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | [5 empty] | 390 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  | 0105 | 1-14-03 |  | 1-69 | #3 TR 81 RY | 81A | #3 Main |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3MA_81A/S | #3MA 81RY | OTHER | [5 empty] | 391 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0110 | 1-35-13 |  | 1-6E | #3 MTR | 81 U/L | #3 Main 使用/閉鎖 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | [5 empty] | 392 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0448 |  |  | 1-3C-00 |  |  | F1 79 RY | 79LOA | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_79_LOA | 11KV東一線(VE21) 79LOA | OTHER | [5 empty] | 393 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F1 81 RY | 81A | 東一線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_81A/S | 11KV東一線(VE21) 81RY | OTHER | [5 empty] | 394 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0449 |  |  | 1-3C-01 |  |  | F2 79 RY | 79LOA | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_79_LOA | 11KV東二線(VE22) 79LOA | OTHER | [5 empty] | 395 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F2 81 RY | 81A | 東二線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_81A/S | 11KV東二線(VE22) 81RY | OTHER | [5 empty] | 396 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | F3 79 RY | 79LOA | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_79_LOA | 11KV東三線(VE23) 79LOA | OTHER | [5 empty] | 397 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F3 81 RY | 81A | 東三線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_81A/S | 11KV東三線(VE23) 81RY | OTHER | [5 empty] | 398 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0451 |  |  | 1-3C-03 |  |  | F4 79 RY | 79LOA | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_79_LOA | 11KV東正線(VE24) 79LOA | OTHER | [5 empty] | 399 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F4 81 RY | 81A | 東正線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_81A/S | 11KV東正線(VE24) 81RY | OTHER | [5 empty] | 400 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0452 |  |  | 1-3C-04 |  |  | F5 79 RY | 79LOA | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_79_LOA | 11KV東五線(VE25) 79LOA | OTHER | [5 empty] | 401 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | F5 81 RY | 81A | 東五線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_81A/S | 11KV東五線(VE25) 81RY | OTHER | [5 empty] | 402 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0453 |  |  | 1-3C-05 |  |  | F6 79 RY | 79LOA | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_79_LOA | 11KV東六線(VE26) 79LOA | OTHER | [5 empty] | 403 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | F6 81 RY | 81A | 東六線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_81A/S | 11KV東六線(VE26) 81RY | OTHER | [5 empty] | 404 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0454 |  |  | 1-3C-06 |  |  | F7 79 RY | 79LOA | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_79_LOA | 11KV東七線(VE27) 79LOA | OTHER | [5 empty] | 405 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F7 81 RY | 81A | 東七線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_81A/S | 11KV東七線(VE27) 81RY | OTHER | [5 empty] | 406 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0455 |  |  | 1-3C-07 |  |  | F8 79 RY | 79LOA | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_79_LOA | 11KV東八線(VE28) 79LOA | OTHER | [5 empty] | 407 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F8 81 RY | 81A | 東八線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_81A/S | 11KV東八線(VE28) 81RY | OTHER | [5 empty] | 408 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0456 |  |  | 1-3C-08 |  |  | F9 79 RY | 79LOA | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_79_LOA | 11KV東九線(VE29) 79LOA | OTHER | [5 empty] | 409 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | F9 81 RY | 81A | 東九線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_81A/S | 11KV東九線(VE29) 81RY | OTHER | [5 empty] | 410 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0457 |  |  | 1-3C-09 |  |  | F10 79 RY | 79LOA | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_79_LOA | 11KV東十線(VE30) 79LOA | OTHER | [5 empty] | 411 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F10 81 RY | 81A | 東十線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_81A/S | 11KV東十線(VE30) 81RY | OTHER | [5 empty] | 412 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0458 |  |  | 1-3C-10 |  |  | F11 79 RY | 79LOA | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_79_LOA | 11KV東忠線(VE31) 79LOA | OTHER | [5 empty] | 413 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 81 RY | 81A | 東忠線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_81A/S | 11KV東忠線(VE31) 81RY | OTHER | [5 empty] | 414 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0459 |  |  | 1-3C-11 |  |  | F12 79 RY | 79LOA | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_79_LOA | 11KV東孝線(VE32) 79LOA | OTHER | [5 empty] | 415 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | F12 81 RY | 81A | 東孝線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_81A/S | 11KV東孝線(VE32) 81RY | OTHER | [5 empty] | 416 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0460 |  |  | 1-3C-12 |  |  | F13 79 RY | 79LOA | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_79_LOA | 11KV東仁線(VE33) 79LOA | OTHER | [5 empty] | 417 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 81 RY | 81A | 東仁線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_81A/S | 11KV東仁線(VE33) 81RY | OTHER | [5 empty] | 418 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0461 |  |  | 1-3C-13 |  |  | F14 79 RY | 79LOA | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_79_LOA | 11KV東愛線(VE34) 79LOA | OTHER | [5 empty] | 419 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F14 81 RY | 81A | 東愛線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_81A/S | 11KV東愛線(VE34) 81RY | OTHER | [5 empty] | 420 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0462 |  |  | 1-3C-14 |  |  | F15 79 RY | 79LOA | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_79_LOA | 11KV東信線(VE35) 79LOA | OTHER | [5 empty] | 421 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | 81AS |  | INSERT | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | F15 81 RY | 81A | 東信線 |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_81A/S | 11KV東信線(VE35) 81RY | OTHER | [5 empty] | 422 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0463 |  |  | 1-3C-15 |  |  | #1MTR IED | RYFA | #1MTR及饋線 IED 故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | [5 empty] | 423 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0464 |  |  | 1-3D-00 |  |  | #2MTR IED | RYFA | #2MTR及饋線 IED 故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | [5 empty] | 424 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0465 |  |  | 1-3D-01 |  |  | #3MTR IED | RYFA | #3MTR及饋線 IED 故障 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | [5 empty] | 425 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | ComPoint |  |  | 81A_RYFA |  | INSERT | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0466 |  |  | 1-3D-02 |  |  | 81RY IED | RYFA | 81RY IED 故障 |  |  | B3/S45_D1 | [8 empty] | 新東SS.81RY_RYFA | 81RY 電驛故障 | OTHER | [5 empty] | 426 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0467 |  |  | 1-3D-03 |  |  | #1MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 427 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0470 |  |  | 1-3D-06 |  |  | #1MTR 871S | 871S | #1MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 428 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0471 |  |  | 1-3D-07 |  |  | #1MTR 872S | 872S | #1MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 429 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0468 |  |  | 1-3D-04 |  |  | #2MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 430 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0472 |  |  | 1-3D-08 |  |  | #2MTR 871S | 871S | #2MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 431 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0473 |  |  | 1-3D-09 |  |  | #2MTR 872S | 872S | #2MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 432 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0469 |  |  | 1-3D-05 |  |  | #3MTR 86RY | 86A | 86RY 跳脫閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 433 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  | INSERT | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0474 |  |  | 1-3D-10 |  |  | #3MTR 871S | 871S | #3MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 434 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0475 |  |  | 1-3D-11 |  |  | #3MTR 872S | 872S | #3MTR 87RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 435 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0476 |  |  | 1-3D-12 |  |  | #1MTR 51ZS | 51Z S | #1MTR 51Z RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 436 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0477 |  |  | 1-3D-13 |  |  | #2MTR 51ZS | 51Z S | #2MTR 51Z RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 437 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0478 |  |  | 1-3D-14 |  |  | #3MTR 51ZS | 51Z S | #3MTR 51Z RY 使用/閉鎖 |  |  | B1/S45_D1 | [8 empty] | 新東SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 438 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS |  |  | 1GIS | #1GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1 GIS CB | CBA | #1 GIS斷路器重故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1GIS_CBA | #1GIS重故障 | OTHER | [5 empty] | 439 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 1GIS | #1GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1 GIS CB | CBF | #1 GIS斷路器輕故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#1GIS_CBF | #1GIS輕故障 | OTHER | [5 empty] | 440 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2GIS | #2GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2 GIS CB | CBA | #2 GIS斷路器重故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2GIS_CBA | #2GIS重故障 | OTHER | [5 empty] | 441 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 2GIS | #2GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2 GIS CB | CBF | #2 GIS斷路器輕故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#2GIS_CBF | #2GIS輕故障 | OTHER | [5 empty] | 442 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3GIS | #3GIS |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3 GIS CB | CBA | #3 GIS斷路器重故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3GIS_CBA | #3GIS重故障 | OTHER | [5 empty] | 443 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS |  |  | 3GIS | #3GIS |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3 GIS CB | CBF | #3 GIS斷路器輕故障 |  |  | B2/S45_D1 | [8 empty] | 新東SS.#3GIS_CBF | #3GIS輕故障 | OTHER | [5 empty] | 444 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 CB | KWH(+) | 東一線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 445 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 CB | KWH(+) | 東二線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 446 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 CB | KWH(+) | 東三線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 447 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 CB | KWH(+) | 東正線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 448 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 CB | KWH(+) | 東五線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 449 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 CB | KWH(+) | 東六線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 450 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 CB | KWH(+) | 東七線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 451 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 CB | KWH(+) | 東八線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 452 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 CB | KWH(+) | 東九線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 453 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 CB | KWH(+) | 東十線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 454 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F11 CB | KWH(+) | 東忠線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 455 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F12 CB | KWH(+) | 東孝線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 456 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F13 CB | KWH(+) | 東仁線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 457 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F14 CB | KWH(+) | 東愛線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 458 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F15 CB | KWH(+) | 東信線 |  |  | B2/S45_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 459 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | F1 81 U/L | 81 U/L | F1 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE21_81U/L | 11KV東一線(VE21) 81RY U/L | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | F2 81 U/L | 81 U/L | F2 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE22_81U/L | 11KV東二線(VE22) 81RY U/L | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0490 |  |  | 1-3E-10 |  |  | F3 81 U/L | 81 U/L | F3 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE23_81U/L | 11KV東三線(VE23) 81RY U/L | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0491 |  |  | 1-3E-11 |  |  | F4 81 U/L | 81 U/L | F4 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE24_81U/L | 11KV東正線(VE24) 81RY U/L | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | F5 81 U/L | 81 U/L | F5 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE25_81U/L | 11KV東五線(VE25) 81RY U/L | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | F6 81 U/L | 81 U/L | F6 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE26_81U/L | 11KV東六線(VE26) 81RY U/L | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | F7 81 U/L | 81 U/L | F7 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE27_81U/L | 11KV東七線(VE27) 81RY U/L | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | F8 81 U/L | 81 U/L | F8 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE28_81U/L | 11KV東八線(VE28) 81RY U/L | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | F9 81 U/L | 81 U/L | F9 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE29_81U/L | 11KV東九線(VE29) 81RY U/L | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | F10 81 U/L | 81 U/L | F10 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE30_81U/L | 11KV東十線(VE30) 81RY U/L | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | F11 81 U/L | 81 U/L | F11 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE31_81U/L | 11KV東忠線(VE31) 81RY U/L | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | F12 81 U/L | 81 U/L | F12 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE32_81U/L | 11KV東孝線(VE32) 81RY U/L | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | F13 81 U/L | 81 U/L | F13 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE33_81U/L | 11KV東仁線(VE33) 81RY U/L | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | F14 81 U/L | 81 U/L | F14 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE34_81U/L | 11KV東愛線(VE34) 81RY U/L | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | F15 81 U/L | 81 U/L | F15 81 U/L |  |  | B2/S45_D1 | [8 empty] | 新東SS.VE35_81U/L | 11KV東信線(VE35) 81RY U/L | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | E1 | 1M_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 475 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 476 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 477 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE21_DS | VE21_DS (非取樣點) | FEEDER | [5 empty] | 478 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE22_DS | VE22_DS (非取樣點) | FEEDER | [5 empty] | 479 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE23_DS | VE23_DS (非取樣點) | FEEDER | [5 empty] | 480 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE24_DS | VE24_DS (非取樣點) | FEEDER | [5 empty] | 481 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE25_DS | VE25_DS (非取樣點) | FEEDER | [5 empty] | 482 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE26_DS | VE26_DS (非取樣點) | FEEDER | [5 empty] | 483 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE27_DS | VE27_DS (非取樣點) | FEEDER | [5 empty] | 484 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE28_DS | VE28_DS (非取樣點) | FEEDER | [5 empty] | 485 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE29_DS | VE29_DS (非取樣點) | FEEDER | [5 empty] | 486 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE30_DS | VE30_DS (非取樣點) | FEEDER | [5 empty] | 487 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE31_DS | VE31_DS (非取樣點) | FEEDER | [5 empty] | 488 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE32_DS | VE32_DS (非取樣點) | FEEDER | [5 empty] | 489 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE33_DS | VE33_DS (非取樣點) | FEEDER | [5 empty] | 490 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE34_DS | VE34_DS (非取樣點) | FEEDER | [5 empty] | 491 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.VE35_DS | VE35_DS (非取樣點) | FEEDER | [5 empty] | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391 (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 493 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 490 | #2SSTR(490 |  | D1 | 491 (非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 495 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 490 | #2SSTR(490 |  | E1 | 491E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M1 | #1MTR(M1) |  | D1 | 1M_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 497 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | D1 | 2MA_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 498 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | D1 | 2MB_ (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 499 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | E1 | 2MA_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 500 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | E1 | 2MB_ES (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 502 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.210DS | 210DS (非取樣點) | SC | [5 empty] | 503 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.220DS | 220DS (非取樣點) | SC | [5 empty] | 504 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.230DS | 230DS (非取樣點) | SC | [5 empty] | 505 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | 201E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.201E | 201E (非取樣點) | TIE | [5 empty] | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | 202E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.202E | 202E (非取樣點) | TIE | [5 empty] | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | 101E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.101E | 101E (非取樣點) | TIE | [5 empty] | 508 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E2 | 102E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.102E | 102E (非取樣點) | TIE | [5 empty] | 509 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 11B1E | 11B1E |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aafb | B2/S45_D1 | [8 empty] | 新東SS.11B1E | 11B1E (非取樣點) | BUS | [5 empty] | 510 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 11B2E | 11B2E |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2ABUS | [13 empty] | abab | B2/S45_D1 | [8 empty] | 新東SS.11B2E | 11B2E (非取樣點) | BUS | [5 empty] | 511 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 11B2BE | 11B2BE |  | BE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BBUS | [13 empty] | acdb | B2/S45_D1 | [8 empty] | 新東SS.11B2BE | 11B2BE (非取樣點) | BUS | [5 empty] | 512 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 3BUS | #3BUS |  | BE3 | 11B3E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S45_D1 | [8 empty] | 新東SS.11B3E | 11B3E (非取樣點) | BUS | [5 empty] | 513 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | 11KV #2A BUS | KV | #2A BUS PT | kV_-9_9(-2000_2000) | aca | B2/S45_D1 | [8 empty] | 新東SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S45 | 新東SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S45_D1 | [12 empty] | 新東SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S45/69/1BUS/V
S45 | 新東SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S45_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S45/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S45 | 新東SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S45_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S45/11/M1/MW; OPRD2: S45/11/M3/MW; OPRD3: S45/69/620/MW; OPRD4: S45/69/650/MW
S45 | 新東SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S45_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S45/0/CalcPoint/OPRN2_MW
S45 | 新東SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S45_D1 | [17 empty] | none
S45 | 新東SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S45_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S45/0/CalcPoint/OPRN1; OPRD2: S45/0/CalcPoint/OPRN2; OPRD3: S45/0/CalcPoint/PRFL_UL
S45 | 新東SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S45_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S45/11/M1/MW; OPRD2: S45/11/M1/MVAR; OPRD3: S45/0/CalcPoint/Vbs1
S45 | 新東SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S45_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S45/11/M3/MW; OPRD2: S45/11/M3/MVAR; OPRD3: S45/0/CalcPoint/Vbs1
S45 | 新東SS | 69 | 69kV | 620 | 新營～新東線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S45_A1 | [12 empty] | 新東SS.620_AMP | 新營新東線 AMP | LINE69 | AMP_CAL | C12R0824 | amp_cal | OPRD1: S45/69/620/MW; OPRD2: S45/69/620/MVAR; OPRD3: NULL
S45 | 新東SS | 69 | 69kV | 650 | 新東～白河線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S45_A1 | [12 empty] | 新東SS.650_AMP | 白河線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S45/69/650/MW; OPRD2: S45/69/650/MVAR; OPRD3: NULL
S45 | 新東SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S45_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S45/11/1BUS/V
S45 | 新東SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S45_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S45/11/2BUS/V
S45 | 新東SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S45_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S45/11/3BUS/V
S45 | 新東SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S45_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新東SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S45/11/M1/MW; OPRD2: S45/11/M1/MVAR
S45 | 新東SS |  |  | 2MTR(A) | #2MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S45_D1 | LG_15 | 14.25 | 16.5 | 18.75 | 30 |  | -14.25 | -16.5 | -18.75 | -30 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S45/11/M2A/MW; OPRD2: S45/11/M2A/MVAR
S45 | 新東SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S45_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 新東SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S45/11/M3/MW; OPRD2: S45/11/M3/MVAR
S45 | 新東SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S45_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S45//1MTR/MVA; OPRD2: 0
S45 | 新東SS |  |  | 2MTR(A) | #2MTR(A) |  | LOAD | [9 empty] | B1/S45_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S45//2MTR(A)/MVA; OPRD2: 0
S45 | 新東SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S45_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S45//3MTR/MVA; OPRD2: 0
S45 | 新東SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S45_D1 | [12 empty] | 新東SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S45/11/M1/MW; OPRD2: S45/11/M1/MVAR
S45 | 新東SS |  |  | 2MTR(A) | #2MTR(A) |  | PF | [9 empty] | B1/S45_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S45/11/M2A/MW; OPRD2: S45/11/M2A/MVAR
S45 | 新東SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S45_D1 | [12 empty] | 新東SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S45/11/M3/MW; OPRD2: S45/11/M3/MVAR
S45 | 新東SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S45_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S45//1MTR/SupLocal; OPRD2: S45//1MTR/Tap Chan; OPRD3: NULL
S45 | 新東SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S45_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S45//2MTR/SupLocal; OPRD2: S45//2MTR/Tap Chan; OPRD3: NULL
S45 | 新東SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S45_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S45//3MTR/SupLocal; OPRD2: S45//3MTR/Tap Chan; OPRD3: NULL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/1BUS/V; OPRD2: S45/11/VE21/I_R; OPRD3: S45/11/VE21/I_S; OPRD4: S45/11/VE21/I_T
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/1BUS/V; OPRD2: S45/11/VE22/I_R; OPRD3: S45/11/VE22/I_S; OPRD4: S45/11/VE22/I_T
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/1BUS/V; OPRD2: S45/11/VE23/I_R; OPRD3: S45/11/VE23/I_S; OPRD4: S45/11/VE23/I_T
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/1BUS/V; OPRD2: S45/11/VE24/I_R; OPRD3: S45/11/VE24/I_S; OPRD4: S45/11/VE24/I_T
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/1BUS/V; OPRD2: S45/11/VE25/I_R; OPRD3: S45/11/VE25/I_S; OPRD4: S45/11/VE25/I_T
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S45/11/VE26/I_R; OPRD3: S45/11/VE26/I_S; OPRD4: S45/11/VE26/I_T
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S45/11/VE27/I_R; OPRD3: S45/11/VE27/I_S; OPRD4: S45/11/VE27/I_T
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S45/11/VE28/I_R; OPRD3: S45/11/VE28/I_S; OPRD4: S45/11/VE28/I_T
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S45/11/VE29/I_R; OPRD3: S45/11/VE29/I_S; OPRD4: S45/11/VE29/I_T
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S45/11/VE30/I_R; OPRD3: S45/11/VE30/I_S; OPRD4: S45/11/VE30/I_T
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/3BUS/V; OPRD2: S45/11/VE31/I_R; OPRD3: S45/11/VE31/I_S; OPRD4: S45/11/VE31/I_T
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/3BUS/V; OPRD2: S45/11/VE32/I_R; OPRD3: S45/11/VE32/I_S; OPRD4: S45/11/VE32/I_T
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/3BUS/V; OPRD2: S45/11/VE33/I_R; OPRD3: S45/11/VE33/I_S; OPRD4: S45/11/VE33/I_T
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/3BUS/V; OPRD2: S45/11/VE34/I_R; OPRD3: S45/11/VE34/I_S; OPRD4: S45/11/VE34/I_T
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S45/11/3BUS/V; OPRD2: S45/11/VE35/I_R; OPRD3: S45/11/VE35/I_S; OPRD4: S45/11/VE35/I_T
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE21/kVA; OPRD2: S45/11/VE21/KVAR
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE22/kVA; OPRD2: S45/11/VE22/KVAR
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE23/kVA; OPRD2: S45/11/VE23/KVAR
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE24/kVA; OPRD2: S45/11/VE24/KVAR
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE25/kVA; OPRD2: S45/11/VE25/KVAR
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE26/kVA; OPRD2: S45/11/VE26/KVAR
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE27/kVA; OPRD2: S45/11/VE27/KVAR
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE28/kVA; OPRD2: S45/11/VE28/KVAR
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE29/kVA; OPRD2: S45/11/VE29/KVAR
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE30/kVA; OPRD2: S45/11/VE30/KVAR
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE31/kVA; OPRD2: S45/11/VE31/KVAR
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE32/kVA; OPRD2: S45/11/VE32/KVAR
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE33/kVA; OPRD2: S45/11/VE33/KVAR
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE34/kVA; OPRD2: S45/11/VE34/KVAR
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S45_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S45/11/VE35/kVA; OPRD2: S45/11/VE35/KVAR
S45 | 新東SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S45_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S45/11/M1/MW; OPRD2: S45/11/M3/MW
S45 | 新東SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S45_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S45/11/M1/MVAR; OPRD2: S45/11/M3/MVAR
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S45_D1 | [12 empty] | 新東SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S45/11/210/CB; OPRD2: 6.9; OPRD3: 0
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S45_D1 | [12 empty] | 新東SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S45/11/220/CB; OPRD2: 6.9; OPRD3: 0
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S45_D1 | [12 empty] | 新東SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S45/11/230/CB; OPRD2: 6.9; OPRD3: 0
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S45_A1 | [12 empty] | 新東SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S45/69/810/CB; OPRD2: 69; OPRD3: 0
S45 | 新東SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S45_D1 | [12 empty] | 新東SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_24 | OPRD1: S45//1MTR/63Q; OPRD2: S45//1MTR/96PA; OPRD3: S45//1MTR/TRA; OPRD4: S45//1MTR/96D; OPRD5: S45//1MTR/96B2; OPRD6: S45//1MTR/96B1; OPRD7: S45//1MTR/51ZA; OPRD8: S45//1MTR/87A; OPRD9: S45//2MTR/51ZA; OPRD10: S45//2MTR/63Q; OPRD11: S45//2MTR/96D; OPRD12: S45//2MTR/96B2; OPRD13: S45//2MTR/96B1; OPRD14: S45//2MTR/96PA; OPRD15: S45//2MTR/TRA; OPRD16: S45//2MTR/87A; OPRD17: S45//3MTR/96B2; OPRD18: S45//3MTR/96B1; OPRD19: S45//3MTR/63Q; OPRD20: S45//3MTR/96D; OPRD21: S45//3MTR/87A; OPRD22: S45//3MTR/51ZA; OPRD23: S45//3MTR/96PA; OPRD24: S45//3MTR/TRA
S45 | 新東SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S45_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S45//1MTR/TRF; OPRD2: S45//2MTR/TRF; OPRD3: S45//3MTR/TRF
S45 | 新東SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S45_A1 | [17 empty] | lamp2CC | OPRD1: S45/0/RTU/RTU_R_L
S45 | 新東SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S45_A1 | [17 empty] | lamp2CC | OPRD1: S45/0/StaDev/PSA
S45 | 新東SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S45_A1 | [17 empty] | lamp2CC | OPRD1: S45/0/StaDev/PSF
S45 | 新東SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S45_A1 | [17 empty] | lamp2CC | OPRD1: S45/0/StaDev/DCA
S45 | 新東SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S45_A1 | [17 empty] | lamp2CC | OPRD1: S45/0/StaDev/DCE
S45 | 新東SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S45_D1 | [17 empty] | lamp2CC | OPRD1: S45/69/ComPoint/CBA
S45 | 新東SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S45_D1 | [17 empty] | lamp2CC | OPRD1: S45/69/ComPoint/CBF
S45 | 新東SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S45_D1 | [17 empty] | lamp2CC | OPRD1: S45/69/ComPoint/ABS_89A
S45 | 新東SS | 69 | 69kV | ComPoint_D1 |  |  | SCA | SC警報 |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP |  | B3/S45_D1 | [17 empty] | lamp2CC | OPRD1: S45/69/ComPoint/SCA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S45 | 新東SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 新東SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S45/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 新東SS.620_AMP | 新營新東線 AMP | LINE69 | S45/69/620/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0824 | 741.599976 | 741.599976 | 824.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 新東SS.650_AMP | 白河線 AMP | LINE69 | S45/69/650/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S45 | 新東SS | 0 |  |  |  |  | 東一線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東一線KVA | 11KV東一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東一線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東一線KW | 11KV東一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東七線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東七線KVA | 11KV東七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東七線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東七線KW | 11KV東七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東九線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東九線KVA | 11KV東九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東九線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東九線KW | 11KV東九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東二線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東二線KVA | 11KV東二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東二線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東二線KW | 11KV東二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東八線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東八線KVA | 11KV東八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東八線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東八線KW | 11KV東八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東十線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東十線KVA | 11KV東十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東十線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東十線KW | 11KV東十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東三線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東三線KVA | 11KV東三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東三線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東三線KW | 11KV東三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東五線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東五線KVA | 11KV東五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東五線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東五線KW | 11KV東五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東仁線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東仁線KVA | 11KV東仁線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東仁線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東仁線KW | 11KV東仁線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東六線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東六線KVA | 11KV東六線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東六線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東六線KW | 11KV東六線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東正線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東正線KVA | 11KV東正線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東正線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東正線KW | 11KV東正線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東孝線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東孝線KVA | 11KV東孝線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東孝線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東孝線KW | 11KV東孝線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東忠線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東忠線KVA | 11KV東忠線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東忠線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東忠線KW | 11KV東忠線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東信線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東信線KVA | 11KV東信線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東信線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東信線KW | 11KV東信線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東愛線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東愛線KVA | 11KV東愛線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  |  |  |  | 東愛線KW | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.東愛線KW | 11KV東愛線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S45//1MTR/MVA |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_PF | #1MTR 功率因素 | DTR | S45//1MTR/PF |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S45//3MTR/MVA |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_PF | #3MTR 功率因素 | DTR | S45//3MTR/PF |  | RPDC_PF_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S45 | 新東SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S45/11/210/MVAR |  | SC_CAL_11 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S45/11/220/MVAR |  | SC_CAL_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S45/11/230/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S45/69/810/MVAR |  | SC_CAL_69 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 69 | 69kV | 620_CB | 新營新東線(620_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.620_CB_3 | 620(新營新東線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 45 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 650_CB | 白河線(650_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.650_CB_3 | 650(白河線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 46 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.810_CB_3 | 810(69KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 新東SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 48 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 新東SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 49 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 新東SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S45/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 50 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 51 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | STATION_FAULT_3 |  |  | 52 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620_AMP | 新營新東線 | [27 empty] | ADCS_N | [8 empty] | 新東SS.620_AMP_A | 新營新東線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 53 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 69 | 69kV | 620_AMP | 新營新東線 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.620_AMP_3 | 新營新東線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 54 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 69 | 69kV | 650_AMP | 白河線 | [27 empty] | ADCS_N | [8 empty] | 新東SS.650_AMP_A | 白河線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 55 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 69 | 69kV | 650_AMP | 白河線 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.650_AMP_3 | 白河線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 56 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 1MTR_MVA | #1MTR |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_MVA_3 | #1MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 57 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 2MTR_MVA | #2MTR |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_MVA_3 | #2MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 3MTR_MVA | #3MTR |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_MVA_3 | #3MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S45 | 新東SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 新東SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 63 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | _SC警報 | SC警報 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.69KV_SC警報_3 | 69KV SC警報 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 64 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S45/0/RTU/ADCH1 |  |  |  | CDC | 65 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S45/0/RTU/ADCH2 |  |  |  | CDC | 66 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S45/0/RTU/ADCL1 |  |  |  | CDC | 67 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S45/0/RTU/ADCL2 |  |  |  | CDC | 68 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S45 | 新東SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新東SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S45/69/1BUS/V |  |  |  | CDC | 69 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S45 | 新東SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S45/11/1BUS/V |  |  |  | CDC | 70 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S45/11/2BUS/V |  |  |  | CDC | 71 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S45/11/3BUS/V |  |  |  | CDC | 72 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新東SS.620_MW | 新營新東線 MW | LINE69 | S45/69/620/MW |  |  |  | CDC | 73 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新東SS.620_MVAR | 新營新東線 MVAR | LINE69 | S45/69/620/MVAR |  |  |  | CDC | 74 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 新東SS.650_MW | 白河線 MW | LINE69 | S45/69/650/MW |  |  |  | CDC | 75 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 新東SS.650_MVAR | 白河線 MVAR | LINE69 | S45/69/650/MVAR |  |  |  | CDC | 76 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東一線 | 東一線 |  | 東一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東一線KVAR | 11KV東一線 KVAR | FEEDER | S45/11/VE21/KVAR |  |  |  | CDC | 77 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東一線 | 東一線 |  | 東一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東一線A1 | 11KV東一線 R相AMP | FEEDER | S45/11/VE21/I_R |  |  |  | CDC | 78 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東一線 | 東一線 |  | 東一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東一線A2 | 11KV東一線 S相AMP | FEEDER | S45/11/VE21/I_S |  |  |  | CDC | 79 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東一線 | 東一線 |  | 東一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東一線A3 | 11KV東一線 T相AMP | FEEDER | S45/11/VE21/I_T |  |  |  | CDC | 80 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東一線 | 東一線 |  | 東一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東一線A0 | 11KV東一線 N相AMP | FEEDER | S45/11/VE21/I_N |  |  |  | CDC | 81 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東七線 | 東七線 |  | 東七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東七線KVAR | 11KV東七線 KVAR | FEEDER | S45/11/VE27/KVAR |  |  |  | CDC | 82 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東七線 | 東七線 |  | 東七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東七線A1 | 11KV東七線 R相AMP | FEEDER | S45/11/VE27/I_R |  |  |  | CDC | 83 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東七線 | 東七線 |  | 東七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東七線A2 | 11KV東七線 S相AMP | FEEDER | S45/11/VE27/I_S |  |  |  | CDC | 84 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東七線 | 東七線 |  | 東七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東七線A3 | 11KV東七線 T相AMP | FEEDER | S45/11/VE27/I_T |  |  |  | CDC | 85 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東七線 | 東七線 |  | 東七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東七線A0 | 11KV東七線 N相AMP | FEEDER | S45/11/VE27/I_N |  |  |  | CDC | 86 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東九線 | 東九線 |  | 東九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東九線KVAR | 11KV東九線 KVAR | FEEDER | S45/11/VE29/KVAR |  |  |  | CDC | 87 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東九線 | 東九線 |  | 東九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東九線A1 | 11KV東九線 R相AMP | FEEDER | S45/11/VE29/I_R |  |  |  | CDC | 88 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東九線 | 東九線 |  | 東九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東九線A2 | 11KV東九線 S相AMP | FEEDER | S45/11/VE29/I_S |  |  |  | CDC | 89 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東九線 | 東九線 |  | 東九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東九線A3 | 11KV東九線 T相AMP | FEEDER | S45/11/VE29/I_T |  |  |  | CDC | 90 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東九線 | 東九線 |  | 東九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東九線A0 | 11KV東九線 N相AMP | FEEDER | S45/11/VE29/I_N |  |  |  | CDC | 91 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東二線 | 東二線 |  | 東二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東二線KVAR | 11KV東二線 KVAR | FEEDER | S45/11/VE22/KVAR |  |  |  | CDC | 92 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東二線 | 東二線 |  | 東二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東二線A1 | 11KV東二線 R相AMP | FEEDER | S45/11/VE22/I_R |  |  |  | CDC | 93 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東二線 | 東二線 |  | 東二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東二線A2 | 11KV東二線 S相AMP | FEEDER | S45/11/VE22/I_S |  |  |  | CDC | 94 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東二線 | 東二線 |  | 東二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東二線A3 | 11KV東二線 T相AMP | FEEDER | S45/11/VE22/I_T |  |  |  | CDC | 95 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東二線 | 東二線 |  | 東二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東二線A0 | 11KV東二線 N相AMP | FEEDER | S45/11/VE22/I_N |  |  |  | CDC | 96 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東八線 | 東八線 |  | 東八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東八線KVAR | 11KV東八線 KVAR | FEEDER | S45/11/VE28/KVAR |  |  |  | CDC | 97 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東八線 | 東八線 |  | 東八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東八線A1 | 11KV東八線 R相AMP | FEEDER | S45/11/VE28/I_R |  |  |  | CDC | 98 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東八線 | 東八線 |  | 東八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東八線A2 | 11KV東八線 S相AMP | FEEDER | S45/11/VE28/I_S |  |  |  | CDC | 99 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東八線 | 東八線 |  | 東八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東八線A3 | 11KV東八線 T相AMP | FEEDER | S45/11/VE28/I_T |  |  |  | CDC | 100 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東八線 | 東八線 |  | 東八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東八線A0 | 11KV東八線 N相AMP | FEEDER | S45/11/VE28/I_N |  |  |  | CDC | 101 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東十線 | 東十線 |  | 東十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東十線KVAR | 11KV東十線 KVAR | FEEDER | S45/11/VE30/KVAR |  |  |  | CDC | 102 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東十線 | 東十線 |  | 東十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東十線A1 | 11KV東十線 R相AMP | FEEDER | S45/11/VE30/I_R |  |  |  | CDC | 103 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東十線 | 東十線 |  | 東十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東十線A2 | 11KV東十線 S相AMP | FEEDER | S45/11/VE30/I_S |  |  |  | CDC | 104 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東十線 | 東十線 |  | 東十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東十線A3 | 11KV東十線 T相AMP | FEEDER | S45/11/VE30/I_T |  |  |  | CDC | 105 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東十線 | 東十線 |  | 東十線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東十線A0 | 11KV東十線 N相AMP | FEEDER | S45/11/VE30/I_N |  |  |  | CDC | 106 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東三線 | 東三線 |  | 東三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東三線KVAR | 11KV東三線 KVAR | FEEDER | S45/11/VE23/KVAR |  |  |  | CDC | 107 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東三線 | 東三線 |  | 東三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東三線A1 | 11KV東三線 R相AMP | FEEDER | S45/11/VE23/I_R |  |  |  | CDC | 108 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東三線 | 東三線 |  | 東三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東三線A2 | 11KV東三線 S相AMP | FEEDER | S45/11/VE23/I_S |  |  |  | CDC | 109 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東三線 | 東三線 |  | 東三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東三線A3 | 11KV東三線 T相AMP | FEEDER | S45/11/VE23/I_T |  |  |  | CDC | 110 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東三線 | 東三線 |  | 東三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東三線A0 | 11KV東三線 N相AMP | FEEDER | S45/11/VE23/I_N |  |  |  | CDC | 111 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東五線 | 東五線 |  | 東五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東五線KVAR | 11KV東五線 KVAR | FEEDER | S45/11/VE25/KVAR |  |  |  | CDC | 112 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東五線 | 東五線 |  | 東五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東五線A1 | 11KV東五線 R相AMP | FEEDER | S45/11/VE25/I_R |  |  |  | CDC | 113 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東五線 | 東五線 |  | 東五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東五線A2 | 11KV東五線 S相AMP | FEEDER | S45/11/VE25/I_S |  |  |  | CDC | 114 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東五線 | 東五線 |  | 東五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東五線A3 | 11KV東五線 T相AMP | FEEDER | S45/11/VE25/I_T |  |  |  | CDC | 115 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東五線 | 東五線 |  | 東五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東五線A0 | 11KV東五線 N相AMP | FEEDER | S45/11/VE25/I_N |  |  |  | CDC | 116 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東仁線 | 東仁線 |  | 東仁線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東仁線KVAR | 11KV東仁線 KVAR | FEEDER | S45/11/VE33/KVAR |  |  |  | CDC | 117 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東仁線 | 東仁線 |  | 東仁線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東仁線A1 | 11KV東仁線 R相AMP | FEEDER | S45/11/VE33/I_R |  |  |  | CDC | 118 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東仁線 | 東仁線 |  | 東仁線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東仁線A2 | 11KV東仁線 S相AMP | FEEDER | S45/11/VE33/I_S |  |  |  | CDC | 119 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東仁線 | 東仁線 |  | 東仁線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東仁線A3 | 11KV東仁線 T相AMP | FEEDER | S45/11/VE33/I_T |  |  |  | CDC | 120 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東仁線 | 東仁線 |  | 東仁線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東仁線A0 | 11KV東仁線 N相AMP | FEEDER | S45/11/VE33/I_N |  |  |  | CDC | 121 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東六線 | 東六線 |  | 東六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東六線KVAR | 11KV東六線 KVAR | FEEDER | S45/11/VE26/KVAR |  |  |  | CDC | 122 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東六線 | 東六線 |  | 東六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東六線A1 | 11KV東六線 R相AMP | FEEDER | S45/11/VE26/I_R |  |  |  | CDC | 123 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東六線 | 東六線 |  | 東六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東六線A2 | 11KV東六線 S相AMP | FEEDER | S45/11/VE26/I_S |  |  |  | CDC | 124 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東六線 | 東六線 |  | 東六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東六線A3 | 11KV東六線 T相AMP | FEEDER | S45/11/VE26/I_T |  |  |  | CDC | 125 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東六線 | 東六線 |  | 東六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東六線A0 | 11KV東六線 N相AMP | FEEDER | S45/11/VE26/I_N |  |  |  | CDC | 126 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東正線 | 東正線 |  | 東正線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東正線KVAR | 11KV東正線 KVAR | FEEDER | S45/11/VE24/KVAR |  |  |  | CDC | 127 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東正線 | 東正線 |  | 東正線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東正線A1 | 11KV東正線 R相AMP | FEEDER | S45/11/VE24/I_R |  |  |  | CDC | 128 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東正線 | 東正線 |  | 東正線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東正線A2 | 11KV東正線 S相AMP | FEEDER | S45/11/VE24/I_S |  |  |  | CDC | 129 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東正線 | 東正線 |  | 東正線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東正線A3 | 11KV東正線 T相AMP | FEEDER | S45/11/VE24/I_T |  |  |  | CDC | 130 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東正線 | 東正線 |  | 東正線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東正線A0 | 11KV東正線 N相AMP | FEEDER | S45/11/VE24/I_N |  |  |  | CDC | 131 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東孝線 | 東孝線 |  | 東孝線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東孝線KVAR | 11KV東孝線 KVAR | FEEDER | S45/11/VE32/KVAR |  |  |  | CDC | 132 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東孝線 | 東孝線 |  | 東孝線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東孝線A1 | 11KV東孝線 R相AMP | FEEDER | S45/11/VE32/I_R |  |  |  | CDC | 133 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東孝線 | 東孝線 |  | 東孝線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東孝線A2 | 11KV東孝線 S相AMP | FEEDER | S45/11/VE32/I_S |  |  |  | CDC | 134 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東孝線 | 東孝線 |  | 東孝線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東孝線A3 | 11KV東孝線 T相AMP | FEEDER | S45/11/VE32/I_T |  |  |  | CDC | 135 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東孝線 | 東孝線 |  | 東孝線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東孝線A0 | 11KV東孝線 N相AMP | FEEDER | S45/11/VE32/I_N |  |  |  | CDC | 136 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東忠線 | 東忠線 |  | 東忠線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東忠線KVAR | 11KV東忠線 KVAR | FEEDER | S45/11/VE31/KVAR |  |  |  | CDC | 137 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東忠線 | 東忠線 |  | 東忠線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東忠線A1 | 11KV東忠線 R相AMP | FEEDER | S45/11/VE31/I_R |  |  |  | CDC | 138 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東忠線 | 東忠線 |  | 東忠線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東忠線A2 | 11KV東忠線 S相AMP | FEEDER | S45/11/VE31/I_S |  |  |  | CDC | 139 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東忠線 | 東忠線 |  | 東忠線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東忠線A3 | 11KV東忠線 T相AMP | FEEDER | S45/11/VE31/I_T |  |  |  | CDC | 140 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東忠線 | 東忠線 |  | 東忠線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東忠線A0 | 11KV東忠線 N相AMP | FEEDER | S45/11/VE31/I_N |  |  |  | CDC | 141 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東信線 | 東信線 |  | 東信線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東信線KVAR | 11KV東信線 KVAR | FEEDER | S45/11/VE35/KVAR |  |  |  | CDC | 142 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東信線 | 東信線 |  | 東信線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東信線A1 | 11KV東信線 R相AMP | FEEDER | S45/11/VE35/I_R |  |  |  | CDC | 143 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東信線 | 東信線 |  | 東信線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東信線A2 | 11KV東信線 S相AMP | FEEDER | S45/11/VE35/I_S |  |  |  | CDC | 144 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東信線 | 東信線 |  | 東信線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東信線A3 | 11KV東信線 T相AMP | FEEDER | S45/11/VE35/I_T |  |  |  | CDC | 145 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東信線 | 東信線 |  | 東信線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東信線A0 | 11KV東信線 N相AMP | FEEDER | S45/11/VE35/I_N |  |  |  | CDC | 146 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東愛線 | 東愛線 |  | 東愛線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東愛線KVAR | 11KV東愛線 KVAR | FEEDER | S45/11/VE34/KVAR |  |  |  | CDC | 147 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東愛線 | 東愛線 |  | 東愛線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東愛線A1 | 11KV東愛線 R相AMP | FEEDER | S45/11/VE34/I_R |  |  |  | CDC | 148 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東愛線 | 東愛線 |  | 東愛線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東愛線A2 | 11KV東愛線 S相AMP | FEEDER | S45/11/VE34/I_S |  |  |  | CDC | 149 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東愛線 | 東愛線 |  | 東愛線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東愛線A3 | 11KV東愛線 T相AMP | FEEDER | S45/11/VE34/I_T |  |  |  | CDC | 150 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | 東愛線 | 東愛線 |  | 東愛線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.東愛線A0 | 11KV東愛線 N相AMP | FEEDER | S45/11/VE34/I_N |  |  |  | CDC | 151 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S45/11/TIE1/I_R |  |  |  | CDC | 152 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S45/11/TIE1/I_S |  |  |  | CDC | 153 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S45/11/TIE1/I_T |  |  |  | CDC | 154 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S45/11/TIE2/I_R |  |  |  | CDC | 155 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S45/11/TIE2/I_S |  |  |  | CDC | 156 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S45/11/TIE2/I_T |  |  |  | CDC | 157 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | C20R1450 | 1305.000000 | 1305.000000 | 1450.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_MW | #1MTR二次側 MW | DTR | S45/11/M1/MW |  |  |  | CDC | 158 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S45/11/M1/MVAR |  |  |  | CDC | 159 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S45/11/M1/I_R |  |  |  | CDC | 160 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S45/11/M1/I_S |  |  |  | CDC | 161 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S45/11/M1/I_T |  |  |  | CDC | 162 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_OIL | #1MTR 油溫 | DTR | S45//1MTR/OilTemp |  |  |  | CDC | 163 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_COIL | #1MTR 線溫 | DTR | S45//1MTR/CoilTemp |  |  |  | CDC | 164 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S45//1MTR/TapPosMv |  |  |  | CDC | 165 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_MW | #2MTR二次側 MW | DTR | S45/11/M2A/MW |  |  |  | CDC | 166 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S45/11/M2A/MVAR |  |  |  | CDC | 167 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S45/11/M2A/I_R |  |  |  | CDC | 168 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S45/11/M2A/I_S |  |  |  | CDC | 169 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S45/11/M2A/I_T |  |  |  | CDC | 170 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_OIL | #2MTR 油溫 | DTR | S45//2MTR/OilTemp |  |  |  | CDC | 171 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_COIL | #2MTR 線溫 | DTR | S45//2MTR/CoilTemp |  |  |  | CDC | 172 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S45//2MTR/TapPosMv |  |  |  | CDC | 173 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_MW | #3MTR二次側 MW | DTR | S45/11/M3/MW |  |  |  | CDC | 174 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S45/11/M3/MVAR |  |  |  | CDC | 175 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S45/11/M3/I_R |  |  |  | CDC | 176 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S45/11/M3/I_S |  |  |  | CDC | 177 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S45/11/M3/I_T |  |  |  | CDC | 178 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_OIL | #3MTR 油溫 | DTR | S45//3MTR/OilTemp |  |  |  | CDC | 179 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_COIL | #3MTR 線溫 | DTR | S45//3MTR/CoilTemp |  |  |  | CDC | 180 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_1 | [8 empty] | 新東SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S45//3MTR/TapPosMv |  |  |  | CDC | 181 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S45 | 新東SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS3_1 | [8 empty] | 新東SS.直流電源電壓 | 直流電源電壓 | OTHER | S45/0/StaDev/DCV |  |  |  | CDC | 182 | GENERICAIPoint | SS305_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 新東SS.620_PHA | 新營新東線(620) 相間RY | LINE69 | S45/69/620/PHA |  |  |  | CDC | 183 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 新東SS.620_GDA | 新營新東線(620) 接地RY | LINE69 | S45/69/620/GDA |  |  |  | CDC | 184 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 新東SS.620_CB | 620(新營新東線) CB | LINE69 | S45/69/620/CB |  |  |  | CDC | 185 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | ABS1 | 621 | [16 empty] | 1-38-08 | 1-38-09 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 新東SS.621_ABS | 621(新營新東線) ABS | LINE69 | S45/69/620/ABS1 |  |  |  | CDC | 186 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | ABS2 | 622 | [16 empty] | 1-38-10 | 1-38-11 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 新東SS.622_ABS | 622(新營新東線) ABS | LINE69 | S45/69/620/ABS2 |  |  |  | CDC | 187 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | E2 | 622E | [16 empty] | 1-38-12 | 1-38-13 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 新東SS.622E_ES | 622E(新營新東線) ES | LINE69 | S45/69/620/ES2 |  |  |  | CDC | 188 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 新東SS.650_PHA | 白河線(650) 相間RY | LINE69 | S45/69/650/PHA |  |  |  | CDC | 189 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 新東SS.650_GDA | 白河線(650) 接地RY | LINE69 | S45/69/650/GDA |  |  |  | CDC | 190 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 新東SS.650_CB | 650(白河線) CB | LINE69 | S45/69/650/CB |  |  |  | CDC | 191 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | ABS1 | 651 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 新東SS.651_ABS | 651(白河線) ABS | LINE69 | S45/69/650/ABS1 |  |  |  | CDC | 192 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | ABS2 | 652 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 新東SS.652_ABS | 652(白河線) ABS | LINE69 | S45/69/650/ABS2 |  |  |  | CDC | 193 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | E2 | 652E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 新東SS.652E_ES | 652E(白河線) ES | LINE69 | S45/69/650/ES2 |  |  |  | CDC | 194 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_PHA | 11KV東一線(VE21) 相間RY | FEEDER | S45/11/VE21/PHA |  |  |  | CDC | 195 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_GDA | 11KV東一線(VE21) 接地RY | FEEDER | S45/11/VE21/GDA |  |  |  | CDC | 196 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_79UL | 11KV東一線(VE21) 79RY U/L | FEEDER | S45/11/VE21/79UL |  |  |  | CDC | 197 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_ADJ | 11KV東一線(VE21) LCO分流器 U/L | FEEDER | S45/11/VE21/ADJ |  |  |  | CDC | 198 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE21 | VE21(11KV東一線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_CB | VE21(11KV東一線) CB | FEEDER | S45/11/VE21/CB |  |  |  | CDC | 199 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_PHA | 11KV東二線(VE22) 相間RY | FEEDER | S45/11/VE22/PHA |  |  |  | CDC | 200 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_GDA | 11KV東二線(VE22) 接地RY | FEEDER | S45/11/VE22/GDA |  |  |  | CDC | 201 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_79UL | 11KV東二線(VE22) 79RY U/L | FEEDER | S45/11/VE22/79UL |  |  |  | CDC | 202 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_ADJ | 11KV東二線(VE22) LCO分流器 U/L | FEEDER | S45/11/VE22/ADJ |  |  |  | CDC | 203 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE22 | VE22(11KV東二線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_CB | VE22(11KV東二線) CB | FEEDER | S45/11/VE22/CB |  |  |  | CDC | 204 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_PHA | 11KV東三線(VE23) 相間RY | FEEDER | S45/11/VE23/PHA |  |  |  | CDC | 205 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_GDA | 11KV東三線(VE23) 接地RY | FEEDER | S45/11/VE23/GDA |  |  |  | CDC | 206 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_79UL | 11KV東三線(VE23) 79RY U/L | FEEDER | S45/11/VE23/79UL |  |  |  | CDC | 207 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_ADJ | 11KV東三線(VE23) LCO分流器 U/L | FEEDER | S45/11/VE23/ADJ |  |  |  | CDC | 208 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE23 | VE23(11KV東三線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_CB | VE23(11KV東三線) CB | FEEDER | S45/11/VE23/CB |  |  |  | CDC | 209 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_PHA | 11KV東正線(VE24) 相間RY | FEEDER | S45/11/VE24/PHA |  |  |  | CDC | 210 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_GDA | 11KV東正線(VE24) 接地RY | FEEDER | S45/11/VE24/GDA |  |  |  | CDC | 211 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_79UL | 11KV東正線(VE24) 79RY U/L | FEEDER | S45/11/VE24/79UL |  |  |  | CDC | 212 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_ADJ | 11KV東正線(VE24) LCO分流器 U/L | FEEDER | S45/11/VE24/ADJ |  |  |  | CDC | 213 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE24 | VE24(11KV東正線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_CB | VE24(11KV東正線) CB | FEEDER | S45/11/VE24/CB |  |  |  | CDC | 214 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_PHA | 11KV東五線(VE25) 相間RY | FEEDER | S45/11/VE25/PHA |  |  |  | CDC | 215 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_GDA | 11KV東五線(VE25) 接地RY | FEEDER | S45/11/VE25/GDA |  |  |  | CDC | 216 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_79UL | 11KV東五線(VE25) 79RY U/L | FEEDER | S45/11/VE25/79UL |  |  |  | CDC | 217 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_ADJ | 11KV東五線(VE25) LCO分流器 U/L | FEEDER | S45/11/VE25/ADJ |  |  |  | CDC | 218 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE25 | VE25(11KV東五線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_CB | VE25(11KV東五線) CB | FEEDER | S45/11/VE25/CB |  |  |  | CDC | 219 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_PHA | 11KV東六線(VE26) 相間RY | FEEDER | S45/11/VE26/PHA |  |  |  | CDC | 220 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_GDA | 11KV東六線(VE26) 接地RY | FEEDER | S45/11/VE26/GDA |  |  |  | CDC | 221 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_79UL | 11KV東六線(VE26) 79RY U/L | FEEDER | S45/11/VE26/79UL |  |  |  | CDC | 222 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_ADJ | 11KV東六線(VE26) LCO分流器 U/L | FEEDER | S45/11/VE26/ADJ |  |  |  | CDC | 223 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE26 | VE26(11KV東六線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_CB | VE26(11KV東六線) CB | FEEDER | S45/11/VE26/CB |  |  |  | CDC | 224 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_PHA | 11KV東七線(VE27) 相間RY | FEEDER | S45/11/VE27/PHA |  |  |  | CDC | 225 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_GDA | 11KV東七線(VE27) 接地RY | FEEDER | S45/11/VE27/GDA |  |  |  | CDC | 226 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_79UL | 11KV東七線(VE27) 79RY U/L | FEEDER | S45/11/VE27/79UL |  |  |  | CDC | 227 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_ADJ | 11KV東七線(VE27) LCO分流器 U/L | FEEDER | S45/11/VE27/ADJ |  |  |  | CDC | 228 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE27 | VE27(11KV東七線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_CB | VE27(11KV東七線) CB | FEEDER | S45/11/VE27/CB |  |  |  | CDC | 229 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_PHA | 11KV東八線(VE28) 相間RY | FEEDER | S45/11/VE28/PHA |  |  |  | CDC | 230 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_GDA | 11KV東八線(VE28) 接地RY | FEEDER | S45/11/VE28/GDA |  |  |  | CDC | 231 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_79UL | 11KV東八線(VE28) 79RY U/L | FEEDER | S45/11/VE28/79UL |  |  |  | CDC | 232 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_ADJ | 11KV東八線(VE28) LCO分流器 U/L | FEEDER | S45/11/VE28/ADJ |  |  |  | CDC | 233 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE28 | VE28(11KV東八線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_CB | VE28(11KV東八線) CB | FEEDER | S45/11/VE28/CB |  |  |  | CDC | 234 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_PHA | 11KV東九線(VE29) 相間RY | FEEDER | S45/11/VE29/PHA |  |  |  | CDC | 235 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_GDA | 11KV東九線(VE29) 接地RY | FEEDER | S45/11/VE29/GDA |  |  |  | CDC | 236 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_79UL | 11KV東九線(VE29) 79RY U/L | FEEDER | S45/11/VE29/79UL |  |  |  | CDC | 237 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_ADJ | 11KV東九線(VE29) LCO分流器 U/L | FEEDER | S45/11/VE29/ADJ |  |  |  | CDC | 238 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE29 | VE29(11KV東九線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_CB | VE29(11KV東九線) CB | FEEDER | S45/11/VE29/CB |  |  |  | CDC | 239 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_PHA | 11KV東十線(VE30) 相間RY | FEEDER | S45/11/VE30/PHA |  |  |  | CDC | 240 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_GDA | 11KV東十線(VE30) 接地RY | FEEDER | S45/11/VE30/GDA |  |  |  | CDC | 241 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_79UL | 11KV東十線(VE30) 79RY U/L | FEEDER | S45/11/VE30/79UL |  |  |  | CDC | 242 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_ADJ | 11KV東十線(VE30) LCO分流器 U/L | FEEDER | S45/11/VE30/ADJ |  |  |  | CDC | 243 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE30 | VE30(11KV東十線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_CB | VE30(11KV東十線) CB | FEEDER | S45/11/VE30/CB |  |  |  | CDC | 244 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_PHA | 11KV東忠線(VE31) 相間RY | FEEDER | S45/11/VE31/PHA |  |  |  | CDC | 245 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_GDA | 11KV東忠線(VE31) 接地RY | FEEDER | S45/11/VE31/GDA |  |  |  | CDC | 246 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_79UL | 11KV東忠線(VE31) 79RY U/L | FEEDER | S45/11/VE31/79UL |  |  |  | CDC | 247 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_ADJ | 11KV東忠線(VE31) LCO分流器 U/L | FEEDER | S45/11/VE31/ADJ |  |  |  | CDC | 248 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE31 | VE31(11KV東忠線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_CB | VE31(11KV東忠線) CB | FEEDER | S45/11/VE31/CB |  |  |  | CDC | 249 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_PHA | 11KV東孝線(VE32) 相間RY | FEEDER | S45/11/VE32/PHA |  |  |  | CDC | 250 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_GDA | 11KV東孝線(VE32) 接地RY | FEEDER | S45/11/VE32/GDA |  |  |  | CDC | 251 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_79UL | 11KV東孝線(VE32) 79RY U/L | FEEDER | S45/11/VE32/79UL |  |  |  | CDC | 252 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_ADJ | 11KV東孝線(VE32) LCO分流器 U/L | FEEDER | S45/11/VE32/ADJ |  |  |  | CDC | 253 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE32 | VE32(11KV東孝線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_CB | VE32(11KV東孝線) CB | FEEDER | S45/11/VE32/CB |  |  |  | CDC | 254 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_PHA | 11KV東仁線(VE33) 相間RY | FEEDER | S45/11/VE33/PHA |  |  |  | CDC | 255 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_GDA | 11KV東仁線(VE33) 接地RY | FEEDER | S45/11/VE33/GDA |  |  |  | CDC | 256 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_79UL | 11KV東仁線(VE33) 79RY U/L | FEEDER | S45/11/VE33/79UL |  |  |  | CDC | 257 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_ADJ | 11KV東仁線(VE33) LCO分流器 U/L | FEEDER | S45/11/VE33/ADJ |  |  |  | CDC | 258 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE33 | VE33(11KV東仁線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_CB | VE33(11KV東仁線) CB | FEEDER | S45/11/VE33/CB |  |  |  | CDC | 259 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_PHA | 11KV東愛線(VE34) 相間RY | FEEDER | S45/11/VE34/PHA |  |  |  | CDC | 260 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_GDA | 11KV東愛線(VE34) 接地RY | FEEDER | S45/11/VE34/GDA |  |  |  | CDC | 261 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_79UL | 11KV東愛線(VE34) 79RY U/L | FEEDER | S45/11/VE34/79UL |  |  |  | CDC | 262 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_ADJ | 11KV東愛線(VE34) LCO分流器 U/L | FEEDER | S45/11/VE34/ADJ |  |  |  | CDC | 263 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE34 | VE34(11KV東愛線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_CB | VE34(11KV東愛線) CB | FEEDER | S45/11/VE34/CB |  |  |  | CDC | 264 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_PHA | 11KV東信線(VE35) 相間RY | FEEDER | S45/11/VE35/PHA |  |  |  | CDC | 265 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_GDA | 11KV東信線(VE35) 接地RY | FEEDER | S45/11/VE35/GDA |  |  |  | CDC | 266 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_79UL | 11KV東信線(VE35) 79RY U/L | FEEDER | S45/11/VE35/79UL |  |  |  | CDC | 267 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_ADJ | 11KV東信線(VE35) LCO分流器 U/L | FEEDER | S45/11/VE35/ADJ |  |  |  | CDC | 268 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S45 | 新東SS | 11 | 11kV | VE35 | VE35(11KV東信線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_CB | VE35(11KV東信線) CB | FEEDER | S45/11/VE35/CB |  |  |  | CDC | 269 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE1_CB | 11KV TIE1 CB | TIE | S45/11/TIE1/CB |  |  |  | CDC | 270 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE1_51A | 11KV TIE1 51RY | TIE | S45/11/TIE1/51A |  |  |  | CDC | 271 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S45/11/TIE1/51NA |  |  |  | CDC | 272 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE2_CB | 11KV TIE2 CB | TIE | S45/11/TIE2/CB |  |  |  | CDC | 273 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE2_51A | 11KV TIE2 51RY | TIE | S45/11/TIE2/51A |  |  |  | CDC | 274 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S45/11/TIE2/51NA |  |  |  | CDC | 275 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.750_CB | 750(#1MTR) CB | DTR | S45/69/750/CB |  |  |  | CDC | 276 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.1M_CB | 1M(#1MTR) CB | DTR | S45/11/M1/CB |  |  |  | CDC | 277 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_51A | #1MTR 51RY | DTR | S45/69/750/51A |  |  |  | CDC | 278 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_51NA | #1MTR 51N RY | DTR | S45/69/750/51NA |  |  |  | CDC | 279 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S45//1MTR/51ZA |  |  |  | CDC | 280 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_87A | #1MTR 87RY | DTR | S45//1MTR/87A |  |  |  | CDC | 281 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S45//1MTR/87UL |  |  |  | CDC | 282 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S45/11/M1/51A |  |  |  | CDC | 283 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_TRA | #1MTR 重故障 | DTR | S45//1MTR/TRA |  |  |  | CDC | 284 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S45//1MTR/TRF |  |  |  | CDC | 285 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S45//1MTR/SupLocal |  |  |  | CDC | 286 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S45//1MTR/Tap Chan |  |  |  | CDC | 287 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.751_ABS | 751(#1MTR) ABS | DTR | S45/69/750/ABS1 |  |  |  | CDC | 288 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_96A | #1MTR 96P RY | DTR | S45//1MTR/96PA |  |  |  | CDC | 289 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S45//1MTR/OLTC_DLY |  |  |  | CDC | 290 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S45//1MTR/AC_Fault |  |  |  | CDC | 291 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.760_CB | 760(#2MTR) CB | DTR | S45/69/760/CB |  |  |  | CDC | 292 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.2MA_CB | 2MA(#2MTR) CB | DTR | S45/11/M2A/CB |  |  |  | CDC | 293 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-46 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.2MB_CB | 2MB(#2MTR) CB | DTR | S45/11/M2B/CB |  |  |  | CDC | 294 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_51A | #2MTR 51RY | DTR | S45/69/760/51A |  |  |  | CDC | 295 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_51NA | #2MTR 51N RY | DTR | S45/69/760/51NA |  |  |  | CDC | 296 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S45//2MTR/51ZA |  |  |  | CDC | 297 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_87A | #2MTR 87RY | DTR | S45//2MTR/87A |  |  |  | CDC | 298 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S45//2MTR/87UL |  |  |  | CDC | 299 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S45/11/M2A/51A |  |  |  | CDC | 300 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S45/11/M2B/51A |  |  |  | CDC | 301 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_TRA | #2MTR 重故障 | DTR | S45//2MTR/TRA |  |  |  | CDC | 302 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S45//2MTR/TRF |  |  |  | CDC | 303 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S45//2MTR/SupLocal |  |  |  | CDC | 304 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S45//2MTR/Tap Chan |  |  |  | CDC | 305 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.761_ABS | 761(#2MTR) ABS | DTR | S45/69/760/ABS1 |  |  |  | CDC | 306 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_96A | #2MTR 96P RY | DTR | S45//2MTR/96PA |  |  |  | CDC | 307 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S45//2MTR/OLTC_DLY |  |  |  | CDC | 308 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S45//2MTR/AC_Fault |  |  |  | CDC | 309 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.770_CB | 770(#3MTR) CB | DTR | S45/69/770/CB |  |  |  | CDC | 310 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.3M_CB | 3M(#3MTR) CB | DTR | S45/11/M3/CB |  |  |  | CDC | 311 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_51A | #3MTR 51RY | DTR | S45/69/770/51A |  |  |  | CDC | 312 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_51NA | #3MTR 51N RY | DTR | S45/69/770/51NA |  |  |  | CDC | 313 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S45//3MTR/51ZA |  |  |  | CDC | 314 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_87A | #3MTR 87RY | DTR | S45//3MTR/87A |  |  |  | CDC | 315 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S45//3MTR/87UL |  |  |  | CDC | 316 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S45/11/M3/51A |  |  |  | CDC | 317 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_TRA | #3MTR 重故障 | DTR | S45//3MTR/TRA |  |  |  | CDC | 318 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S45//3MTR/TRF |  |  |  | CDC | 319 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S45//3MTR/SupLocal |  |  |  | CDC | 320 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S45//3MTR/Tap Chan |  |  |  | CDC | 321 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-38-04 | 1-38-05 | 1-2C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.771_ABS | 771(#3MTR) ABS | DTR | S45/69/770/ABS1 |  |  |  | CDC | 322 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_96A | #3MTR 96P RY | DTR | S45//3MTR/96PA |  |  |  | CDC | 323 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S45//3MTR/OLTC_DLY |  |  |  | CDC | 324 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S45//3MTR/AC_Fault |  |  |  | CDC | 325 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.210_CB | 210(11KV #1SC) CB | SC | S45/11/210/CB |  |  |  | CDC | 326 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S45/11/210/Tap Chan |  |  |  | CDC | 327 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.210_SCA | 11KV #1SC 51,51N RY | SC | S45/11/210/SCA |  |  |  | CDC | 328 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S45/11/210/UVA |  |  |  | CDC | 329 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.220_CB | 220(11KV #2SC) CB | SC | S45/11/220/CB |  |  |  | CDC | 330 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S45/11/220/Tap Chan |  |  |  | CDC | 331 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.220_SCA | 11KV #2SC 51,51N RY | SC | S45/11/220/SCA |  |  |  | CDC | 332 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S45/11/220/UVA |  |  |  | CDC | 333 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.230_CB | 230(11KV #3SC) CB | SC | S45/11/230/CB |  |  |  | CDC | 334 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S45/11/230/Tap Chan |  |  |  | CDC | 335 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.230_SCA | 11KV #3SC 51,51N RY | SC | S45/11/230/SCA |  |  |  | CDC | 336 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S45/11/230/UVA |  |  |  | CDC | 337 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 新東SS.810_CB | 810(69KV #1SC) CB | SC | S45/69/810/CB |  |  |  | CDC | 338 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_N | [8 empty] | 新東SS.811_ABS | 811(69KV #1SC) ABS | SC | S45/69/810/ABS1 |  |  |  | CDC | 339 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 新東SS.810_SCA | 69KV #1SC 51,51N RY | SC | S45/69/810/SCA |  |  |  | CDC | 340 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 新東SS.810_OUVA | 69KV #1SC 27,59RY | SC | S45/69/810/UVA |  |  |  | CDC | 341 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 新東SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S45/69/1BUS/BUS_VUA |  |  |  | CDC | 342 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S45/11/ComPoint/CBA |  |  |  | CDC | 343 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S45/11/ComPoint/CBF |  |  |  | CDC | 344 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S45/69/ComPoint/ABS_89A |  |  |  | CDC | 345 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S45/69/ComPoint/CBA |  |  |  | CDC | 346 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S45/69/ComPoint/CBF |  |  |  | CDC | 347 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S45/0/RTU/RTU_R_L |  |  |  | CDC | 348 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S45 | 新東SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.TEST_CB | TEST CB | OTHER | S45/0/RTU/Test_CB |  |  |  | CDC | 349 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-31-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.火災警報(1) | CO2警報 | OTHER | S45/0/StaDev/Fire1 |  |  |  | CDC | 350 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.火災警報(2) | CO2故障 | OTHER | S45/0/StaDev/Fire2 |  |  |  | CDC | 351 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-30-10 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.火災警報(3) | 火災警報(3) | OTHER | S45/0/StaDev/Fire3 |  |  |  | CDC | 352 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.其他重故障 | 變電所內其他重故障 | OTHER | S45/0/StaDev/PSA |  |  |  | CDC | 353 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S45/0/StaDev/PSF |  |  |  | CDC | 354 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S45/0/StaDev/STUV |  |  |  | CDC | 355 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.直流充電機故障 | 變電所直流充電機故障 | OTHER | S45/0/StaDev/CHG1 |  |  |  | CDC | 356 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.直流電源DCA | NFB跳脫監視 | OTHER | S45/0/StaDev/DCA |  |  |  | CDC | 357 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S45/0/StaDev/DCE |  |  |  | CDC | 358 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S45/0/StaDev/OilLeak |  |  |  | CDC | 359 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | S45/0/StaDev/CHG2 |  |  |  | CDC | 360 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化防盜(1) | 水氣霧警報 | OTHER | S45/0/StaDev/Burglar1 |  |  |  | CDC | 361 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化防盜(2) | 水氣霧故障 | OTHER | S45/0/StaDev/Burglar2 |  |  |  | CDC | 362 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化防盜(3) | MCSG偵煙警報 | OTHER | S45/0/StaDev/Burglar3 |  |  |  | CDC | 363 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化門禁(1) | 水氣霧釋放 | OTHER | S45/0/StaDev/Door1 |  |  |  | CDC | 364 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化門禁(2) | 所內淹水高水位 | OTHER | S45/0/StaDev/Door2 |  |  |  | CDC | 365 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.無人化門禁(3) | 所內淹水低水位 | OTHER | S45/0/StaDev/Door3 |  |  |  | CDC | 366 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.開關場照明(A) | 開關場照明(A) | OTHER | S45/0/StaDev/Lights1 |  |  |  | CDC | 367 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S45 | 新東SS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.開關場照明(B) | 開關場照明(B) | OTHER | S45/0/StaDev/Lights2 |  |  |  | CDC | 368 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S45 | 新東SS | 69 | 69kV |  |  |  | SC警報 | [17 empty] | 1-31-08 | [7 empty] | 69KV_N | [8 empty] | 新東SS.69KV_SC警報 | 69KV SC警報 | OTHER | S45/69/ComPoint/SCA |  |  |  | CDC | 369 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  |  |  |  | Door | [17 empty] | 1-30-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.門禁 | 門禁 | OTHER | S45/0/StaDev/Door |  |  |  | CDC | 370 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 新東SS.620_87A | 新營新東線(620) 87RY | LINE69 | S45/69/620/87A |  |  |  | CDC | 371 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 新東SS.620_87UL | 新營新東線(620) 87RY U/L | LINE69 | S45/69/620/87UL |  |  |  | CDC | 372 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 620 | 國聖線(620) |  | 87CFA | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 新東SS.620_87CFA | 新營新東線(620)87RY通訊故障 | OTHER | S45/69/620/87CFA |  |  |  | CDC | 373 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 620 | 國聖線(620) |  | 87RYFA | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 新東SS.620_87RYFA | 新營新東線(620)數位電驛故障 | OTHER | S45/69/620/RYFA |  |  |  | CDC | 374 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 新東SS.650_87A | 白河線(650) 87RY | LINE69 | S45/69/650/87A |  |  |  | CDC | 375 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 新東SS.650_87UL | 白河線(650) 87RY U/L | LINE69 | S45/69/650/87UL |  |  |  | CDC | 376 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 650 | 白河線(650) |  | 87CFA | [17 empty] | 1-37-07 | [7 empty] | 69KV_N | [8 empty] | 新東SS.650_87CFA | 650 87RY通訊故障 | OTHER | S45/69/650/87CFA |  |  |  | CDC | 377 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 650 | 白河線(650) |  | 87RYFA | [17 empty] | 1-37-06 | [7 empty] | 69KV_N | [8 empty] | 新東SS.650_87RYFA | 650 數位電驛故障 | OTHER | S45/69/650/RYFA |  |  |  | CDC | 378 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 810 | #1SC(810) |  | CFA | [17 empty] | 1-37-15 | [7 empty] | 69KV_N | [8 empty] | 新東SS.810_CFA | 810 RY通訊故障 | OTHER | S45/69/810/87CFA |  |  |  | CDC | 379 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 810 | #1SC(810) |  | RYFA | [17 empty] | 1-37-14 | [7 empty] | 69KV_N | [8 empty] | 新東SS.810_RYFA | 810 數位電驛故障 | OTHER | S45/69/810/RYFA |  |  |  | CDC | 380 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-06-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | S45//1MTR/63Q |  |  |  | CDC | 381 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-05-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | S45//1MTR/96B1 |  |  |  | CDC | 382 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-05-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | S45//1MTR/96B2 |  |  |  | CDC | 383 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-05-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | S45//1MTR/96D |  |  |  | CDC | 384 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-05-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | S45//1MTR/96P |  |  |  | CDC | 385 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-06-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | S45//2MTR/63Q |  |  |  | CDC | 386 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-06-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | S45//2MTR/96B1 |  |  |  | CDC | 387 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-06-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | S45//2MTR/96B2 |  |  |  | CDC | 388 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-06-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | S45//2MTR/96D |  |  |  | CDC | 389 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-06-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | S45//2MTR/96P |  |  |  | CDC | 390 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-07-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | S45//3MTR/63Q |  |  |  | CDC | 391 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-06-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | S45//3MTR/96B1 |  |  |  | CDC | 392 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-06-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | S45//3MTR/96B2 |  |  |  | CDC | 393 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-07-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | S45//3MTR/96D |  |  |  | CDC | 394 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-07-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | S45//3MTR/96P |  |  |  | CDC | 395 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV |  |  |  | RYFA | [17 empty] | 1-33-14 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | S45/11/ComPoint/RYFA |  |  |  | CDC | 396 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-33-15 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.PMA | POWER METER故障 | OTHER | S45/0/ComPoint/PMA |  |  |  | CDC | 397 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-16-04 |  | 1-42 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.390_CB | 390(#1SSTR) CB | OTHER | S45/11/390/CB |  |  |  | CDC | 398 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-16-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S45/11/390/51A |  |  |  | CDC | 399 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-16-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S45/11/390/51NA |  |  |  | CDC | 400 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-16-07 |  | 1-43 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.490_CB | 490(#3SSTR) CB | OTHER | S45/11/490/CB |  |  |  | CDC | 401 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-17-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3SSTR_51A | #3SSTR 51RY | OTHER | S45/11/490/51A |  |  |  | CDC | 402 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-17-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | S45/11/490/51NA |  |  |  | CDC | 403 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MA | #1MA |  | 81AS | [17 empty] | 1-14-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MA_81A/S | #1MA 81RY | OTHER | S45/11/M1/81AS |  |  |  | CDC | 404 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S45 | 新東SS | 0 |  | 1MA | #1MA |  | 81UL | [17 empty] | 1-33-13 |  | 1-6B | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | S45/11/M1/81UL |  |  |  | CDC | 405 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MA | #2MA |  | 81AS | [17 empty] | 1-14-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MA_81A/S | #2MA 81RY | OTHER | S45/11/M2A/81AS |  |  |  | CDC | 406 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S45 | 新東SS | 0 |  | 2MA | #2MA |  | 81UL | [17 empty] | 1-34-13 |  | 1-6C | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | S45/11/M2A/81UL |  |  |  | CDC | 407 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MB | #2MB |  | 81AS | [17 empty] | 1-14-02 |  | 1-57 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MB_81A/S | #2MB 81RY | OTHER | S45/11/M2B/81AS |  |  |  | CDC | 408 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S45 | 新東SS | 0 |  | 2MB | #2MB |  | 81UL | [17 empty] | 1-34-14 |  | 1-6D | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | S45/11/M2B/81UL |  |  |  | CDC | 409 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 3MA | #3MA |  | 81AS | [17 empty] | 1-14-03 |  | 1-69 | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MA_81A/S | #3MA 81RY | OTHER | S45/11/M3/81AS |  |  |  | CDC | 410 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S45 | 新東SS | 0 |  | 3MA | #3MA |  | 81UL | [17 empty] | 1-35-13 |  | 1-6E | [5 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | S45/11/M3/81UL |  |  |  | CDC | 411 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE21_79 | 東一線(VE21) |  | LOA | [17 empty] | 1-3C-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_79_LOA | 11KV東一線(VE21) 79LOA | OTHER | S45/11/VE21/LOA |  |  |  | CDC | 412 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) |  | 81AS | [17 empty] | 1-14-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_81A/S | 11KV東一線(VE21) 81RY | OTHER | S45/11/VE21/81AS |  |  |  | CDC | 413 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22_79 | 東二線(VE22) |  | LOA | [17 empty] | 1-3C-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_79_LOA | 11KV東二線(VE22) 79LOA | OTHER | S45/11/VE22/LOA |  |  |  | CDC | 414 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) |  | 81AS | [17 empty] | 1-14-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_81A/S | 11KV東二線(VE22) 81RY | OTHER | S45/11/VE22/81AS |  |  |  | CDC | 415 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23_79 | 東三線(VE23) |  | LOA | [17 empty] | 1-3C-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_79_LOA | 11KV東三線(VE23) 79LOA | OTHER | S45/11/VE23/LOA |  |  |  | CDC | 416 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) |  | 81AS | [17 empty] | 1-14-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_81A/S | 11KV東三線(VE23) 81RY | OTHER | S45/11/VE23/81AS |  |  |  | CDC | 417 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24_79 | 東正線(VE24) |  | LOA | [17 empty] | 1-3C-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_79_LOA | 11KV東正線(VE24) 79LOA | OTHER | S45/11/VE24/LOA |  |  |  | CDC | 418 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) |  | 81AS | [17 empty] | 1-15-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_81A/S | 11KV東正線(VE24) 81RY | OTHER | S45/11/VE24/81AS |  |  |  | CDC | 419 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25_79 | 東五線(VE25) |  | LOA | [17 empty] | 1-3C-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_79_LOA | 11KV東五線(VE25) 79LOA | OTHER | S45/11/VE25/LOA |  |  |  | CDC | 420 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) |  | 81AS | [17 empty] | 1-15-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_81A/S | 11KV東五線(VE25) 81RY | OTHER | S45/11/VE25/81AS |  |  |  | CDC | 421 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26_79 | 東六線(VE26) |  | LOA | [17 empty] | 1-3C-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_79_LOA | 11KV東六線(VE26) 79LOA | OTHER | S45/11/VE26/LOA |  |  |  | CDC | 422 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) |  | 81AS | [17 empty] | 1-15-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_81A/S | 11KV東六線(VE26) 81RY | OTHER | S45/11/VE26/81AS |  |  |  | CDC | 423 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27_79 | 東七線(VE27) |  | LOA | [17 empty] | 1-3C-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_79_LOA | 11KV東七線(VE27) 79LOA | OTHER | S45/11/VE27/LOA |  |  |  | CDC | 424 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) |  | 81AS | [17 empty] | 1-15-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_81A/S | 11KV東七線(VE27) 81RY | OTHER | S45/11/VE27/81AS |  |  |  | CDC | 425 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28_79 | 東八線(VE28) |  | LOA | [17 empty] | 1-3C-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_79_LOA | 11KV東八線(VE28) 79LOA | OTHER | S45/11/VE28/LOA |  |  |  | CDC | 426 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) |  | 81AS | [17 empty] | 1-15-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_81A/S | 11KV東八線(VE28) 81RY | OTHER | S45/11/VE28/81AS |  |  |  | CDC | 427 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29_79 | 東九線(VE29) |  | LOA | [17 empty] | 1-3C-08 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_79_LOA | 11KV東九線(VE29) 79LOA | OTHER | S45/11/VE29/LOA |  |  |  | CDC | 428 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) |  | 81AS | [17 empty] | 1-15-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_81A/S | 11KV東九線(VE29) 81RY | OTHER | S45/11/VE29/81AS |  |  |  | CDC | 429 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30_79 | 東十線(VE30) |  | LOA | [17 empty] | 1-3C-09 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_79_LOA | 11KV東十線(VE30) 79LOA | OTHER | S45/11/VE30/LOA |  |  |  | CDC | 430 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) |  | 81AS | [17 empty] | 1-15-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_81A/S | 11KV東十線(VE30) 81RY | OTHER | S45/11/VE30/81AS |  |  |  | CDC | 431 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31_79 | 東忠線(VE31) |  | LOA | [17 empty] | 1-3C-10 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_79_LOA | 11KV東忠線(VE31) 79LOA | OTHER | S45/11/VE31/LOA |  |  |  | CDC | 432 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) |  | 81AS | [17 empty] | 1-15-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_81A/S | 11KV東忠線(VE31) 81RY | OTHER | S45/11/VE31/81AS |  |  |  | CDC | 433 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32_79 | 東孝線(VE32) |  | LOA | [17 empty] | 1-3C-11 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_79_LOA | 11KV東孝線(VE32) 79LOA | OTHER | S45/11/VE32/LOA |  |  |  | CDC | 434 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) |  | 81AS | [17 empty] | 1-16-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_81A/S | 11KV東孝線(VE32) 81RY | OTHER | S45/11/VE32/81AS |  |  |  | CDC | 435 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33_79 | 東仁線(VE33) |  | LOA | [17 empty] | 1-3C-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_79_LOA | 11KV東仁線(VE33) 79LOA | OTHER | S45/11/VE33/LOA |  |  |  | CDC | 436 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) |  | 81AS | [17 empty] | 1-16-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_81A/S | 11KV東仁線(VE33) 81RY | OTHER | S45/11/VE33/81AS |  |  |  | CDC | 437 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34_79 | 東愛線(VE34) |  | LOA | [17 empty] | 1-3C-13 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_79_LOA | 11KV東愛線(VE34) 79LOA | OTHER | S45/11/VE34/LOA |  |  |  | CDC | 438 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) |  | 81AS | [17 empty] | 1-16-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_81A/S | 11KV東愛線(VE34) 81RY | OTHER | S45/11/VE34/81AS |  |  |  | CDC | 439 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35_79 | 東信線(VE35) |  | LOA | [17 empty] | 1-3C-14 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_79_LOA | 11KV東信線(VE35) 79LOA | OTHER | S45/11/VE35/LOA |  |  |  | CDC | 440 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) |  | 81AS | [17 empty] | 1-16-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_81A/S | 11KV東信線(VE35) 81RY | OTHER | S45/11/VE35/81AS |  |  |  | CDC | 441 | GENERICDIPoint | SS305_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-3C-15 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | S45//1MTR/RYFA |  |  |  | CDC | 442 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-3D-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | S45//2MTR/RYFA |  |  |  | CDC | 443 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 1-3D-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | S45//3MTR/RYFA |  |  |  | CDC | 444 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 81RY | 81RY |  | RYFA | [17 empty] | 1-3D-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.81RY_RYFA | 81RY 電驛故障 | OTHER | S45/11/ComPoint/81A_RYFA |  |  |  | CDC | 445 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-3D-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | S45//1MTR/MTR_86A |  |  |  | CDC | 446 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 871S | [17 empty] | 1-3D-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | S45//1MTR/1_87UL1 |  |  |  | CDC | 447 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 872S | [17 empty] | 1-3D-07 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | S45//1MTR/1_87UL2 |  |  |  | CDC | 448 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-3D-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | S45//2MTR/MTR_86A |  |  |  | CDC | 449 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 871S | [17 empty] | 1-3D-08 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | S45//2MTR/1_87UL1 |  |  |  | CDC | 450 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 872S | [17 empty] | 1-3D-09 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | S45//2MTR/1_87UL2 |  |  |  | CDC | 451 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-3D-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | S45//3MTR/MTR_86A |  |  |  | CDC | 452 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 871S | [17 empty] | 1-3D-10 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | S45//3MTR/1_87UL1 |  |  |  | CDC | 453 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 872S | [17 empty] | 1-3D-11 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | S45//3MTR/1_87UL2 |  |  |  | CDC | 454 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3D-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | S45//1MTR/51Z_UL |  |  |  | CDC | 455 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3D-13 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | S45//2MTR/51Z_UL |  |  |  | CDC | 456 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3D-14 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | S45//3MTR/51Z_UL |  |  |  | CDC | 457 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | 1GIS | #1GIS |  | CBA | [17 empty] | 1-3E-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1GIS_CBA | #1GIS重故障 | OTHER | S45/11/1GIS/CBA |  |  |  | CDC | 458 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 1GIS | #1GIS |  | CBF | [17 empty] | 1-3E-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#1GIS_CBF | #1GIS輕故障 | OTHER | S45/11/1GIS/CBF |  |  |  | CDC | 459 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2GIS | #2GIS |  | CBA | [17 empty] | 1-3E-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2GIS_CBA | #2GIS重故障 | OTHER | S45/11/2GIS/CBA |  |  |  | CDC | 460 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 2GIS | #2GIS |  | CBF | [17 empty] | 1-3E-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#2GIS_CBF | #2GIS輕故障 | OTHER | S45/11/2GIS/CBF |  |  |  | CDC | 461 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3GIS | #3GIS |  | CBA | [17 empty] | 1-3E-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3GIS_CBA | #3GIS重故障 | OTHER | S45/11/3GIS/CBA |  |  |  | CDC | 462 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 0 |  | 3GIS | #3GIS |  | CBF | [17 empty] | 1-3E-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.#3GIS_CBF | #3GIS輕故障 | OTHER | S45/11/3GIS/CBF |  |  |  | CDC | 463 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S45 | 新東SS | 11 | 11kV | VE21 | 東一線(VE21) 81RY |  | 81UL | [17 empty] | 1-3E-08 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_81U/L | 11KV東一線(VE21) 81RY U/L | OTHER | S45/11/VE21/81UL |  |  |  | CDC | 464 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE22 | 東二線(VE22) 81RY |  | 81UL | [17 empty] | 1-3E-09 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_81U/L | 11KV東二線(VE22) 81RY U/L | OTHER | S45/11/VE22/81UL |  |  |  | CDC | 465 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE23 | 東三線(VE23) 81RY |  | 81UL | [17 empty] | 1-3E-10 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_81U/L | 11KV東三線(VE23) 81RY U/L | OTHER | S45/11/VE23/81UL |  |  |  | CDC | 466 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE24 | 東正線(VE24) 81RY |  | 81UL | [17 empty] | 1-3E-11 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_81U/L | 11KV東正線(VE24) 81RY U/L | OTHER | S45/11/VE24/81UL |  |  |  | CDC | 467 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE25 | 東五線(VE25) 81RY |  | 81UL | [17 empty] | 1-3E-12 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_81U/L | 11KV東五線(VE25) 81RY U/L | OTHER | S45/11/VE25/81UL |  |  |  | CDC | 468 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE26 | 東六線(VE26) 81RY |  | 81UL | [17 empty] | 1-3E-13 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_81U/L | 11KV東六線(VE26) 81RY U/L | OTHER | S45/11/VE26/81UL |  |  |  | CDC | 469 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE27 | 東七線(VE27) 81RY |  | 81UL | [17 empty] | 1-3E-14 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_81U/L | 11KV東七線(VE27) 81RY U/L | OTHER | S45/11/VE27/81UL |  |  |  | CDC | 470 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE28 | 東八線(VE28) 81RY |  | 81UL | [17 empty] | 1-3E-15 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_81U/L | 11KV東八線(VE28) 81RY U/L | OTHER | S45/11/VE28/81UL |  |  |  | CDC | 471 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE29 | 東九線(VE29) 81RY |  | 81UL | [17 empty] | 1-3F-00 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_81U/L | 11KV東九線(VE29) 81RY U/L | OTHER | S45/11/VE29/81UL |  |  |  | CDC | 472 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE30 | 東十線(VE30) 81RY |  | 81UL | [17 empty] | 1-3F-01 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_81U/L | 11KV東十線(VE30) 81RY U/L | OTHER | S45/11/VE30/81UL |  |  |  | CDC | 473 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE31 | 東忠線(VE31) 81RY |  | 81UL | [17 empty] | 1-3F-02 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_81U/L | 11KV東忠線(VE31) 81RY U/L | OTHER | S45/11/VE31/81UL |  |  |  | CDC | 474 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE32 | 東孝線(VE32) 81RY |  | 81UL | [17 empty] | 1-3F-03 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_81U/L | 11KV東孝線(VE32) 81RY U/L | OTHER | S45/11/VE32/81UL |  |  |  | CDC | 475 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE33 | 東仁線(VE33) 81RY |  | 81UL | [17 empty] | 1-3F-04 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_81U/L | 11KV東仁線(VE33) 81RY U/L | OTHER | S45/11/VE33/81UL |  |  |  | CDC | 476 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE34 | 東愛線(VE34) 81RY |  | 81UL | [17 empty] | 1-3F-05 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_81U/L | 11KV東愛線(VE34) 81RY U/L | OTHER | S45/11/VE34/81UL |  |  |  | CDC | 477 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | VE35 | 東信線(VE35) 81RY |  | 81UL | [17 empty] | 1-3F-06 | [7 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_81U/L | 11KV東信線(VE35) 81RY U/L | OTHER | S45/11/VE35/81UL |  |  |  | CDC | 478 | GENERICDIPoint | SS305_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S45 | 新東SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 479 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 480 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 481 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS3_1 | [8 empty] | 新東SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 482 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 新東SS.620BE | 620BE (非取樣點) | LINE69 | S45/69/620/BE0 |  |  |  |  | 483 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 新東SS.650BE | 650BE (非取樣點) | LINE69 | S45/69/650/BE0 |  |  |  |  | 484 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE21 | VE21_ES |  | LE0 | VE21_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_ES | VE21_ES (非取樣點) | FEEDER | S45/11/VE21/ES |  |  |  |  | 485 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE22 | VE22_ES |  | LE0 | VE22_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_ES | VE22_ES (非取樣點) | FEEDER | S45/11/VE22/ES |  |  |  |  | 486 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE23 | VE23_ES |  | LE0 | VE23_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_ES | VE23_ES (非取樣點) | FEEDER | S45/11/VE23/ES |  |  |  |  | 487 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE24 | VE24_ES |  | LE0 | VE24_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_ES | VE24_ES (非取樣點) | FEEDER | S45/11/VE24/ES |  |  |  |  | 488 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE25 | VE25_ES |  | LE0 | VE25_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_ES | VE25_ES (非取樣點) | FEEDER | S45/11/VE25/ES |  |  |  |  | 489 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE26 | VE26_ES |  | LE0 | VE26_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_ES | VE26_ES (非取樣點) | FEEDER | S45/11/VE26/ES |  |  |  |  | 490 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE27 | VE27_ES |  | LE0 | VE27_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_ES | VE27_ES (非取樣點) | FEEDER | S45/11/VE27/ES |  |  |  |  | 491 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE28 | VE28_ES |  | LE0 | VE28_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_ES | VE28_ES (非取樣點) | FEEDER | S45/11/VE28/ES |  |  |  |  | 492 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE29 | VE29_ES |  | LE0 | VE29_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_ES | VE29_ES (非取樣點) | FEEDER | S45/11/VE29/ES |  |  |  |  | 493 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE30 | VE30_ES |  | LE0 | VE30_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_ES | VE30_ES (非取樣點) | FEEDER | S45/11/VE30/ES |  |  |  |  | 494 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE31 | VE31_ES |  | LE0 | VE31_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_ES | VE31_ES (非取樣點) | FEEDER | S45/11/VE31/ES |  |  |  |  | 495 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE32 | VE32_ES |  | LE0 | VE32_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_ES | VE32_ES (非取樣點) | FEEDER | S45/11/VE32/ES |  |  |  |  | 496 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE33 | VE33_ES |  | LE0 | VE33_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_ES | VE33_ES (非取樣點) | FEEDER | S45/11/VE33/ES |  |  |  |  | 497 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE34 | VE34_ES |  | LE0 | VE34_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_ES | VE34_ES (非取樣點) | FEEDER | S45/11/VE34/ES |  |  |  |  | 498 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | VE35 | VE35_ES |  | LE0 | VE35_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_ES | VE35_ES (非取樣點) | FEEDER | S45/11/VE35/ES |  |  |  |  | 499 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S45/11/TIE1/D1 |  |  |  |  | 500 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S45/11/TIE2/D1 |  |  |  |  | 501 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.750TE | 750TE (非取樣點) | DTR | S45/69/750/TE0 |  |  |  |  | 502 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.750BE | 750BE (非取樣點) | DTR | S45/69/750/BE0 |  |  |  |  | 503 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.1M_ES | 1M_ES (非取樣點) | DTR | S45/11/M1/ES |  |  |  |  | 504 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.760TE | 760TE (非取樣點) | DTR | S45/69/760/TE0 |  |  |  |  | 505 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.760BE | 760BE (非取樣點) | DTR | S45/69/760/BE0 |  |  |  |  | 506 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.2M_ES | 2M_ES (非取樣點) | DTR | S45/11/M2/ES |  |  |  |  | 507 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.770TE | 770TE (非取樣點) | DTR | S45/69/770/TE0 |  |  |  |  | 508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.770BE | 770BE (非取樣點) | DTR | S45/69/770/BE0 |  |  |  |  | 509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.3M_ES | 3M_ES (非取樣點) | DTR | S45/11/M3/ES |  |  |  |  | 510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.210ES | 210ES (非取樣點) | SC | S45/11/210/ES |  |  |  |  | 511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 220ES | 220ES |  | 220ES | 220ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.220ES | 220ES (非取樣點) | SC | S45/11/220/ES |  |  |  |  | 512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 230ES | 230ES |  | 230ES | 230ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.230ES | 230ES (非取樣點) | SC | S45/11/230/ES |  |  |  |  | 513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 新東SS.810BE | 810BE (非取樣點) | SC | S45/69/810/BE0 |  |  |  |  | 514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 810LE | 810LE |  | 810LE | 810LE | [24 empty] | ADCS_N | [8 empty] | 新東SS.810LE | 810LE (非取樣點) | SC | S45/69/810/LE0 |  |  |  |  | 515 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 新東SS.69B1E | 69B1E (非取樣點) | BUS | S45/69/1BUS/BE1 |  |  |  |  | 516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 517 | NotelDIPoint | [38 empty] | START/STOP | STOP
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新東SS.620_PW1UL | 新營線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 518 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新東SS.620_PW2UL | 新營線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 519 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S45 | 新東SS | 69 | 69kV | 620 | 國聖線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新東SS.620_HCBUL | 新營線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 520 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | PW1UL | 650_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新東SS.650_PW1UL | 白河線(650)PW1_UL(非取樣點) | LINE69 | [5 empty] | 521 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | PW2UL | 650_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新東SS.650_PW2UL | 白河線(650)PW2_UL(非取樣點) | LINE69 | [5 empty] | 522 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S45 | 新東SS | 69 | 69kV | 650 | 白河線(650) |  | HCBUL | 650_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新東SS.650_HCBUL | 白河線(650)HCB_UL(非取樣點) | LINE69 | [5 empty] | 523 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S45 | 新東SS | 0 |  | VE21 | VE21_DS |  | DS1 | VE21_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE21_DS | VE21_DS (非取樣點) | FEEDER | S45/11/VE21/DS |  |  |  |  | 524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE22 | VE22_DS |  | DS1 | VE22_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE22_DS | VE22_DS (非取樣點) | FEEDER | S45/11/VE22/DS |  |  |  |  | 525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE23 | VE23_DS |  | DS1 | VE23_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE23_DS | VE23_DS (非取樣點) | FEEDER | S45/11/VE23/DS |  |  |  |  | 526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE24 | VE24_DS |  | DS1 | VE24_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE24_DS | VE24_DS (非取樣點) | FEEDER | S45/11/VE24/DS |  |  |  |  | 527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE25 | VE25_DS |  | DS1 | VE25_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE25_DS | VE25_DS (非取樣點) | FEEDER | S45/11/VE25/DS |  |  |  |  | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE26 | VE26_DS |  | DS1 | VE26_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE26_DS | VE26_DS (非取樣點) | FEEDER | S45/11/VE26/DS |  |  |  |  | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE27 | VE27_DS |  | DS1 | VE27_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE27_DS | VE27_DS (非取樣點) | FEEDER | S45/11/VE27/DS |  |  |  |  | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE28 | VE28_DS |  | DS1 | VE28_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE28_DS | VE28_DS (非取樣點) | FEEDER | S45/11/VE28/DS |  |  |  |  | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE29 | VE29_DS |  | DS1 | VE29_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE29_DS | VE29_DS (非取樣點) | FEEDER | S45/11/VE29/DS |  |  |  |  | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE30 | VE30_DS |  | DS1 | VE30_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE30_DS | VE30_DS (非取樣點) | FEEDER | S45/11/VE30/DS |  |  |  |  | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE31 | VE31_DS |  | DS1 | VE31_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE31_DS | VE31_DS (非取樣點) | FEEDER | S45/11/VE31/DS |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE32 | VE32_DS |  | DS1 | VE32_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE32_DS | VE32_DS (非取樣點) | FEEDER | S45/11/VE32/DS |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE33 | VE33_DS |  | DS1 | VE33_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE33_DS | VE33_DS (非取樣點) | FEEDER | S45/11/VE33/DS |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE34 | VE34_DS |  | DS1 | VE34_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE34_DS | VE34_DS (非取樣點) | FEEDER | S45/11/VE34/DS |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | VE35 | VE35_DS |  | DS1 | VE35_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.VE35_DS | VE35_DS (非取樣點) | FEEDER | S45/11/VE35/DS |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.391 | 391 (非取樣點) | OTHER | S45/11/390/D1 |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.391E | 391E (非取樣點) | OTHER | S45/11/390/E1 |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.491 | 491 (非取樣點) | OTHER | S45/11/490/D1 |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.491E | 491E (非取樣點) | OTHER | S45/11/490/E1 |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.1M_DS | 1M_DS (非取樣點) | DTR | S45/11/M1/DS |  |  |  |  | 543 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S45/11/M2A/DS |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S45/11/M2B/DS |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S45/11/M2A/ES |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S45/11/M2B/ES |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.3M_DS | 3M_DS (非取樣點) | DTR | S45/11/M3/DS |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 210DS | 210DS |  | 210DS | 210DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.210DS | 210DS (非取樣點) | SC | S45/11/210/DS |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 220DS | 220DS |  | 220DS | 220DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.220DS | 220DS (非取樣點) | SC | S45/11/220/DS |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 230DS | 230DS |  | 230DS | 230DS | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.230DS | 230DS (非取樣點) | SC | S45/11/230/DS |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | TIE1 | TIE1_DS2 |  | DS2 | TIE1_DS2 | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | S45/11/TIE1/D2 |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | TIE2 | TIE2_DS2 |  | DS2 | TIE2_DS2 | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | S45/11/TIE2/D2 |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S45 | 新東SS | 0 |  | 200 | 200 |  | E1 | 201E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.201E | 201E (非取樣點) | TIE | S45/11/TIE2/E1 |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 200 | 200 |  | E2 | 202E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.202E | 202E (非取樣點) | TIE | S45/11/TIE2/E2 |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.101E | 101E (非取樣點) | TIE | S45/11/TIE1/E1 |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | DDCS3_1 | [8 empty] | 新東SS.102E | 102E (非取樣點) | TIE | S45/11/TIE1/E2 |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 11B1E | 11B1E |  | BE1 | 11B1E | [24 empty] | ADCS_N | [8 empty] | 新東SS.11B1E | 11B1E (非取樣點) | BUS | S45/11/1BUS/BE1 |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 11B2E | 11B2E |  | BE2 | 11B2E | [24 empty] | ADCS_N | [8 empty] | 新東SS.11B2E | 11B2E (非取樣點) | BUS | S45/11/2BUS/BE2 |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 11B2BE | 11B2BE |  | B2BE0 | 11B2BE | [24 empty] | ADCS_N | [8 empty] | 新東SS.11B2BE | 11B2BE (非取樣點) | BUS | S45/11/2BUS/BE0 |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S45 | 新東SS | 0 |  | 11B3E | 11B3E |  | BE3 | 11B3E | [24 empty] | ADCS_N | [8 empty] | 新東SS.11B3E | 11B3E (非取樣點) | BUS | S45/11/3BUS/BE3 |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo