## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV #1BUS | KV | 69KV#1BUS PT | kV_-90_90(-2000_2000) | aaa | B2/S47_A1 | [8 empty] | 永華SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV #2BUS | KV | 69KV#2BUS PT | kV_-90_90(-2000_2000) | aab | B2/S47_A1 | [8 empty] | 永華SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S47 | 永華SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | 11KV #1 BUS | KV | 一號 BUS PT | kV_-9_9(-2000_2000) | aaa | B2/S47_D1 | [8 empty] | 永華SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0059 |  |  | 1-BB |  |  | 11KV #2A BUS | KV | 2A BUS PT | kV_-9_9(-2000_2000) | aba | B2/S47_D1 | [8 empty] | 永華SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 11 | 11kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | 11KV #3 BUS | KV | 三號 BUS PT | kV_-9_9(-2000_2000) | ada | B2/S47_D1 | [8 empty] | 永華SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 69 | 69kV | 69B1E | 69B1E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/1BUS | [13 empty] | aaaz | B2/S47_A1 | [8 empty] | 永華SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV #1BUS | UVA (27B1) | 衡相監視 (Bus1欠壓) |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 69KV #1BUS RY | 87 B1A | 69KV #1BUS RY 87 B1 |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0302 |  | 0038 | 1-32-14 |  | 1-26 | 69KV #1BUS | 87 B1S | 69KV #1 BUS 87RY U/L |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#1BUS_87UL | 69#1BUS87U/L | OTHER |  |  |  |  | CDC | 10 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 69B2E | 69B2E |  | BE1 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/2BUS | [13 empty] | aaaz | B2/S47_A1 | [8 empty] | 永華SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 11 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV #2BUS | UVA (27B2) | 衡相監視 (Bus2欠壓) |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 69KV #2BUS RY | 87 B2A | 69KV #2BUS RY 87 B2 |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0303 |  | 0039 | 1-32-15 |  | 1-27 | 69KV #2BUS | 87 B2S | 69KV #2 BUS 87RY U/L |  |  | B2/S47_A1 | [8 empty] | 永華SS.69#2BUS_87UL | 69#2BUS87U/L | OTHER |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 640 | MW | 新塭-永華線 | MW_-120_120(-2000_2000) |  | B2/S47_A1 | [8 empty] | 永華SS.640_MW | 新塭線 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 640 | MVAR | 新塭-永華線 | MVAR_-120_120(-2000_2000) |  | B2/S47_A1 | [8 empty] | 永華SS.640_MVAR | 新塭線 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 640 | MWH(+) | 新塭-永華線 |  |  | B2/S47_A1 | [15 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 630 | MW | 永華-學甲線 | MW_-96_96(-2000_2000) |  | B2/S47_A1 | [8 empty] | 永華SS.630_MW | 學甲線 MW | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 630 | MVAR | 永華-學甲線 | MVAR_-96_96(-2000_2000) |  | B2/S47_A1 | [8 empty] | 永華SS.630_MVAR | 學甲線 MVAR | LINE69 |  |  |  |  | CDC | 19 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 630 | MWH(+) | 永華-學甲線 |  |  | B2/S47_A1 | [15 empty] | CDC | 20 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 650 | MW | 69KV備一線 |  |  | B2/S47_A1 | [15 empty] | CDC | 21 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 650 | MVAR | 69KV備一線 |  |  | B2/S47_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 650 | MWH(+) | 備用 |  |  | B2/S47_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 23 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 640 | PHA | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_PHA | 新塭線(640) 相間RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 640 | GDA | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_GDA | 新塭線(640) 接地RY | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 640 | 87A | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_87A | 新塭線(640) 87RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | Locate Empty |  |  |  |  | B2/S47_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 27 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 630 | PHA | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_PHA | 學甲線(630) 相間RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 630 | GDA | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_GDA | 學甲線(630) 接地RY | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 630 | 87A | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_87A | 學甲線(630) 87RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | Locate Empty |  |  |  |  | B2/S47_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 31 | DI_LINE69(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 640 | 87 U/L | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_87UL | 新塭線(640) 87RY U/L | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 630 | 87 U/L | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_87UL | 學甲線(630) 87RY U/L | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S32S47/T2 |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 640 | CB ON/OFF | 新塭-永華線 |  | aaba | B2/S47_A1 | [8 empty] | 永華SS.640_CB | 640(新塭線) CB | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L/S47S43/T1 |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 630 | CB ON/OFF | 永華-學甲線 |  | aada | B2/S47_A1 | [8 empty] | 永華SS.630_CB | 630(學甲線) CB | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0016 | 1-38-00 | 1-38-01 | 1-10 | 641 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.641_DS | 641(新塭線) DS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0017 | 1-38-02 | 1-38-03 | 1-11 | 642 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.642_DS | 642(新塭線) DS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | DS1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0020 | 1-38-08 | 1-38-09 | 1-14 | 631 | ABS ON | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.631_DS | 631(學甲線) DS | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | DS2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0021 | 1-38-10 | 1-38-11 | 1-15 | 632 | ABS ON | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.632_DS | 632(學甲線) DS | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0018 | 1-38-04 | 1-38-05 | 1-12 | 643 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.643_DS | 643(新塭線) DS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | E3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0390 | 391 | 0019 | 1-38-06 | 1-38-07 | 1-13 | 643E | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.643E_ES | 643E(新塭線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | DS3 | 633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0396 | 397 | 0022 | 1-38-12 | 1-38-13 | 1-16 | 633 | ABS ON | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.633_DS | 633(學甲線) DS | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | E3 | 633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0398 | 399 | 0023 | 1-38-14 | 1-38-15 | 1-17 | 633E | ABS ON | 永華-學甲線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.633E_ES | 633E(學甲線) ES | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 46 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 47 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | F1 PH RY | PHA | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_PHA | 11KV永一線(VI21) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | F1 GD RY | GDA | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_GDA | 11KV永一線(VI21) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0062 | 1-33-06 |  | 1-3E | F1 CB | 79 U/L | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_79UL | 11KV永一線(VI21) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | F1 LCO | ADJ(U/L) | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_ADJ | 11KV永一線(VI21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | F2 PH RY | PHA | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_PHA | 11KV永二線(VI22) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | F2 GD RY | GDA | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_GDA | 11KV永二線(VI22) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0063 | 1-33-07 |  | 1-3F | F2 CB | 79 U/L | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_79UL | 11KV永二線(VI22) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | F2 LCO | ADJ(U/L) | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_ADJ | 11KV永二線(VI22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | F3 PH RY | PHA | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_PHA | 11KV永三線(VI23) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | F3 GD RY | GDA | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_GDA | 11KV永三線(VI23) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0064 | 1-33-08 |  | 1-40 | F3 CB | 79 U/L | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_79UL | 11KV永三線(VI23) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | F3 LCO | ADJ(U/L) | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_ADJ | 11KV永三線(VI23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | F4 PH RY | PHA | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_PHA | 11KV永正線(VI24) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | F4 GD RY | GDA | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_GDA | 11KV永正線(VI24) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0065 | 1-33-09 |  | 1-41 | F4 CB | 79 U/L | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_79UL | 11KV永正線(VI24) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | F4 LCO | ADJ(U/L) | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_ADJ | 11KV永正線(VI24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | F5 PH RY | PHA | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_PHA | 11KV永五線(VI25) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | F5 GD RY | GDA | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_GDA | 11KV永五線(VI25) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0066 | 1-33-10 |  | 1-42 | F5 CB | 79 U/L | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_79UL | 11KV永五線(VI25) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | F5 LCO | ADJ(U/L) | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_ADJ | 11KV永五線(VI25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | F6 PH RY | PHA | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_PHA | 11KV永六線(VI26) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | F6 GD RY | GDA | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_GDA | 11KV永六線(VI26) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0081 | 1-34-06 |  | 1-51 | F6 CB | 79 U/L | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_79UL | 11KV永六線(VI26) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | F6 LCO | ADJ(U/L) | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_ADJ | 11KV永六線(VI26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0F-01 |  |  | F7 PH RY | PHA | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_PHA | 11KV永七線(VI27) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0122 |  |  | 1-0F-02 |  |  | F7 GD RY | GDA | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_GDA | 11KV永七線(VI27) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0082 | 1-34-07 |  | 1-52 | F7 CB | 79 U/L | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_79UL | 11KV永七線(VI27) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | F7 LCO | ADJ(U/L) | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_ADJ | 11KV永七線(VI27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | F8 PH RY | PHA | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_PHA | 11KV永八線(VI28) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | F8 GD RY | GDA | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_GDA | 11KV永八線(VI28) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0083 | 1-34-08 |  | 1-53 | F8 CB | 79 U/L | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_79UL | 11KV永八線(VI28) 79RY U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | F8 LCO | ADJ(U/L) | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_ADJ | 11KV永八線(VI28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | F9 PH RY | PHA | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_PHA | 11KV永九線(VI29) 相間RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | F9 GD RY | GDA | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_GDA | 11KV永九線(VI29) 接地RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0084 | 1-34-09 |  | 1-54 | F9 CB | 79 U/L | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_79UL | 11KV永九線(VI29) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | F9 LCO | ADJ(U/L) | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_ADJ | 11KV永九線(VI29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F10 PH RY | PHA | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_PHA | 11KV永十線(VI30) 相間RY | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | F10 GD RY | GDA | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_GDA | 11KV永十線(VI30) 接地RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0085 | 1-34-10 |  | 1-55 | F10 CB | 79 U/L | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_79UL | 11KV永十線(VI30) 79RY U/L | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | F10 LCO | ADJ(U/L) | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_ADJ | 11KV永十線(VI30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-04 |  |  | F11 PH RY | PHA | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_PHA | 11KV永忠線(VI31) 相間RY | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F11 GD RY | GDA | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_GDA | 11KV永忠線(VI31) 接地RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0100 | 1-35-06 |  | 1-64 | F11 CB | 79 U/L | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_79UL | 11KV永忠線(VI31) 79RY U/L | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | F11 LCO | ADJ(U/L) | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_ADJ | 11KV永忠線(VI31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | F12 PH RY | PHA | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_PHA | 11KV永孝線(VI32) 相間RY | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | F12 GD RY | GDA | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_GDA | 11KV永孝線(VI32) 接地RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0101 | 1-35-07 |  | 1-65 | F12 CB | 79 U/L | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_79UL | 11KV永孝線(VI32) 79RY U/L | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | F12 LCO | ADJ(U/L) | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_ADJ | 11KV永孝線(VI32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | F13 PH RY | PHA | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_PHA | 11KV永仁線(VI33) 相間RY | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | F13 GD RY | GDA | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_GDA | 11KV永仁線(VI33) 接地RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0102 | 1-35-08 |  | 1-66 | F13 CB | 79 U/L | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_79UL | 11KV永仁線(VI33) 79RY U/L | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | F13 LCO | ADJ(U/L) | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_ADJ | 11KV永仁線(VI33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | F14 PH RY | PHA | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_PHA | 11KV永愛線(VI34) 相間RY | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F14 GD RY | GDA | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_GDA | 11KV永愛線(VI34) 接地RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0103 | 1-35-09 |  | 1-67 | F14 CB | 79 U/L | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_79UL | 11KV永愛線(VI34) 79RY U/L | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | F14 LCO | ADJ(U/L) | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_ADJ | 11KV永愛線(VI34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | F15 PH RY | PHA | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_PHA | 11KV永信線(VI35) 相間RY | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F15 GD RY | GDA | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_GDA | 11KV永信線(VI35) 接地RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0104 | 1-35-10 |  | 1-68 | F15 CB | 79 U/L | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_79UL | 11KV永信線(VI35) 79RY U/L | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | F15 LCO | ADJ(U/L) | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_ADJ | 11KV永信線(VI35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VI21/T1 |  |  | 0095 |  | 0053 | 1-0B-07 |  | 1-35 | F1 CB | CB ON/OFF | 永一線 |  | aaab | B2/S47_D1 | [8 empty] | 永華SS.VI21_CB | VI21(11KV永一線) CB | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI21_DS | VI21_DS (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI21_ES | VI21_ES (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VI22/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | F2 CB | CB ON/OFF | 永二線 |  | aabb | B2/S47_D1 | [8 empty] | 永華SS.VI22_CB | VI22(11KV永二線) CB | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI22_DS | VI22_DS (非取樣點) | FEEDER | [5 empty] | 112 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI22_ES | VI22_ES (非取樣點) | FEEDER | [5 empty] | 113 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VI23/T1 |  |  | 0101 |  | 0055 | 1-0C-05 |  | 1-37 | F3 CB | CB ON/OFF | 永三線 |  | aadb | B2/S47_D1 | [8 empty] | 永華SS.VI23_CB | VI23(11KV永三線) CB | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI23_DS | VI23_DS (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI23_ES | VI23_ES (非取樣點) | FEEDER | [5 empty] | 116 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VI24/T1 |  |  | 0104 |  | 0056 | 1-0D-00 |  | 1-38 | F4 CB | CB ON/OFF | 永正線 |  | aaeb | B2/S47_D1 | [8 empty] | 永華SS.VI24_CB | VI24(11KV永正線) CB | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI24_DS | VI24_DS (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI24_ES | VI24_ES (非取樣點) | FEEDER | [5 empty] | 119 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BUS | L/VI25/T1 |  |  | 0107 |  | 0057 | 1-0D-03 |  | 1-39 | F5 CB | CB ON/OFF | 永五線 |  | aafb | B2/S47_D1 | [8 empty] | 永華SS.VI25_CB | VI25(11KV永五線) CB | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI25_DS | VI25_DS (非取樣點) | FEEDER | [5 empty] | 121 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI25_ES | VI25_ES (非取樣點) | FEEDER | [5 empty] | 122 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VI26/T1 |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | F6 CB | CB ON/OFF | 永六線 |  | abab | B2/S47_D1 | [8 empty] | 永華SS.VI26_CB | VI26(11KV永六線) CB | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI26_DS | VI26_DS (非取樣點) | FEEDER | [5 empty] | 124 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI26_ES | VI26_ES (非取樣點) | FEEDER | [5 empty] | 125 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VI27/T1 |  |  | 0120 |  | 0073 | 1-0F-00 |  | 1-49 | F7 CB | CB ON/OFF | 永七線 |  | abcb | B2/S47_D1 | [8 empty] | 永華SS.VI27_CB | VI27(11KV永七線) CB | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI27_DS | VI27_DS (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI27_ES | VI27_ES (非取樣點) | FEEDER | [5 empty] | 128 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABUS | L/VI28/T1 |  |  | 0123 |  | 0074 | 1-0F-03 |  | 1-4A | F8 CB | CB ON/OFF | 永八線 |  | abdb | B2/S47_D1 | [8 empty] | 永華SS.VI28_CB | VI28(11KV永八線) CB | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI28_DS | VI28_DS (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI28_ES | VI28_ES (非取樣點) | FEEDER | [5 empty] | 131 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBUS | L/VI29/T1 |  |  | 0126 |  | 0075 | 1-0F-06 |  | 1-4B | F9 CB | CB ON/OFF | 永九線 |  | acab | B2/S47_D1 | [8 empty] | 永華SS.VI29_CB | VI29(11KV永九線) CB | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI29_DS | VI29_DS (非取樣點) | FEEDER | [5 empty] | 133 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI29_ES | VI29_ES (非取樣點) | FEEDER | [5 empty] | 134 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBUS | L/VI30/T1 |  |  | 0129 |  | 0076 | 1-10-01 |  | 1-4C | F10 CB | CB ON/OFF | 永十線 |  | accb | B2/S47_D1 | [8 empty] | 永華SS.VI30_CB | VI30(11KV永十線) CB | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI30_DS | VI30_DS (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI30_ES | VI30_ES (非取樣點) | FEEDER | [5 empty] | 137 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VI31/T1 |  |  | 0139 |  | 0092 | 1-11-03 |  | 1-5C | F11 CB | CB ON/OFF | 永忠線 |  | adab | B2/S47_D1 | [8 empty] | 永華SS.VI31_CB | VI31(11KV永忠線) CB | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI31_DS | VI31_DS (非取樣點) | FEEDER | [5 empty] | 139 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI31_ES | VI31_ES (非取樣點) | FEEDER | [5 empty] | 140 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VI32/T1 |  |  | 0142 |  | 0093 | 1-11-06 |  | 1-5D | F12 CB | CB ON/OFF | 永孝線 |  | adbb | B2/S47_D1 | [8 empty] | 永華SS.VI32_CB | VI32(11KV永孝線) CB | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI32_DS | VI32_DS (非取樣點) | FEEDER | [5 empty] | 142 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI32_ES | VI32_ES (非取樣點) | FEEDER | [5 empty] | 143 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VI33/T1 |  |  | 0145 |  | 0094 | 1-12-01 |  | 1-5E | F13 CB | CB ON/OFF | 永仁線 |  | adcb | B2/S47_D1 | [8 empty] | 永華SS.VI33_CB | VI33(11KV永仁線) CB | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI33_DS | VI33_DS (非取樣點) | FEEDER | [5 empty] | 145 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI33_ES | VI33_ES (非取樣點) | FEEDER | [5 empty] | 146 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VI34/T1 |  |  | 0148 |  | 0095 | 1-12-04 |  | 1-5F | F14 CB | CB ON/OFF | 永愛線 |  | adeb | B2/S47_D1 | [8 empty] | 永華SS.VI34_CB | VI34(11KV永愛線) CB | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI34_DS | VI34_DS (非取樣點) | FEEDER | [5 empty] | 148 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI34_ES | VI34_ES (非取樣點) | FEEDER | [5 empty] | 149 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BUS | L/VI35/T1 |  |  | 0151 |  | 0096 | 1-12-07 |  | 1-60 | F15 CB | CB ON/OFF | 永信線 |  | adfb | B2/S47_D1 | [8 empty] | 永華SS.VI35_CB | VI35(11KV永信線) CB | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI35_DS | VI35_DS (非取樣點) | FEEDER | [5 empty] | 151 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.VI35_ES | VI35_ES (非取樣點) | FEEDER | [5 empty] | 152 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 600 | A | TIE (600)R相電流 | A_-1200_1200(-2000_2000) |  | B2/S47_A1 | [8 empty] | 永華SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 153 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1 TIE R相電流 | A1 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 154 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1 TIE S相電流 | A2 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 155 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1 TIE T相電流 | A3 | 一號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 156 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2 TIE R相電流 | A1 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 157 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2 TIE S相電流 | A2 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 158 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2 TIE T相電流 | A3 | 二號 TIE 11KV | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 159 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1BUS | B/2BUS |  |  | 0034 |  | 0007 | 1-04-02 |  | 1-07 | 600 | TIE | TIE(600)CB |  | aafz | B2/S47_A1 | [8 empty] | 永華SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 160 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 600 | PHA(1) | TIE(600) CB 67(1) RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | TIE |  |  |  |  | CDC | 161 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | 51NA |  | B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 600 | GDA(1) | TIE(600) CB 67N(1) RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | TIE |  |  |  |  | CDC | 162 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2ABUS |  |  | 0113 |  | 0058 | 1-0E-01 |  | 1-3A | #1 TIE CB | CB ON/OFF | #1 TIE CB |  | zzzz | B2/S47_D1 | [8 empty] | 永華SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 163 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #1 TIE PH RY | PHA | #1 TIE CB |  |  | B2/S47_D1 | [8 empty] | 永華SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 164 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 TIE GD RY | GDA | #1 TIE CB |  |  | B2/S47_D1 | [8 empty] | 永華SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 165 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BBUS | B/3BUS |  |  | 0135 |  | 0077 | 1-10-07 |  | 1-4D | #2 TIE CB | CB ON/OFF | #2 TIE CB |  | zzzz | B2/S47_D1 | [8 empty] | 永華SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 166 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | #2 TIEPH RY | PHA | #2 TIE CB |  |  | B2/S47_D1 | [8 empty] | 永華SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 167 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2 TIEGD RY | GDA | #2 TIE CB |  |  | B2/S47_D1 | [8 empty] | 永華SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 168 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | 433 | 0042 | 1-3B-00 | 1-3B-01 | 1-2A | 601 | ABS ON | 600 TIE (601) ABS |  |  | B2/S47_A1 | [8 empty] | 永華SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 169 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0043 | 1-3B-02 | 1-3B-03 | 1-2B | 602 | ABS ON | 600 TIE (602) ABS |  |  | B2/S47_A1 | [8 empty] | 永華SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 170 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 171 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 172 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 MTR | MW | 一號主變 | MW_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 173 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 MTR | MVAR | 一號主變 | MVAR_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 174 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 MTR R電流 | A1 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 175 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 MTR S電流 | A2 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 176 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 MTR T電流 | A3 | 一號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 177 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 MTR | MW | 二號主變 | MW_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 178 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 MTR | MVAR | 二號主變 | MVAR_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 179 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 MTR R電流 | A1 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 180 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 MTR S電流 | A2 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 181 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 MTR T電流 | A3 | 二號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 182 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 MTR | MW | 三號主變 | MW_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 183 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 MTR | MVAR | 三號主變 | MVAR_-36_36(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 184 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 MTR R電流 | A1 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 185 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 MTR S電流 | A2 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 186 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 MTR T電流 | A3 | 三號主變二次側 | A_-2000_2000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 187 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 MTR | 油溫 | 一號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 188 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 MTR | 線溫 | 一號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 189 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0059 | 1-9B |  | 1-3B | #1 MTR | TAP | 一號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 190 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1TR | MWH | 一號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 191 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1TR | MVARH(+) | 一號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 192 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 MTR | 油溫 | 二號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 193 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 MTR | 線溫 | 二號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 194 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 MTR | TAP | 二號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 195 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2TR | MWH | 二號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 196 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 2MTR | #2MTR |  | MVARH_M |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2TR | MVARH(+) | 二號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 197 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 MTR | 油溫 | 三號主變油溫 | OIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 198 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 MTR | 線溫 | 三號主變線溫 | COIL_-120_120(-2000_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 199 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 MTR | TAP | 三號主變OLTC | TAP_-4.5_12.5(0_2000) |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 200 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3TR | MWH | 三號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 201 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3TR | MVARH(+) | 三號主變 |  |  | B1/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 202 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/1MTR |  | 0001 |  | 0050 | 1-00-01 |  | 1-32 | 750 | CB ON/OFF | 一號主變一次側 |  | aacb | B3/S47_D1 | [8 empty] | 永華SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 203 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 204 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 205 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/2MTR |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | 760 | CB ON/OFF | 二號主變一次側 |  | aaeb | B3/S47_D1 | [8 empty] | 永華SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 206 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 207 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 208 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | T/3MTR |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | 770 | CB ON/OFF | 三號主變一次側 |  | aaib | B3/S47_D1 | [8 empty] | 永華SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 209 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 210 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S47_D1 | [8 empty] | 永華SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 211 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB | 1M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0007 |  | 0051 | 1-00-07 |  | 1-33 | #1 MTR | CB ON/OFF | 一號主變二次側 |  | aaca | B2/S47_D1 | [8 empty] | 永華SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 212 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | CB | 2MA | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | T/2MTR |  |  | 0016 |  | 0069 | 1-02-00 |  | 1-45 | #2 MTR A | CB ON/OFF | 二號主變二次側(A) |  | abba | B2/S47_D1 | [8 empty] | 永華SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 213 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | CB | 2MB | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | T/2MTR |  |  | 0017 |  | 0070 | 1-02-01 |  | 1-46 | #2 MTR B | CB ON/OFF | 二號主變二次側(B) |  | acba | B2/S47_D1 | [8 empty] | 永華SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 214 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB | 3M | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0028 |  | 0089 | 1-03-04 |  | 1-59 | #3 MTR | CB ON/OFF | 三號主變二次側 |  | adda | B2/S47_D1 | [8 empty] | 永華SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 215 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 750 | PHA | 一號主變 51 RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 216 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 750 | GDA | 一號主變 51N RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 217 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1 MTR | 51ZA | 一號主變 51Z RY |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 218 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1 MTR | 87A | 一號主變差動電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 219 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1 MTR | 87 LS | 一號 主變87 RY 使用/閉鎖 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 220 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  | 0067 | 1-0E-04 |  | 1-43 | Locate Empty |  |  |  |  | ELEM/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 221 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 760 | PHA | 二號主變 51 RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 222 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 760 | GDA | 二號主變 51N RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 223 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2 MTR | 51ZA | 二號主變 51Z RY |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 224 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2 MTR | 87A | 二號主變差動電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 225 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2 MTR | 87 LS | 二號 主變87 RY 使用/閉鎖 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 226 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  | 0086 | 1-11-02 |  | 1-56 | Locate Empty |  |  |  |  | ELEM/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 227 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 770 | PHA | 三號主變 51 RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 228 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 770 | GDA | 三號主變 51N RY |  |  | B3/S47_D1 | [8 empty] | 永華SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 229 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3 MTR | 51ZA | 三號主變 51Z RY |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 230 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3MTR | 87A | 三號主變差動電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 231 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3 MTR | 87 LS | 三號 主變87 RY 使用/閉鎖 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 232 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  | 0105 | 1-13-05 |  | 1-69 | Locate Empty |  |  |  |  | ELEM/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 233 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1 MTR | PHA | 一號主變二次側 51 RY |  |  | B2/S47_D1 | [8 empty] | 永華SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 234 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #1 MTR | TRA | 一號主變重故障 |  | a | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 235 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1 MTR | TRF | 一號主變輕故障 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 236 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1 MTR | S/L | 一號主變 OLTC(中心/現場) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 237 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0060 | 1-33-05 |  | 1-3C | #1 MTR | A/M | 一號主變 OLTC (自動/手動) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 238 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2 MTR A | PHA | 二號主變二次(A)51 RY |  |  | B2/S47_D1 | [8 empty] | 永華SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 239 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | #2 MTR B | PHA | 二號主變二次(B)51 RY |  |  | B2/S47_D1 | [8 empty] | 永華SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 240 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #2 MTR | TRA | 二號主變重故障 |  | a | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 241 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2 MTR | TRF | 二號主變輕故障 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 242 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2 MTR | S/L | 二號主變 OLTC (中心/現場) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 243 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2 MTR | A/M | 二號主變 OLTC (自動/手動) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 244 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #3 MTR | PHA | 三號主變二次51 RY |  |  | B2/S47_D1 | [8 empty] | 永華SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 245 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0336 |  |  | 1-35-00 |  |  | #3 MTR | 3TRA | 三號主變重故障 |  | a | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 246 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3 MTR | 3TRF | 三號主變輕故障 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 247 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3 MTR | S/L | 三號主變 OLTC(中心/現場) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 248 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3 MTR | A/M | 三號主變 OLTC (自動/手動) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 249 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0368 | 369 | 0044 | 1-37-00 | 1-37-01 | 1-2C | 751 | ABS ON | 一號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 250 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0370 | 371 | 0045 | 1-37-02 | 1-37-03 | 1-2D | 752 | ABS ON | 一號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 251 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0372 | 373 | 0046 | 1-37-04 | 1-37-05 | 1-2E | 761 | ABS ON | 二號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 252 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0374 | 375 | 0047 | 1-37-06 | 1-37-07 | 1-2F | 762 | ABS ON | 二號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 253 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0376 | 377 | 0048 | 1-37-08 | 1-37-09 | 1-30 | 771 | ABS ON | 三號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.771_DS | 771(#3MTR) DS | DTR |  |  |  |  | CDC | 254 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0378 | 379 | 0049 | 1-37-10 | 1-37-11 | 1-31 | 772 | ABS ON | 三號主變 |  |  | B3/S47_D1 | [8 empty] | 永華SS.772_DS | 772(#3MTR) DS | DTR |  |  |  |  | CDC | 255 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | 1M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 256 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1 MTR | 96A | 一號主變 96PA 電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 257 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1 MTR | TAPA | 一號主變TAP遲滯 (48TX) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 258 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #1MTR | 1ACF | 一號主變AC電源失效 (27欠壓) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 259 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | DS | 2MA(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 260 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | ES | 2MA_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 261 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | DS | 2MB(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 262 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | ES | 2MB_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 263 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2 MTR | 96A | 二號主變 96D,63A RY |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_96A | #2MTR 96P RY | DTR |  |  |  |  | CDC | 264 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2 MTR | TAPA | 二號主變TAP遲滯 (48TX) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 265 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0333 |  |  | 1-34-13 |  |  | #2MTR | 2ACF | 二號主變AC電源失效 (27欠壓) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 266 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | 3M(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 267 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 96PA | 96A | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3MTR | 96A | 三號主變 96D,63A RY |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_96A | #3MTR 96P RY | DTR |  |  |  |  | CDC | 268 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3 MTR | TAPA | 三號主變TAP遲滯 (48TX) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 269 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0367 |  |  | 1-36-15 |  |  | #3MTR | 3ACF | 三號主變AC電源失效 (27欠壓) |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 270 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1BUS | B/2BUS | C/1SC |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 810 | CB ON/OFF | SC 69KV |  | aaha | B2/S47_A1 | [8 empty] | 永華SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 271 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.810ES | 810ES (非取樣點) | SC | [5 empty] | 272 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/1BUS | C/1SC |  |  | 0110 |  | 0052 | 1-0D-06 |  | 1-34 | #1 11KV SC | CB ON/OFF | #1 11KV SC |  | aagb | B2/S47_D1 | [8 empty] | 永華SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 273 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0061 | 1-33-11 |  | 1-3D | #1 SC | A/M | 一號 SC 乏控器 (自動/手動) |  |  | B2/S47_D1 | [8 empty] | 永華SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 274 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 275 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/2BBUS | C/2SC |  |  | 0132 |  | 0071 | 1-10-04 |  | 1-47 | #2 11KV SC | CB ON/OFF | #2 11KV SC |  | acdb | B2/S47_D1 | [8 empty] | 永華SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 276 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0080 | 1-34-11 |  | 1-50 | #2 SC | A/M | 二號 SC 乏控器 (自動/手動) |  |  | B2/S47_D1 | [8 empty] | 永華SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 277 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 278 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrA | B/3BUS | C/3SC |  |  | 0154 |  | 0091 | 1-13-02 |  | 1-5B | #3 11KV SC | CB ON/OFF | #3 11KV SC |  | adgb | B2/S47_D1 | [8 empty] | 永華SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 279 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0099 | 1-35-11 |  | 1-63 | #3 SC | A/M | 三號 SC 乏控器 (自動/手動) |  |  | B2/S47_D1 | [8 empty] | 永華SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 280 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Low | 1 |  |  | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 281 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0380 | 381 | 0040 | 1-37-12 | 1-37-13 | 1-28 | 811 | ABS ON | 69KVSC (備用) |  |  | B2/S47_A1 | [8 empty] | 永華SS.811_DS | 811(69KV #1SC) DS | SC |  |  |  |  | CDC | 282 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0382 | 383 | 0041 | 1-37-14 | 1-37-15 | 1-29 | 812 | ABS ON | 69KVSC (備用) |  |  | B2/S47_A1 | [8 empty] | 永華SS.812_DS | 812(69KV #1SC) DS | SC |  |  |  |  | CDC | 283 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 810 | PHA GDA | SC 69KV 51 51N RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 284 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 810 | UVA OVA | SC 69KV 27 59N RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 285 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | #1 SC5151NRY | SCA | #1 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 286 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | #1 SC2759RY | UVA | #1 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 287 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | #2 SC5151NRY | SCA | #2 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 288 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | #2 SC2759RY | UVA | #2 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 289 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | #3SC5151NRY | SCA | #3 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 290 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | #3SC2759RY | UVA | #3 11KV SC |  |  | B2/S47_D1 | [8 empty] | 永華SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 291 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 292 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 293 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 294 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 295 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 296 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 297 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 298 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 299 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 300 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 永華SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 301 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | RTU | RTU |  | RTU_R_L | R_L | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 302 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 其他重故障 |  | 其他重故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 303 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  | 其他輕故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 304 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 水氣霧釋放動作 |  | 無人化門禁(1) |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 305 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 控制室旁 |  | 所内淹水高水位 |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化門禁(2) | 所內淹水高水位 | OTHER |  |  |  |  | CDC | 306 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 控制室旁 |  | 所内淹水低水位 |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化門禁(3) | 所內淹水低水位 | OTHER |  |  |  |  | CDC | 307 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | 水氣霧系統警報 |  | 無人化防盜(1) |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化防盜(1) | 無人化防盜(1) | OTHER |  |  |  |  | CDC | 308 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0275 |  |  | 1-31-03 |  |  | 水氣霧系統警報 |  | 無人化防盜(2) |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化防盜(2) | 無人化防盜(2) | OTHER |  |  |  |  | CDC | 309 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | MCSG偵煙警報 |  | 無人化防盜(3) |  |  | B3/S47_D1 | [8 empty] | 永華SS.無人化防盜(3) | 無人化防盜(3) | OTHER |  |  |  |  | CDC | 310 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0106 | 1-30-06 |  | 1-6A | 所內開關場 | FL-A ON/OFF | 所內開關場照明(A) |  |  | B3/S47_D1 | [8 empty] | 永華SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 311 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明自動手動 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0107 | 1-30-07 |  | 1-6B | 所外路燈 | FL-B ON/OFF | 所外路燈照明(B) |  |  | B3/S47_D1 | [8 empty] | 永華SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | CO2系統警報 |  | CO2系統警報 |  |  | B3/S47_D1 | [8 empty] | 永華SS.火災警報(2) | CO2警報 | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | CO2系統故障 |  | CO2系統故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.火災警報(3) | CO2故障 | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1S |  | 所內電源第一組 |  |  | B3/S47_D1 | [8 empty] | 永華SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2S |  | 所內電源第二組 |  |  | B3/S47_D1 | [8 empty] | 永華SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 所內電源ACBA |  | 所內電源ACBA |  |  | B3/S47_D1 | [8 empty] | 永華SS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內電源 | ACB A | 所內電源欠壓 |  |  | B3/S47_D1 | [8 empty] | 永華SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC接地 | DCE | 直流電源接地故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB | CBA | 69KV 斷路器重故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB | CBF | 69KV斷路器輕故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB | CBA | 11KV 斷路器重故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB | CBF | 11KV 斷路器輕故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  | 洩油池泵警報 |  |  | B3/S47_D1 | [8 empty] | 永華SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS | ABS 89A | ABS NFB跳脫警報 |  |  | B3/S47_D1 | [8 empty] | 永華SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB跳脫監視 | DCA | NFB跳脫監視 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | 通訊設備 |  | 通訊設備AC故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0349 |  |  | 1-35-13 |  |  | 通訊設備 |  | 通訊設備光纖主故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0350 |  |  | 1-35-14 |  |  | 通訊設備 |  | 通訊設備光纖次故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 通訊PCM警報 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0351 |  |  | 1-35-15 |  |  | 通訊設備 |  | 博碼調變器PCM故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火災警報 | FIRE | 火警警報 |  |  | B3/S47_D1 | [8 empty] | 永華SS.火災警報(1) | 火警 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | 直流充電機 | 故障(CHG1) | 直流充電機故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 通訊充電機 | 故障(CHG2) | 通訊充電機故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | SC | SC 60A | SC 60A |  |  | B3/S47_D1 | [8 empty] | 永華SS.11KV_SC_60A | 11KV電容器組 60RY | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Door4 | 門禁小門 | Element | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 無人化門禁 | 大門 ON/OFF | 大門開關 |  |  | B3/S47_D1 | [8 empty] | 永華SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Water3 | 變電所水位高 | Element | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所水位高 | HA | 變電所水位高 |  |  | B3/S47_D1 | [8 empty] | 永華SS.變電所水位高 | 變電所水位高 | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Burglar | 安全監控 | Element | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  | 安全監控 |  |  | B3/S47_D1 | [8 empty] | 永華SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-32-10 |  |  | RTU DC故障 |  | RTU DC故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 緊急發電機啟動 |  | 緊急發電機啟動 |  |  | B3/S47_D1 | [8 empty] | 永華SS.緊急發電機啟動 | 緊急發電機啟動 | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Water1 | 水位警報_1 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0334 |  |  | 1-34-14 |  |  | Locate Empty | 水位警報 1 | 水位警報 1 |  |  | B3/S47_D1 | [8 empty] | 永華SS.水位警報_1 | 水位警報 1 | OTHER |  |  |  |  | CDC | 340 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | Water2 | 水位警報_2 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0335 |  |  | 1-34-15 |  |  | Locate Empty | 水位警報 2 | 水位警報 2 |  |  | B3/S47_D1 | [8 empty] | 永華SS.水位警報_2 | 水位警報 2 | OTHER |  |  |  |  | CDC | 341 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | FDR_60A | #1SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | #1 SC | #1 SC60A | #1 SC60A |  |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | FDR_60A | #2SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | #2 SC | #2 SC60A | #2 SC60A |  |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_#2SC_60A | 11KV #2SC 60A | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | FDR_60A | #3SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | #3 SC | #3 SC60A | #3 SC60A |  |  | B2/S47_D1 | [8 empty] | 永華SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER |  |  |  |  | CDC | 344 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F1 81 RY | 81A | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_81A/S | 11KV永一線(VI21) 81RY | OTHER |  |  |  |  | CDC | 345 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F2 81 RY | 81A | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_81A/S | 11KV永二線(VI22) 81RY | OTHER |  |  |  |  | CDC | 346 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F3 81 RY | 81A | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_81A/S | 11KV永三線(VI23) 81RY | OTHER |  |  |  |  | CDC | 347 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F4 81 RY | 81A | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_81A/S | 11KV永正線(VI24) 81RY | OTHER |  |  |  |  | CDC | 348 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | F5 81 RY | 81A | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_81A/S | 11KV永五線(VI25) 81RY | OTHER |  |  |  |  | CDC | 349 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | F6 81 RY | 81A | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_81A/S | 11KV永六線(VI26) 81RY | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F7 81 RY | 81A | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_81A/S | 11KV永七線(VI27) 81RY | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F8 81 RY | 81A | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_81A/S | 11KV永八線(VI28) 81RY | OTHER |  |  |  |  | CDC | 352 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | F9 81 RY | 81A | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_81A/S | 11KV永九線(VI29) 81RY | OTHER |  |  |  |  | CDC | 353 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F10 81 RY | 81A | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_81A/S | 11KV永十線(VI30) 81RY | OTHER |  |  |  |  | CDC | 354 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 81 RY | 81A | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_81A/S | 11KV永忠線(VI31) 81RY | OTHER |  |  |  |  | CDC | 355 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | F12 81 RY | 81A | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_81A/S | 11KV永孝線(VI32) 81RY | OTHER |  |  |  |  | CDC | 356 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 81 RY | 81A | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_81A/S | 11KV永仁線(VI33) 81RY | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F14 81 RY | 81A | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_81A/S | 11KV永愛線(VI34) 81RY | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | 81AS |  | B2,B3,Element | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | F15 81 RY | 81A | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_81A/S | 11KV永信線(VI35) 81RY | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | #1 TR 81 RY | 81A | #1 Main |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.#1MA_81A/S | #1MA 81RY | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL | #1MA_81U/L | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0465 |  | 0108 | 1-3D-01 |  | 1-6C | #1MT81RY | 81S | #1MT 81S 使用/閉鎖 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#1MA_81U/L | #1MA 81RY U/L | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | #2 TRA 81 RY | 81A | #2A Main |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.#2MA_81A/S | #2MA 81RY | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S47 | 永華SS | 11 | 11kV | M2A | #2MTR(A)(M2A) |  | 81UL | #2MA_81U/L | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0466 |  | 0109 | 1-3D-02 |  | 1-6D | #2MA81RY | 81S | #2MA 81S 使用/閉鎖 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#2MA_81U/L | #2MA 81RY U/L | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | #2 TRB 81 RY | 81A | #2B Main |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.#2MB_81A/S | #2MB 81RY | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S47 | 永華SS | 11 | 11kV | M2B | #2MTR(B)(M2B) |  | 81UL | #2MB_81U/L | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0467 |  | 0110 | 1-3D-03 |  | 1-6E | #2MB81RY | 81S | #2MB 81S 使用/閉鎖 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#2MB_81U/L | #2MB 81RY U/L | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | #3 TR 81 RY | 81A | #3 Main |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.#3MA_81A/S | #3MA 81RY | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | 81UL | #3MA_81U/L | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0468 |  | 0111 | 1-3D-04 |  | 1-6F | #3MT81RY | 81S | #3MT 81S 使用/閉鎖 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#3MA_81U/L | #3MA 81RY U/L | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0448 |  |  | 1-3C-00 |  |  | F1 79 RY | 79LOA | 永一線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_79_LOA | 11KV永一線(VI21) 79LOA | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0449 |  |  | 1-3C-01 |  |  | F2 79 RY | 79LOA | 永二線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_79_LOA | 11KV永二線(VI22) 79LOA | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | F3 79 RY | 79LOA | 永三線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_79_LOA | 11KV永三線(VI23) 79LOA | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0451 |  |  | 1-3C-03 |  |  | F4 79 RY | 79LOA | 永正線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_79_LOA | 11KV永正線(VI24) 79LOA | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0452 |  |  | 1-3C-04 |  |  | F5 79 RY | 79LOA | 永五線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_79_LOA | 11KV永五線(VI25) 79LOA | OTHER |  |  |  |  | CDC | 372 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0453 |  |  | 1-3C-05 |  |  | F6 79 RY | 79LOA | 永六線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_79_LOA | 11KV永六線(VI26) 79LOA | OTHER |  |  |  |  | CDC | 373 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0454 |  |  | 1-3C-06 |  |  | F7 79 RY | 79LOA | 永七線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_79_LOA | 11KV永七線(VI27) 79LOA | OTHER |  |  |  |  | CDC | 374 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0455 |  |  | 1-3C-07 |  |  | F8 79 RY | 79LOA | 永八線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_79_LOA | 11KV永八線(VI28) 79LOA | OTHER |  |  |  |  | CDC | 375 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0456 |  |  | 1-3C-08 |  |  | F9 79 RY | 79LOA | 永九線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_79_LOA | 11KV永九線(VI29) 79LOA | OTHER |  |  |  |  | CDC | 376 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0457 |  |  | 1-3C-09 |  |  | F10 79 RY | 79LOA | 永十線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_79_LOA | 11KV永十線(VI30) 79LOA | OTHER |  |  |  |  | CDC | 377 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0458 |  |  | 1-3C-10 |  |  | F11 79 RY | 79LOA | 永忠線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_79_LOA | 11KV永忠線(VI31) 79LOA | OTHER |  |  |  |  | CDC | 378 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0459 |  |  | 1-3C-11 |  |  | F12 79 RY | 79LOA | 永孝線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_79_LOA | 11KV永孝線(VI32) 79LOA | OTHER |  |  |  |  | CDC | 379 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0460 |  |  | 1-3C-12 |  |  | F13 79 RY | 79LOA | 永仁線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_79_LOA | 11KV永仁線(VI33) 79LOA | OTHER |  |  |  |  | CDC | 380 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0461 |  |  | 1-3C-13 |  |  | F14 79 RY | 79LOA | 永愛線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_79_LOA | 11KV永愛線(VI34) 79LOA | OTHER |  |  |  |  | CDC | 381 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | LOA |  | B2,B3,Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0462 |  |  | 1-3C-14 |  |  | F15 79 RY | 79LOA | 永信線 |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_79_LOA | 11KV永信線(VI35) 79LOA | OTHER |  |  |  |  | CDC | 382 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | ComPoint |  |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0463 |  |  | 1-3C-15 |  |  | IED | RYFA | 11KV IED 故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.11KV_RYFA | 11KV數位電驛故障 | OTHER |  |  |  |  | CDC | 383 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0464 |  |  | 1-3D-00 |  |  | PM | PMA | PowerMeter 故障 |  |  | ELEM/S47_D1 | [8 empty] | 永華SS.PMA | POWER METER故障 | OTHER |  |  |  |  | CDC | 384 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | F1 乏 | VAR | 永一線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永一線KVAR | 11KV永一線 KVAR | FEEDER |  |  |  |  | CDC | 385 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | F1 R相電流 | A1 | 永一線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永一線A1 | 11KV永一線 R相AMP | FEEDER |  |  |  |  | CDC | 386 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | F1 S相電流 | A2 | 永一線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永一線A2 | 11KV永一線 S相AMP | FEEDER |  |  |  |  | CDC | 387 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | F1 T相電流 | A3 | 永一線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永一線A3 | 11KV永一線 T相AMP | FEEDER |  |  |  |  | CDC | 388 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | F1 N相電流 | AMP | 永一線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永一線A0 | 11KV永一線 N相AMP | FEEDER |  |  |  |  | CDC | 389 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F7 乏 | VAR | 永七線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永七線KVAR | 11KV永七線 KVAR | FEEDER |  |  |  |  | CDC | 390 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F7 R相電流 | A1 | 永七線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永七線A1 | 11KV永七線 R相AMP | FEEDER |  |  |  |  | CDC | 391 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F7 S相電流 | A2 | 永七線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永七線A2 | 11KV永七線 S相AMP | FEEDER |  |  |  |  | CDC | 392 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F7 T相電流 | A3 | 永七線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永七線A3 | 11KV永七線 T相AMP | FEEDER |  |  |  |  | CDC | 393 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F7 N相電流 | AMP | 永七線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永七線A0 | 11KV永七線 N相AMP | FEEDER |  |  |  |  | CDC | 394 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F9 乏 | VAR | 永九線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永九線KVAR | 11KV永九線 KVAR | FEEDER |  |  |  |  | CDC | 395 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F9 R相電流 | A1 | 永九線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永九線A1 | 11KV永九線 R相AMP | FEEDER |  |  |  |  | CDC | 396 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F9 S相電流 | A2 | 永九線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永九線A2 | 11KV永九線 S相AMP | FEEDER |  |  |  |  | CDC | 397 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F9 T相電流 | A3 | 永九線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永九線A3 | 11KV永九線 T相AMP | FEEDER |  |  |  |  | CDC | 398 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F9 N相電流 | AMP | 永九線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永九線A0 | 11KV永九線 N相AMP | FEEDER |  |  |  |  | CDC | 399 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | F2 乏 | VAR | 永二線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永二線KVAR | 11KV永二線 KVAR | FEEDER |  |  |  |  | CDC | 400 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | F2 R相電流 | A1 | 永二線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永二線A1 | 11KV永二線 R相AMP | FEEDER |  |  |  |  | CDC | 401 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | F2 S相電流 | A2 | 永二線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永二線A2 | 11KV永二線 S相AMP | FEEDER |  |  |  |  | CDC | 402 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F2 T相電流 | A3 | 永二線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永二線A3 | 11KV永二線 T相AMP | FEEDER |  |  |  |  | CDC | 403 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | F2 N相電流 | AMP | 永二線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永二線A0 | 11KV永二線 N相AMP | FEEDER |  |  |  |  | CDC | 404 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F8 乏 | VAR | 永八線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永八線KVAR | 11KV永八線 KVAR | FEEDER |  |  |  |  | CDC | 405 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F8 R相電流 | A1 | 永八線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永八線A1 | 11KV永八線 R相AMP | FEEDER |  |  |  |  | CDC | 406 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F8 S相電流 | A2 | 永八線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永八線A2 | 11KV永八線 S相AMP | FEEDER |  |  |  |  | CDC | 407 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F8 T相電流 | A3 | 永八線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永八線A3 | 11KV永八線 T相AMP | FEEDER |  |  |  |  | CDC | 408 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F8 N相電流 | AMP | 永八線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永八線A0 | 11KV永八線 N相AMP | FEEDER |  |  |  |  | CDC | 409 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F10 乏 | VAR | 永十線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永十線KVAR | 11KV永十線 KVAR | FEEDER |  |  |  |  | CDC | 410 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F10 R相電流 | A1 | 永十線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永十線A1 | 11KV永十線 R相AMP | FEEDER |  |  |  |  | CDC | 411 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F10 S相電流 | A2 | 永十線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永十線A2 | 11KV永十線 S相AMP | FEEDER |  |  |  |  | CDC | 412 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F10 T相電流 | A3 | 永十線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永十線A3 | 11KV永十線 T相AMP | FEEDER |  |  |  |  | CDC | 413 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F10 N相電流 | AMP | 永十線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永十線A0 | 11KV永十線 N相AMP | FEEDER |  |  |  |  | CDC | 414 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F3 乏 | VAR | 永三線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永三線KVAR | 11KV永三線 KVAR | FEEDER |  |  |  |  | CDC | 415 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F3 R相電流 | A1 | 永三線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永三線A1 | 11KV永三線 R相AMP | FEEDER |  |  |  |  | CDC | 416 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F3 S相電流 | A2 | 永三線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永三線A2 | 11KV永三線 S相AMP | FEEDER |  |  |  |  | CDC | 417 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F3 T相電流 | A3 | 永三線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永三線A3 | 11KV永三線 T相AMP | FEEDER |  |  |  |  | CDC | 418 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | F3 N相電流 | AMP | 永三線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永三線A0 | 11KV永三線 N相AMP | FEEDER |  |  |  |  | CDC | 419 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F5 乏 | VAR | 永五線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永五線KVAR | 11KV永五線 KVAR | FEEDER |  |  |  |  | CDC | 420 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F5 R相電流 | A1 | 永五線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永五線A1 | 11KV永五線 R相AMP | FEEDER |  |  |  |  | CDC | 421 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F5 S相電流 | A2 | 永五線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永五線A2 | 11KV永五線 S相AMP | FEEDER |  |  |  |  | CDC | 422 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F5 T相電流 | A3 | 永五線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永五線A3 | 11KV永五線 T相AMP | FEEDER |  |  |  |  | CDC | 423 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | F5 N相電流 | AMP | 永五線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永五線A0 | 11KV永五線 N相AMP | FEEDER |  |  |  |  | CDC | 424 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 乏 | VAR | 永仁線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永仁線KVAR | 11KV永仁線 KVAR | FEEDER |  |  |  |  | CDC | 425 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 R相電流 | A1 | 永仁線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永仁線A1 | 11KV永仁線 R相AMP | FEEDER |  |  |  |  | CDC | 426 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 S相電流 | A2 | 永仁線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永仁線A2 | 11KV永仁線 S相AMP | FEEDER |  |  |  |  | CDC | 427 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 T相電流 | A3 | 永仁線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永仁線A3 | 11KV永仁線 T相AMP | FEEDER |  |  |  |  | CDC | 428 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F13 N相電流 | AMP | 永仁線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永仁線A0 | 11KV永仁線 N相AMP | FEEDER |  |  |  |  | CDC | 429 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 乏 | VAR | 永六線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永六線KVAR | 11KV永六線 KVAR | FEEDER |  |  |  |  | CDC | 430 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F6 R相電流 | A1 | 永六線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永六線A1 | 11KV永六線 R相AMP | FEEDER |  |  |  |  | CDC | 431 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F6 S相電流 | A2 | 永六線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永六線A2 | 11KV永六線 S相AMP | FEEDER |  |  |  |  | CDC | 432 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F6 T相電流 | A3 | 永六線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永六線A3 | 11KV永六線 T相AMP | FEEDER |  |  |  |  | CDC | 433 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | F6 N相電流 | AMP | 永六線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永六線A0 | 11KV永六線 N相AMP | FEEDER |  |  |  |  | CDC | 434 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F4 乏 | VAR | 永正線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永正線KVAR | 11KV永正線 KVAR | FEEDER |  |  |  |  | CDC | 435 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F4 R相電流 | A1 | 永正線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永正線A1 | 11KV永正線 R相AMP | FEEDER |  |  |  |  | CDC | 436 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F4 S相電流 | A2 | 永正線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永正線A2 | 11KV永正線 S相AMP | FEEDER |  |  |  |  | CDC | 437 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F4 T相電流 | A3 | 永正線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永正線A3 | 11KV永正線 T相AMP | FEEDER |  |  |  |  | CDC | 438 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | F4 N相電流 | AMP | 永正線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永正線A0 | 11KV永正線 N相AMP | FEEDER |  |  |  |  | CDC | 439 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 乏 | VAR | 永孝線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永孝線KVAR | 11KV永孝線 KVAR | FEEDER |  |  |  |  | CDC | 440 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 R相電流 | A1 | 永孝線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永孝線A1 | 11KV永孝線 R相AMP | FEEDER |  |  |  |  | CDC | 441 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 S相電流 | A2 | 永孝線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永孝線A2 | 11KV永孝線 S相AMP | FEEDER |  |  |  |  | CDC | 442 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F12 T相電流 | A3 | 永孝線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永孝線A3 | 11KV永孝線 T相AMP | FEEDER |  |  |  |  | CDC | 443 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F12 N相電流 | AMP | 永孝線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永孝線A0 | 11KV永孝線 N相AMP | FEEDER |  |  |  |  | CDC | 444 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 乏 | VAR | 永忠線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永忠線KVAR | 11KV永忠線 KVAR | FEEDER |  |  |  |  | CDC | 445 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 R相電流 | A1 | 永忠線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永忠線A1 | 11KV永忠線 R相AMP | FEEDER |  |  |  |  | CDC | 446 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F11 S相電流 | A2 | 永忠線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永忠線A2 | 11KV永忠線 S相AMP | FEEDER |  |  |  |  | CDC | 447 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F11 T相電流 | A3 | 永忠線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永忠線A3 | 11KV永忠線 T相AMP | FEEDER |  |  |  |  | CDC | 448 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F11 N相電流 | AMP | 永忠線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永忠線A0 | 11KV永忠線 N相AMP | FEEDER |  |  |  |  | CDC | 449 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 乏 | VAR | 永信線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永信線KVAR | 11KV永信線 KVAR | FEEDER |  |  |  |  | CDC | 450 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 R相電流 | A1 | 永信線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永信線A1 | 11KV永信線 R相AMP | FEEDER |  |  |  |  | CDC | 451 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 S相電流 | A2 | 永信線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永信線A2 | 11KV永信線 S相AMP | FEEDER |  |  |  |  | CDC | 452 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F15 T相電流 | A3 | 永信線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永信線A3 | 11KV永信線 T相AMP | FEEDER |  |  |  |  | CDC | 453 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F15 N相電流 | AMP | 永信線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永信線A0 | 11KV永信線 N相AMP | FEEDER |  |  |  |  | CDC | 454 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 乏 | VAR | 永愛線 | KVAR_-9000_9000(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永愛線KVAR | 11KV永愛線 KVAR | FEEDER |  |  |  |  | CDC | 455 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 R相電流 | A1 | 永愛線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永愛線A1 | 11KV永愛線 R相AMP | FEEDER |  |  |  |  | CDC | 456 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F14 S相電流 | A2 | 永愛線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永愛線A2 | 11KV永愛線 S相AMP | FEEDER |  |  |  |  | CDC | 457 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F14 T相電流 | A3 | 永愛線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永愛線A3 | 11KV永愛線 T相AMP | FEEDER |  |  |  |  | CDC | 458 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F14 N相電流 | AMP | 永愛線 | A_-500_500(-2000_2000) |  | B2/S47_D1 | [8 empty] | 永華SS.永愛線A0 | 11KV永愛線 N相AMP | FEEDER |  |  |  |  | CDC | 459 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | DC電壓 | DCV | 直流電壓 | DCVolt_-150_150(-2000_2000) |  | B3/S47_D1 | [8 empty] | 永華SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 460 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 600 | GDA(2) | TIE(600) CB 67N(2) RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | TIE | [5 empty] | 461 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 600 | PHA(2) | TIE(600) CB 67(2) RY |  |  | B2/S47_A1 | [8 empty] | 永華SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | TIE | [5 empty] | 462 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1MTR | #1 63Q | #1MTR ULTC保護 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | [5 empty] | 463 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #1MTR | #1 96B1 | #1MTR撲氣一段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 464 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #1MTR | #1 96B2 | #1MTR撲氣二段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | [5 empty] | 465 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1MTR | #1 96D | #1MTR放壓裝置 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | [5 empty] | 466 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1MTR | #1 96P | #1MTR突壓電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | [5 empty] | 467 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #2MTR | #2 63Q | #2MTR ULTC保護 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | [5 empty] | 468 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #2MTR | #2 96B1 | #2MTR撲氣一段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 469 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #2MTR | #2 96B2 | #2MTR撲氣二段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | [5 empty] | 470 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #2MTR | #2 96D | #2MTR放壓裝置 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | [5 empty] | 471 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2MTR | #2 96P | #2MTR突壓電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | [5 empty] | 472 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #3MTR | #3 63Q | #3MTR ULTC保護 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | [5 empty] | 473 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #3MTR | #3 96B1 | #3MTR撲氣一段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | [5 empty] | 474 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #3MTR | #3 96B2 | #3MTR撲氣二段 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | [5 empty] | 475 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #3MTR | #3 96D | #3MTR放壓裝置 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | [5 empty] | 476 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #3MTR | #3 96P | #3MTR突壓電驛 |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | [5 empty] | 477 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 1-32-09 |  |  | 630 | 630 CFA | 永華學甲線電驛通訊故障 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_87CFA | 永華學甲(630)87RY通訊故 | OTHER | [5 empty] | 478 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 1-32-08 |  |  | 630 | 630 RYFA | 永華學甲線電驛故障 |  |  | B2/S47_A1 | [8 empty] | 永華SS.630_RYFA | 永華學甲(630)數位電驛故障 | OTHER | [5 empty] | 479 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 640 | 640 CFA | 新塭永華線電驛通訊故障 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_87CFA | 新塭永華(640)87RY通訊故障 | OTHER | [5 empty] | 480 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-32-06 |  |  | 640 | 640 RYFA | 新塭永華線電驛故障 |  |  | B2/S47_A1 | [8 empty] | 永華SS.640_RYFA | 新塭永華(640)數位電驛故障 | OTHER | [5 empty] | 481 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | 600 | 600 RYFA | 600TIE數位電驛故障 |  |  | B2/S47_A1 | [8 empty] | 永華SS.600_RYFA | 600TIE數位電驛故障 | OTHER | [5 empty] | 482 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | ComPoint |  |  | BUS_RYFA |  | INSERT | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0470 |  |  | 1-3D-06 |  |  | 69KV BUS | RYFA | 69BUS數位電驛故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.69BUS_RYFA | 69BUS數位電驛故障 | OTHER | [5 empty] | 483 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | ComPoint |  |  | 12B_CTFA |  | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0471 |  |  | 1-3D-07 |  |  | 69KV BUS | CTFA | 69BUS數位電驛CT故障 |  |  | B3/S47_D1 | [8 empty] | 永華SS.69BUS_CTFA | 69BUS數位電驛CT故障 | OTHER | [5 empty] | 484 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | F1 CB | KWH | 永一線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 485 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | F2 CB | KWH | 永二線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 486 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | F3 CB | KWH | 永三線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 487 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | F4 CB | KWH | 永正線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 488 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | F5 CB | KWH | 永五線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 489 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | F6 CB | KWH | 永六線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 490 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | F7 CB | KWH | 永七線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 491 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | F8 CB | KWH | 永八線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 492 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | F9 CB | KWH | 永九線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 493 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | F10 CB | KWH | 永十線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 494 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | F11 CB | KWH | 永忠線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 495 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | F12 CB | KWH | 永孝線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 496 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | F13 CB | KWH | 永仁線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 497 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | F14 CB | KWH | 永愛線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 498 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | F15 CB | KWH | 永信線 |  |  | B2/S47_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 499 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S47 | 永華SS |  |  | 1GIS | #1GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1 GIS CB | CBA | #1 GIS斷路器重故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#1GIS_CBA | #1GIS重故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1GIS | #1GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1 GIS CB | CBF | #1 GIS斷路器輕故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#1GIS_CBF | #1GIS輕故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2GIS | #2GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2 GIS CB | CBA | #2 GIS斷路器重故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#2GIS_CBA | #2GIS重故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2GIS | #2GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2 GIS CB | CBF | #2 GIS斷路器輕故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#2GIS_CBF | #2GIS輕故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3GIS | #3GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3 GIS CB | CBA | #3 GIS斷路器重故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#3GIS_CBA | #3GIS重故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3GIS | #3GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3 GIS CB | CBF | #3 GIS斷路器輕故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#3GIS_CBF | #3GIS輕故障 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 4GIS | #4GIS |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0487 |  |  | 1-3E-07 |  |  | #4 GIS CB | CBA | #4 GIS斷路器重故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#4GIS_CBA | #4GIS重故障 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 4GIS | #4GIS |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0486 |  |  | 1-3E-06 |  |  | #4 GIS CB | CBF | #4 GIS斷路器輕故障 |  |  | B2/S47_D1 | [8 empty] | 永華SS.#4GIS_CBF | #4GIS輕故障 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | F1 81 U/L | 81 U/L | F1 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI21_81U/L | 11KV永一線(VI21) 81RY U/L | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | F2 81 U/L | 81 U/L | F2 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI22_81U/L | 11KV永二線(VI22) 81RY U/L | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0490 |  |  | 1-3E-10 |  |  | F3 81 U/L | 81 U/L | F3 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI23_81U/L | 11KV永三線(VI23) 81RY U/L | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0491 |  |  | 1-3E-11 |  |  | F4 81 U/L | 81 U/L | F4 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI24_81U/L | 11KV永正線(VI24) 81RY U/L | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | F5 81 U/L | 81 U/L | F5 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI25_81U/L | 11KV永五線(VI25) 81RY U/L | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | F6 81 U/L | 81 U/L | F6 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI26_81U/L | 11KV永六線(VI26) 81RY U/L | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | F7 81 U/L | 81 U/L | F7 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI27_81U/L | 11KV永七線(VI27) 81RY U/L | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | F8 81 U/L | 81 U/L | F8 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI28_81U/L | 11KV永八線(VI28) 81RY U/L | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | F9 81 U/L | 81 U/L | F9 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI29_81U/L | 11KV永九線(VI29) 81RY U/L | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | F10 81 U/L | 81 U/L | F10 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI30_81U/L | 11KV永十線(VI30) 81RY U/L | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | F11 81 U/L | 81 U/L | F11 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI31_81U/L | 11KV永忠線(VI31) 81RY U/L | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | F12 81 U/L | 81 U/L | F12 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI32_81U/L | 11KV永孝線(VI32) 81RY U/L | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | F13 81 U/L | 81 U/L | F13 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI33_81U/L | 11KV永仁線(VI33) 81RY U/L | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | F14 81 U/L | 81 U/L | F14 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI34_81U/L | 11KV永愛線(VI34) 81RY U/L | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | F15 81 U/L | 81 U/L | F15 81 U/L |  |  | B2/S47_D1 | [8 empty] | 永華SS.VI35_81U/L | 11KV永信線(VI35) 81RY U/L | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS |  |  | 1MTR | #1MTR |  | IRFA |  |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0472 |  |  | 1-3D-08 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | IRFA |  |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0473 |  |  | 1-3D-09 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | IRFA |  |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0474 |  |  | 1-3D-10 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | ComPoint |  |  | 81A_RYFA |  |  | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0469 |  |  | 1-3D-05 |  |  | Locate Empty |  |  |  |  | B3/S47_D1 | [8 empty] | 永華SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0475 |  |  | 1-3D-11 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 87AS1 | [14 empty] | 0478 |  |  | 1-3D-14 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 87AS2 | [14 empty] | 0479 |  |  | 1-3D-15 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0476 |  |  | 1-3D-12 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 87AS1 | [14 empty] | 0503 |  |  | 1-3F-07 |  |  | F16 81 U/L | 81 U/L | F16 81 U/L |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 87AS2 | [14 empty] | 0504 |  |  | 1-3F-08 |  |  | F17 81 U/L | 81 U/L | F17 81 U/L |  |  | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 3MTR | #3MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0477 |  |  | 1-3D-13 |  |  | Locate Empty |  |  |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 87AS1 | [14 empty] | 0505 |  |  | 1-3F-09 |  |  | F18 81 U/L | 81 U/L | F18 81 U/L |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 87AS2 | [14 empty] | 0506 |  |  | 1-3F-10 |  |  | F19 81 U/L | 81 U/L | F19 81 U/L |  |  | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | USE/LOCK | USE
S47 | 永華SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0507 |  |  | 1-3F-11 |  |  | F20 81 U/L | 81 U/L | F20 81 U/L |  |  | B1/S47_D1 | [8 empty] | 永華SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 1-3F-12 | [7 empty] | B1/S47_D1 | [8 empty] | 永華SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 1-3F-13 | [7 empty] | B1/S47_D1 | [8 empty] | 永華SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | 101E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.101E | 101E (非取樣點) | TIE | [5 empty] | 539 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E2 | 102E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.102E | 102E (非取樣點) | TIE | [5 empty] | 540 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | 201E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.201E | 201E (非取樣點) | TIE | [5 empty] | 541 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E2 | 202E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.202E | 202E (非取樣點) | TIE | [5 empty] | 542 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | TIE1_DS2 (非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | [5 empty] | 543 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D2 | TIE2_DS2 (非取樣點) | DELETE | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | [5 empty] | 544 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 545 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 546 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 1BUS | #1BUS |  | BE1 | 11B1E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.11B1E | 11B1E (非取樣點) | BUS | [5 empty] | 547 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 2BUS | #2BUS |  | BE2 | 11B2E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.11B2E | 11B2E (非取樣點) | BUS | [5 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 2BUS | #2BUS |  | BE0 | 11B2BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.11B2BE | 11B2BE (非取樣點) | BUS | [5 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 3BUS | #3BUS |  | BE3 | 11B3E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_D1 | [8 empty] | 永華SS.11B3E | 11B3E (非取樣點) | BUS | [5 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0059 |  |  | 1-BB |  |  | 11KV #2A BUS | KV | 2A BUS PT | kV_-9_9(-2000_2000) | aca | B2/S47_D1 | [8 empty] | 永華SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | 433 | 0042 | 1-3B-00 | 1-3B-01 | 1-2A | 601 | ABS ON | 600 TIE (601) ABS |  |  | B2/S47_A1 | [8 empty] | 永華SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 169 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0043 | 1-3B-02 | 1-3B-03 | 1-2B | 602 | ABS ON | 600 TIE (602) ABS |  |  | B2/S47_A1 | [8 empty] | 永華SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 170 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.810ES | 810ES (非取樣點) | SC | [5 empty] | 272 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1BUS | B/2BUS | L |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 640 | CB ON/OFF | 新塭-永華線 |  | aaga | B2/S47_A1 | [8 empty] | 永華SS.640_CB | 640(新塭線) CB | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | DS1 | 651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0016 | 1-38-00 | 1-38-01 | 1-10 | 641 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.641_DS | 641(新塭線) DS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | DS2 | 652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0017 | 1-38-02 | 1-38-03 | 1-11 | 642 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.642_DS | 642(新塭線) DS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | DS3 | 653 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0018 | 1-38-04 | 1-38-05 | 1-12 | 643 | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.643_DS | 643(新塭線) DS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | E3 | 653E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0390 | 391 | 0019 | 1-38-06 | 1-38-07 | 1-13 | 643E | ABS ON | 新塭-永華線 |  |  | B2/S47_A1 | [8 empty] | 永華SS.643E_ES | 643E(新塭線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S47_A1 | [8 empty] | 永華SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 43 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S47 | 永華SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S47_D1 | [12 empty] | 永華SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S47/69/1BUS/V; OPRD2: S47/69/2BUS/V
S47 | 永華SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S47_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S47/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S47 | 永華SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S47_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_5 | OPRD1: S47/11/M1/MW; OPRD2: S47/11/M3/MW; OPRD3: S47/69/630/MW; OPRD4: S47/69/640/MW; OPRD5: S47/69/650/MW
S47 | 永華SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S47_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S47/0/CalcPoint/OPRN2_MW
S47 | 永華SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S47_D1 | [17 empty] | none
S47 | 永華SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S47_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S47/0/CalcPoint/OPRN1; OPRD2: S47/0/CalcPoint/OPRN2; OPRD3: S47/0/CalcPoint/PRFL_UL
S47 | 永華SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S47_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S47/11/M1/MW; OPRD2: S47/11/M1/MVAR; OPRD3: S47/0/CalcPoint/Vbs2
S47 | 永華SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S47_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S47/11/M3/MW; OPRD2: S47/11/M3/MVAR; OPRD3: S47/0/CalcPoint/Vbs2
S47 | 永華SS | 69 | 69kV | 630 | 永華～學甲線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S47_A1 | [12 empty] | 永華SS.630_AMP | 學甲線 AMP | LINE69 | AMP_CAL | C08R0800 | amp_cal | OPRD1: S47/69/630/MW; OPRD2: S47/69/630/MVAR; OPRD3: S47/0/CalcPoint/Vbs2
S47 | 永華SS | 69 | 69kV | 640 | 新塭～永華線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S47_A1 | [12 empty] | 永華SS.640_AMP | 新塭線 AMP | LINE69 | AMP_CAL | C10R0831 | amp_cal | OPRD1: S47/69/640/MW; OPRD2: S47/69/640/MVAR; OPRD3: S47/0/CalcPoint/Vbs2
S47 | 永華SS | 69 | 69kV | 650 | 預備線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S47_A1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S47/69/650/MW; OPRD2: S47/69/650/MVAR; OPRD3: NULL
S47 | 永華SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S47_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S47/11/1BUS/V
S47 | 永華SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S47_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S47/11/2BUS/V
S47 | 永華SS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S47_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S47/11/3BUS/V
S47 | 永華SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S47_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 永華SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S47/11/M1/MW; OPRD2: S47/11/M1/MVAR
S47 | 永華SS |  |  | 2MTR(A) | #2MTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S47_D1 | LG_15 | 14.25 | 16.5 | 18.75 | 30 |  | -14.25 | -16.5 | -18.75 | -30 | [5 empty] | MVA_CAL |  | va_million | OPRD1: S47/11/M2A/MW; OPRD2: S47/11/M2A/MVAR
S47 | 永華SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S47_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 永華SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S47/11/M3/MW; OPRD2: S47/11/M3/MVAR
S47 | 永華SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S47_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S47//1MTR/MVA; OPRD2: 0
S47 | 永華SS |  |  | 2MTR(A) | #2MTR(A) |  | LOAD | [9 empty] | B1/S47_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S47//2MTR(A)/MVA; OPRD2: 0
S47 | 永華SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S47_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S47//3MTR/MVA; OPRD2: 0
S47 | 永華SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S47_D1 | [12 empty] | 永華SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S47/11/M1/MW; OPRD2: S47/11/M1/MVAR
S47 | 永華SS |  |  | 2MTR(A) | #2MTR(A) |  | PF | [9 empty] | B1/S47_D1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: S47/11/M2A/MW; OPRD2: S47/11/M2A/MVAR
S47 | 永華SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S47_D1 | [12 empty] | 永華SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S47/11/M3/MW; OPRD2: S47/11/M3/MVAR
S47 | 永華SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S47_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S47//1MTR/SupLocal; OPRD2: S47//1MTR/Tap Chan; OPRD3: NULL
S47 | 永華SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S47_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S47//2MTR/SupLocal; OPRD2: S47//2MTR/Tap Chan; OPRD3: NULL
S47 | 永華SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S47_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S47//3MTR/SupLocal; OPRD2: S47//3MTR/Tap Chan; OPRD3: NULL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/1BUS/V; OPRD2: S47/11/VI21/I_R; OPRD3: S47/11/VI21/I_S; OPRD4: S47/11/VI21/I_T
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/1BUS/V; OPRD2: S47/11/VI22/I_R; OPRD3: S47/11/VI22/I_S; OPRD4: S47/11/VI22/I_T
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/1BUS/V; OPRD2: S47/11/VI23/I_R; OPRD3: S47/11/VI23/I_S; OPRD4: S47/11/VI23/I_T
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/1BUS/V; OPRD2: S47/11/VI24/I_R; OPRD3: S47/11/VI24/I_S; OPRD4: S47/11/VI24/I_T
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/1BUS/V; OPRD2: S47/11/VI25/I_R; OPRD3: S47/11/VI25/I_S; OPRD4: S47/11/VI25/I_T
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S47/11/VI26/I_R; OPRD3: S47/11/VI26/I_S; OPRD4: S47/11/VI26/I_T
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S47/11/VI27/I_R; OPRD3: S47/11/VI27/I_S; OPRD4: S47/11/VI27/I_T
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S47/11/VI28/I_R; OPRD3: S47/11/VI28/I_S; OPRD4: S47/11/VI28/I_T
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S47/11/VI29/I_R; OPRD3: S47/11/VI29/I_S; OPRD4: S47/11/VI29/I_T
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S47/11/VI30/I_R; OPRD3: S47/11/VI30/I_S; OPRD4: S47/11/VI30/I_T
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/3BUS/V; OPRD2: S47/11/VI31/I_R; OPRD3: S47/11/VI31/I_S; OPRD4: S47/11/VI31/I_T
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/3BUS/V; OPRD2: S47/11/VI32/I_R; OPRD3: S47/11/VI32/I_S; OPRD4: S47/11/VI32/I_T
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/3BUS/V; OPRD2: S47/11/VI33/I_R; OPRD3: S47/11/VI33/I_S; OPRD4: S47/11/VI33/I_T
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/3BUS/V; OPRD2: S47/11/VI34/I_R; OPRD3: S47/11/VI34/I_S; OPRD4: S47/11/VI34/I_T
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S47/11/3BUS/V; OPRD2: S47/11/VI35/I_R; OPRD3: S47/11/VI35/I_S; OPRD4: S47/11/VI35/I_T
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI21/kVA; OPRD2: S47/11/VI21/KVAR
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI22/kVA; OPRD2: S47/11/VI22/KVAR
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI23/kVA; OPRD2: S47/11/VI23/KVAR
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI24/kVA; OPRD2: S47/11/VI24/KVAR
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI25/kVA; OPRD2: S47/11/VI25/KVAR
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI26/kVA; OPRD2: S47/11/VI26/KVAR
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI27/kVA; OPRD2: S47/11/VI27/KVAR
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI28/kVA; OPRD2: S47/11/VI28/KVAR
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI29/kVA; OPRD2: S47/11/VI29/KVAR
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI30/kVA; OPRD2: S47/11/VI30/KVAR
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI31/kVA; OPRD2: S47/11/VI31/KVAR
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI32/kVA; OPRD2: S47/11/VI32/KVAR
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI33/kVA; OPRD2: S47/11/VI33/KVAR
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI34/kVA; OPRD2: S47/11/VI34/KVAR
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S47_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S47/11/VI35/kVA; OPRD2: S47/11/VI35/KVAR
S47 | 永華SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S47_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S47/11/M1/MW; OPRD2: S47/11/M3/MW
S47 | 永華SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S47_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S47/11/M1/MVAR; OPRD2: S47/11/M3/MVAR
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S47_D1 | [12 empty] | 永華SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S47/11/210/CB; OPRD2: 6.9; OPRD3: 0
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S47_D1 | [12 empty] | 永華SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S47/11/220/CB; OPRD2: 6.9; OPRD3: 0
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S47_D1 | [12 empty] | 永華SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S47/11/230/CB; OPRD2: 6.9; OPRD3: 0
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S47_A1 | [12 empty] | 永華SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S47/69/810/CB; OPRD2: 69; OPRD3: 0
S47 | 永華SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S47_D1 | [12 empty] | 永華SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_26 | OPRD1: S47//1MTR/TRA; OPRD2: S47//1MTR/96B1; OPRD3: S47//1MTR/96B2; OPRD4: S47//1MTR/96D; OPRD5: S47//1MTR/63Q; OPRD6: S47//1MTR/96PA; OPRD7: S47//1MTR/87A; OPRD8: S47//1MTR/51ZA; OPRD9: S47//2MTR/96B2; OPRD10: S47//2MTR/96D; OPRD11: S47//2MTR/63Q; OPRD12: S47//2MTR/96B1; OPRD13: S47//2MTR/96PA; OPRD14: S47//2MTR/87A; OPRD15: S47//2MTR/51ZA; OPRD16: S47//2MTR/TRA; OPRD17: S47//3MTR/63Q; OPRD18: S47//3MTR/96D; OPRD19: S47//3MTR/96B2; OPRD20: S47//3MTR/96B1; OPRD21: S47//3MTR/51ZA; OPRD22: S47//3MTR/87A; OPRD23: S47//3MTR/TRA; OPRD24: S47//3MTR/96PA; OPRD25: S47/69/1BUS/87A; OPRD26: S47/69/2BUS/87A
S47 | 永華SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S47_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S47//1MTR/TRF; OPRD2: S47//2MTR/TRF; OPRD3: S47//3MTR/TRF
S47 | 永華SS | 69 | 69kV | 750_A1 | #1MTR(750) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/69/750/81A
S47 | 永華SS | 69 | 69kV | 760_A1 | #2MTR(760) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/69/760/81A
S47 | 永華SS | 69 | 69kV | 770_A1 | #3MTR(770) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/69/770/81A
S47 | 永華SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | R_L |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/RTU/RTU_R_L
S47 | 永華SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/StaDev/PSA
S47 | 永華SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/StaDev/PSF
S47 | 永華SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/StaDev/DCE
S47 | 永華SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S47_D1 | [17 empty] | lamp2CC | OPRD1: S47/69/ComPoint/CBA
S47 | 永華SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S47_D1 | [17 empty] | lamp2CC | OPRD1: S47/69/ComPoint/CBF
S47 | 永華SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S47_D1 | [17 empty] | lamp2CC | OPRD1: S47/69/ComPoint/ABS_89A
S47 | 永華SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/StaDev/DCA
S47 | 永華SS | 11 | 11kV | M1_A1 | #1MTR(M1) |  | 81A | #1MA_81A/S |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/11/M1/81A
S47 | 永華SS | 11 | 11kV | M2A_A1 | #2MTR(A)(M2A) |  | 81A | #2MA_81A/S |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/11/M2A/81A
S47 | 永華SS | 11 | 11kV | M2B_A1 | #2MTR(B)(M2B) |  | 81A | #2MB_81A/S |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/11/M2B/81A
S47 | 永華SS | 11 | 11kV | M3_A1 | #3MTR(M3) |  | 81A | #3MA_81A/S |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/11/M3/81A
S47 | 永華SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S47_A1 | [17 empty] | lamp2CC | OPRD1: S47/0/StaDev/PMA
S47 | 永華SS | 69 | 69kV | ComPoint_D1 |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S47_D1 | [17 empty] | lamp2CC | OPRD1: S47/69/ComPoint/BUS_RYFA
S47 | 永華SS | 69 | 69kV | ComPoint_D1 |  |  | 12B_CTFA |  |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S47_D1 | [17 empty] | lamp2CC | OPRD1: S47/69/ComPoint/12B_CTFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S47 | 永華SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 永華SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S47/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 永華SS.630_AMP | 學甲線 AMP | LINE69 | S47/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 永華SS.640_AMP | 新塭線 AMP | LINE69 | S47/69/640/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C10R0831 | 747.900024 | 747.900024 | 831.000000 | 1000.000000 | 0.830000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S47 | 永華SS | 0 |  |  |  |  | 永一線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永一線KVA | 11KV永一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永一線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永一線KW | 11KV永一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永七線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永七線KVA | 11KV永七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永七線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永七線KW | 11KV永七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永九線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永九線KVA | 11KV永九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永九線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永九線KW | 11KV永九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永二線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永二線KVA | 11KV永二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永二線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永二線KW | 11KV永二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永八線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永八線KVA | 11KV永八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永八線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永八線KW | 11KV永八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永十線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永十線KVA | 11KV永十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永十線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永十線KW | 11KV永十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永三線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永三線KVA | 11KV永三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永三線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永三線KW | 11KV永三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永五線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永五線KVA | 11KV永五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永五線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永五線KW | 11KV永五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永仁線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永仁線KVA | 11KV永仁線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永仁線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永仁線KW | 11KV永仁線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永六線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永六線KVA | 11KV永六線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永六線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永六線KW | 11KV永六線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永正線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永正線KVA | 11KV永正線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永正線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永正線KW | 11KV永正線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永孝線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永孝線KVA | 11KV永孝線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永孝線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永孝線KW | 11KV永孝線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永忠線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永忠線KVA | 11KV永忠線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永忠線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永忠線KW | 11KV永忠線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永信線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永信線KVA | 11KV永信線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永信線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永信線KW | 11KV永信線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永愛線KVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永愛線KVA | 11KV永愛線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  |  |  |  | 永愛線KW | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.永愛線KW | 11KV永愛線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S47//1MTR/MVA |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_PF | #1MTR 功率因素 | DTR | S47//1MTR/PF |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_MVA | #2MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_PF | #2MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S47//3MTR/MVA |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_PF | #3MTR 功率因素 | DTR | S47//3MTR/PF |  | RPDC_PF_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S47 | 永華SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S47/11/210/MVAR |  | SC_CAL_11 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S47/11/220/MVAR |  | SC_CAL_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S47/11/230/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S47/69/810/MVAR |  | SC_CAL_69 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 69 | 69kV | 630_CB | 學甲線(630_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.630_CB_3 | 630(學甲線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 45 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 640_CB | 新塭線(640_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.640_CB_3 | 640(新塭線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 46 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 600_CB | 600(600_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.600_CB_3 | 600 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.810_CB_3 | 810(69KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 48 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 永華SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 49 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 永華SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 50 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_N | [8 empty] | 永華SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 51 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 永華SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S47/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 52 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 53 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | STATION_FAULT_3 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630_AMP | 學甲線 | [27 empty] | ADCS_N | [8 empty] | 永華SS.630_AMP_A | 學甲線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 55 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 69 | 69kV | 630_AMP | 學甲線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.630_AMP_3 | 學甲線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 56 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 69 | 69kV | 640_AMP | 新塭線 | [27 empty] | ADCS_N | [8 empty] | 永華SS.640_AMP_A | 新塭線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 57 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 69 | 69kV | 640_AMP | 新塭線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.640_AMP_3 | 新塭線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 1MTR_MVA | #1MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_MVA_3 | #1MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 2MTR_MVA | #2MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_MVA_3 | #2MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 3MTR_MVA | #3MTR |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_MVA_3 | #3MTR MVA 點燈 (D3) | DTR |  |  | MAP_SET |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S47 | 永華SS | 69 | 69kV | _ABS_89A | ABS | [27 empty] | ADCS_N | [8 empty] | 永華SS.69KV_ABS_89A_A | 69KV ABS NFB 跳脫警報 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 65 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 691BUS_87A | #1BUS | [27 empty] | DDCS3_2 | [8 empty] | 永華SS.69#1BUS_87A_A | 69KV #1BUS 87RY (D3) | BUS |  |  | AD_LAMP_DD_5 |  |  | 66 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 692BUS_87A | #2BUS | [27 empty] | DDCS3_2 | [8 empty] | 永華SS.69#2BUS_87A_A | 69KV #2BUS 87RY (D3) | BUS |  |  | AD_LAMP_DD_5 |  |  | 67 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 630_87CFA | 永華學甲(630)87RY通訊故 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.630_87CFA_3 | 永華學甲(630)87RY通訊故 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 68 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 630_RYFA | 永華學甲(630)數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.630_RYFA_3 | 永華學甲(630)數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 69 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 640_87CFA | 新塭永華(640)87RY通訊故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.640_87CFA_3 | 新塭永華(640)87RY通訊故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 70 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 640_RYFA | 新塭永華(640)數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.640_RYFA_3 | 新塭永華(640)數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 71 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 600_RYFA | 600TIE數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.600_RYFA_3 | 600TIE數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 72 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 69BUS_RYFA | 69BUS數位電驛故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.69BUS_RYFA_3 | 69BUS數位電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 73 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 69BUS_CTFA | 69BUS數位電驛CT故障 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.69BUS_CTFA_3 | 69BUS數位電驛CT故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 74 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S47/0/RTU/ADCH1 |  |  |  | CDC | 75 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S47/0/RTU/ADCH2 |  |  |  | CDC | 76 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S47/0/RTU/ADCH3 |  |  |  | CDC | 77 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S47/0/RTU/ADCL1 |  |  |  | CDC | 78 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S47/0/RTU/ADCL2 |  |  |  | CDC | 79 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S47/0/RTU/ADCL3 |  |  |  | CDC | 80 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S47/69/1BUS/V |  |  |  | CDC | 81 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S47/69/2BUS/V |  |  |  | CDC | 82 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S47 | 永華SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S47/11/1BUS/V |  |  |  | CDC | 83 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S47/11/2BUS/V |  |  |  | CDC | 84 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S47/11/3BUS/V |  |  |  | CDC | 85 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.630_MW | 學甲線 MW | LINE69 | S47/69/630/MW |  |  |  | CDC | 86 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.630_MVAR | 學甲線 MVAR | LINE69 | S47/69/630/MVAR |  |  |  | CDC | 87 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.640_MW | 新塭線 MW | LINE69 | S47/69/640/MW |  |  |  | CDC | 88 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.640_MVAR | 新塭線 MVAR | LINE69 | S47/69/640/MVAR |  |  |  | CDC | 89 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永一線 | 永一線 |  | 永一線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永一線KVAR | 11KV永一線 KVAR | FEEDER | S47/11/VI21/KVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永一線 | 永一線 |  | 永一線A1 | [17 empty] | 1-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永一線A1 | 11KV永一線 R相AMP | FEEDER | S47/11/VI21/I_R |  |  |  | CDC | 91 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永一線 | 永一線 |  | 永一線A2 | [17 empty] | 1-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永一線A2 | 11KV永一線 S相AMP | FEEDER | S47/11/VI21/I_S |  |  |  | CDC | 92 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永一線 | 永一線 |  | 永一線A3 | [17 empty] | 1-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永一線A3 | 11KV永一線 T相AMP | FEEDER | S47/11/VI21/I_T |  |  |  | CDC | 93 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永一線 | 永一線 |  | 永一線A0 | [17 empty] | 1-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永一線A0 | 11KV永一線 N相AMP | FEEDER | S47/11/VI21/I_N |  |  |  | CDC | 94 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永七線 | 永七線 |  | 永七線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永七線KVAR | 11KV永七線 KVAR | FEEDER | S47/11/VI27/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永七線 | 永七線 |  | 永七線A1 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永七線A1 | 11KV永七線 R相AMP | FEEDER | S47/11/VI27/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永七線 | 永七線 |  | 永七線A2 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永七線A2 | 11KV永七線 S相AMP | FEEDER | S47/11/VI27/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永七線 | 永七線 |  | 永七線A3 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永七線A3 | 11KV永七線 T相AMP | FEEDER | S47/11/VI27/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永七線 | 永七線 |  | 永七線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永七線A0 | 11KV永七線 N相AMP | FEEDER | S47/11/VI27/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永九線 | 永九線 |  | 永九線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永九線KVAR | 11KV永九線 KVAR | FEEDER | S47/11/VI29/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永九線 | 永九線 |  | 永九線A1 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永九線A1 | 11KV永九線 R相AMP | FEEDER | S47/11/VI29/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永九線 | 永九線 |  | 永九線A2 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永九線A2 | 11KV永九線 S相AMP | FEEDER | S47/11/VI29/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永九線 | 永九線 |  | 永九線A3 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永九線A3 | 11KV永九線 T相AMP | FEEDER | S47/11/VI29/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永九線 | 永九線 |  | 永九線A0 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永九線A0 | 11KV永九線 N相AMP | FEEDER | S47/11/VI29/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永二線 | 永二線 |  | 永二線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永二線KVAR | 11KV永二線 KVAR | FEEDER | S47/11/VI22/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永二線 | 永二線 |  | 永二線A1 | [17 empty] | 1-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永二線A1 | 11KV永二線 R相AMP | FEEDER | S47/11/VI22/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永二線 | 永二線 |  | 永二線A2 | [17 empty] | 1-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永二線A2 | 11KV永二線 S相AMP | FEEDER | S47/11/VI22/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永二線 | 永二線 |  | 永二線A3 | [17 empty] | 1-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永二線A3 | 11KV永二線 T相AMP | FEEDER | S47/11/VI22/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永二線 | 永二線 |  | 永二線A0 | [17 empty] | 1-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永二線A0 | 11KV永二線 N相AMP | FEEDER | S47/11/VI22/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永八線 | 永八線 |  | 永八線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永八線KVAR | 11KV永八線 KVAR | FEEDER | S47/11/VI28/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永八線 | 永八線 |  | 永八線A1 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永八線A1 | 11KV永八線 R相AMP | FEEDER | S47/11/VI28/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永八線 | 永八線 |  | 永八線A2 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永八線A2 | 11KV永八線 S相AMP | FEEDER | S47/11/VI28/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永八線 | 永八線 |  | 永八線A3 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永八線A3 | 11KV永八線 T相AMP | FEEDER | S47/11/VI28/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永八線 | 永八線 |  | 永八線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永八線A0 | 11KV永八線 N相AMP | FEEDER | S47/11/VI28/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永十線 | 永十線 |  | 永十線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永十線KVAR | 11KV永十線 KVAR | FEEDER | S47/11/VI30/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永十線 | 永十線 |  | 永十線A1 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永十線A1 | 11KV永十線 R相AMP | FEEDER | S47/11/VI30/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永十線 | 永十線 |  | 永十線A2 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永十線A2 | 11KV永十線 S相AMP | FEEDER | S47/11/VI30/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永十線 | 永十線 |  | 永十線A3 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永十線A3 | 11KV永十線 T相AMP | FEEDER | S47/11/VI30/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永十線 | 永十線 |  | 永十線A0 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永十線A0 | 11KV永十線 N相AMP | FEEDER | S47/11/VI30/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永三線 | 永三線 |  | 永三線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永三線KVAR | 11KV永三線 KVAR | FEEDER | S47/11/VI23/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永三線 | 永三線 |  | 永三線A1 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永三線A1 | 11KV永三線 R相AMP | FEEDER | S47/11/VI23/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永三線 | 永三線 |  | 永三線A2 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永三線A2 | 11KV永三線 S相AMP | FEEDER | S47/11/VI23/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永三線 | 永三線 |  | 永三線A3 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永三線A3 | 11KV永三線 T相AMP | FEEDER | S47/11/VI23/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永三線 | 永三線 |  | 永三線A0 | [17 empty] | 1-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永三線A0 | 11KV永三線 N相AMP | FEEDER | S47/11/VI23/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永五線 | 永五線 |  | 永五線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永五線KVAR | 11KV永五線 KVAR | FEEDER | S47/11/VI25/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永五線 | 永五線 |  | 永五線A1 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永五線A1 | 11KV永五線 R相AMP | FEEDER | S47/11/VI25/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永五線 | 永五線 |  | 永五線A2 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永五線A2 | 11KV永五線 S相AMP | FEEDER | S47/11/VI25/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永五線 | 永五線 |  | 永五線A3 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永五線A3 | 11KV永五線 T相AMP | FEEDER | S47/11/VI25/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永五線 | 永五線 |  | 永五線A0 | [17 empty] | 1-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永五線A0 | 11KV永五線 N相AMP | FEEDER | S47/11/VI25/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永仁線 | 永仁線 |  | 永仁線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永仁線KVAR | 11KV永仁線 KVAR | FEEDER | S47/11/VI33/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永仁線 | 永仁線 |  | 永仁線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永仁線A1 | 11KV永仁線 R相AMP | FEEDER | S47/11/VI33/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永仁線 | 永仁線 |  | 永仁線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永仁線A2 | 11KV永仁線 S相AMP | FEEDER | S47/11/VI33/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永仁線 | 永仁線 |  | 永仁線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永仁線A3 | 11KV永仁線 T相AMP | FEEDER | S47/11/VI33/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永仁線 | 永仁線 |  | 永仁線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永仁線A0 | 11KV永仁線 N相AMP | FEEDER | S47/11/VI33/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永六線 | 永六線 |  | 永六線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永六線KVAR | 11KV永六線 KVAR | FEEDER | S47/11/VI26/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永六線 | 永六線 |  | 永六線A1 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永六線A1 | 11KV永六線 R相AMP | FEEDER | S47/11/VI26/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永六線 | 永六線 |  | 永六線A2 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永六線A2 | 11KV永六線 S相AMP | FEEDER | S47/11/VI26/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永六線 | 永六線 |  | 永六線A3 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永六線A3 | 11KV永六線 T相AMP | FEEDER | S47/11/VI26/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永六線 | 永六線 |  | 永六線A0 | [17 empty] | 1-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永六線A0 | 11KV永六線 N相AMP | FEEDER | S47/11/VI26/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永正線 | 永正線 |  | 永正線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永正線KVAR | 11KV永正線 KVAR | FEEDER | S47/11/VI24/KVAR |  |  |  | CDC | 140 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永正線 | 永正線 |  | 永正線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永正線A1 | 11KV永正線 R相AMP | FEEDER | S47/11/VI24/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永正線 | 永正線 |  | 永正線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永正線A2 | 11KV永正線 S相AMP | FEEDER | S47/11/VI24/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永正線 | 永正線 |  | 永正線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永正線A3 | 11KV永正線 T相AMP | FEEDER | S47/11/VI24/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永正線 | 永正線 |  | 永正線A0 | [17 empty] | 1-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永正線A0 | 11KV永正線 N相AMP | FEEDER | S47/11/VI24/I_N |  |  |  | CDC | 144 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永孝線 | 永孝線 |  | 永孝線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永孝線KVAR | 11KV永孝線 KVAR | FEEDER | S47/11/VI32/KVAR |  |  |  | CDC | 145 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永孝線 | 永孝線 |  | 永孝線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永孝線A1 | 11KV永孝線 R相AMP | FEEDER | S47/11/VI32/I_R |  |  |  | CDC | 146 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永孝線 | 永孝線 |  | 永孝線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永孝線A2 | 11KV永孝線 S相AMP | FEEDER | S47/11/VI32/I_S |  |  |  | CDC | 147 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永孝線 | 永孝線 |  | 永孝線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永孝線A3 | 11KV永孝線 T相AMP | FEEDER | S47/11/VI32/I_T |  |  |  | CDC | 148 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永孝線 | 永孝線 |  | 永孝線A0 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永孝線A0 | 11KV永孝線 N相AMP | FEEDER | S47/11/VI32/I_N |  |  |  | CDC | 149 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永忠線 | 永忠線 |  | 永忠線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永忠線KVAR | 11KV永忠線 KVAR | FEEDER | S47/11/VI31/KVAR |  |  |  | CDC | 150 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永忠線 | 永忠線 |  | 永忠線A1 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永忠線A1 | 11KV永忠線 R相AMP | FEEDER | S47/11/VI31/I_R |  |  |  | CDC | 151 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永忠線 | 永忠線 |  | 永忠線A2 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永忠線A2 | 11KV永忠線 S相AMP | FEEDER | S47/11/VI31/I_S |  |  |  | CDC | 152 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永忠線 | 永忠線 |  | 永忠線A3 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永忠線A3 | 11KV永忠線 T相AMP | FEEDER | S47/11/VI31/I_T |  |  |  | CDC | 153 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永忠線 | 永忠線 |  | 永忠線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永忠線A0 | 11KV永忠線 N相AMP | FEEDER | S47/11/VI31/I_N |  |  |  | CDC | 154 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永信線 | 永信線 |  | 永信線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永信線KVAR | 11KV永信線 KVAR | FEEDER | S47/11/VI35/KVAR |  |  |  | CDC | 155 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永信線 | 永信線 |  | 永信線A1 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永信線A1 | 11KV永信線 R相AMP | FEEDER | S47/11/VI35/I_R |  |  |  | CDC | 156 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永信線 | 永信線 |  | 永信線A2 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永信線A2 | 11KV永信線 S相AMP | FEEDER | S47/11/VI35/I_S |  |  |  | CDC | 157 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永信線 | 永信線 |  | 永信線A3 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永信線A3 | 11KV永信線 T相AMP | FEEDER | S47/11/VI35/I_T |  |  |  | CDC | 158 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永信線 | 永信線 |  | 永信線A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永信線A0 | 11KV永信線 N相AMP | FEEDER | S47/11/VI35/I_N |  |  |  | CDC | 159 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永愛線 | 永愛線 |  | 永愛線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永愛線KVAR | 11KV永愛線 KVAR | FEEDER | S47/11/VI34/KVAR |  |  |  | CDC | 160 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永愛線 | 永愛線 |  | 永愛線A1 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永愛線A1 | 11KV永愛線 R相AMP | FEEDER | S47/11/VI34/I_R |  |  |  | CDC | 161 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永愛線 | 永愛線 |  | 永愛線A2 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永愛線A2 | 11KV永愛線 S相AMP | FEEDER | S47/11/VI34/I_S |  |  |  | CDC | 162 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永愛線 | 永愛線 |  | 永愛線A3 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永愛線A3 | 11KV永愛線 T相AMP | FEEDER | S47/11/VI34/I_T |  |  |  | CDC | 163 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | 永愛線 | 永愛線 |  | 永愛線A0 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.永愛線A0 | 11KV永愛線 N相AMP | FEEDER | S47/11/VI34/I_N |  |  |  | CDC | 164 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-90 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 永華SS.600TIE_AMP | 600TIE AMP | TIE | S47/69/600/I |  |  |  | CDC | 165 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S47/11/TIE1/I_R |  |  |  | CDC | 166 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S47/11/TIE1/I_S |  |  |  | CDC | 167 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S47/11/TIE1/I_T |  |  |  | CDC | 168 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S47/11/TIE2/I_R |  |  |  | CDC | 169 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S47/11/TIE2/I_S |  |  |  | CDC | 170 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S47/11/TIE2/I_T |  |  |  | CDC | 171 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_MW | #1MTR二次側 MW | DTR | S47/11/M1/MW |  |  |  | CDC | 172 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S47/11/M1/MVAR |  |  |  | CDC | 173 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S47/11/M1/I_R |  |  |  | CDC | 174 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S47/11/M1/I_S |  |  |  | CDC | 175 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S47/11/M1/I_T |  |  |  | CDC | 176 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_OIL | #1MTR 油溫 | DTR | S47//1MTR/OilTemp |  |  |  | CDC | 177 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_COIL | #1MTR 線溫 | DTR | S47//1MTR/CoilTemp |  |  |  | CDC | 178 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-3B |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S47//1MTR/TapPosMv |  |  |  | CDC | 179 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_MW | #2MTR二次側 MW | DTR | S47/11/M2A/MW |  |  |  | CDC | 180 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S47/11/M2A/MVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S47/11/M2A/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S47/11/M2A/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S47/11/M2A/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_OIL | #2MTR 油溫 | DTR | S47//2MTR/OilTemp |  |  |  | CDC | 185 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_COIL | #2MTR 線溫 | DTR | S47//2MTR/CoilTemp |  |  |  | CDC | 186 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S47//2MTR/TapPosMv |  |  |  | CDC | 187 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_MW | #3MTR二次側 MW | DTR | S47/11/M3/MW |  |  |  | CDC | 188 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S47/11/M3/MVAR |  |  |  | CDC | 189 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S47/11/M3/I_R |  |  |  | CDC | 190 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S47/11/M3/I_S |  |  |  | CDC | 191 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S47/11/M3/I_T |  |  |  | CDC | 192 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_OIL | #3MTR 油溫 | DTR | S47//3MTR/OilTemp |  |  |  | CDC | 193 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_COIL | #3MTR 線溫 | DTR | S47//3MTR/CoilTemp |  |  |  | CDC | 194 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS3_2 | [8 empty] | 永華SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S47//3MTR/TapPosMv |  |  |  | CDC | 195 | GENERICAIPoint | SS307_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S47 | 永華SS | 0 |  |  |  |  | DCV | [17 empty] | 2-82 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS3_2 | [8 empty] | 永華SS.直流電源電壓 | 直流電源電壓 | OTHER | S47/0/StaDev/DCV |  |  |  | CDC | 196 | GENERICAIPoint | SS307_L2 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_N | [8 empty] | 永華SS.630_PHA | 學甲線(630) 相間RY | LINE69 | S47/69/630/PHA |  |  |  | CDC | 197 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_N | [8 empty] | 永華SS.630_GDA | 學甲線(630) 接地RY | LINE69 | S47/69/630/GDA |  |  |  | CDC | 198 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 永華SS.630_CB | 630(學甲線) CB | LINE69 | S47/69/630/CB |  |  |  | CDC | 199 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | DS1 | 631 | [16 empty] | 1-38-08 | 1-38-09 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 永華SS.631_DS | 631(學甲線) DS | LINE69 | S47/69/630/DS1 |  |  |  | CDC | 200 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | DS2 | 632 | [16 empty] | 1-38-10 | 1-38-11 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 永華SS.632_DS | 632(學甲線) DS | LINE69 | S47/69/630/DS2 |  |  |  | CDC | 201 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | DS3 | 633 | [16 empty] | 1-38-12 | 1-38-13 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 永華SS.633_DS | 633(學甲線) DS | LINE69 | S47/69/630/DS3 |  |  |  | CDC | 202 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | E3 | 633E | [16 empty] | 1-38-14 | 1-38-15 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 永華SS.633E_ES | 633E(學甲線) ES | LINE69 | S47/69/630/ES3 |  |  |  | CDC | 203 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 永華SS.640_PHA | 新塭線(640) 相間RY | LINE69 | S47/69/640/PHA |  |  |  | CDC | 204 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 永華SS.640_GDA | 新塭線(640) 接地RY | LINE69 | S47/69/640/GDA |  |  |  | CDC | 205 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 永華SS.640_CB | 640(新塭線) CB | LINE69 | S47/69/640/CB |  |  |  | CDC | 206 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | DS1 | 641 | [16 empty] | 1-38-00 | 1-38-01 | 1-10 | [5 empty] | ADCS_N | [8 empty] | 永華SS.641_DS | 641(新塭線) DS | LINE69 | S47/69/640/DS1 |  |  |  | CDC | 207 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | DS2 | 642 | [16 empty] | 1-38-02 | 1-38-03 | 1-11 | [5 empty] | ADCS_N | [8 empty] | 永華SS.642_DS | 642(新塭線) DS | LINE69 | S47/69/640/DS2 |  |  |  | CDC | 208 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | DS3 | 643 | [16 empty] | 1-38-04 | 1-38-05 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 永華SS.643_DS | 643(新塭線) DS | LINE69 | S47/69/640/DS3 |  |  |  | CDC | 209 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | E3 | 643E | [16 empty] | 1-38-06 | 1-38-07 | 1-13 | [5 empty] | ADCS_N | [8 empty] | 永華SS.643E_ES | 643E(新塭線) ES | LINE69 | S47/69/640/ES3 |  |  |  | CDC | 210 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | PHA | [17 empty] | 1-0C-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_PHA | 11KV永一線(VI21) 相間RY | FEEDER | S47/11/VI21/PHA |  |  |  | CDC | 211 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | GDA | [17 empty] | 1-0C-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_GDA | 11KV永一線(VI21) 接地RY | FEEDER | S47/11/VI21/GDA |  |  |  | CDC | 212 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) 79RY |  | 79UL | [17 empty] | 1-33-06 |  | 1-3E | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_79UL | 11KV永一線(VI21) 79RY U/L | FEEDER | S47/11/VI21/79UL |  |  |  | CDC | 213 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_ADJ | 11KV永一線(VI21) LCO分流器 U/L | FEEDER | S47/11/VI21/ADJ |  |  |  | CDC | 214 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI21 | VI21(11KV永一線) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_CB | VI21(11KV永一線) CB | FEEDER | S47/11/VI21/CB |  |  |  | CDC | 215 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_PHA | 11KV永二線(VI22) 相間RY | FEEDER | S47/11/VI22/PHA |  |  |  | CDC | 216 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_GDA | 11KV永二線(VI22) 接地RY | FEEDER | S47/11/VI22/GDA |  |  |  | CDC | 217 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3F | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_79UL | 11KV永二線(VI22) 79RY U/L | FEEDER | S47/11/VI22/79UL |  |  |  | CDC | 218 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_ADJ | 11KV永二線(VI22) LCO分流器 U/L | FEEDER | S47/11/VI22/ADJ |  |  |  | CDC | 219 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI22 | VI22(11KV永二線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_CB | VI22(11KV永二線) CB | FEEDER | S47/11/VI22/CB |  |  |  | CDC | 220 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_PHA | 11KV永三線(VI23) 相間RY | FEEDER | S47/11/VI23/PHA |  |  |  | CDC | 221 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_GDA | 11KV永三線(VI23) 接地RY | FEEDER | S47/11/VI23/GDA |  |  |  | CDC | 222 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-40 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_79UL | 11KV永三線(VI23) 79RY U/L | FEEDER | S47/11/VI23/79UL |  |  |  | CDC | 223 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_ADJ | 11KV永三線(VI23) LCO分流器 U/L | FEEDER | S47/11/VI23/ADJ |  |  |  | CDC | 224 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI23 | VI23(11KV永三線) |  | CB | [17 empty] | 1-0C-05 |  | 1-37 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_CB | VI23(11KV永三線) CB | FEEDER | S47/11/VI23/CB |  |  |  | CDC | 225 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_PHA | 11KV永正線(VI24) 相間RY | FEEDER | S47/11/VI24/PHA |  |  |  | CDC | 226 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_GDA | 11KV永正線(VI24) 接地RY | FEEDER | S47/11/VI24/GDA |  |  |  | CDC | 227 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-41 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_79UL | 11KV永正線(VI24) 79RY U/L | FEEDER | S47/11/VI24/79UL |  |  |  | CDC | 228 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_ADJ | 11KV永正線(VI24) LCO分流器 U/L | FEEDER | S47/11/VI24/ADJ |  |  |  | CDC | 229 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI24 | VI24(11KV永正線) |  | CB | [17 empty] | 1-0D-00 |  | 1-38 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_CB | VI24(11KV永正線) CB | FEEDER | S47/11/VI24/CB |  |  |  | CDC | 230 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_PHA | 11KV永五線(VI25) 相間RY | FEEDER | S47/11/VI25/PHA |  |  |  | CDC | 231 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_GDA | 11KV永五線(VI25) 接地RY | FEEDER | S47/11/VI25/GDA |  |  |  | CDC | 232 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-42 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_79UL | 11KV永五線(VI25) 79RY U/L | FEEDER | S47/11/VI25/79UL |  |  |  | CDC | 233 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_ADJ | 11KV永五線(VI25) LCO分流器 U/L | FEEDER | S47/11/VI25/ADJ |  |  |  | CDC | 234 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI25 | VI25(11KV永五線) |  | CB | [17 empty] | 1-0D-03 |  | 1-39 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_CB | VI25(11KV永五線) CB | FEEDER | S47/11/VI25/CB |  |  |  | CDC | 235 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | PHA | [17 empty] | 1-0E-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_PHA | 11KV永六線(VI26) 相間RY | FEEDER | S47/11/VI26/PHA |  |  |  | CDC | 236 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | GDA | [17 empty] | 1-0E-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_GDA | 11KV永六線(VI26) 接地RY | FEEDER | S47/11/VI26/GDA |  |  |  | CDC | 237 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) 79RY |  | 79UL | [17 empty] | 1-34-06 |  | 1-51 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_79UL | 11KV永六線(VI26) 79RY U/L | FEEDER | S47/11/VI26/79UL |  |  |  | CDC | 238 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_ADJ | 11KV永六線(VI26) LCO分流器 U/L | FEEDER | S47/11/VI26/ADJ |  |  |  | CDC | 239 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI26 | VI26(11KV永六線) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_CB | VI26(11KV永六線) CB | FEEDER | S47/11/VI26/CB |  |  |  | CDC | 240 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | PHA | [17 empty] | 1-0F-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_PHA | 11KV永七線(VI27) 相間RY | FEEDER | S47/11/VI27/PHA |  |  |  | CDC | 241 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | GDA | [17 empty] | 1-0F-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_GDA | 11KV永七線(VI27) 接地RY | FEEDER | S47/11/VI27/GDA |  |  |  | CDC | 242 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-52 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_79UL | 11KV永七線(VI27) 79RY U/L | FEEDER | S47/11/VI27/79UL |  |  |  | CDC | 243 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_ADJ | 11KV永七線(VI27) LCO分流器 U/L | FEEDER | S47/11/VI27/ADJ |  |  |  | CDC | 244 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI27 | VI27(11KV永七線) |  | CB | [17 empty] | 1-0F-00 |  | 1-49 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_CB | VI27(11KV永七線) CB | FEEDER | S47/11/VI27/CB |  |  |  | CDC | 245 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | PHA | [17 empty] | 1-0F-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_PHA | 11KV永八線(VI28) 相間RY | FEEDER | S47/11/VI28/PHA |  |  |  | CDC | 246 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | GDA | [17 empty] | 1-0F-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_GDA | 11KV永八線(VI28) 接地RY | FEEDER | S47/11/VI28/GDA |  |  |  | CDC | 247 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-53 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_79UL | 11KV永八線(VI28) 79RY U/L | FEEDER | S47/11/VI28/79UL |  |  |  | CDC | 248 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_ADJ | 11KV永八線(VI28) LCO分流器 U/L | FEEDER | S47/11/VI28/ADJ |  |  |  | CDC | 249 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI28 | VI28(11KV永八線) |  | CB | [17 empty] | 1-0F-03 |  | 1-4A | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_CB | VI28(11KV永八線) CB | FEEDER | S47/11/VI28/CB |  |  |  | CDC | 250 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_PHA | 11KV永九線(VI29) 相間RY | FEEDER | S47/11/VI29/PHA |  |  |  | CDC | 251 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_GDA | 11KV永九線(VI29) 接地RY | FEEDER | S47/11/VI29/GDA |  |  |  | CDC | 252 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-54 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_79UL | 11KV永九線(VI29) 79RY U/L | FEEDER | S47/11/VI29/79UL |  |  |  | CDC | 253 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_ADJ | 11KV永九線(VI29) LCO分流器 U/L | FEEDER | S47/11/VI29/ADJ |  |  |  | CDC | 254 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI29 | VI29(11KV永九線) |  | CB | [17 empty] | 1-0F-06 |  | 1-4B | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_CB | VI29(11KV永九線) CB | FEEDER | S47/11/VI29/CB |  |  |  | CDC | 255 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_PHA | 11KV永十線(VI30) 相間RY | FEEDER | S47/11/VI30/PHA |  |  |  | CDC | 256 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_GDA | 11KV永十線(VI30) 接地RY | FEEDER | S47/11/VI30/GDA |  |  |  | CDC | 257 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-55 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_79UL | 11KV永十線(VI30) 79RY U/L | FEEDER | S47/11/VI30/79UL |  |  |  | CDC | 258 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_ADJ | 11KV永十線(VI30) LCO分流器 U/L | FEEDER | S47/11/VI30/ADJ |  |  |  | CDC | 259 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI30 | VI30(11KV永十線) |  | CB | [17 empty] | 1-10-01 |  | 1-4C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_CB | VI30(11KV永十線) CB | FEEDER | S47/11/VI30/CB |  |  |  | CDC | 260 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | PHA | [17 empty] | 1-11-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_PHA | 11KV永忠線(VI31) 相間RY | FEEDER | S47/11/VI31/PHA |  |  |  | CDC | 261 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | GDA | [17 empty] | 1-11-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_GDA | 11KV永忠線(VI31) 接地RY | FEEDER | S47/11/VI31/GDA |  |  |  | CDC | 262 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) 79RY |  | 79UL | [17 empty] | 1-35-06 |  | 1-64 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_79UL | 11KV永忠線(VI31) 79RY U/L | FEEDER | S47/11/VI31/79UL |  |  |  | CDC | 263 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_ADJ | 11KV永忠線(VI31) LCO分流器 U/L | FEEDER | S47/11/VI31/ADJ |  |  |  | CDC | 264 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI31 | VI31(11KV永忠線) |  | CB | [17 empty] | 1-11-03 |  | 1-5C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_CB | VI31(11KV永忠線) CB | FEEDER | S47/11/VI31/CB |  |  |  | CDC | 265 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | PHA | [17 empty] | 1-11-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_PHA | 11KV永孝線(VI32) 相間RY | FEEDER | S47/11/VI32/PHA |  |  |  | CDC | 266 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | GDA | [17 empty] | 1-12-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_GDA | 11KV永孝線(VI32) 接地RY | FEEDER | S47/11/VI32/GDA |  |  |  | CDC | 267 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-65 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_79UL | 11KV永孝線(VI32) 79RY U/L | FEEDER | S47/11/VI32/79UL |  |  |  | CDC | 268 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_ADJ | 11KV永孝線(VI32) LCO分流器 U/L | FEEDER | S47/11/VI32/ADJ |  |  |  | CDC | 269 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI32 | VI32(11KV永孝線) |  | CB | [17 empty] | 1-11-06 |  | 1-5D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_CB | VI32(11KV永孝線) CB | FEEDER | S47/11/VI32/CB |  |  |  | CDC | 270 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | PHA | [17 empty] | 1-12-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_PHA | 11KV永仁線(VI33) 相間RY | FEEDER | S47/11/VI33/PHA |  |  |  | CDC | 271 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | GDA | [17 empty] | 1-12-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_GDA | 11KV永仁線(VI33) 接地RY | FEEDER | S47/11/VI33/GDA |  |  |  | CDC | 272 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-66 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_79UL | 11KV永仁線(VI33) 79RY U/L | FEEDER | S47/11/VI33/79UL |  |  |  | CDC | 273 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_ADJ | 11KV永仁線(VI33) LCO分流器 U/L | FEEDER | S47/11/VI33/ADJ |  |  |  | CDC | 274 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI33 | VI33(11KV永仁線) |  | CB | [17 empty] | 1-12-01 |  | 1-5E | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_CB | VI33(11KV永仁線) CB | FEEDER | S47/11/VI33/CB |  |  |  | CDC | 275 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_PHA | 11KV永愛線(VI34) 相間RY | FEEDER | S47/11/VI34/PHA |  |  |  | CDC | 276 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_GDA | 11KV永愛線(VI34) 接地RY | FEEDER | S47/11/VI34/GDA |  |  |  | CDC | 277 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-67 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_79UL | 11KV永愛線(VI34) 79RY U/L | FEEDER | S47/11/VI34/79UL |  |  |  | CDC | 278 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_ADJ | 11KV永愛線(VI34) LCO分流器 U/L | FEEDER | S47/11/VI34/ADJ |  |  |  | CDC | 279 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI34 | VI34(11KV永愛線) |  | CB | [17 empty] | 1-12-04 |  | 1-5F | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_CB | VI34(11KV永愛線) CB | FEEDER | S47/11/VI34/CB |  |  |  | CDC | 280 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_PHA | 11KV永信線(VI35) 相間RY | FEEDER | S47/11/VI35/PHA |  |  |  | CDC | 281 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_GDA | 11KV永信線(VI35) 接地RY | FEEDER | S47/11/VI35/GDA |  |  |  | CDC | 282 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-68 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_79UL | 11KV永信線(VI35) 79RY U/L | FEEDER | S47/11/VI35/79UL |  |  |  | CDC | 283 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_ADJ | 11KV永信線(VI35) LCO分流器 U/L | FEEDER | S47/11/VI35/ADJ |  |  |  | CDC | 284 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S47 | 永華SS | 11 | 11kV | VI35 | VI35(11KV永信線) |  | CB | [17 empty] | 1-12-07 |  | 1-60 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_CB | VI35(11KV永信線) CB | FEEDER | S47/11/VI35/CB |  |  |  | CDC | 285 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-02 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 永華SS.600_CB | 600(TIE) CB | TIE | S47/69/600/CB |  |  |  | CDC | 286 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 永華SS.601_DS | 601(TIE) DS | TIE | S47/69/600/DS1 |  |  |  | CDC | 287 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 永華SS.602_DS | 602(TIE) DS | TIE | S47/69/600/DS2 |  |  |  | CDC | 288 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0E-01 |  | 1-3A | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE1_CB | 11KV TIE1 CB | TIE | S47/11/TIE1/CB |  |  |  | CDC | 289 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE1_51A | 11KV TIE1 51RY | TIE | S47/11/TIE1/51A |  |  |  | CDC | 290 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S47/11/TIE1/51NA |  |  |  | CDC | 291 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-10-07 |  | 1-4D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE2_CB | 11KV TIE2 CB | TIE | S47/11/TIE2/CB |  |  |  | CDC | 292 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE2_51A | 11KV TIE2 51RY | TIE | S47/11/TIE2/51A |  |  |  | CDC | 293 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S47/11/TIE2/51NA |  |  |  | CDC | 294 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-32 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.750_CB | 750(#1MTR) CB | DTR | S47/69/750/CB |  |  |  | CDC | 295 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-33 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.1M_CB | 1M(#1MTR) CB | DTR | S47/11/M1/CB |  |  |  | CDC | 296 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_51A | #1MTR 51RY | DTR | S47/69/750/51A |  |  |  | CDC | 297 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_51NA | #1MTR 51N RY | DTR | S47/69/750/51NA |  |  |  | CDC | 298 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S47//1MTR/51ZA |  |  |  | CDC | 299 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_87A | #1MTR 87RY | DTR | S47//1MTR/87A |  |  |  | CDC | 300 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S47//1MTR/87UL |  |  |  | CDC | 301 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S47/11/M1/51A |  |  |  | CDC | 302 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_TRA | #1MTR 重故障 | DTR | S47//1MTR/TRA |  |  |  | CDC | 303 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S47//1MTR/TRF |  |  |  | CDC | 304 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S47//1MTR/SupLocal |  |  |  | CDC | 305 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S47//1MTR/Tap Chan |  |  |  | CDC | 306 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-37-00 | 1-37-01 | 1-2C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.751_DS | 751(#1MTR) DS | DTR | S47/69/750/DS1 |  |  |  | CDC | 307 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-37-02 | 1-37-03 | 1-2D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.752_DS | 752(#1MTR) DS | DTR | S47/69/750/DS2 |  |  |  | CDC | 308 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_96A | #1MTR 96P RY | DTR | S47//1MTR/96PA |  |  |  | CDC | 309 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S47//1MTR/OLTC_DLY |  |  |  | CDC | 310 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S47//1MTR/AC_Fault |  |  |  | CDC | 311 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.760_CB | 760(#2MTR) CB | DTR | S47/69/760/CB |  |  |  | CDC | 312 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-02-00 |  | 1-45 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.2MA_CB | 2MA(#2MTR) CB | DTR | S47/11/M2A/CB |  |  |  | CDC | 313 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-02-01 |  | 1-46 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.2MB_CB | 2MB(#2MTR) CB | DTR | S47/11/M2B/CB |  |  |  | CDC | 314 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_51A | #2MTR 51RY | DTR | S47/69/760/51A |  |  |  | CDC | 315 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_51NA | #2MTR 51N RY | DTR | S47/69/760/51NA |  |  |  | CDC | 316 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S47//2MTR/51ZA |  |  |  | CDC | 317 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_87A | #2MTR 87RY | DTR | S47//2MTR/87A |  |  |  | CDC | 318 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S47//2MTR/87UL |  |  |  | CDC | 319 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S47/11/M2A/51A |  |  |  | CDC | 320 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S47/11/M2B/51A |  |  |  | CDC | 321 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_TRA | #2MTR 重故障 | DTR | S47//2MTR/TRA |  |  |  | CDC | 322 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S47//2MTR/TRF |  |  |  | CDC | 323 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S47//2MTR/SupLocal |  |  |  | CDC | 324 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S47//2MTR/Tap Chan |  |  |  | CDC | 325 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-37-04 | 1-37-05 | 1-2E | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.761_DS | 761(#2MTR) DS | DTR | S47/69/760/DS1 |  |  |  | CDC | 326 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-37-06 | 1-37-07 | 1-2F | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.762_DS | 762(#2MTR) DS | DTR | S47/69/760/DS2 |  |  |  | CDC | 327 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_96A | #2MTR 96P RY | DTR | S47//2MTR/96PA |  |  |  | CDC | 328 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S47//2MTR/OLTC_DLY |  |  |  | CDC | 329 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S47//2MTR/AC_Fault |  |  |  | CDC | 330 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.770_CB | 770(#3MTR) CB | DTR | S47/69/770/CB |  |  |  | CDC | 331 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-03-04 |  | 1-59 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.3M_CB | 3M(#3MTR) CB | DTR | S47/11/M3/CB |  |  |  | CDC | 332 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-02-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_51A | #3MTR 51RY | DTR | S47/69/770/51A |  |  |  | CDC | 333 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_51NA | #3MTR 51N RY | DTR | S47/69/770/51NA |  |  |  | CDC | 334 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-03-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S47//3MTR/51ZA |  |  |  | CDC | 335 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_87A | #3MTR 87RY | DTR | S47//3MTR/87A |  |  |  | CDC | 336 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S47//3MTR/87UL |  |  |  | CDC | 337 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S47/11/M3/51A |  |  |  | CDC | 338 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_TRA | #3MTR 重故障 | DTR | S47//3MTR/TRA |  |  |  | CDC | 339 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S47//3MTR/TRF |  |  |  | CDC | 340 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S47//3MTR/SupLocal |  |  |  | CDC | 341 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S47//3MTR/Tap Chan |  |  |  | CDC | 342 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-37-08 | 1-37-09 | 1-30 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.771_DS | 771(#3MTR) DS | DTR | S47/69/770/DS1 |  |  |  | CDC | 343 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-37-10 | 1-37-11 | 1-31 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.772_DS | 772(#3MTR) DS | DTR | S47/69/770/DS2 |  |  |  | CDC | 344 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_96A | #3MTR 96P RY | DTR | S47//3MTR/96PA |  |  |  | CDC | 345 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S47//3MTR/OLTC_DLY |  |  |  | CDC | 346 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-36-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S47//3MTR/AC_Fault |  |  |  | CDC | 347 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0D-06 |  | 1-34 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.210_CB | 210(11KV #1SC) CB | SC | S47/11/210/CB |  |  |  | CDC | 348 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-11 |  | 1-3D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S47/11/210/Tap Chan |  |  |  | CDC | 349 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0D-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.210_SCA | 11KV #1SC 51,51N RY | SC | S47/11/210/SCA |  |  |  | CDC | 350 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0E-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S47/11/210/UVA |  |  |  | CDC | 351 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-10-04 |  | 1-47 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.220_CB | 220(11KV #2SC) CB | SC | S47/11/220/CB |  |  |  | CDC | 352 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-11 |  | 1-50 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S47/11/220/Tap Chan |  |  |  | CDC | 353 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-10-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.220_SCA | 11KV #2SC 51,51N RY | SC | S47/11/220/SCA |  |  |  | CDC | 354 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-10-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S47/11/220/UVA |  |  |  | CDC | 355 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-13-02 |  | 1-5B | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.230_CB | 230(11KV #3SC) CB | SC | S47/11/230/CB |  |  |  | CDC | 356 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-11 |  | 1-63 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S47/11/230/Tap Chan |  |  |  | CDC | 357 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-13-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.230_SCA | 11KV #3SC 51,51N RY | SC | S47/11/230/SCA |  |  |  | CDC | 358 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-13-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S47/11/230/UVA |  |  |  | CDC | 359 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 永華SS.810_CB | 810(69KV #1SC) CB | SC | S47/69/810/CB |  |  |  | CDC | 360 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 1-37-12 | 1-37-13 | 1-28 | [5 empty] | ADCS_N | [8 empty] | 永華SS.811_DS | 811(69KV #1SC) DS | SC | S47/69/810/DS1 |  |  |  | CDC | 361 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 1-37-14 | 1-37-15 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 永華SS.812_DS | 812(69KV #1SC) DS | SC | S47/69/810/DS2 |  |  |  | CDC | 362 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_N | [8 empty] | 永華SS.810_SCA | 69KV #1SC 51,51N RY | SC | S47/69/810/SCA |  |  |  | CDC | 363 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_N | [8 empty] | 永華SS.810_OUVA | 69KV #1SC 27,59RY | SC | S47/69/810/UVA |  |  |  | CDC | 364 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 永華SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S47/69/1BUS/BUS_VUA |  |  |  | CDC | 365 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 永華SS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | S47/69/1BUS/87A |  |  |  | CDC | 366 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 691BUS | 69#1BUS |  | 87UL | [17 empty] | 1-32-14 |  | 1-26 | [5 empty] | 69KV_N | [8 empty] | 永華SS.69#1BUS_87UL | 69#1BUS87U/L | OTHER | S47/69/1BUS/87UL |  |  |  | CDC | 367 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 永華SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S47/69/2BUS/BUS_VUA |  |  |  | CDC | 368 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | 69KV_N | [8 empty] | 永華SS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | S47/69/2BUS/87A |  |  |  | CDC | 369 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 692BUS | 69#2BUS |  | 87UL | [17 empty] | 1-32-15 |  | 1-27 | [5 empty] | 69KV_N | [8 empty] | 永華SS.69#2BUS_87UL | 69#2BUS87U/L | OTHER | S47/69/2BUS/87UL |  |  |  | CDC | 370 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S47/11/ComPoint/CBA |  |  |  | CDC | 371 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S47/11/ComPoint/CBF |  |  |  | CDC | 372 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | _SC | 電容器組 |  | 60A | [17 empty] | 1-33-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_SC_60A | 11KV電容器組 60RY | OTHER | S47/11/ComPoint/FDR_60A |  |  |  | CDC | 373 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S47/69/ComPoint/ABS_89A |  |  |  | CDC | 374 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S47/69/ComPoint/CBA |  |  |  | CDC | 375 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S47/69/ComPoint/CBF |  |  |  | CDC | 376 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S47/0/RTU/RTU_R_L |  |  |  | CDC | 377 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S47 | 永華SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.TEST_CB | TEST CB | OTHER | S47/0/RTU/Test_CB |  |  |  | CDC | 378 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.火災警報(1) | 火警 | OTHER | S47/0/StaDev/Fire1 |  |  |  | CDC | 379 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-31-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.火災警報(2) | CO2警報 | OTHER | S47/0/StaDev/Fire2 |  |  |  | CDC | 380 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-31-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.火災警報(3) | CO2故障 | OTHER | S47/0/StaDev/Fire3 |  |  |  | CDC | 381 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-30-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.其他重故障 | 變電所內其他重故障 | OTHER | S47/0/StaDev/PSA |  |  |  | CDC | 382 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S47/0/StaDev/PSF |  |  |  | CDC | 383 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S47/0/StaDev/ACB1 |  |  |  | CDC | 384 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S47 | 永華SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S47/0/StaDev/ACB2 |  |  |  | CDC | 385 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S47 | 永華SS | 0 |  |  |  |  | ACBA | [17 empty] | 1-31-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.所內電源ACBA | 所內電源故障警報 | OTHER | S47/0/StaDev/ACBA |  |  |  | CDC | 386 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S47/0/StaDev/STUV |  |  |  | CDC | 387 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.直流充電機故障 | 直流充電機故障 | OTHER | S47/0/StaDev/CHG1 |  |  |  | CDC | 388 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S47/0/StaDev/DCA |  |  |  | CDC | 389 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S47/0/StaDev/DCE |  |  |  | CDC | 390 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S47/0/StaDev/OilLeak |  |  |  | CDC | 391 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-35-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S47/0/StaDev/2A5Other |  |  |  | CDC | 392 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-35-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S47/0/StaDev/3A5Other |  |  |  | CDC | 393 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-35-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S47/0/StaDev/4A5Other |  |  |  | CDC | 394 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S47/0/StaDev/CHG2 |  |  |  | CDC | 395 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-35-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S47/0/StaDev/CommACF |  |  |  | CDC | 396 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-31-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化防盜(1) | 無人化防盜(1) | OTHER | S47/0/StaDev/Burglar1 |  |  |  | CDC | 397 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-31-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化防盜(2) | 無人化防盜(2) | OTHER | S47/0/StaDev/Burglar2 |  |  |  | CDC | 398 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-31-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化防盜(3) | 無人化防盜(3) | OTHER | S47/0/StaDev/Burglar3 |  |  |  | CDC | 399 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S47/0/StaDev/Door1 |  |  |  | CDC | 400 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Door2 | [17 empty] | 1-31-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化門禁(2) | 所內淹水高水位 | OTHER | S47/0/StaDev/Door2 |  |  |  | CDC | 401 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Door3 | [17 empty] | 1-31-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.無人化門禁(3) | 所內淹水低水位 | OTHER | S47/0/StaDev/Door3 |  |  |  | CDC | 402 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-6A | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S47/0/StaDev/Lights1 |  |  |  | CDC | 403 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S47 | 永華SS | 11 | 11kV | _1SC | #1SC |  | 60A | [17 empty] | 1-33-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER | S47/11/210/FDR_60A |  |  |  | CDC | 404 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | _2SC | #2SC |  | 60A | [17 empty] | 1-33-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_#2SC_60A | 11KV #2SC 60A | OTHER | S47/11/220/FDR_60A |  |  |  | CDC | 405 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | _3SC | #3SC |  | 60A | [17 empty] | 1-33-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER | S47/11/230/FDR_60A |  |  |  | CDC | 406 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.RTU_DC故障 | RTU DC故障 | OTHER | S47/0/RTU/DCA |  |  |  | CDC | 407 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 水位警報 | 水位警報 |  | 1 | [17 empty] | 1-34-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.水位警報_1 | 水位警報 1 | OTHER | S47/0/StaDev/Water1 |  |  |  | CDC | 408 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 水位警報 | 水位警報 | [19 empty] | 1-34-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.水位警報_2 | 水位警報 2 | OTHER | S47/0/StaDev/Water2 |  |  |  | CDC | 409 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.安全監控 | 安全監控 | OTHER | S47/0/StaDev/Burglar |  |  |  | CDC | 410 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.門禁小門 | 門禁小門 | OTHER | S47/0/StaDev/Door4 |  |  |  | CDC | 411 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-6B | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S47/0/StaDev/Lights2 |  |  |  | CDC | 412 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  |  |  |  | 緊急發電機啟動 | [17 empty] | 1-32-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.緊急發電機啟動 | 緊急發電機啟動 | OTHER | S47/0/StaDev/1A5Other |  |  |  | CDC | 413 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 0 |  |  |  |  | 變電所水位高 | [17 empty] | 1-30-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.變電所水位高 | 變電所水位高 | OTHER | S47/0/StaDev/Water3 |  |  |  | CDC | 414 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | 600GDA(1) | [17 empty] | 1-04-04 | [7 empty] | 69KV_N | [8 empty] | 永華SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | TIE | S47/69/600/51NA |  |  |  | CDC | 415 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | 600GDA(2) | [17 empty] | 1-05-00 | [7 empty] | 69KV_N | [8 empty] | 永華SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | TIE | S47/69/600/GDA |  |  |  | CDC | 416 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 1BUS | #1BUS |  | 600PHA(1) | [17 empty] | 1-04-03 | [7 empty] | 69KV_N | [8 empty] | 永華SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | TIE | S47/69/600/51A |  |  |  | CDC | 417 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 2BUS | #2BUS |  | 600PHA(2) | [17 empty] | 1-04-07 | [7 empty] | 69KV_N | [8 empty] | 永華SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | TIE | S47/69/600/PHA |  |  |  | CDC | 418 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MA | #1MA |  | 81AS | [17 empty] | 1-14-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MA_81A/S | #1MA 81RY | OTHER | S47/11/M1/81A |  |  |  | CDC | 419 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S47 | 永華SS | 0 |  | 1MA | #1MA |  | 81UL | [17 empty] | 1-3D-01 |  | 1-6C | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MA_81U/L | #1MA 81RY U/L | OTHER | S47/11/M1/81UL |  |  |  | CDC | 420 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MA | #2MA |  | 81AS | [17 empty] | 1-14-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MA_81A/S | #2MA 81RY | OTHER | S47/11/M2A/81A |  |  |  | CDC | 421 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S47 | 永華SS | 0 |  | 2MA | #2MA |  | 81UL | [17 empty] | 1-3D-02 |  | 1-6D | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MA_81U/L | #2MA 81RY U/L | OTHER | S47/11/M2A/81UL |  |  |  | CDC | 422 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MB | #2MB |  | 81AS | [17 empty] | 1-14-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MB_81A/S | #2MB 81RY | OTHER | S47/11/M2B/81A |  |  |  | CDC | 423 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S47 | 永華SS | 0 |  | 2MB | #2MB |  | 81UL | [17 empty] | 1-3D-03 |  | 1-6E | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MB_81U/L | #2MB 81RY U/L | OTHER | S47/11/M2B/81UL |  |  |  | CDC | 424 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 3MA | #3MA |  | 81AS | [17 empty] | 1-14-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MA_81A/S | #3MA 81RY | OTHER | S47/11/M3/81A |  |  |  | CDC | 425 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S47 | 永華SS | 0 |  | 3MA | #3MA |  | 81UL | [17 empty] | 1-3D-04 |  | 1-6F | [5 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MA_81U/L | #3MA 81RY U/L | OTHER | S47/11/M3/81UL |  |  |  | CDC | 426 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV |  |  |  | RYFA | [17 empty] | 1-3C-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.11KV_RYFA | 11KV數位電驛故障 | OTHER | S47/11/ComPoint/RYFA |  |  |  | CDC | 427 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | POWER | POWER |  | PMA | [17 empty] | 1-3D-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.PMA | POWER METER故障 | OTHER | S47/0/StaDev/PMA |  |  |  | CDC | 428 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21_79 | 永一線(VI21) |  | LOA | [17 empty] | 1-3C-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_79_LOA | 11KV永一線(VI21) 79LOA | OTHER | S47/11/VI21/LOA |  |  |  | CDC | 429 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) |  | 81AS | [17 empty] | 1-14-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_81A/S | 11KV永一線(VI21) 81RY | OTHER | S47/11/VI21/81AS |  |  |  | CDC | 430 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22_79 | 永二線(VI22) |  | LOA | [17 empty] | 1-3C-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_79_LOA | 11KV永二線(VI22) 79LOA | OTHER | S47/11/VI22/LOA |  |  |  | CDC | 431 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) |  | 81AS | [17 empty] | 1-14-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_81A/S | 11KV永二線(VI22) 81RY | OTHER | S47/11/VI22/81AS |  |  |  | CDC | 432 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23_79 | 永三線(VI23) |  | LOA | [17 empty] | 1-3C-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_79_LOA | 11KV永三線(VI23) 79LOA | OTHER | S47/11/VI23/LOA |  |  |  | CDC | 433 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) |  | 81AS | [17 empty] | 1-14-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_81A/S | 11KV永三線(VI23) 81RY | OTHER | S47/11/VI23/81AS |  |  |  | CDC | 434 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24_79 | 永正線(VI24) |  | LOA | [17 empty] | 1-3C-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_79_LOA | 11KV永正線(VI24) 79LOA | OTHER | S47/11/VI24/LOA |  |  |  | CDC | 435 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) |  | 81AS | [17 empty] | 1-15-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_81A/S | 11KV永正線(VI24) 81RY | OTHER | S47/11/VI24/81AS |  |  |  | CDC | 436 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25_79 | 永五線(VI25) |  | LOA | [17 empty] | 1-3C-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_79_LOA | 11KV永五線(VI25) 79LOA | OTHER | S47/11/VI25/LOA |  |  |  | CDC | 437 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) |  | 81AS | [17 empty] | 1-15-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_81A/S | 11KV永五線(VI25) 81RY | OTHER | S47/11/VI25/81AS |  |  |  | CDC | 438 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26_79 | 永六線(VI26) |  | LOA | [17 empty] | 1-3C-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_79_LOA | 11KV永六線(VI26) 79LOA | OTHER | S47/11/VI26/LOA |  |  |  | CDC | 439 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) |  | 81AS | [17 empty] | 1-15-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_81A/S | 11KV永六線(VI26) 81RY | OTHER | S47/11/VI26/81AS |  |  |  | CDC | 440 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27_79 | 永七線(VI27) |  | LOA | [17 empty] | 1-3C-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_79_LOA | 11KV永七線(VI27) 79LOA | OTHER | S47/11/VI27/LOA |  |  |  | CDC | 441 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) |  | 81AS | [17 empty] | 1-15-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_81A/S | 11KV永七線(VI27) 81RY | OTHER | S47/11/VI27/81AS |  |  |  | CDC | 442 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28_79 | 永八線(VI28) |  | LOA | [17 empty] | 1-3C-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_79_LOA | 11KV永八線(VI28) 79LOA | OTHER | S47/11/VI28/LOA |  |  |  | CDC | 443 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) |  | 81AS | [17 empty] | 1-15-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_81A/S | 11KV永八線(VI28) 81RY | OTHER | S47/11/VI28/81AS |  |  |  | CDC | 444 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29_79 | 永九線(VI29) |  | LOA | [17 empty] | 1-3C-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_79_LOA | 11KV永九線(VI29) 79LOA | OTHER | S47/11/VI29/LOA |  |  |  | CDC | 445 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) |  | 81AS | [17 empty] | 1-15-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_81A/S | 11KV永九線(VI29) 81RY | OTHER | S47/11/VI29/81AS |  |  |  | CDC | 446 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30_79 | 永十線(VI30) |  | LOA | [17 empty] | 1-3C-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_79_LOA | 11KV永十線(VI30) 79LOA | OTHER | S47/11/VI30/LOA |  |  |  | CDC | 447 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) |  | 81AS | [17 empty] | 1-15-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_81A/S | 11KV永十線(VI30) 81RY | OTHER | S47/11/VI30/81AS |  |  |  | CDC | 448 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31_79 | 永忠線(VI31) |  | LOA | [17 empty] | 1-3C-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_79_LOA | 11KV永忠線(VI31) 79LOA | OTHER | S47/11/VI31/LOA |  |  |  | CDC | 449 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) |  | 81AS | [17 empty] | 1-15-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_81A/S | 11KV永忠線(VI31) 81RY | OTHER | S47/11/VI31/81AS |  |  |  | CDC | 450 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32_79 | 永孝線(VI32) |  | LOA | [17 empty] | 1-3C-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_79_LOA | 11KV永孝線(VI32) 79LOA | OTHER | S47/11/VI32/LOA |  |  |  | CDC | 451 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) |  | 81AS | [17 empty] | 1-16-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_81A/S | 11KV永孝線(VI32) 81RY | OTHER | S47/11/VI32/81AS |  |  |  | CDC | 452 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33_79 | 永仁線(VI33) |  | LOA | [17 empty] | 1-3C-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_79_LOA | 11KV永仁線(VI33) 79LOA | OTHER | S47/11/VI33/LOA |  |  |  | CDC | 453 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) |  | 81AS | [17 empty] | 1-16-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_81A/S | 11KV永仁線(VI33) 81RY | OTHER | S47/11/VI33/81AS |  |  |  | CDC | 454 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34_79 | 永愛線(VI34) |  | LOA | [17 empty] | 1-3C-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_79_LOA | 11KV永愛線(VI34) 79LOA | OTHER | S47/11/VI34/LOA |  |  |  | CDC | 455 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) |  | 81AS | [17 empty] | 1-16-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_81A/S | 11KV永愛線(VI34) 81RY | OTHER | S47/11/VI34/81AS |  |  |  | CDC | 456 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35_79 | 永信線(VI35) |  | LOA | [17 empty] | 1-3C-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_79_LOA | 11KV永信線(VI35) 79LOA | OTHER | S47/11/VI35/LOA |  |  |  | CDC | 457 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) |  | 81AS | [17 empty] | 1-16-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_81A/S | 11KV永信線(VI35) 81RY | OTHER | S47/11/VI35/81AS |  |  |  | CDC | 458 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-06-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_63Q | #1MTR ULTC保護電驛 | OTHER | S47//1MTR/63Q |  |  |  | CDC | 459 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-05-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_96B1 | #1MTR撲氣電驛ㄧ段 | OTHER | S47//1MTR/96B1 |  |  |  | CDC | 460 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-05-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_96B2 | #1MTR撲氣電驛二段 | OTHER | S47//1MTR/96B2 |  |  |  | CDC | 461 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-05-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_96D | #1MTR放壓裝置 | OTHER | S47//1MTR/96D |  |  |  | CDC | 462 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-05-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_96P | #1MTR突壓電驛 | OTHER | S47//1MTR/96P |  |  |  | CDC | 463 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-06-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_63Q | #2MTR ULTC保護電驛 | OTHER | S47//2MTR/63Q |  |  |  | CDC | 464 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-06-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_96B1 | #2MTR撲氣電驛ㄧ段 | OTHER | S47//2MTR/96B1 |  |  |  | CDC | 465 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-06-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_96B2 | #2MTR撲氣電驛二段 | OTHER | S47//2MTR/96B2 |  |  |  | CDC | 466 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-06-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_96D | #2MTR放壓裝置 | OTHER | S47//2MTR/96D |  |  |  | CDC | 467 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-06-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_96P | #2MTR突壓電驛 | OTHER | S47//2MTR/96P |  |  |  | CDC | 468 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-07-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_63Q | #3MTR ULTC保護電驛 | OTHER | S47//3MTR/63Q |  |  |  | CDC | 469 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-06-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_96B1 | #3MTR撲氣電驛ㄧ段 | OTHER | S47//3MTR/96B1 |  |  |  | CDC | 470 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-06-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_96B2 | #3MTR撲氣電驛二段 | OTHER | S47//3MTR/96B2 |  |  |  | CDC | 471 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-07-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_96D | #3MTR放壓裝置 | OTHER | S47//3MTR/96D |  |  |  | CDC | 472 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-07-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_96P | #3MTR突壓電驛 | OTHER | S47//3MTR/96P |  |  |  | CDC | 473 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_N | [8 empty] | 永華SS.630_87A | 學甲線(630) 87RY | LINE69 | S47/69/630/87A |  |  |  | CDC | 474 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 永華SS.630_87UL | 學甲線(630) 87RY U/L | LINE69 | S47/69/630/87UL |  |  |  | CDC | 475 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 630 | 學甲線(630) |  | 87CFA | [17 empty] | 1-32-09 | [7 empty] | 69KV_N | [8 empty] | 永華SS.630_87CFA | 永華學甲(630)87RY通訊故 | OTHER | S47/69/630/87CFA |  |  |  | CDC | 476 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 630 | 學甲線(630) |  | RYFA | [17 empty] | 1-32-08 | [7 empty] | 69KV_N | [8 empty] | 永華SS.630_RYFA | 永華學甲(630)數位電驛故障 | OTHER | S47/69/630/RYFA |  |  |  | CDC | 477 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_N | [8 empty] | 永華SS.640_87A | 新塭線(640) 87RY | LINE69 | S47/69/640/87A |  |  |  | CDC | 478 | GENERICDIPoint | SS307_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 永華SS.640_87UL | 新塭線(640) 87RY U/L | LINE69 | S47/69/640/87UL |  |  |  | CDC | 479 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 640 | 新塭線(640) |  | 87CFA | [17 empty] | 1-32-07 | [7 empty] | 69KV_N | [8 empty] | 永華SS.640_87CFA | 新塭永華(640)87RY通訊故障 | OTHER | S47/69/640/87CFA |  |  |  | CDC | 480 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 640 | 新塭線(640) |  | RYFA | [17 empty] | 1-32-06 | [7 empty] | 69KV_N | [8 empty] | 永華SS.640_RYFA | 新塭永華(640)數位電驛故障 | OTHER | S47/69/640/RYFA |  |  |  | CDC | 481 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 1-32-05 | [7 empty] | 69KV_N | [8 empty] | 永華SS.600_RYFA | 600TIE數位電驛故障 | OTHER | S47/69/600/RYFA |  |  |  | CDC | 482 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 69BUS | 69BUS |  | RYFA | [17 empty] | 1-3D-06 | [7 empty] | 69KV_N | [8 empty] | 永華SS.69BUS_RYFA | 69BUS數位電驛故障 | OTHER | S47/69/ComPoint/BUS_RYFA |  |  |  | CDC | 483 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 69BUS | 69BUS |  | 87CTFA | [17 empty] | 1-3D-07 | [7 empty] | 69KV_N | [8 empty] | 永華SS.69BUS_CTFA | 69BUS數位電驛CT故障 | OTHER | S47/69/ComPoint/12B_CTFA |  |  |  | CDC | 484 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1GIS | #1GIS |  | CBA | [17 empty] | 1-3E-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1GIS_CBA | #1GIS重故障 | OTHER | S47/11/1GIS/CBA |  |  |  | CDC | 485 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1GIS | #1GIS |  | CBF | [17 empty] | 1-3E-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1GIS_CBF | #1GIS輕故障 | OTHER | S47/11/1GIS/CBF |  |  |  | CDC | 486 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2GIS | #2GIS |  | CBA | [17 empty] | 1-3E-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2GIS_CBA | #2GIS重故障 | OTHER | S47/11/2GIS/CBA |  |  |  | CDC | 487 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2GIS | #2GIS |  | CBF | [17 empty] | 1-3E-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2GIS_CBF | #2GIS輕故障 | OTHER | S47/11/2GIS/CBF |  |  |  | CDC | 488 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3GIS | #3GIS |  | CBA | [17 empty] | 1-3E-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3GIS_CBA | #3GIS重故障 | OTHER | S47/11/3GIS/CBA |  |  |  | CDC | 489 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3GIS | #3GIS |  | CBF | [17 empty] | 1-3E-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3GIS_CBF | #3GIS輕故障 | OTHER | S47/11/3GIS/CBF |  |  |  | CDC | 490 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 4GIS | #4GIS |  | CBA | [17 empty] | 1-3E-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#4GIS_CBA | #4GIS重故障 | OTHER | S47/11/4GIS/CBA |  |  |  | CDC | 491 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 4GIS | #4GIS |  | CBF | [17 empty] | 1-3E-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#4GIS_CBF | #4GIS輕故障 | OTHER | S47/11/4GIS/CBF |  |  |  | CDC | 492 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 11 | 11kV | VI21 | 永一線(VI21) 81RY |  | 81UL | [17 empty] | 1-3E-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_81U/L | 11KV永一線(VI21) 81RY U/L | OTHER | S47/11/VI21/81UL |  |  |  | CDC | 493 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI22 | 永二線(VI22) 81RY |  | 81UL | [17 empty] | 1-3E-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_81U/L | 11KV永二線(VI22) 81RY U/L | OTHER | S47/11/VI22/81UL |  |  |  | CDC | 494 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI23 | 永三線(VI23) 81RY |  | 81UL | [17 empty] | 1-3E-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_81U/L | 11KV永三線(VI23) 81RY U/L | OTHER | S47/11/VI23/81UL |  |  |  | CDC | 495 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI24 | 永正線(VI24) 81RY |  | 81UL | [17 empty] | 1-3E-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_81U/L | 11KV永正線(VI24) 81RY U/L | OTHER | S47/11/VI24/81UL |  |  |  | CDC | 496 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI25 | 永五線(VI25) 81RY |  | 81UL | [17 empty] | 1-3E-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_81U/L | 11KV永五線(VI25) 81RY U/L | OTHER | S47/11/VI25/81UL |  |  |  | CDC | 497 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI26 | 永六線(VI26) 81RY |  | 81UL | [17 empty] | 1-3E-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_81U/L | 11KV永六線(VI26) 81RY U/L | OTHER | S47/11/VI26/81UL |  |  |  | CDC | 498 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI27 | 永七線(VI27) 81RY |  | 81UL | [17 empty] | 1-3E-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_81U/L | 11KV永七線(VI27) 81RY U/L | OTHER | S47/11/VI27/81UL |  |  |  | CDC | 499 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI28 | 永八線(VI28) 81RY |  | 81UL | [17 empty] | 1-3E-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_81U/L | 11KV永八線(VI28) 81RY U/L | OTHER | S47/11/VI28/81UL |  |  |  | CDC | 500 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI29 | 永九線(VI29) 81RY |  | 81UL | [17 empty] | 1-3F-00 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_81U/L | 11KV永九線(VI29) 81RY U/L | OTHER | S47/11/VI29/81UL |  |  |  | CDC | 501 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI30 | 永十線(VI30) 81RY |  | 81UL | [17 empty] | 1-3F-01 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_81U/L | 11KV永十線(VI30) 81RY U/L | OTHER | S47/11/VI30/81UL |  |  |  | CDC | 502 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI31 | 永忠線(VI31) 81RY |  | 81UL | [17 empty] | 1-3F-02 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_81U/L | 11KV永忠線(VI31) 81RY U/L | OTHER | S47/11/VI31/81UL |  |  |  | CDC | 503 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI32 | 永孝線(VI32) 81RY |  | 81UL | [17 empty] | 1-3F-03 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_81U/L | 11KV永孝線(VI32) 81RY U/L | OTHER | S47/11/VI32/81UL |  |  |  | CDC | 504 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI33 | 永仁線(VI33) 81RY |  | 81UL | [17 empty] | 1-3F-04 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_81U/L | 11KV永仁線(VI33) 81RY U/L | OTHER | S47/11/VI33/81UL |  |  |  | CDC | 505 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI34 | 永愛線(VI34) 81RY |  | 81UL | [17 empty] | 1-3F-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_81U/L | 11KV永愛線(VI34) 81RY U/L | OTHER | S47/11/VI34/81UL |  |  |  | CDC | 506 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | VI35 | 永信線(VI35) 81RY |  | 81UL | [17 empty] | 1-3F-06 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_81U/L | 11KV永信線(VI35) 81RY U/L | OTHER | S47/11/VI35/81UL |  |  |  | CDC | 507 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-3D-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_RYFA | #1MTR及饋線數位電驛故障 | OTHER | S47//1MTR/IRFA |  |  |  | CDC | 508 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-3D-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_RYFA | #2MTR及饋線數位電驛故障 | OTHER | S47//2MTR/IRFA |  |  |  | CDC | 509 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 1-3D-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_RYFA | #3MTR及饋線數位電驛故障 | OTHER | S47//3MTR/IRFA |  |  |  | CDC | 510 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 81RY | 81RY |  | RYFA | [17 empty] | 1-3D-05 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.81RY_RYFA | 81RY數位電驛故障 | OTHER | S47/0/ComPoint/81A_RYFA |  |  |  | CDC | 511 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-3D-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_86A | #1MTR 86RY跳脫閉鎖 | OTHER | S47//1MTR/MTR_86A |  |  |  | CDC | 512 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 871S | [17 empty] | 1-3D-14 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_871S | #1MTR 87RY1S使用閉鎖 | OTHER | S47//1MTR/87AS1 |  |  |  | CDC | 513 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 872S | [17 empty] | 1-3D-15 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_872S | #1MTR 87RY2S使用閉鎖 | OTHER | S47//1MTR/87AS2 |  |  |  | CDC | 514 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-3D-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_86A | #2MTR 86RY跳脫閉鎖 | OTHER | S47//2MTR/MTR_86A |  |  |  | CDC | 515 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 871S | [17 empty] | 1-3F-07 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_871S | #2MTR 87RY1S使用閉鎖 | OTHER | S47//2MTR/87AS1 |  |  |  | CDC | 516 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 872S | [17 empty] | 1-3F-08 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_872S | #2MTR 87RY2S使用閉鎖 | OTHER | S47//2MTR/87AS2 |  |  |  | CDC | 517 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-3D-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_86A | #3MTR 86RY跳脫閉鎖 | OTHER | S47//3MTR/MTR_86A |  |  |  | CDC | 518 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 871S | [17 empty] | 1-3F-09 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_871S | #3MTR 87RY1S使用閉鎖 | OTHER | S47//3MTR/87AS1 |  |  |  | CDC | 519 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 872S | [17 empty] | 1-3F-10 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_872S | #3MTR 87RY2S使用閉鎖 | OTHER | S47//3MTR/87AS2 |  |  |  | CDC | 520 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3F-11 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#1MTR_51ZS | #1MTR 51Z電驛使用閉鎖 | OTHER | S47//1MTR/51Z_UL |  |  |  | CDC | 521 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3F-12 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#2MTR_51ZS | #2MTR 51Z電驛使用閉鎖 | OTHER | S47//2MTR/51Z_UL |  |  |  | CDC | 522 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3F-13 | [7 empty] | DDCS3_2 | [8 empty] | 永華SS.#3MTR_51ZS | #3MTR 51Z電驛使用閉鎖 | OTHER | S47//3MTR/51Z_UL |  |  |  | CDC | 523 | GENERICDIPoint | SS307_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S47 | 永華SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 524 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 525 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 526 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS3_2 | [8 empty] | 永華SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 527 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 永華SS.630LE | 630LE (非取樣點) | LINE69 | S47/69/630/LE0 |  |  |  |  | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 630 | 學甲線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 永華SS.630BE | 630BE (非取樣點) | LINE69 | S47/69/630/BE0 |  |  |  |  | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 永華SS.640LE | 640LE (非取樣點) | LINE69 | S47/69/640/LE0 |  |  |  |  | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 640 | 新塭線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 永華SS.640BE | 640BE (非取樣點) | LINE69 | S47/69/640/BE0 |  |  |  |  | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI21 | VI21_DS |  | DS1 | VI21_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_DS | VI21_DS (非取樣點) | FEEDER | S47/11/VI21/DS |  |  |  |  | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI21 | VI21_ES |  | LE0 | VI21_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI21_ES | VI21_ES (非取樣點) | FEEDER | S47/11/VI21/ES |  |  |  |  | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI22 | VI22_DS |  | DS1 | VI22_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_DS | VI22_DS (非取樣點) | FEEDER | S47/11/VI22/DS |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI22 | VI22_ES |  | LE0 | VI22_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI22_ES | VI22_ES (非取樣點) | FEEDER | S47/11/VI22/ES |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI23 | VI23_DS |  | DS1 | VI23_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_DS | VI23_DS (非取樣點) | FEEDER | S47/11/VI23/DS |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI23 | VI23_ES |  | LE0 | VI23_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI23_ES | VI23_ES (非取樣點) | FEEDER | S47/11/VI23/ES |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI24 | VI24_DS |  | DS1 | VI24_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_DS | VI24_DS (非取樣點) | FEEDER | S47/11/VI24/DS |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI24 | VI24_ES |  | LE0 | VI24_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI24_ES | VI24_ES (非取樣點) | FEEDER | S47/11/VI24/ES |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI25 | VI25_DS |  | DS1 | VI25_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_DS | VI25_DS (非取樣點) | FEEDER | S47/11/VI25/DS |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI25 | VI25_ES |  | LE0 | VI25_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI25_ES | VI25_ES (非取樣點) | FEEDER | S47/11/VI25/ES |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI26 | VI26_DS |  | DS1 | VI26_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_DS | VI26_DS (非取樣點) | FEEDER | S47/11/VI26/DS |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI26 | VI26_ES |  | LE0 | VI26_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI26_ES | VI26_ES (非取樣點) | FEEDER | S47/11/VI26/ES |  |  |  |  | 543 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI27 | VI27_DS |  | DS1 | VI27_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_DS | VI27_DS (非取樣點) | FEEDER | S47/11/VI27/DS |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI27 | VI27_ES |  | LE0 | VI27_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI27_ES | VI27_ES (非取樣點) | FEEDER | S47/11/VI27/ES |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI28 | VI28_DS |  | DS1 | VI28_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_DS | VI28_DS (非取樣點) | FEEDER | S47/11/VI28/DS |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI28 | VI28_ES |  | LE0 | VI28_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI28_ES | VI28_ES (非取樣點) | FEEDER | S47/11/VI28/ES |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI29 | VI29_DS |  | DS1 | VI29_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_DS | VI29_DS (非取樣點) | FEEDER | S47/11/VI29/DS |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI29 | VI29_ES |  | LE0 | VI29_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI29_ES | VI29_ES (非取樣點) | FEEDER | S47/11/VI29/ES |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI30 | VI30_DS |  | DS1 | VI30_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_DS | VI30_DS (非取樣點) | FEEDER | S47/11/VI30/DS |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI30 | VI30_ES |  | LE0 | VI30_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI30_ES | VI30_ES (非取樣點) | FEEDER | S47/11/VI30/ES |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI31 | VI31_DS |  | DS1 | VI31_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_DS | VI31_DS (非取樣點) | FEEDER | S47/11/VI31/DS |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI31 | VI31_ES |  | LE0 | VI31_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI31_ES | VI31_ES (非取樣點) | FEEDER | S47/11/VI31/ES |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI32 | VI32_DS |  | DS1 | VI32_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_DS | VI32_DS (非取樣點) | FEEDER | S47/11/VI32/DS |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI32 | VI32_ES |  | LE0 | VI32_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI32_ES | VI32_ES (非取樣點) | FEEDER | S47/11/VI32/ES |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI33 | VI33_DS |  | DS1 | VI33_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_DS | VI33_DS (非取樣點) | FEEDER | S47/11/VI33/DS |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI33 | VI33_ES |  | LE0 | VI33_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI33_ES | VI33_ES (非取樣點) | FEEDER | S47/11/VI33/ES |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI34 | VI34_DS |  | DS1 | VI34_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_DS | VI34_DS (非取樣點) | FEEDER | S47/11/VI34/DS |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI34 | VI34_ES |  | LE0 | VI34_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI34_ES | VI34_ES (非取樣點) | FEEDER | S47/11/VI34/ES |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | VI35 | VI35_DS |  | DS1 | VI35_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_DS | VI35_DS (非取樣點) | FEEDER | S47/11/VI35/DS |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | VI35 | VI35_ES |  | LE0 | VI35_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.VI35_ES | VI35_ES (非取樣點) | FEEDER | S47/11/VI35/ES |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S47/11/TIE1/DS |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S47/11/TIE2/DS |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.750TE | 750TE (非取樣點) | DTR | S47/69/750/TE0 |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.750BE | 750BE (非取樣點) | DTR | S47/69/750/BE0 |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.1M_DS | 1M_DS (非取樣點) | DTR | S47/11/M1/DS |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.760TE | 760TE (非取樣點) | DTR | S47/69/760/TE0 |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.760BE | 760BE (非取樣點) | DTR | S47/69/760/BE0 |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S47/11/M2A/DS |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S47/11/M2B/DS |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S47/11/M2A/ES |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S47/11/M2B/ES |  |  |  |  | 572 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.770TE | 770TE (非取樣點) | DTR | S47/69/770/TE0 |  |  |  |  | 573 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.770BE | 770BE (非取樣點) | DTR | S47/69/770/BE0 |  |  |  |  | 574 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.3M_DS | 3M_DS (非取樣點) | DTR | S47/11/M3/DS |  |  |  |  | 575 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.210_ES | 210_ES (非取樣點) | SC | S47/11/210/ES |  |  |  |  | 576 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.210_DS | 210_DS (非取樣點) | SC | S47/11/210/DS |  |  |  |  | 577 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.220_ES | 220_ES (非取樣點) | SC | S47/11/220/ES |  |  |  |  | 578 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.220_DS | 220_DS (非取樣點) | SC | S47/11/220/DS |  |  |  |  | 579 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.230_ES | 230_ES (非取樣點) | SC | S47/11/230/ES |  |  |  |  | 580 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.230_DS | 230_DS (非取樣點) | SC | S47/11/230/DS |  |  |  |  | 581 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 810ES | 810ES |  | 810ES | 810ES | [24 empty] | ADCS_N | [8 empty] | 永華SS.810ES | 810ES (非取樣點) | SC | S47/69/810/ES |  |  |  |  | 582 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 永華SS.69B1E | 69B1E (非取樣點) | BUS | S47/69/1BUS/BE1 |  |  |  |  | 583 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 永華SS.69B2E | 69B2E (非取樣點) | BUS | S47/69/2BUS/BE2 |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 585 | NotelDIPoint | [38 empty] | START/STOP | STOP
S47 | 永華SS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.101E | 101E (非取樣點) | TIE | S47/11/TIE1/E1 |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.102E | 102E (非取樣點) | TIE | S47/11/TIE1/E2 |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 200 | 200 |  | E1 | 201E | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.201E | 201E (非取樣點) | TIE | S47/11/TIE2/E1 |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 200 | 200 |  | E2 | 202E | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.202E | 202E (非取樣點) | TIE | S47/11/TIE2/E2 |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | TIE1 | TIE1_DS2 |  | DS2 | TIE1_DS2 | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE1_DS2 | TIE1_DS2 (非取樣點) | TIE | S47/11/TIE1/D2 |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | TIE2 | TIE2_DS2 |  | DS2 | TIE2_DS2 | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.TIE2_DS2 | TIE2_DS2 (非取樣點) | TIE | S47/11/TIE2/D2 |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S47 | 永華SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.1M_ES | 1M_ES (非取樣點) | DTR | S47/11/M1/ES |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS3_2 | [8 empty] | 永華SS.3M_ES | 3M_ES (非取樣點) | DTR | S47/11/M3/ES |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 11B1E | 11B1E |  | BE1 | 11B1E | [24 empty] | ADCS_N | [8 empty] | 永華SS.11B1E | 11B1E (非取樣點) | BUS | S47/11/1BUS/BE1 |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 11B2E | 11B2E |  | BE2 | 11B2E | [24 empty] | ADCS_N | [8 empty] | 永華SS.11B2E | 11B2E (非取樣點) | BUS | S47/11/2BUS/BE2 |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 11B2BE | 11B2BE |  | B2BE0 | 11B2BE | [24 empty] | ADCS_N | [8 empty] | 永華SS.11B2BE | 11B2BE (非取樣點) | BUS | S47/11/2BUS/BE0 |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S47 | 永華SS | 0 |  | 11B3E | 11B3E |  | BE3 | 11B3E | [24 empty] | ADCS_N | [8 empty] | 永華SS.11B3E | 11B3E (非取樣點) | BUS | S47/11/3BUS/BE3 |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo