## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S64 | 開元SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S64_A1 | [8 empty] | 開元SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S64 | 開元SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 TR R相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S64_D1 | [8 empty] | 開元SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 11 | 11kV | 1BUS | #1BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0053 |  |  | 1-B5 |  |  | #1 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S64_D1 | [8 empty] | 開元SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 11 | 11kV | 1BUS | #1BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0054 |  |  | 1-B6 |  |  | #1 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S64_D1 | [8 empty] | 開元SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S64_A1 | [8 empty] | 開元SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 6 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 7 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 元寶線 (F1) 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC21_PHA | 11KV元寶線(KC21) 相間RY | FEEDER |  |  |  |  | CDC | 8 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 元寶線 (F1) 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC21_GDA | 11KV元寶線(KC21) 接地RY | FEEDER |  |  |  |  | CDC | 9 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | 元寶線 (F1) 79RY U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC21_79UL | 11KV元寶線(KC21) 79RY U/L | FEEDER |  |  |  |  | CDC | 10 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | 元寶線 (F1) LCO ADJ U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC21_ADJ | 11KV元寶線(KC21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 11 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | 大道線 (F2) 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC22_PHA | 11KV大道線(KC22) 相間RY | FEEDER |  |  |  |  | CDC | 12 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 大道線 (F2) 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC22_GDA | 11KV大道線(KC22) 接地RY | FEEDER |  |  |  |  | CDC | 13 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | 大道線 (F2) 79RY U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC22_79UL | 11KV大道線(KC22) 79RY U/L | FEEDER |  |  |  |  | CDC | 14 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | 大道線 (F2) LCO ADJ U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC22_ADJ | 11KV大道線(KC22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 15 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 北門線 (F3) 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC23_PHA | 11KV北門線(KC23) 相間RY | FEEDER |  |  |  |  | CDC | 16 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 北門線 (F3) 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC23_GDA | 11KV北門線(KC23) 接地RY | FEEDER |  |  |  |  | CDC | 17 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | 北門線 (F3) 79RY U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC23_79UL | 11KV北門線(KC23) 79RY U/L | FEEDER |  |  |  |  | CDC | 18 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | 北門線 (F3) LCO ADJ U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC23_ADJ | 11KV北門線(KC23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 19 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 成功線 (F4) 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC24_PHA | 11KV成功線(KC24) 相間RY | FEEDER |  |  |  |  | CDC | 20 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 成功線 (F4) 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC24_GDA | 11KV成功線(KC24) 接地RY | FEEDER |  |  |  |  | CDC | 21 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | 成功線 (F4) 79RY U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC24_79UL | 11KV成功線(KC24) 79RY U/L | FEEDER |  |  |  |  | CDC | 22 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | 成功線 (F4) LCO ADJ U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC24_ADJ | 11KV成功線(KC24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 23 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 小東線 (F5) 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC25_PHA | 11KV小東線(KC25) 相間RY | FEEDER |  |  |  |  | CDC | 24 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 小東線 (F5) 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC25_GDA | 11KV小東線(KC25) 接地RY | FEEDER |  |  |  |  | CDC | 25 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | 小東線 (F5) 79RY U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC25_79UL | 11KV小東線(KC25) 79RY U/L | FEEDER |  |  |  |  | CDC | 26 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | 小東線 (F5) LCO ADJ U/L |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC25_ADJ | 11KV小東線(KC25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 27 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KC21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | 元寶線 (F1) CB |  |  |  | aabb | B2/S64_D1 | [8 empty] | 開元SS.KC21_CB | KC21(11KV元寶線) CB | FEEDER |  |  |  |  | CDC | 28 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC21_DS | KC21_DS (非取樣點) | FEEDER | [5 empty] | 29 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | ES | KC21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC21_ES | KC21_ES (非取樣點) | FEEDER | [5 empty] | 30 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KC22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | 大道線 (F2) CB |  |  |  | aacb | B2/S64_D1 | [8 empty] | 開元SS.KC22_CB | KC22(11KV大道線) CB | FEEDER |  |  |  |  | CDC | 31 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC22_DS | KC22_DS (非取樣點) | FEEDER | [5 empty] | 32 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | ES | KC22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC22_ES | KC22_ES (非取樣點) | FEEDER | [5 empty] | 33 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KC23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | 北門線 (F3) CB |  |  |  | aaeb | B2/S64_D1 | [8 empty] | 開元SS.KC23_CB | KC23(11KV北門線) CB | FEEDER |  |  |  |  | CDC | 34 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC23_DS | KC23_DS (非取樣點) | FEEDER | [5 empty] | 35 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | ES | KC23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC23_ES | KC23_ES (非取樣點) | FEEDER | [5 empty] | 36 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KC24/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | 成功線 (F4) CB |  |  |  | aafb | B2/S64_D1 | [8 empty] | 開元SS.KC24_CB | KC24(11KV成功線) CB | FEEDER |  |  |  |  | CDC | 37 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC24_DS | KC24_DS (非取樣點) | FEEDER | [5 empty] | 38 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | ES | KC24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC24_ES | KC24_ES (非取樣點) | FEEDER | [5 empty] | 39 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KC25/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | 小東線 (F5) CB |  |  |  | aagb | B2/S64_D1 | [8 empty] | 開元SS.KC25_CB | KC25(11KV小東線) CB | FEEDER |  |  |  |  | CDC | 40 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC25_DS | KC25_DS (非取樣點) | FEEDER | [5 empty] | 41 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | ES | KC25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.KC25_ES | KC25_ES (非取樣點) | FEEDER | [5 empty] | 42 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S64_D1 | [8 empty] | 開元SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 43 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S64_D1 | [8 empty] | 開元SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 44 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S64_D1 | [8 empty] | 開元SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 45 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S64_D1 | [8 empty] | 開元SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 46 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S64_D1 | [8 empty] | 開元SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 47 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 48 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S64 | 開元SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 49 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S64 | 開元SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 50 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S64 | 開元SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1 TR MWH(+) |  |  |  |  | B1/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 51 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 52 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrB | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | #1TR 一次 CB (610) |  |  |  | aaab | B2/S64_A1 | [8 empty] | 開元SS.610_CB | 610(#1MTR) CB | DTR |  |  |  |  | CDC | 53 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1TR 二次 CB |  |  |  | aada | B2/S64_D1 | [8 empty] | 開元SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 54 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次 51 RY |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 55 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 一次 51N RY |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 56 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 51Z RY |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 57 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 87 RY |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 58 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 59 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0065 | 1-0C-06 |  | 1-41 | #1 BUS 81 RY |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 60 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1TR 二次 51 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 61 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 62 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 63 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 64 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S64 | 開元SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1TR OLTC A/M |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 65 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | DS1 | 611 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | #1TR AS (611) |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.611_ABS | 611(#1MTR) ABS | DTR |  |  |  |  | CDC | 66 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S64 | 開元SS | 69 | 69kV | 610 | 後甲～開元線(610) |  | LE0 | 611E | B2 | [12 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | #1TR ES AS (611E) |  |  |  |  | B2/S64_A1 | [8 empty] | 開元SS.61E_ABS | 611E(#1MTR) ABS | DTR |  |  |  |  | CDC | 67 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 68 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 69 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 機械保護動作(96PA) |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 70 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 71 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1TR 冷卻電源故障 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 72 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC CB |  |  |  | aaab | B2/S64_D1 | [8 empty] | 開元SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 73 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1SC Q-CTL A/M |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 74 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 75 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 76 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 77 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 78 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S64_D1 | [8 empty] | 開元SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 79 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S64_D1 | [8 empty] | 開元SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 80 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S64_D1 | [8 empty] | 開元SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 81 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S64_D1 | [8 empty] | 開元SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 82 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 開元SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 83 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 84 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 85 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 86 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 開關場照明 C/T |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 87 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 88 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1S |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 89 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2S |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 90 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 91 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 92 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 93 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 94 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 95 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 96 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 97 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 98 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-37-00 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 99 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 1-37-01 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 100 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-37-02 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 101 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0371 |  |  | 1-37-03 |  |  | 博碼調變器故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 102 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 103 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 104 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 105 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 開關場照明 A/M |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 106 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 107 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 108 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 109 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次 51N RY |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER |  |  |  |  | CDC | 110 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.火災警報 | 火警 | OTHER |  |  |  |  | CDC | 111 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 112 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 113 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 114 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0165 |  | 0087 | 1-14-05 |  | 1-57 | 全所故障指示器復歸點 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 115 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 | Element | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S64_D1 | [8 empty] | 開元SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 116 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | [13 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 117 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 118 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 119 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 120 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | 元寶線 (F1) LOA |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC21_LOA | 元寶線 復閉失敗閉鎖 | OTHER | [5 empty] | 121 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | 大道線 (F2) LOA |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC22_LOA | 大道線 復閉失敗閉鎖 | OTHER | [5 empty] | 122 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | 北門線 (F3) LOA |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC23_LOA | 北門線 復閉失敗閉鎖 | OTHER | [5 empty] | 123 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | 成功線 (F4) LOA |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC24_LOA | 成功線 復閉失敗閉鎖 | OTHER | [5 empty] | 124 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | 小東線 (F5) LOA |  |  |  |  | B2/S64_D1 | [8 empty] | 開元SS.KC25_LOA | 小東線 復閉失敗閉鎖 | OTHER | [5 empty] | 125 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | CommACF | DDCC充電機AC | INSERT | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0428 |  |  | 1-3A-12 |  |  | DDCC通訊室充電機AC電源故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.DDCC充電機AC | DDCC通訊室充電機AC電源故障 | OTHER | [5 empty] | 126 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | 9A5Other | DDCC充電機故障 | INSERT | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0429 |  |  | 1-3A-13 |  |  | DDCC通訊室充電機故障 |  |  |  |  | B3/S64_D1 | [8 empty] | 開元SS.DDCC充電機故障 | DDCC通訊室充電機故障 | OTHER | [5 empty] | 127 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1DTR 63Q |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 128 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1DTR 96B1 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 129 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1DTR 96B2 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 130 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1DTR 96D |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 131 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1DTR 96P |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 132 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 133 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #1DTR 86A |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 134 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 135 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S64 | 開元SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S64_D1 | [8 empty] | 開元SS.MTR_IED故障 | MTR_IED故障 | OTHER | [5 empty] | 136 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 元寶線 (F1) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.元寶線KVAR | 11KV元寶線 KVAR | FEEDER |  |  |  |  | CDC | 137 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 元寶線 (F1) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.元寶線A1 | 11KV元寶線 R相AMP | FEEDER |  |  |  |  | CDC | 138 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 元寶線 (F1) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.元寶線A2 | 11KV元寶線 S相AMP | FEEDER |  |  |  |  | CDC | 139 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 元寶線 (F1) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.元寶線A3 | 11KV元寶線 T相AMP | FEEDER |  |  |  |  | CDC | 140 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 元寶線 (F1) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.元寶線A0 | 11KV元寶線 N相AMP | FEEDER |  |  |  |  | CDC | 141 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 元寶線 (F1) KWH(+) |  |  |  |  | B2/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 142 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 大道線 (F2) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.大道線KVAR | 11KV大道線 KVAR | FEEDER |  |  |  |  | CDC | 143 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 大道線 (F2) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.大道線A1 | 11KV大道線 R相AMP | FEEDER |  |  |  |  | CDC | 144 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 大道線 (F2) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.大道線A2 | 11KV大道線 S相AMP | FEEDER |  |  |  |  | CDC | 145 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 大道線 (F2) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.大道線A3 | 11KV大道線 T相AMP | FEEDER |  |  |  |  | CDC | 146 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 大道線 (F2) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.大道線A0 | 11KV大道線 N相AMP | FEEDER |  |  |  |  | CDC | 147 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 大道線 (F2) KWH(+) |  |  |  |  | B2/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 148 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 北門線 (F3) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.北門線KVAR | 11KV北門線 KVAR | FEEDER |  |  |  |  | CDC | 149 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 北門線 (F3) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.北門線A1 | 11KV北門線 R相AMP | FEEDER |  |  |  |  | CDC | 150 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 北門線 (F3) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.北門線A2 | 11KV北門線 S相AMP | FEEDER |  |  |  |  | CDC | 151 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 北門線 (F3) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.北門線A3 | 11KV北門線 T相AMP | FEEDER |  |  |  |  | CDC | 152 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 北門線 (F3) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.北門線A0 | 11KV北門線 N相AMP | FEEDER |  |  |  |  | CDC | 153 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 北門線 (F3) KWH(+) |  |  |  |  | B2/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 154 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 成功線 (F4) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.成功線KVAR | 11KV成功線 KVAR | FEEDER |  |  |  |  | CDC | 155 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 成功線 (F4) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.成功線A1 | 11KV成功線 R相AMP | FEEDER |  |  |  |  | CDC | 156 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 成功線 (F4) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.成功線A2 | 11KV成功線 S相AMP | FEEDER |  |  |  |  | CDC | 157 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 成功線 (F4) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.成功線A3 | 11KV成功線 T相AMP | FEEDER |  |  |  |  | CDC | 158 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 成功線 (F4) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.成功線A0 | 11KV成功線 N相AMP | FEEDER |  |  |  |  | CDC | 159 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 成功線 (F4) KWH(+) |  |  |  |  | B2/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 160 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 小東線 (F5) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.小東線KVAR | 11KV小東線 KVAR | FEEDER |  |  |  |  | CDC | 161 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 小東線 (F5) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.小東線A1 | 11KV小東線 R相AMP | FEEDER |  |  |  |  | CDC | 162 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 小東線 (F5) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.小東線A2 | 11KV小東線 S相AMP | FEEDER |  |  |  |  | CDC | 163 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 小東線 (F5) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.小東線A3 | 11KV小東線 T相AMP | FEEDER |  |  |  |  | CDC | 164 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 小東線 (F5) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S64_D1 |  |  | 600 | [5 empty] | 開元SS.小東線A0 | 11KV小東線 N相AMP | FEEDER |  |  |  |  | CDC | 165 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 小東線 (F5) KWH(+) |  |  |  |  | B2/S64_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 166 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S64 | 開元SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S64_D1 | [8 empty] | 開元SS.直流電源電壓 | 直流電源電壓 | OTHER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S64_D1 | [8 empty] | 開元SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 168 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S64 | 開元SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S64_D1 | [12 empty] | 開元SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S64/69/1BUS/V
S64 | 開元SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S64_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S64/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S64 | 開元SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S64_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_1 | OPRD1: S64/11/M1/MW
S64 | 開元SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S64_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S64/0/CalcPoint/OPRN2_MW
S64 | 開元SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S64_D1 | [17 empty] | none
S64 | 開元SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S64_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S64/0/CalcPoint/OPRN1; OPRD2: S64/0/CalcPoint/OPRN2; OPRD3: S64/0/CalcPoint/PRFL_UL
S64 | 開元SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S64_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S64/11/M1/MW; OPRD2: S64/11/M1/MVAR; OPRD3: NULL
S64 | 開元SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S64_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 開元SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S64/11/M1/MW; OPRD2: S64/11/M1/MVAR
S64 | 開元SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S64_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S64//1MTR/MVA; OPRD2: 0
S64 | 開元SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S64_D1 | [12 empty] | 開元SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S64/11/M1/MW; OPRD2: S64/11/M1/MVAR
S64 | 開元SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S64_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S64//1MTR/SupLocal; OPRD2: S64//1MTR/Tap Chan; OPRD3: NULL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S64/11/KC21/I_R; OPRD3: S64/11/KC21/I_S; OPRD4: S64/11/KC21/I_T
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S64/11/KC22/I_R; OPRD3: S64/11/KC22/I_S; OPRD4: S64/11/KC22/I_T
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S64/11/KC23/I_R; OPRD3: S64/11/KC23/I_S; OPRD4: S64/11/KC23/I_T
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S64/11/KC24/I_R; OPRD3: S64/11/KC24/I_S; OPRD4: S64/11/KC24/I_T
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S64/11/KC25/I_R; OPRD3: S64/11/KC25/I_S; OPRD4: S64/11/KC25/I_T
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S64/11/KC21/kVA; OPRD2: S64/11/KC21/KVAR
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S64/11/KC22/kVA; OPRD2: S64/11/KC22/KVAR
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S64/11/KC23/kVA; OPRD2: S64/11/KC23/KVAR
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S64/11/KC24/kVA; OPRD2: S64/11/KC24/KVAR
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S64_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S64/11/KC25/kVA; OPRD2: S64/11/KC25/KVAR
S64 | 開元SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S64_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_1 | OPRD1: S64/11/M1/MW
S64 | 開元SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S64_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_1 | OPRD1: S64/11/M1/MVAR
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S64_D1 | [12 empty] | 開元SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S64/11/210/CB; OPRD2: 6.9; OPRD3: 0
S64 | 開元SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S64_D1 | [12 empty] | 開元SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_4 |  | com_alarm_8 | OPRD1: S64//1MTR/96B1; OPRD2: S64//1MTR/63Q; OPRD3: S64//1MTR/96D; OPRD4: S64//1MTR/96B2; OPRD5: S64//1MTR/87A; OPRD6: S64//1MTR/51ZA; OPRD7: S64//1MTR/96PA; OPRD8: S64//1MTR/TRA
S64 | 開元SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S64_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_1 | OPRD1: S64//1MTR/TRF
S64 | 開元SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/RTU/RTU_R_L
S64 | 開元SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/StaDev/PSF
S64 | 開元SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/StaDev/DCE
S64 | 開元SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S64_D1 | [17 empty] | lamp2CC | OPRD1: S64/69/ComPoint/CBA
S64 | 開元SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S64_D1 | [17 empty] | lamp2CC | OPRD1: S64/69/ComPoint/CBF
S64 | 開元SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S64_D1 | [17 empty] | lamp2CC | OPRD1: S64/69/ComPoint/ABS_89A
S64 | 開元SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/StaDev/DCA
S64 | 開元SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/StaDev/Fire
S64 | 開元SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S64_A1 | [17 empty] | lamp2CC | OPRD1: S64/0/StaDev/PMA
S64 | 開元SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S64_D1 | [17 empty] | lamp2CC | OPRD1: S64/69/ComPoint/CFA
S64 | 開元SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S64_D1 | [17 empty] | lamp2CC | OPRD1: S64/69/ComPoint/IRFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S64 | 開元SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 開元SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S64/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S64 | 開元SS | 0 |  |  |  |  | 大道線KVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.大道線KVA | 11KV大道線KVA | FEEDER |  |  | KVA_CAL |  |  | 3 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 大道線KW | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.大道線KW | 11KV大道線KW | FEEDER |  |  | KW_CAL |  |  | 4 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 小東線KVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.小東線KVA | 11KV小東線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 小東線KW | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.小東線KW | 11KV小東線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 元寶線KVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.元寶線KVA | 11KV元寶線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 元寶線KW | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.元寶線KW | 11KV元寶線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 北門線KVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.北門線KVA | 11KV北門線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 北門線KW | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.北門線KW | 11KV北門線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 成功線KVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.成功線KVA | 11KV成功線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  |  |  |  | 成功線KW | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.成功線KW | 11KV成功線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S64//1MTR/MVA |  | MVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_PF | #1MTR 功率因素 | DTR | S64//1MTR/PF |  | RPDC_PF_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S64 | 開元SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S64/11/210/MVAR |  | SC_CAL_11 |  |  | 15 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 69 | 69kV | 610_CB | 610_LINE(610_CB) | [27 empty] | ADCS_S | [8 empty] | 開元SS.610_CB_A | 610_LINE 點燈 | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 16 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_S | [8 empty] | 開元SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 17 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_S | [8 empty] | 開元SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 18 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 69SC警報 | 69SC警報 | [27 empty] | ADCS_S | [8 empty] | 開元SS.69SC警報_A | 69SC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 19 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_S | [8 empty] | 開元SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 20 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 開元SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S64/0/CalcPoint/SUBA |  | STATION_FAULT_4 |  |  | 21 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 22 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_1 |  |  | 23 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_MVA_A | #1MTR MVA 點燈 (AD) | DTR |  |  | MAP_SET |  |  | 24 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S64 | 開元SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | AD_LAMP_DD_2 |  |  | 25 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 26 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S64 | 開元SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 開元SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 27 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S64/0/RTU/ADCH1 |  |  |  | CDC | 28 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S64/0/RTU/ADCH2 |  |  |  | CDC | 29 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S64/0/RTU/ADCL1 |  |  |  | CDC | 30 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S64/0/RTU/ADCL2 |  |  |  | CDC | 31 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S64 | 開元SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 開元SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S64/69/1BUS/V |  |  |  | CDC | 32 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S64 | 開元SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S64/11/1BUS/V_R |  |  |  | CDC | 33 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 11 | 11kV | 大道線 | 大道線 |  | 大道線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.大道線KVAR | 11KV大道線 KVAR | FEEDER | S64/11/KC22/KVAR |  |  |  | CDC | 34 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | 大道線 | 大道線 |  | 大道線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.大道線A1 | 11KV大道線 R相AMP | FEEDER | S64/11/KC22/I_R |  |  |  | CDC | 35 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 大道線 | 大道線 |  | 大道線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.大道線A2 | 11KV大道線 S相AMP | FEEDER | S64/11/KC22/I_S |  |  |  | CDC | 36 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 大道線 | 大道線 |  | 大道線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.大道線A3 | 11KV大道線 T相AMP | FEEDER | S64/11/KC22/I_T |  |  |  | CDC | 37 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 大道線 | 大道線 |  | 大道線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.大道線A0 | 11KV大道線 N相AMP | FEEDER | S64/11/KC22/I_N |  |  |  | CDC | 38 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 小東線 | 小東線 |  | 小東線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.小東線KVAR | 11KV小東線 KVAR | FEEDER | S64/11/KC25/KVAR |  |  |  | CDC | 39 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | 小東線 | 小東線 |  | 小東線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.小東線A1 | 11KV小東線 R相AMP | FEEDER | S64/11/KC25/I_R |  |  |  | CDC | 40 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 小東線 | 小東線 |  | 小東線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.小東線A2 | 11KV小東線 S相AMP | FEEDER | S64/11/KC25/I_S |  |  |  | CDC | 41 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 小東線 | 小東線 |  | 小東線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.小東線A3 | 11KV小東線 T相AMP | FEEDER | S64/11/KC25/I_T |  |  |  | CDC | 42 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 小東線 | 小東線 |  | 小東線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.小東線A0 | 11KV小東線 N相AMP | FEEDER | S64/11/KC25/I_N |  |  |  | CDC | 43 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 元寶線 | 元寶線 |  | 元寶線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.元寶線KVAR | 11KV元寶線 KVAR | FEEDER | S64/11/KC21/KVAR |  |  |  | CDC | 44 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | 元寶線 | 元寶線 |  | 元寶線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.元寶線A1 | 11KV元寶線 R相AMP | FEEDER | S64/11/KC21/I_R |  |  |  | CDC | 45 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 元寶線 | 元寶線 |  | 元寶線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.元寶線A2 | 11KV元寶線 S相AMP | FEEDER | S64/11/KC21/I_S |  |  |  | CDC | 46 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 元寶線 | 元寶線 |  | 元寶線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.元寶線A3 | 11KV元寶線 T相AMP | FEEDER | S64/11/KC21/I_T |  |  |  | CDC | 47 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 元寶線 | 元寶線 |  | 元寶線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.元寶線A0 | 11KV元寶線 N相AMP | FEEDER | S64/11/KC21/I_N |  |  |  | CDC | 48 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 北門線 | 北門線 |  | 北門線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.北門線KVAR | 11KV北門線 KVAR | FEEDER | S64/11/KC23/KVAR |  |  |  | CDC | 49 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | 北門線 | 北門線 |  | 北門線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.北門線A1 | 11KV北門線 R相AMP | FEEDER | S64/11/KC23/I_R |  |  |  | CDC | 50 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 北門線 | 北門線 |  | 北門線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.北門線A2 | 11KV北門線 S相AMP | FEEDER | S64/11/KC23/I_S |  |  |  | CDC | 51 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 北門線 | 北門線 |  | 北門線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.北門線A3 | 11KV北門線 T相AMP | FEEDER | S64/11/KC23/I_T |  |  |  | CDC | 52 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 北門線 | 北門線 |  | 北門線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.北門線A0 | 11KV北門線 N相AMP | FEEDER | S64/11/KC23/I_N |  |  |  | CDC | 53 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 成功線 | 成功線 |  | 成功線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.成功線KVAR | 11KV成功線 KVAR | FEEDER | S64/11/KC24/KVAR |  |  |  | CDC | 54 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S64 | 開元SS | 11 | 11kV | 成功線 | 成功線 |  | 成功線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.成功線A1 | 11KV成功線 R相AMP | FEEDER | S64/11/KC24/I_R |  |  |  | CDC | 55 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 成功線 | 成功線 |  | 成功線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.成功線A2 | 11KV成功線 S相AMP | FEEDER | S64/11/KC24/I_S |  |  |  | CDC | 56 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 成功線 | 成功線 |  | 成功線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.成功線A3 | 11KV成功線 T相AMP | FEEDER | S64/11/KC24/I_T |  |  |  | CDC | 57 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 11 | 11kV | 成功線 | 成功線 |  | 成功線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.成功線A0 | 11KV成功線 N相AMP | FEEDER | S64/11/KC24/I_N |  |  |  | CDC | 58 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_MW | #1MTR二次側 MW | DTR | S64/11/M1/MW |  |  |  | CDC | 59 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S64/11/M1/MVAR |  |  |  | CDC | 60 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S64/11/M1/I_R |  |  |  | CDC | 61 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S64/11/M1/I_S |  |  |  | CDC | 62 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S64/11/M1/I_T |  |  |  | CDC | 63 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_OIL | #1MTR 油溫 | DTR | S64//1MTR/OilTemp |  |  |  | CDC | 64 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_COIL | #1MTR 線溫 | DTR | S64//1MTR/CoilTemp |  |  |  | CDC | 65 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_1 | [8 empty] | 開元SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S64//1MTR/TapPosMv |  |  |  | CDC | 66 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S64 | 開元SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.直流電源電壓 | 直流電源電壓 | OTHER | S64/0/StaDev/DCV |  |  |  | CDC | 67 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S64 | 開元SS | 0 |  | 11S11BUS | 11S1 |  | V | [17 empty] | 1-B5 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | S64/11/1BUS/V_S |  |  |  | CDC | 68 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 0 |  | 11T11BUS | 11T1 |  | V | [17 empty] | 1-B6 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 開元SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | S64/11/1BUS/V_T |  |  |  | CDC | 69 | GENERICAIPoint | SS406_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_PHA | 11KV元寶線(KC21) 相間RY | FEEDER | S64/11/KC21/PHA |  |  |  | CDC | 70 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_GDA | 11KV元寶線(KC21) 接地RY | FEEDER | S64/11/KC21/GDA |  |  |  | CDC | 71 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_79UL | 11KV元寶線(KC21) 79RY U/L | FEEDER | S64/11/KC21/79UL |  |  |  | CDC | 72 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC21 | 元寶線(KC21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_ADJ | 11KV元寶線(KC21) LCO分流器 U/L | FEEDER | S64/11/KC21/ADJ |  |  |  | CDC | 73 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC21 | KC21(11KV元寶線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_CB | KC21(11KV元寶線) CB | FEEDER | S64/11/KC21/CB |  |  |  | CDC | 74 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_PHA | 11KV大道線(KC22) 相間RY | FEEDER | S64/11/KC22/PHA |  |  |  | CDC | 75 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_GDA | 11KV大道線(KC22) 接地RY | FEEDER | S64/11/KC22/GDA |  |  |  | CDC | 76 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_79UL | 11KV大道線(KC22) 79RY U/L | FEEDER | S64/11/KC22/79UL |  |  |  | CDC | 77 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC22 | 大道線(KC22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_ADJ | 11KV大道線(KC22) LCO分流器 U/L | FEEDER | S64/11/KC22/ADJ |  |  |  | CDC | 78 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC22 | KC22(11KV大道線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_CB | KC22(11KV大道線) CB | FEEDER | S64/11/KC22/CB |  |  |  | CDC | 79 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_PHA | 11KV北門線(KC23) 相間RY | FEEDER | S64/11/KC23/PHA |  |  |  | CDC | 80 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_GDA | 11KV北門線(KC23) 接地RY | FEEDER | S64/11/KC23/GDA |  |  |  | CDC | 81 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_79UL | 11KV北門線(KC23) 79RY U/L | FEEDER | S64/11/KC23/79UL |  |  |  | CDC | 82 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC23 | 北門線(KC23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_ADJ | 11KV北門線(KC23) LCO分流器 U/L | FEEDER | S64/11/KC23/ADJ |  |  |  | CDC | 83 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC23 | KC23(11KV北門線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_CB | KC23(11KV北門線) CB | FEEDER | S64/11/KC23/CB |  |  |  | CDC | 84 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_PHA | 11KV成功線(KC24) 相間RY | FEEDER | S64/11/KC24/PHA |  |  |  | CDC | 85 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_GDA | 11KV成功線(KC24) 接地RY | FEEDER | S64/11/KC24/GDA |  |  |  | CDC | 86 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_79UL | 11KV成功線(KC24) 79RY U/L | FEEDER | S64/11/KC24/79UL |  |  |  | CDC | 87 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC24 | 成功線(KC24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_ADJ | 11KV成功線(KC24) LCO分流器 U/L | FEEDER | S64/11/KC24/ADJ |  |  |  | CDC | 88 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC24 | KC24(11KV成功線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_CB | KC24(11KV成功線) CB | FEEDER | S64/11/KC24/CB |  |  |  | CDC | 89 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_PHA | 11KV小東線(KC25) 相間RY | FEEDER | S64/11/KC25/PHA |  |  |  | CDC | 90 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_GDA | 11KV小東線(KC25) 接地RY | FEEDER | S64/11/KC25/GDA |  |  |  | CDC | 91 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_79UL | 11KV小東線(KC25) 79RY U/L | FEEDER | S64/11/KC25/79UL |  |  |  | CDC | 92 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 11 | 11kV | KC25 | 小東線(KC25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_ADJ | 11KV小東線(KC25) LCO分流器 U/L | FEEDER | S64/11/KC25/ADJ |  |  |  | CDC | 93 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S64 | 開元SS | 11 | 11kV | KC25 | KC25(11KV小東線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_CB | KC25(11KV小東線) CB | FEEDER | S64/11/KC25/CB |  |  |  | CDC | 94 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 69 | 69kV | 610 | #1MTR(610) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.610_CB | 610(#1MTR) CB | DTR | S64/69/610/CB |  |  |  | CDC | 95 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.1M_CB | 1M(#1MTR) CB | DTR | S64/11/M1/CB |  |  |  | CDC | 96 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_51A | #1MTR 51RY | DTR | S64/69/610/51A |  |  |  | CDC | 97 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_51NA | #1MTR 51N RY | DTR | S64/69/610/51NA |  |  |  | CDC | 98 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S64//1MTR/51ZA |  |  |  | CDC | 99 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_87A | #1MTR 87RY | DTR | S64//1MTR/87A |  |  |  | CDC | 100 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S64/69/610/81AS |  |  |  | CDC | 101 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S64 | 開元SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S64/11/M1/51A |  |  |  | CDC | 102 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_TRA | #1MTR 重故障 | DTR | S64//1MTR/TRA |  |  |  | CDC | 103 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S64//1MTR/TRF |  |  |  | CDC | 104 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S64//1MTR/SupLocal |  |  |  | CDC | 105 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S64//1MTR/Tap Chan |  |  |  | CDC | 106 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S64 | 開元SS | 69 | 69kV | 610 | #1MTR(610) |  | ABS1 | 611 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.611_ABS | 611(#1MTR) ABS | DTR | S64/69/610/ABS1 |  |  |  | CDC | 107 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S64 | 開元SS | 0 |  | 61E | #1MTR |  | ABS1 | 61E | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.61E_ABS | 611E(#1MTR) ABS | DTR | S64/69/610/ABS |  |  |  | CDC | 108 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S64//1MTR/OLTC_DLY |  |  |  | CDC | 109 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S64//1MTR/AC_Fault |  |  |  | CDC | 110 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.210_CB | 210(11KV #1SC) CB | SC | S64/11/210/CB |  |  |  | CDC | 111 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S64/11/210/SC_A_M |  |  |  | CDC | 112 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.210_SCA | 11KV #1SC 51,51N RY | SC | S64/11/210/SCA |  |  |  | CDC | 113 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S64/11/210/UVA |  |  |  | CDC | 114 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 開元SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S64/69/1BUS/BUS_VUA |  |  |  | CDC | 115 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S64/11/ComPoint/CBA |  |  |  | CDC | 116 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S64/11/ComPoint/CBF |  |  |  | CDC | 117 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S64/69/ComPoint/ABS_89A |  |  |  | CDC | 118 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S64/69/ComPoint/CBA |  |  |  | CDC | 119 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S64/69/ComPoint/CBF |  |  |  | CDC | 120 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S64/0/RTU/RTU_R_L |  |  |  | CDC | 121 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S64 | 開元SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.TEST_CB | TEST CB | OTHER | S64/0/RTU/Test_CB |  |  |  | CDC | 122 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S64/0/StaDev/PSF |  |  |  | CDC | 123 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S64/0/StaDev/ACB1 |  |  |  | CDC | 124 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S64 | 開元SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S64/0/StaDev/ACB2 |  |  |  | CDC | 125 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S64 | 開元SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S64/0/StaDev/STUV |  |  |  | CDC | 126 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.直流充電機故障 | 直流充電機故障 | OTHER | S64/0/StaDev/CHG1 |  |  |  | CDC | 127 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S64/0/StaDev/DCA |  |  |  | CDC | 128 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S64/0/StaDev/DCE |  |  |  | CDC | 129 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S64/0/StaDev/OilLeak |  |  |  | CDC | 130 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S64/0/StaDev/5A5Other |  |  |  | CDC | 131 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S64/0/StaDev/6A5Other |  |  |  | CDC | 132 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S64/0/StaDev/7A5Other |  |  |  | CDC | 133 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S64/0/StaDev/CHG2 |  |  |  | CDC | 134 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S64/0/StaDev/CommACF |  |  |  | CDC | 135 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S64/0/StaDev/Door1 |  |  |  | CDC | 136 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S64 | 開元SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S64/0/StaDev/Lights1 |  |  |  | CDC | 137 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S64 | 開元SS | 0 |  | 1_MAIN | #1 |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER | S64/11/M1/51NA |  |  |  | CDC | 138 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 69SC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.69SC警報 | 69SC警報 | OTHER |  |  |  |  | CDC | 139 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.RTU_DC故障 | RTU DC故障 | OTHER | S64/0/RTU/DCA |  |  |  | CDC | 140 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.水氣霧故障 | 水氣霧故障 | OTHER | S64/0/StaDev/2A5Other |  |  |  | CDC | 141 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.水氣霧警報 | 水氣霧警報 | OTHER | S64/0/StaDev/3A5Other |  |  |  | CDC | 142 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.火災警報 | 火警 | OTHER | S64/0/StaDev/Fire |  |  |  | CDC | 143 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.安全監控 | 保全設定 | OTHER | S64/0/StaDev/1A5Other |  |  |  | CDC | 144 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.門禁小門 | 門禁小門 | OTHER | S64/0/StaDev/Door2 |  |  |  | CDC | 145 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S64/0/StaDev/Lights |  |  |  | CDC | 146 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-05 |  | 1-57 | [5 empty] | DDCS4_1 | [8 empty] | 開元SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S64/0/StaDev/4A5Other |  |  |  | CDC | 147 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S64 | 開元SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.PM_CFA | PM通訊故障 | OTHER | S64/0/StaDev/PMA |  |  |  | CDC | 148 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.81RY_IED_FA | 低頻IED故障 | OTHER | S64/0/StaDev/81A_RYFA |  |  |  | CDC | 149 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 開元SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S64/69/ComPoint/CFA |  |  |  | CDC | 150 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 開元SS.69KV_IED_FA | 69KV IED故障 | OTHER | S64/69/ComPoint/IRFA |  |  |  | CDC | 151 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.11KV_IED_FA | 11KV IED故障 | OTHER | S64/11/ComPoint/IRFA |  |  |  | CDC | 152 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | KC21 | 元寶線 |  | LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_LOA | 元寶線 復閉失敗閉鎖 | OTHER | S64/11/KC21/LOA |  |  |  | CDC | 153 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | KC22 | 大道線 |  | LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_LOA | 大道線 復閉失敗閉鎖 | OTHER | S64/11/KC22/LOA |  |  |  | CDC | 154 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | KC23 | 北門線 |  | LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_LOA | 北門線 復閉失敗閉鎖 | OTHER | S64/11/KC23/LOA |  |  |  | CDC | 155 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | KC24 | 成功線 |  | LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_LOA | 成功線 復閉失敗閉鎖 | OTHER | S64/11/KC24/LOA |  |  |  | CDC | 156 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | KC25 | 小東線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_LOA | 小東線 復閉失敗閉鎖 | OTHER | S64/11/KC25/LOA |  |  |  | CDC | 157 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | DDCC充電機AC | [17 empty] | 1-3A-12 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.DDCC充電機AC | DDCC通訊室充電機AC電源故障 | OTHER | S64/0/StaDev/8A5Other |  |  |  | CDC | 158 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | DDCC充電機故障 | [17 empty] | 1-3A-13 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.DDCC充電機故障 | DDCC通訊室充電機故障 | OTHER | S64/0/StaDev/9A5Other |  |  |  | CDC | 159 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-18-02 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S64//1MTR/63Q |  |  |  | CDC | 160 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-18-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S64//1MTR/96B1 |  |  |  | CDC | 161 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-18-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S64//1MTR/96B2 |  |  |  | CDC | 162 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-18-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S64//1MTR/96D |  |  |  | CDC | 163 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-18-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S64//1MTR/96P |  |  |  | CDC | 164 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.變電所低水位 | 變電所低水位 | OTHER | S64/0/StaDev/Water1 |  |  |  | CDC | 165 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.變電所高水位 | 變電所高水位 | OTHER | S64/0/StaDev/Water2 |  |  |  | CDC | 166 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S64//1MTR/96PA |  |  |  | CDC | 167 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | S64//1MTR/51Z_UL |  |  |  | CDC | 168 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | S64//1MTR/MTR_86A |  |  |  | CDC | 169 | GENERICDIPoint | SS406_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER | S64//1MTR/87UL |  |  |  | CDC | 170 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | S64//1MTR/1_87UL2 |  |  |  | CDC | 171 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S64 | 開元SS | 0 |  | MTR | MTR |  | IEDGA | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_1 | [8 empty] | 開元SS.MTR_IED故障 | MTR_IED故障 | OTHER | S64/0/MTR/IRFA |  |  |  | CDC | 172 | GENERICDIPoint | SS406_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S64 | 開元SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_1 | [8 empty] | 開元SS.210_SC_CAP | 11KV#1SC 容量 | SC | S64/11/210/1AI_Oth |  |  |  |  | 173 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S64 | 開元SS | 0 |  | KC21 | KC21_DS |  | DS1 | KC21_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_DS | KC21_DS (非取樣點) | FEEDER | S64/11/KC21/DS |  |  |  |  | 174 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | KC21 | KC21_ES |  | LE0 | KC21_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC21_ES | KC21_ES (非取樣點) | FEEDER | S64/11/KC21/ES |  |  |  |  | 175 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | KC22 | KC22_DS |  | DS1 | KC22_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_DS | KC22_DS (非取樣點) | FEEDER | S64/11/KC22/DS |  |  |  |  | 176 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | KC22 | KC22_ES |  | LE0 | KC22_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC22_ES | KC22_ES (非取樣點) | FEEDER | S64/11/KC22/ES |  |  |  |  | 177 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | KC23 | KC23_DS |  | DS1 | KC23_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_DS | KC23_DS (非取樣點) | FEEDER | S64/11/KC23/DS |  |  |  |  | 178 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | KC23 | KC23_ES |  | LE0 | KC23_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC23_ES | KC23_ES (非取樣點) | FEEDER | S64/11/KC23/ES |  |  |  |  | 179 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | KC24 | KC24_DS |  | DS1 | KC24_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_DS | KC24_DS (非取樣點) | FEEDER | S64/11/KC24/DS |  |  |  |  | 180 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | KC24 | KC24_ES |  | LE0 | KC24_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC24_ES | KC24_ES (非取樣點) | FEEDER | S64/11/KC24/ES |  |  |  |  | 181 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | KC25 | KC25_DS |  | DS1 | KC25_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_DS | KC25_DS (非取樣點) | FEEDER | S64/11/KC25/DS |  |  |  |  | 182 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | KC25 | KC25_ES |  | LE0 | KC25_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.KC25_ES | KC25_ES (非取樣點) | FEEDER | S64/11/KC25/ES |  |  |  |  | 183 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.1M_DS | 1M_DS (非取樣點) | DTR | S64/11/M1/DS |  |  |  |  | 184 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.1M_ES | 1M_ES (非取樣點) | DTR | S64/11/M1/ES |  |  |  |  | 185 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.210_ES | 210_ES (非取樣點) | SC | S64/11/210/ES |  |  |  |  | 186 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.210_DS | 210_DS (非取樣點) | SC | S64/11/210/DS |  |  |  |  | 187 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S64 | 開元SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 開元SS.69B1E | 69B1E (非取樣點) | BUS | S64/69/1BUS/BE1 |  |  |  |  | 188 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S64 | 開元SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_1 | [8 empty] | 開元SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 189 | NotelDIPoint | [38 empty] | START/STOP | STOP

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo