## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S65 | 保安SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S65_A1 | [8 empty] | 保安SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S65 | 保安SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S65_D1 | [8 empty] | 保安SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2MA 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S65_D1 | [8 empty] | 保安SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0170 |  |  | 2-AA |  |  | #2A TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S65_D1 | [8 empty] | 保安SS.11S1#2ABUS_KV | 11S1 #2ABUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0171 |  |  | 2-AB |  |  | #2A TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S65_D1 | [8 empty] | 保安SS.11T1#2ABUS_KV | 11T1 #2ABUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0017 |  |  | 1-91 |  |  | #2MB 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S65_D1 | [8 empty] | 保安SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0172 |  |  | 2-AC |  |  | #2B TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S65_D1 | [8 empty] | 保安SS.11S1#2BBUS_KV | 11S1 #2BBUS KV | BUS |  |  |  |  | CDC | 8 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0173 |  |  | 2-AD |  |  | #2B TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S65_D1 | [8 empty] | 保安SS.11T1#2BBUS_KV | 11T1 #2BBUS KV | BUS |  |  |  |  | CDC | 9 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 3BUS | #3BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | #3 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S65_D1 | [8 empty] | 保安SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 10 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 3BUS | #3BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0174 |  |  | 2-AE |  |  | #3 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S65_D1 | [8 empty] | 保安SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS |  |  |  |  | CDC | 11 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 3BUS | #3BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0175 |  |  | 2-AF |  |  | #3 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S65_D1 | [8 empty] | 保安SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS |  |  |  |  | CDC | 12 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 22 | 22kV | 4BUS | #4BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0137 |  |  | 2-89 |  |  | #4 11KV 電壓 |  |  | kV_-18_18(-2000_2000) | aea | B2/S65_D1 | [8 empty] | 保安SS.23KV#4BUS_KV | 23KV #4BUS KV | BUS |  |  |  |  | CDC | 13 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | ABS1 | 621 | B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0436 | 437 | 0017 | 1-3B-04 | 1-3B-05 | 1-11 | 台南保安線 (621) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.621_ABS | 621(台南保安線) ABS | LINE69 |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S65_A1 | [8 empty] | 保安SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 15 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.69BUS_VUA | 69KV BUS 衡相RY | BUS |  |  |  |  | CDC | 16 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 備用線 (610) 瓦 |  |  | MW_-72_72(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.610_MW | 備用線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 備用線 (610) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.610_MVAR | 備用線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | 備用線 (610) MWH(+) |  |  |  |  | B2/S65_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 台南保安線 (620) 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.620_MW | 台南保安線 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 台南保安線 (620) 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.620_MVAR | 台南保安線 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0036 |  |  | 2-44 |  |  | 台南保安線 (620) MWH(+) |  |  |  |  | B2/S65_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 保安歸仁線 (660) 瓦 |  |  | MW_-120_120(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.660_MW | 歸仁保安線 MW | LINE69 |  |  |  |  | CDC | 23 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 保安歸仁線 (660) 乏 |  |  | MVAR_-120_120(-2000_2000) |  | B2/S65_A1 | [8 empty] | 保安SS.660_MVAR | 歸仁保安線 MVAR | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0038 |  |  | 2-46 |  |  | 保安歸仁線 (660) MWH(+) |  |  |  |  | B2/S65_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 25 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 備用線 (610) 67 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.610_PHA | 備用線(610) 相間RY | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 備用線 (610) 67N RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.610_GDA | 備用線(610) 接地RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 備用線 (610) 85 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.610_85A | 備用線(610) 85RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | 備用線 (610) 74RY U/L |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.610_74A | 備用線(610) 74RY | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 台南保安線 (620) 67 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.620_PHA | 台南保安線(620) 相間RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 台南保安線 (620) 67N RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.620_GDA | 台南保安線(620) 接地RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 保安歸仁線 (660) 67 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.660_PHA | 歸仁保安線(660) 相間RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 保安歸仁線 (660) 67N RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.660_GDA | 歸仁保安線(660) 接地RY | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 保安歸仁線 (660) 87 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.660_87A | 660歸仁保安線87RY | OTHER |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0006 | 1-32-00 |  | 1-06 | 備用線 (610) 85RY U/L |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.610_85UL | 備用線(610) 85RY U/L | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0009 | 1-32-06 |  | 1-09 | 保安歸仁線 (660) 85RY U/L |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.660_87UL | 660歸仁保安線87RY UL | OTHER |  |  |  |  | CDC | 36 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 備用線 (610) CB |  |  |  | aaaa | B2/S65_A1 | [8 empty] | 保安SS.610_CB | 610(備用線) CB | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 台南保安線 (620) CB |  |  |  | aada | B2/S65_A1 | [8 empty] | 保安SS.620_CB | 620(台南保安線) CB | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 保安歸仁線 (660) CB |  |  |  | aafa | B2/S65_A1 | [8 empty] | 保安SS.660_CB | 660(歸仁保安線) CB | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | ABS1 | 611 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0011 | 1-39-10 | 1-39-11 | 1-0B | 備用線 (611) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.611_ABS | 611(備用線) ABS | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | ABS2 | 612 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0012 | 1-39-12 | 1-39-13 | 1-0C | 備用線 (612) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.612_ABS | 612(備用線) ABS | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0424 | 425 | 0018 | 1-3A-08 | 1-3A-09 | 1-12 | 台南保安線 (622) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.622_ABS | 622(台南保安線) ABS | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ABS1 | 661 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0428 | 429 | 0020 | 1-3A-12 | 1-3A-13 | 1-14 | 保安歸仁線 (661) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.661_ABS | 661(歸仁保安線) ABS | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0013 | 1-39-14 | 1-39-15 | 1-0D | 備用線 (612E) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.612E_ES | 612E(備用線) ES | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | LE0 | 610LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_A1 | [8 empty] | 保安SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 45 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0426 | 427 | 0019 | 1-3A-10 | 1-3A-11 | 1-13 | 台南保安線 (622E) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.622E_ES | 622E(台南保安線) ES | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | LE0 | 620LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_A1 | [8 empty] | 保安SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 47 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ES2 | 662E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0432 | 433 | 0022 | 1-3B-00 | 1-3B-01 | 1-16 | 保安歸仁線 (662E) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.662E_ES | 662E(歸仁保安線) ES | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | LE0 | 660LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_A1 | [8 empty] | 保安SS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 49 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 保34線 (F4) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保34線KVAR | 11KV保34線 KVAR | FEEDER |  |  |  |  | CDC | 50 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 保34線 (F4) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保34線A1 | 11KV保34線 R相AMP | FEEDER |  |  |  |  | CDC | 51 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 保34線 (F4) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保34線A2 | 11KV保34線 S相AMP | FEEDER |  |  |  |  | CDC | 52 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 保34線 (F4) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保34線A3 | 11KV保34線 T相AMP | FEEDER |  |  |  |  | CDC | 53 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 保34線 (F4) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保34線A0 | 11KV保34線 N相AMP | FEEDER |  |  |  |  | CDC | 54 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 保34線 (F4) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 55 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 保29線 (F14) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保29線KVAR | 11KV保29線 KVAR | FEEDER |  |  |  |  | CDC | 56 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 保29線 (F14) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保29線A1 | 11KV保29線 R相AMP | FEEDER |  |  |  |  | CDC | 57 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 保29線 (F14) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保29線A2 | 11KV保29線 S相AMP | FEEDER |  |  |  |  | CDC | 58 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 保29線 (F14) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保29線A3 | 11KV保29線 T相AMP | FEEDER |  |  |  |  | CDC | 59 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 保29線 (F14) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保29線A0 | 11KV保29線 N相AMP | FEEDER |  |  |  |  | CDC | 60 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | 保29線 (F14) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 61 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | KVAR |  | B2,B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 保51線 (F16) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保51線KVAR | 23KV保51線 KVAR | FEEDER |  |  |  |  | CDC | 62 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 保51線 (F16) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保51線A1 | 23KV保51線 R相AMP | FEEDER |  |  |  |  | CDC | 63 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 保51線 (F16) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保51線A2 | 23KV保51線 S相AMP | FEEDER |  |  |  |  | CDC | 64 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 保51線 (F16) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保51線A3 | 23KV保51線 T相AMP | FEEDER |  |  |  |  | CDC | 65 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | I_N |  | B2,B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 保51線 (F16) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保51線A0 | 23KV保51線 N相AMP | FEEDER |  |  |  |  | CDC | 66 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | kWh |  | B2,B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | 保51線 (F16) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 67 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | KVAR |  | B2,B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 保52線 (F17) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保52線KVAR | 23KV保52線 KVAR | FEEDER |  |  |  |  | CDC | 68 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 保52線 (F17) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保52線A1 | 23KV保52線 R相AMP | FEEDER |  |  |  |  | CDC | 69 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 保52線 (F17) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保52線A2 | 23KV保52線 S相AMP | FEEDER |  |  |  |  | CDC | 70 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 保52線 (F17) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保52線A3 | 23KV保52線 T相AMP | FEEDER |  |  |  |  | CDC | 71 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | I_N |  | B2,B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 保52線 (F17) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保52線A0 | 23KV保52線 N相AMP | FEEDER |  |  |  |  | CDC | 72 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | kWh |  | B2,B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0016 |  |  | 1-50 |  |  | 保52線 (F17) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 73 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | KVAR |  | B2,B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 保53線 (F18) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保53線KVAR | 23KV保53線 KVAR | FEEDER |  |  |  |  | CDC | 74 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 保53線 (F18) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保53線A1 | 23KV保53線 R相AMP | FEEDER |  |  |  |  | CDC | 75 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 保53線 (F18) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保53線A2 | 23KV保53線 S相AMP | FEEDER |  |  |  |  | CDC | 76 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 保53線 (F18) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保53線A3 | 23KV保53線 T相AMP | FEEDER |  |  |  |  | CDC | 77 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | I_N |  | B2,B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 保53線 (F18) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保53線A0 | 23KV保53線 N相AMP | FEEDER |  |  |  |  | CDC | 78 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | kWh |  | B2,B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0017 |  |  | 1-51 |  |  | 保53線 (F18) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 79 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | KVAR |  | B2,B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 備54線 (F19) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備54線KVAR | 23KV備54線 KVAR | FEEDER |  |  |  |  | CDC | 80 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 備54線 (F19) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備54線A1 | 23KV備54線 R相AMP | FEEDER |  |  |  |  | CDC | 81 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 備54線 (F19) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備54線A2 | 23KV備54線 S相AMP | FEEDER |  |  |  |  | CDC | 82 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 備54線 (F19) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備54線A3 | 23KV備54線 T相AMP | FEEDER |  |  |  |  | CDC | 83 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | I_N |  | B2,B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 備54線 (F19) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備54線A0 | 23KV備54線 N相AMP | FEEDER |  |  |  |  | CDC | 84 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | kWh |  | B2,B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | 備54線 (F19) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 85 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | KVAR |  | B2,B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 備55線 (F20) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備55線KVAR | 23KV備55線 KVAR | FEEDER |  |  |  |  | CDC | 86 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 備55線 (F20) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備55線A1 | 23KV備55線 R相AMP | FEEDER |  |  |  |  | CDC | 87 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 備55線 (F20) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備55線A2 | 23KV備55線 S相AMP | FEEDER |  |  |  |  | CDC | 88 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 備55線 (F20) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備55線A3 | 23KV備55線 T相AMP | FEEDER |  |  |  |  | CDC | 89 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | I_N |  | B2,B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 備55線 (F20) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.備55線A0 | 23KV備55線 N相AMP | FEEDER |  |  |  |  | CDC | 90 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | kWh |  | B2,B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0019 |  |  | 1-53 |  |  | 備55線 (F20) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 91 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 保甲線 (F1) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM31_PHA | 11KV保甲線(KM31) 相間RY | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 保甲線 (F1) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM31_GDA | 11KV保甲線(KM31) 接地RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0042 | 1-33-07 |  | 1-2A | 保甲線 (F1) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM31_79UL | 11KV保甲線(KM31) 79RY U/L | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0368 |  | 0104 | 1-37-00 |  | 1-68 | 保甲線 (F1) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM31_ADJ | 11KV保甲線(KM31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | 中生線 (F2) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM32_PHA | 11KV中生線(KM32) 相間RY | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 中生線 (F2) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM32_GDA | 11KV中生線(KM32) 接地RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0043 | 1-33-08 |  | 1-2B | 中生線 (F2) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM32_79UL | 11KV中生線(KM32) 79RY U/L | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0369 |  | 0105 | 1-37-01 |  | 1-69 | 中生線 (F2) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM32_ADJ | 11KV中生線(KM32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 新崙線 (F3) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM33_PHA | 11KV新崙線(KM33) 相間RY | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 新崙線 (F3) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM33_GDA | 11KV新崙線(KM33) 接地RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0044 | 1-33-09 |  | 1-2C | 新崙線 (F3) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM33_79UL | 11KV新崙線(KM33) 79RY U/L | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0370 |  | 0106 | 1-37-02 |  | 1-6A | 新崙線 (F3) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM33_ADJ | 11KV新崙線(KM33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 保34線 (F4) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM34_PHA | 11KV保34線(KM34) 相間RY | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 保34線 (F4) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM34_GDA | 11KV保34線(KM34) 接地RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0045 | 1-33-10 |  | 1-2D | 保34線 (F4) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM34_79UL | 11KV保34線(KM34) 79RY U/L | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0371 |  | 0107 | 1-37-03 |  | 1-6B | 保34線 (F4) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM34_ADJ | 11KV保34線(KM34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 中洲線 (F5) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM35_PHA | 11KV中洲線(KM35) 相間RY | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 中洲線 (F5) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM35_GDA | 11KV中洲線(KM35) 接地RY | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0046 | 1-33-11 |  | 1-2E | 中洲線 (F5) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM35_79UL | 11KV中洲線(KM35) 79RY U/L | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0372 |  | 0108 | 1-37-04 |  | 1-6C | 中洲線 (F5) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM35_ADJ | 11KV中洲線(KM35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 三甲線 (F6) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM21_PHA | 11KV三甲線(KM21) 相間RY | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 三甲線 (F6) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM21_GDA | 11KV三甲線(KM21) 接地RY | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0061 | 1-34-07 |  | 1-3D | 三甲線 (F6) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM21_79UL | 11KV三甲線(KM21) 79RY U/L | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0373 |  | 0109 | 1-37-05 |  | 1-6D | 三甲線 (F6) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM21_ADJ | 11KV三甲線(KM21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 仁工線 (F7) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM22_PHA | 11KV仁工線(KM22) 相間RY | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 仁工線 (F7) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM22_GDA | 11KV仁工線(KM22) 接地RY | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0062 | 1-34-08 |  | 1-3E | 仁工線 (F7) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM22_79UL | 11KV仁工線(KM22) 79RY U/L | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0374 |  | 0110 | 1-37-06 |  | 1-6E | 仁工線 (F7) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM22_ADJ | 11KV仁工線(KM22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 保安線 (F8) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM23_PHA | 11KV保安線(KM23) 相間RY | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 保安線 (F8) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM23_GDA | 11KV保安線(KM23) 接地RY | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0063 | 1-34-09 |  | 1-3F | 保安線 (F8) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM23_79UL | 11KV保安線(KM23) 79RY U/L | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0375 |  | 0111 | 1-37-07 |  | 1-6F | 保安線 (F8) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM23_ADJ | 11KV保安線(KM23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 二行線 (F9) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM24_PHA | 11KV二行線(KM24) 相間RY | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 二行線 (F9) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM24_GDA | 11KV二行線(KM24) 接地RY | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0064 | 1-34-10 |  | 1-40 | 二行線 (F9) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM24_79UL | 11KV二行線(KM24) 79RY U/L | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0376 |  | 0112 | 1-37-08 |  | 1-70 | 二行線 (F9) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM24_ADJ | 11KV二行線(KM24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 豐和線 (F10) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM25_PHA | 11KV豐和線(KM25) 相間RY | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 豐和線 (F10) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM25_GDA | 11KV豐和線(KM25) 接地RY | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0065 | 1-34-11 |  | 1-41 | 豐和線 (F10) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM25_79UL | 11KV豐和線(KM25) 79RY U/L | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0377 |  | 0113 | 1-37-09 |  | 1-71 | 豐和線 (F10) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM25_ADJ | 11KV豐和線(KM25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | 安廟線 (F11) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM26_PHA | 11KV安廟線(KM26) 相間RY | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 安廟線 (F11) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM26_GDA | 11KV安廟線(KM26) 接地RY | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0080 | 1-35-07 |  | 1-50 | 安廟線 (F11) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM26_79UL | 11KV安廟線(KM26) 79RY U/L | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0378 |  | 0114 | 1-37-10 |  | 1-72 | 安廟線 (F11) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM26_ADJ | 11KV安廟線(KM26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | 上崙線 (F12) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM27_PHA | 11KV上崙線(KM27) 相間RY | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | 上崙線 (F12) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM27_GDA | 11KV上崙線(KM27) 接地RY | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0081 | 1-35-08 |  | 1-51 | 上崙線 (F12) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM27_79UL | 11KV上崙線(KM27) 79RY U/L | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0379 |  | 0115 | 1-37-11 |  | 1-73 | 上崙線 (F12) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM27_ADJ | 11KV上崙線(KM27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | 藥專線 (F13) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM28_PHA | 11KV藥專線(KM28) 相間RY | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | 藥專線 (F13) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM28_GDA | 11KV藥專線(KM28) 接地RY | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0082 | 1-35-09 |  | 1-52 | 藥專線 (F13) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM28_79UL | 11KV藥專線(KM28) 79RY U/L | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0380 |  | 0116 | 1-37-12 |  | 1-74 | 藥專線 (F13) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM28_ADJ | 11KV藥專線(KM28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | 保29線 (F14) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM29_PHA | 11KV保29線(KM29) 相間RY | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | 保29線 (F14) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM29_GDA | 11KV保29線(KM29) 接地RY | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0083 | 1-35-10 |  | 1-53 | 保29線 (F14) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM29_79UL | 11KV保29線(KM29) 79RY U/L | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0381 |  | 0117 | 1-37-13 |  | 1-75 | 保29線 (F14) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM29_ADJ | 11KV保29線(KM29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 仁七線 (F15) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM30_PHA | 11KV仁七線(KM30) 相間RY | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 1-13-06 |  |  | 仁七線 (F15) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM30_GDA | 11KV仁七線(KM30) 接地RY | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0084 | 1-35-11 |  | 1-54 | 仁七線 (F15) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM30_79UL | 11KV仁七線(KM30) 79RY U/L | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0382 |  | 0118 | 1-37-14 |  | 1-76 | 仁七線 (F15) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM30_ADJ | 11KV仁七線(KM30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 保51線 (F16) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM51_PHA | 22KV保51線(KM51) 相間RY | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 保51線 (F16) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM51_GDA | 22KV保51線(KM51) 接地RY | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | 79UL |  | B2 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0359 |  | 0098 | 1-36-07 |  | 1-62 | 保51線 (F16) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM51_79UL | 22KV保51線(KM51) 79RY U/L | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | ADJ |  | B2,Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0383 |  | 0119 | 1-37-15 |  | 1-77 | 保51線 (F16) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM51_ADJ | 22KV保51線(KM51) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 保52線 (F17) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM52_PHA | 22KV保52線(KM52) 相間RY | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | 保52線 (F17) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM52_GDA | 22KV保52線(KM52) 接地RY | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | 79UL |  | B2 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0360 |  | 0099 | 1-36-08 |  | 1-63 | 保52線 (F17) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM52_79UL | 22KV保52線(KM52) 79RY U/L | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | ADJ |  | B2,Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0384 |  | 0120 | 1-38-00 |  | 1-78 | 保52線 (F17) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM52_ADJ | 22KV保52線(KM52) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 保53線 (F18) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM53_PHA | 22KV保53線(KM53) 相間RY | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | 保53線 (F18) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM53_GDA | 22KV保53線(KM53) 接地RY | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | 79UL |  | B2 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0361 |  | 0100 | 1-36-09 |  | 1-64 | 保53線 (F18) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM53_79UL | 22KV保53線(KM53) 79RY U/L | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | ADJ |  | B2,Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0385 |  | 0121 | 1-38-01 |  | 1-79 | 保53線 (F18) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM53_ADJ | 22KV保53線(KM53) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | 備54線 (F19) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM54_PHA | 22KV備54線(KM54) 相間RY | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 備54線 (F19) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM54_GDA | 22KV備54線(KM54) 接地RY | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | 79UL |  | B2 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0362 |  | 0101 | 1-36-10 |  | 1-65 | 備54線 (F19) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM54_79UL | 22KV備54線(KM54) 79RY U/L | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | ADJ |  | B2,Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0386 |  | 0122 | 1-38-02 |  | 1-7A | 備54線 (F19) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM54_ADJ | 22KV備54線(KM54) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | 備55線 (F20) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM55_PHA | 22KV備55線(KM55) 相間RY | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | 備55線 (F20) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM55_GDA | 22KV備55線(KM55) 接地RY | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | 79UL |  | B2 | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0363 |  | 0102 | 1-36-11 |  | 1-66 | 備55線 (F20) 79RY U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM55_79UL | 22KV備55線(KM55) 79RY U/L | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | ADJ |  | B2,Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0387 |  | 0123 | 1-38-03 |  | 1-7B | 備55線 (F20) LCO ADJ U/L |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM55_ADJ | 22KV備55線(KM55) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 171 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KM31/T1 |  |  | 0096 |  | 0034 | 1-0C-00 |  | 1-22 | 保甲線 (F1) CB |  |  |  | adab | B2/S65_D1 | [8 empty] | 保安SS.KM31_CB | KM31(11KV保甲線) CB | FEEDER |  |  |  |  | CDC | 172 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM31_DS | KM31_DS (非取樣點) | FEEDER | [5 empty] | 173 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | ES | KM31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM31_ES | KM31_ES (非取樣點) | FEEDER | [5 empty] | 174 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KM32/T1 |  |  | 0097 |  | 0035 | 1-0C-01 |  | 1-23 | 中生線 (F2) CB |  |  |  | adbb | B2/S65_D1 | [8 empty] | 保安SS.KM32_CB | KM32(11KV中生線) CB | FEEDER |  |  |  |  | CDC | 175 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM32_DS | KM32_DS (非取樣點) | FEEDER | [5 empty] | 176 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | ES | KM32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM32_ES | KM32_ES (非取樣點) | FEEDER | [5 empty] | 177 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KM33/T1 |  |  | 0098 |  | 0036 | 1-0C-02 |  | 1-24 | 新崙線 (F3) CB |  |  |  | addb | B2/S65_D1 | [8 empty] | 保安SS.KM33_CB | KM33(11KV新崙線) CB | FEEDER |  |  |  |  | CDC | 178 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM33_DS | KM33_DS (非取樣點) | FEEDER | [5 empty] | 179 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | ES | KM33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM33_ES | KM33_ES (非取樣點) | FEEDER | [5 empty] | 180 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KM34/T1 |  |  | 0099 |  | 0037 | 1-0C-03 |  | 1-25 | 保34線 (F4) CB |  |  |  | adfb | B2/S65_D1 | [8 empty] | 保安SS.KM34_CB | KM34(11KV保34線) CB | FEEDER |  |  |  |  | CDC | 181 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM34_DS | KM34_DS (非取樣點) | FEEDER | [5 empty] | 182 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | ES | KM34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM34_ES | KM34_ES (非取樣點) | FEEDER | [5 empty] | 183 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KM35/T1 |  |  | 0100 |  | 0038 | 1-0C-04 |  | 1-26 | 中洲線 (F5) CB |  |  |  | adgb | B2/S65_D1 | [8 empty] | 保安SS.KM35_CB | KM35(11KV中洲線) CB | FEEDER |  |  |  |  | CDC | 184 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM35_DS | KM35_DS (非取樣點) | FEEDER | [5 empty] | 185 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | ES | KM35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM35_ES | KM35_ES (非取樣點) | FEEDER | [5 empty] | 186 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KM21/T1 |  |  | 0118 |  | 0053 | 1-0E-06 |  | 1-35 | 三甲線 (F6) CB |  |  |  | aabb | B2/S65_D1 | [8 empty] | 保安SS.KM21_CB | KM21(11KV三甲線) CB | FEEDER |  |  |  |  | CDC | 187 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM21_DS | KM21_DS (非取樣點) | FEEDER | [5 empty] | 188 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | ES | KM21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM21_ES | KM21_ES (非取樣點) | FEEDER | [5 empty] | 189 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KM22/T1 |  |  | 0119 |  | 0054 | 1-0E-07 |  | 1-36 | 仁工線 (F7) CB |  |  |  | aacb | B2/S65_D1 | [8 empty] | 保安SS.KM22_CB | KM22(11KV仁工線) CB | FEEDER |  |  |  |  | CDC | 190 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM22_DS | KM22_DS (非取樣點) | FEEDER | [5 empty] | 191 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | ES | KM22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM22_ES | KM22_ES (非取樣點) | FEEDER | [5 empty] | 192 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KM23/T1 |  |  | 0120 |  | 0055 | 1-0F-00 |  | 1-37 | 保安線 (F8) CB |  |  |  | aaeb | B2/S65_D1 | [8 empty] | 保安SS.KM23_CB | KM23(11KV保安線) CB | FEEDER |  |  |  |  | CDC | 193 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM23_DS | KM23_DS (非取樣點) | FEEDER | [5 empty] | 194 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | ES | KM23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM23_ES | KM23_ES (非取樣點) | FEEDER | [5 empty] | 195 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KM24/T1 |  |  | 0121 |  | 0056 | 1-0F-01 |  | 1-38 | 二行線 (F9) CB |  |  |  | aafb | B2/S65_D1 | [8 empty] | 保安SS.KM24_CB | KM24(11KV二行線) CB | FEEDER |  |  |  |  | CDC | 196 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM24_DS | KM24_DS (非取樣點) | FEEDER | [5 empty] | 197 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | ES | KM24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM24_ES | KM24_ES (非取樣點) | FEEDER | [5 empty] | 198 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KM25/T1 |  |  | 0122 |  | 0057 | 1-0F-02 |  | 1-39 | 豐和線 (F10) CB |  |  |  | aagb | B2/S65_D1 | [8 empty] | 保安SS.KM25_CB | KM25(11KV豐和線) CB | FEEDER |  |  |  |  | CDC | 199 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM25_DS | KM25_DS (非取樣點) | FEEDER | [5 empty] | 200 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | ES | KM25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM25_ES | KM25_ES (非取樣點) | FEEDER | [5 empty] | 201 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KM26/T1 |  |  | 0140 |  | 0072 | 1-11-04 |  | 1-48 | 安廟線 (F11) CB |  |  |  | acbb | B2/S65_D1 | [8 empty] | 保安SS.KM26_CB | KM26(11KV安廟線) CB | FEEDER |  |  |  |  | CDC | 202 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM26_DS | KM26_DS (非取樣點) | FEEDER | [5 empty] | 203 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | ES | KM26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM26_ES | KM26_ES (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KM27/T1 |  |  | 0141 |  | 0073 | 1-11-05 |  | 1-49 | 上崙線 (F12) CB |  |  |  | accb | B2/S65_D1 | [8 empty] | 保安SS.KM27_CB | KM27(11KV上崙線) CB | FEEDER |  |  |  |  | CDC | 205 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM27_DS | KM27_DS (非取樣點) | FEEDER | [5 empty] | 206 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | ES | KM27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM27_ES | KM27_ES (非取樣點) | FEEDER | [5 empty] | 207 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KM28/T1 |  |  | 0142 |  | 0074 | 1-11-06 |  | 1-4A | 藥專線 (F13) CB |  |  |  | acdb | B2/S65_D1 | [8 empty] | 保安SS.KM28_CB | KM28(11KV藥專線) CB | FEEDER |  |  |  |  | CDC | 208 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM28_DS | KM28_DS (非取樣點) | FEEDER | [5 empty] | 209 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | ES | KM28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM28_ES | KM28_ES (非取樣點) | FEEDER | [5 empty] | 210 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | L/KM29/T1 |  |  | 0143 |  | 0075 | 1-11-07 |  | 1-4B | 保29線 (F14) CB |  |  |  | abab | B2/S65_D1 | [8 empty] | 保安SS.KM29_CB | KM29(11KV保29線) CB | FEEDER |  |  |  |  | CDC | 211 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM29_DS | KM29_DS (非取樣點) | FEEDER | [5 empty] | 212 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | ES | KM29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM29_ES | KM29_ES (非取樣點) | FEEDER | [5 empty] | 213 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | L/KM30/T1 |  |  | 0144 |  | 0076 | 1-12-00 |  | 1-4C | 仁七線 (F15) CB |  |  |  | abbb | B2/S65_D1 | [8 empty] | 保安SS.KM30_CB | KM30(11KV仁七線) CB | FEEDER |  |  |  |  | CDC | 214 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM30_DS | KM30_DS (非取樣點) | FEEDER | [5 empty] | 215 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | ES | KM30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM30_ES | KM30_ES (非取樣點) | FEEDER | [5 empty] | 216 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KM51/T1 |  |  | 0162 |  | 0090 | 1-14-02 |  | 1-5A | 保51線 (F16) CB |  |  |  | aeab | B2/S65_D1 | [8 empty] | 保安SS.KM51_CB | KM51(22KV保51線) CB | FEEDER |  |  |  |  | CDC | 217 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM51_DS | KM51_DS (非取樣點) | FEEDER | [5 empty] | 218 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | ES | KM51_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM51_ES | KM51_ES (非取樣點) | FEEDER | [5 empty] | 219 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KM52/T1 |  |  | 0163 |  | 0091 | 1-14-03 |  | 1-5B | 保52線 (F17) CB |  |  |  | aebb | B2/S65_D1 | [8 empty] | 保安SS.KM52_CB | KM52(22KV保52線) CB | FEEDER |  |  |  |  | CDC | 220 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM52_DS | KM52_DS (非取樣點) | FEEDER | [5 empty] | 221 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | ES | KM52_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM52_ES | KM52_ES (非取樣點) | FEEDER | [5 empty] | 222 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KM53/T1 |  |  | 0164 |  | 0092 | 1-14-04 |  | 1-5C | 保53線 (F18) CB |  |  |  | aecb | B2/S65_D1 | [8 empty] | 保安SS.KM53_CB | KM53(22KV保53線) CB | FEEDER |  |  |  |  | CDC | 223 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM53_DS | KM53_DS (非取樣點) | FEEDER | [5 empty] | 224 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | ES | KM53_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM53_ES | KM53_ES (非取樣點) | FEEDER | [5 empty] | 225 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KM54/T1 |  |  | 0165 |  | 0093 | 1-14-05 |  | 1-5D | 備54線 (F19) CB |  |  |  | aeeb | B2/S65_D1 | [8 empty] | 保安SS.KM54_CB | KM54(22KV備54線) CB | FEEDER |  |  |  |  | CDC | 226 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM54_DS | KM54_DS (非取樣點) | FEEDER | [5 empty] | 227 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | ES | KM54_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM54_ES | KM54_ES (非取樣點) | FEEDER | [5 empty] | 228 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KM55/T1 |  |  | 0166 |  | 0094 | 1-14-06 |  | 1-5E | 備55線 (F20) CB |  |  |  | aefb | B2/S65_D1 | [8 empty] | 保安SS.KM55_CB | KM55(22KV備55線) CB | FEEDER |  |  |  |  | CDC | 229 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM55_DS | KM55_DS (非取樣點) | FEEDER | [5 empty] | 230 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | ES | KM55_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.KM55_ES | KM55_ES (非取樣點) | FEEDER | [5 empty] | 231 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R | #2MB-#1 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #2B-1 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 232 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S | #2MB-#1 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #2B-1 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 233 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T | #2MB-#1 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #2B-1 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 234 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R | #3-#2MA | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #3-#2A TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 235 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S | #3-#2MA | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #3-#2A TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 236 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T | #3-#2MA | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #3-#2A TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 237 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 備用 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE |  |  |  |  | CDC | 238 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 備用 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE |  |  |  |  | CDC | 239 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 備用 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE |  |  |  |  | CDC | 240 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB | #2MB-#1 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2ABUS |  |  | 0101 |  | 0032 | 1-0C-05 |  | 1-20 | #2B-#1 TIE CB |  |  |  | zzzz | B2/S65_D1 | [8 empty] | 保安SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 241 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A | #2MB-#1 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #2B-#1 TIE 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 242 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA | #2MB-#1 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #2B-#1 TIE 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 243 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB | #3-#2MA |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1A | B/2BBUS | B/3BUS |  |  | 0123 |  | 0051 | 1-0F-03 |  | 1-33 | #3-#2A TIE CB |  |  |  | zzzz | B2/S65_D1 | [8 empty] | 保安SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 244 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A | #3-#2MA |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #3-#2A TIE 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 245 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA | #3-#2MA |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #3-#2A TIE 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 246 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/4BUS |  |  |  | 0145 |  | 0070 | 1-12-01 |  | 1-46 | 備用 TIE CB |  |  |  | zzzz | B2/S65_D1 | [8 empty] | 保安SS.TIE3_CB | 11KV TIE3 CB | TIE |  |  |  |  | CDC | 247 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | 備用 TIE 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE3_51A | 11KV TIE3 51RY | TIE |  |  |  |  | CDC | 248 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | 備用 TIE 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.TIE3_51NA | 11KV TIE3 51N RY | TIE |  |  |  |  | CDC | 249 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | #2MB-#1(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 250 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | DS1 | #3-#2MA(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 251 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D1 | TIE3(非取樣點) | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 252 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 253 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 254 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 255 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 256 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 257 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 258 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 259 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 260 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 261 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 262 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 263 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 264 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 265 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 266 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 267 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | #4 TR 瓦 |  |  | MW_-39.6_39.6(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#4MTR_MW | #4MTR二次側 MW | DTR |  |  |  |  | CDC | 268 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.0792 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.079200 | 0.010000
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | #4 TR 乏 |  |  | MVAR_-39.6_39.6(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR |  |  |  |  | CDC | 269 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.0792 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.079200 | 0.010000
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | #4 TR R相電流 |  |  | A_-1100_1100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 270 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | #4 TR S相電流 |  |  | A_-1100_1100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 271 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | #4 TR T相電流 |  |  | A_-1100_1100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 272 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 273 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 274 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0039 | 1-9B |  | 1-27 | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 275 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0020 |  |  | 1-54 |  |  | #1 TR MWH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 276 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0021 |  |  | 1-55 |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 277 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 278 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 279 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0058 | 1-BF |  | 1-3A | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 280 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0023 |  |  | 1-57 |  |  | #2 TR MWH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 281 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0024 |  |  | 1-58 |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 282 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 283 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 284 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0077 | 1-E5 |  | 1-4D | #3 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 285 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | #3 TR MWH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 286 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0027 |  |  | 1-5B |  |  | #3 TR MVARH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 287 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | #4 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_OIL | #4MTR 油溫 | DTR |  |  |  |  | CDC | 288 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | #4 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_COIL | #4MTR 線溫 | DTR |  |  |  |  | CDC | 289 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0140 |  | 0095 | 2-8C |  | 1-5F | #4 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_TAP | #4MTR OLTC TAP | DTR |  |  |  |  | CDC | 290 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS |  |  | 4MTR | #4MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0029 |  |  | 1-5D |  |  | #4 TR MWH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 291 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS |  |  | 4MTR | #4MTR |  | MVARH_P |  | Element | [12 empty] | 0030 |  |  | 1-5E |  |  | #4 TR MVARH(+) |  |  |  |  | B1/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 292 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0030 | 1-00-01 |  | 1-1E | #1TR 一次 (750) CB |  |  |  | aabb | B3/S65_D1 | [8 empty] | 保安SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 293 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0048 | 1-01-02 |  | 1-30 | #2TR 一次 (760) CB |  |  |  | aaeb | B3/S65_D1 | [8 empty] | 保安SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 294 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0022 |  | 0067 | 1-02-06 |  | 1-43 | #3TR 一次 (770) CB |  |  |  | aagb | B3/S65_D1 | [8 empty] | 保安SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 295 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/4MTR |  |  | 0034 |  | 0086 | 1-04-02 |  | 1-56 | #4TR 一次 (780) CB |  |  |  | aahb | B3/S65_D1 | [8 empty] | 保安SS.780_CB | 780(#4MTR) CB | DTR |  |  |  |  | CDC | 296 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0002 |  | 0031 | 1-00-02 |  | 1-1F | #1TR 二次 (#1MT) CB |  |  |  | aada | B2/S65_D1 | [8 empty] | 保安SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 297 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | T/2MTR |  |  | 0011 |  | 0049 | 1-01-03 |  | 1-31 | #2TR 二次 (M2A) CB |  |  |  | acaa | B2/S65_D1 | [8 empty] | 保安SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 298 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M2B | #2MTR(M2B) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | T/2MTR |  |  | 0012 |  | 0050 | 1-01-04 |  | 1-32 | #2TR 二次 (M2B) CB |  |  |  | abda | B2/S65_D1 | [8 empty] | 保安SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 299 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/3BUS | T/3MTR |  |  | 0023 |  | 0068 | 1-02-07 |  | 1-44 | #3TR 二次 (#3MT) CB |  |  |  | adea | B2/S65_D1 | [8 empty] | 保安SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 300 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | T/4MTR |  |  | 0035 |  | 0087 | 1-04-03 |  | 1-57 | #4TR 二次 (#4MT) CB |  |  |  | aeda | B2/S65_D1 | [8 empty] | 保安SS.4M_CB | 4M(#4MTR) CB | DTR |  |  |  |  | CDC | 301 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次 (750) 51 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 302 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 一次 (750) 51N RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 303 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 51Z RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 304 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 87 RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 305 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 306 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0047 | 1-0C-06 |  | 1-2F | #1 BUS 81 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 307 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 一次 (760) 51 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 308 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 一次 (760) 51N RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 309 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2TR 51Z RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 310 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2TR 87 RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 311 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2TR 87 LS1S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 312 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  | 0066 | 1-0F-04 |  | 1-42 | #760 BUS 81 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#2MTR_81A/S | #760 81RY A/S | DTR |  |  |  |  | CDC | 313 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3TR 一次 (770) 51 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 314 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3TR 一次 (770) 51N RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 315 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3TR 51Z RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 316 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3TR 87 RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 317 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3TR 87 LS1S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 318 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  | 0085 | 1-12-02 |  | 1-55 | #770 BUS 81 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#3MTR_81A/S | #770 81RY A/S | DTR |  |  |  |  | CDC | 319 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #4TR 一次 (780) 51 RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#4MTR_51A | #4MTR 51RY | DTR |  |  |  |  | CDC | 320 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #4TR 一次 (780) 51N RY |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.#4MTR_51NA | #4MTR 51N RY | DTR |  |  |  |  | CDC | 321 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #4TR 51Z RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_51ZA | #4MTR 51Z RY | DTR |  |  |  |  | CDC | 322 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | #4TR 87 RY |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_87A | #4MTR 87RY | DTR |  |  |  |  | CDC | 323 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0355 |  |  | 1-36-03 |  |  | #4TR 87 LS1S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_87UL1 | #4MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 324 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1TR 二次 (#1MT) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 325 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 326 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 327 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 328 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0040 | 1-33-05 |  | 1-28 | #1TR OLTC A/M |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 329 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2TR 二次 (M2A) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 330 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2TR 二次 (M2B) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 331 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-34-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 332 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 333 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 334 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0059 | 1-34-05 |  | 1-3B | #2TR OLTC A/M |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 335 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3TR 二次 (#3MT) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 336 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0336 |  |  | 1-35-00 |  |  | #3TR 重故障 |  |  |  | a | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 337 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3TR 輕故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 338 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3TR OLTC R/L |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 339 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0078 | 1-35-05 |  | 1-4E | #3TR OLTC A/M |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 340 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | #4TR 二次 (#4MT) 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.4M_51A | #4MTR二次側(4M) 51RY | DTR |  |  |  |  | CDC | 341 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0352 |  |  | 1-36-00 |  |  | #4TR 重故障 |  |  |  | a | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_TRA | #4MTR 重故障 | DTR |  |  |  |  | CDC | 342 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0353 |  |  | 1-36-01 |  |  | #4TR 輕故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_TRF | #4MTR 輕故障 | DTR |  |  |  |  | CDC | 343 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 1-36-04 |  |  | #4TR OLTC R/L |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_S/L | #4MTR OLTC S/L | DTR |  |  |  |  | CDC | 344 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS |  |  | 4MTR | #4MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0357 |  | 0096 | 1-36-05 |  | 1-60 | #4TR OLTC A/M |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_A/M | #4MTR OLTC A/M | DTR |  |  |  |  | CDC | 345 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0024 | 1-39-00 | 1-39-01 | 1-18 | #1TR (751) ABS |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 346 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0402 | 403 | 0025 | 1-39-02 | 1-39-03 | 1-19 | #2TR (761) ABS |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 347 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0026 | 1-39-04 | 1-39-05 | 1-1A | #3TR (771) ABS |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 348 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0027 | 1-39-06 | 1-39-07 | 1-1B | #4TR (781) ABS |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.781_ABS | 781(#4MTR) ABS | DTR |  |  |  |  | CDC | 349 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 350 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 351 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 機械保護動作(96PA) |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 352 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 353 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1TR 冷卻電源故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 354 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | DS1 | 2MA_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 355 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | ES | 2MA_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 356 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | M2B | #2MTR(M2B) |  | DS1 | 2MB_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 357 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M2B | #2MTR(M2B) |  | ES | 2MB_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 358 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 359 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 360 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2TR 冷卻電源故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 361 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS1 | 3M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 362 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 363 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3TR 機械保護動作(96PA) |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR |  |  |  |  | CDC | 364 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3TR OLTC 遲滯 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 365 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | #3TR 冷卻電源故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 366 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.4M_DS | 4M_DS (非取樣點) | DTR | [5 empty] | 367 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | ES | 4M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.4M_ES | 4M_ES (非取樣點) | DTR | [5 empty] | 368 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #4TR 機械保護動作(96PA) |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR |  |  |  |  | CDC | 369 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0354 |  |  | 1-36-02 |  |  | #4TR OLTC 遲滯 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 370 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0364 |  |  | 1-36-12 |  |  | #4TR 冷卻電源故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR |  |  |  |  | CDC | 371 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | T/2SSTR |  |  | 0184 |  | 0124 | 1-17-00 |  | 1-7C | #1 SSTR CB |  |  |  | abeb | B2/S65_D1 | [8 empty] | 保安SS.490_CB | 490(#2SSTR) CB | OTHER |  |  |  |  | CDC | 372 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #1 SSTR 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 373 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #1 SSTR 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  |  |  |  | CDC | 374 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 490 | #2SSTR(490) |  | DS1 | 491(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.491 | 491 (非取樣點) | OTHER | [5 empty] | 375 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 490 | #2SSTR(490) |  | ES | 491E(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.491E | 491E (非取樣點) | OTHER | [5 empty] | 376 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 590 | #3SSTR(590) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/3BUS | T/3SSTR |  |  | 0187 |  | 0125 | 1-17-03 |  | 1-7D | #2 SSTR CB |  |  |  | adhb | B2/S65_D1 | [8 empty] | 保安SS.590_CB | 590(#3SSTR) CB | OTHER |  |  |  |  | CDC | 377 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 590 | #3SSTR(590) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | #2 SSTR 51 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#3SSTR_51A | #3SSTR 51RY | OTHER |  |  |  |  | CDC | 378 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 590 | #3SSTR(590) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | #2 SSTR 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER |  |  |  |  | CDC | 379 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 590 | #3SSTR(590) |  | DS1 | 591(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.591 | 591 (非取樣點) | OTHER | [5 empty] | 380 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 590 | #3SSTR(590) |  | ES | 591E(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.591E | 591E (非取樣點) | OTHER | [5 empty] | 381 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0092 |  | 0005 | 1-0B-04 |  | 1-05 | 69KV (810) SC CB |  |  |  | aacb | B2/S65_A1 | [8 empty] | 保安SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 382 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0095 |  | 0033 | 1-0B-07 |  | 1-21 | #1 11KV SC CB |  |  |  | aaab | B2/S65_D1 | [8 empty] | 保安SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 383 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0041 | 1-33-06 |  | 1-29 | #1SC Q-CTL A/M |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 384 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 385 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | C/2SC |  |  | 0117 |  | 0052 | 1-0E-05 |  | 1-34 | #2 11KV SC CB |  |  |  | abcb | B2/S65_D1 | [8 empty] | 保安SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 386 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0326 |  | 0060 | 1-34-06 |  | 1-3C | #2SC Q-CTL A/M |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 387 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 388 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/3BUS | C/3SC |  |  | 0139 |  | 0071 | 1-11-03 |  | 1-47 | #3 11KV SC CB |  |  |  | adcb | B2/S65_D1 | [8 empty] | 保安SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 389 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0342 |  | 0079 | 1-35-06 |  | 1-4F | #3SC Q-CTL A/M |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 390 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 391 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | C/4SC |  |  | 0161 |  | 0089 | 1-14-01 |  | 1-59 | #4 11KV SC CB |  |  |  | aegb | B2/S65_D1 | [8 empty] | 保安SS.240_CB | 240(23KV #4SC) CB | SC |  |  |  |  | CDC | 392 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M |  | B2,B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0358 |  | 0097 | 1-36-06 |  | 1-61 | #4SC Q-CTL A/M |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.240_A/M | 23KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 393 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | ES | 240_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 394 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0408 | 409 | 0023 | 1-39-08 | 1-39-09 | 1-17 | 69KV SC (811) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 395 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 69KV (810) SC 51,51N RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 396 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 69KV (810) SC 27,59 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 397 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 398 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 399 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 400 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 401 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #3SC 51,51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 402 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | #3SC 27,59 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 403 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  | B2,B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #4SC 51,51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.240_SCA | 23KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 404 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  | B2,B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | #4SC 27,59 RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.240_UVA | 23KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 405 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 406 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 407 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 408 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 409 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 410 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 411 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 412 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 413 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 414 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 415 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 保安SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 416 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 417 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 418 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 419 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 420 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 421 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0028 | 1-30-06 |  | 1-1C | 開關場照明 C/T |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 422 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 423 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1S |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 424 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2S |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 425 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 426 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 427 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 428 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 429 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0388 |  |  | 1-38-04 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0389 |  |  | 1-38-05 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0390 |  |  | 1-38-06 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0391 |  |  | 1-38-07 |  |  | 博碼調變器故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 437 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 438 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0029 | 1-30-07 |  | 1-1D | 開關場照明 A/M |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 439 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 440 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 441 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV (810) SC 警報 |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 443 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次 (#1MT) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#1_MAIN_51NA | #1MCB GDA | OTHER |  |  |  |  | CDC | 444 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 二次 (M2A) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#2_MA_51NA | #2MA GDA | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | #2TR 二次 (M2B) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#2_MB_51NA | #2MB GDA | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #3TR 二次 (#3MT) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#3_MAIN_51NA | #3MCB GDA | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | M4 | #4MTR(M4) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | #4TR 二次 (#4MT) 51N RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#4_MAIN_51NA | #4MCB GDA | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.火災警報 | 火警 | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛IED故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0167 |  | 0103 | 1-14-07 |  | 1-67 | 全所故障指示器復歸點 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 | Element | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S65_D1 | [8 empty] | 保安SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | [13 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S65_D1 | [8 empty] | 保安SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 台南保安線 (620) 87 RY |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.620_87A | 620台南保安線87RY | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0008 | 1-32-04 |  | 1-08 | 台南保安線 (620) 87RY U/L |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.620_87UL | 620台南保安線87RY UL | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | ES | 2BR_ES | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2BR_ES | 2BR ES(非取樣點) | OTHER | [5 empty] | 461 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | #2MA-#1(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.TIE1_ES | TIE1 ES(非取樣點) | OTHER | [5 empty] | 462 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | #3-#2MA(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.TIE2_ES | TIE2 ES(非取樣點) | OTHER | [5 empty] | 463 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 二行線 (F9) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.二行線KVAR | 11KV二行線 KVAR | FEEDER |  |  |  |  | CDC | 464 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 二行線 (F9) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.二行線A1 | 11KV二行線 R相AMP | FEEDER |  |  |  |  | CDC | 465 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 二行線 (F9) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.二行線A2 | 11KV二行線 S相AMP | FEEDER |  |  |  |  | CDC | 466 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 二行線 (F9) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.二行線A3 | 11KV二行線 T相AMP | FEEDER |  |  |  |  | CDC | 467 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 二行線 (F9) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.二行線A0 | 11KV二行線 N相AMP | FEEDER |  |  |  |  | CDC | 468 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 三甲線 (F6) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.三甲線KVAR | 11KV三甲線 KVAR | FEEDER |  |  |  |  | CDC | 469 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 三甲線 (F6) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.三甲線A1 | 11KV三甲線 R相AMP | FEEDER |  |  |  |  | CDC | 470 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 三甲線 (F6) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.三甲線A2 | 11KV三甲線 S相AMP | FEEDER |  |  |  |  | CDC | 471 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 三甲線 (F6) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.三甲線A3 | 11KV三甲線 T相AMP | FEEDER |  |  |  |  | CDC | 472 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 三甲線 (F6) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.三甲線A0 | 11KV三甲線 N相AMP | FEEDER |  |  |  |  | CDC | 473 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 上崙線 (F12) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.上崙線KVAR | 11KV上崙線 KVAR | FEEDER |  |  |  |  | CDC | 474 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 上崙線 (F12) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.上崙線A1 | 11KV上崙線 R相AMP | FEEDER |  |  |  |  | CDC | 475 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 上崙線 (F12) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.上崙線A2 | 11KV上崙線 S相AMP | FEEDER |  |  |  |  | CDC | 476 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 上崙線 (F12) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.上崙線A3 | 11KV上崙線 T相AMP | FEEDER |  |  |  |  | CDC | 477 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 上崙線 (F12) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.上崙線A0 | 11KV上崙線 N相AMP | FEEDER |  |  |  |  | CDC | 478 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 中生線 (F2) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中生線KVAR | 11KV中生線 KVAR | FEEDER |  |  |  |  | CDC | 479 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 中生線 (F2) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中生線A1 | 11KV中生線 R相AMP | FEEDER |  |  |  |  | CDC | 480 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 中生線 (F2) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中生線A2 | 11KV中生線 S相AMP | FEEDER |  |  |  |  | CDC | 481 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 中生線 (F2) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中生線A3 | 11KV中生線 T相AMP | FEEDER |  |  |  |  | CDC | 482 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 中生線 (F2) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中生線A0 | 11KV中生線 N相AMP | FEEDER |  |  |  |  | CDC | 483 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 中洲線 (F5) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中洲線KVAR | 11KV中洲線 KVAR | FEEDER |  |  |  |  | CDC | 484 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 中洲線 (F5) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中洲線A1 | 11KV中洲線 R相AMP | FEEDER |  |  |  |  | CDC | 485 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 中洲線 (F5) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中洲線A2 | 11KV中洲線 S相AMP | FEEDER |  |  |  |  | CDC | 486 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 中洲線 (F5) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中洲線A3 | 11KV中洲線 T相AMP | FEEDER |  |  |  |  | CDC | 487 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 中洲線 (F5) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.中洲線A0 | 11KV中洲線 N相AMP | FEEDER |  |  |  |  | CDC | 488 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 仁七線 (F15) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁七線KVAR | 11KV仁七線 KVAR | FEEDER |  |  |  |  | CDC | 489 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 仁七線 (F15) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁七線A1 | 11KV仁七線 R相AMP | FEEDER |  |  |  |  | CDC | 490 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 仁七線 (F15) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁七線A2 | 11KV仁七線 S相AMP | FEEDER |  |  |  |  | CDC | 491 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 仁七線 (F15) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁七線A3 | 11KV仁七線 T相AMP | FEEDER |  |  |  |  | CDC | 492 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 仁七線 (F15) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁七線A0 | 11KV仁七線 N相AMP | FEEDER |  |  |  |  | CDC | 493 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 仁工線 (F7) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁工線KVAR | 11KV仁工線 KVAR | FEEDER |  |  |  |  | CDC | 494 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 仁工線 (F7) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁工線A1 | 11KV仁工線 R相AMP | FEEDER |  |  |  |  | CDC | 495 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 仁工線 (F7) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁工線A2 | 11KV仁工線 S相AMP | FEEDER |  |  |  |  | CDC | 496 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 仁工線 (F7) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁工線A3 | 11KV仁工線 T相AMP | FEEDER |  |  |  |  | CDC | 497 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 仁工線 (F7) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.仁工線A0 | 11KV仁工線 N相AMP | FEEDER |  |  |  |  | CDC | 498 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 安廟線 (F11) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.安廟線KVAR | 11KV安廟線 KVAR | FEEDER |  |  |  |  | CDC | 499 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 安廟線 (F11) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.安廟線A1 | 11KV安廟線 R相AMP | FEEDER |  |  |  |  | CDC | 500 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 安廟線 (F11) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.安廟線A2 | 11KV安廟線 S相AMP | FEEDER |  |  |  |  | CDC | 501 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 安廟線 (F11) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.安廟線A3 | 11KV安廟線 T相AMP | FEEDER |  |  |  |  | CDC | 502 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 安廟線 (F11) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.安廟線A0 | 11KV安廟線 N相AMP | FEEDER |  |  |  |  | CDC | 503 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 保甲線 (F1) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保甲線KVAR | 11KV保甲線 KVAR | FEEDER |  |  |  |  | CDC | 504 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 保甲線 (F1) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保甲線A1 | 11KV保甲線 R相AMP | FEEDER |  |  |  |  | CDC | 505 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 保甲線 (F1) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保甲線A2 | 11KV保甲線 S相AMP | FEEDER |  |  |  |  | CDC | 506 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 保甲線 (F1) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保甲線A3 | 11KV保甲線 T相AMP | FEEDER |  |  |  |  | CDC | 507 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 保甲線 (F1) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保甲線A0 | 11KV保甲線 N相AMP | FEEDER |  |  |  |  | CDC | 508 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 保安線 (F8) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保安線KVAR | 11KV保安線 KVAR | FEEDER |  |  |  |  | CDC | 509 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 保安線 (F8) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保安線A1 | 11KV保安線 R相AMP | FEEDER |  |  |  |  | CDC | 510 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 保安線 (F8) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保安線A2 | 11KV保安線 S相AMP | FEEDER |  |  |  |  | CDC | 511 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 保安線 (F8) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保安線A3 | 11KV保安線 T相AMP | FEEDER |  |  |  |  | CDC | 512 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 保安線 (F8) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.保安線A0 | 11KV保安線 N相AMP | FEEDER |  |  |  |  | CDC | 513 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 新崙線 (F3) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.新崙線KVAR | 11KV新崙線 KVAR | FEEDER |  |  |  |  | CDC | 514 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 新崙線 (F3) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.新崙線A1 | 11KV新崙線 R相AMP | FEEDER |  |  |  |  | CDC | 515 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 新崙線 (F3) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.新崙線A2 | 11KV新崙線 S相AMP | FEEDER |  |  |  |  | CDC | 516 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 新崙線 (F3) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.新崙線A3 | 11KV新崙線 T相AMP | FEEDER |  |  |  |  | CDC | 517 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 新崙線 (F3) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.新崙線A0 | 11KV新崙線 N相AMP | FEEDER |  |  |  |  | CDC | 518 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 豐和線 (F10) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.豐和線KVAR | 11KV豐和線 KVAR | FEEDER |  |  |  |  | CDC | 519 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 豐和線 (F10) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.豐和線A1 | 11KV豐和線 R相AMP | FEEDER |  |  |  |  | CDC | 520 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 豐和線 (F10) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.豐和線A2 | 11KV豐和線 S相AMP | FEEDER |  |  |  |  | CDC | 521 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 豐和線 (F10) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.豐和線A3 | 11KV豐和線 T相AMP | FEEDER |  |  |  |  | CDC | 522 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 豐和線 (F10) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.豐和線A0 | 11KV豐和線 N相AMP | FEEDER |  |  |  |  | CDC | 523 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 藥專線 (F13) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.藥專線KVAR | 11KV藥專線 KVAR | FEEDER |  |  |  |  | CDC | 524 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 藥專線 (F13) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.藥專線A1 | 11KV藥專線 R相AMP | FEEDER |  |  |  |  | CDC | 525 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 藥專線 (F13) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.藥專線A2 | 11KV藥專線 S相AMP | FEEDER |  |  |  |  | CDC | 526 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 藥專線 (F13) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.藥專線A3 | 11KV藥專線 T相AMP | FEEDER |  |  |  |  | CDC | 527 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 藥專線 (F13) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.藥專線A0 | 11KV藥專線 N相AMP | FEEDER |  |  |  |  | CDC | 528 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S65_D1 | [8 empty] | 保安SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 529 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S65 | 保安SS | 11 | 11kV | 1BUS | #1BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0168 |  |  | 2-A8 |  |  | #1 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S65_D1 | [8 empty] | 保安SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | [5 empty] | 530 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 1BUS | #1BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | #1 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S65_D1 | [8 empty] | 保安SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | [5 empty] | 531 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 22 | 22kV | 4BUS | #4BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0176 |  |  | 2-B0 |  |  | #4 TR S相電壓 |  |  | kV_-18_18(-2000_2000) | aea | B2/S65_D1 | [8 empty] | 保安SS.23S1#4BUS_KV | 23S1 #4BUS KV | BUS | [5 empty] | 532 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 22 | 22kV | 4BUS | #4BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0177 |  |  | 2-B1 |  |  | #4 TR T相電壓 |  |  | kV_-18_18(-2000_2000) | aea | B2/S65_D1 | [8 empty] | 保安SS.23T1#4BUS_KV | 23T1 #4BUS KV | BUS | [5 empty] | 533 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 11 | 11kV | 6BUS | 奇美實業B廠 |  | V_R |  | DELETE | MvMoment | R相電壓 |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 奇美實業B廠(二甲K645)太陽光電R相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.1CR1#6BUS_KV | 1CR1 #6BUS KV | BUS | [5 empty] | 534 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 6BUS | 奇美實業B廠 |  | V_S |  | DELETE | MvMoment | S相電壓 |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 奇美實業B廠(二甲K645)太陽光電S相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.1CS1#6BUS_KV | 1CS1 #6BUS KV | BUS | [5 empty] | 535 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 6BUS | 奇美實業B廠 |  | V_T |  | DELETE | MvMoment | T相電壓 |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 奇美實業B廠(二甲K645)太陽光電T相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.1CT1#6BUS_KV | 1CT1 #6BUS KV | BUS | [5 empty] | 536 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 5BUS | 奇美新田廠 |  | V_R |  | DELETE | MvMoment | R相電壓 |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 奇美新田廠(仁德K461)太陽光電R相電壓 |  |  | kV_-18_18(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.2CR1#5BUS_KV | 2CR1 #5BUS KV | BUS | [5 empty] | 537 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 11 | 11kV | 5BUS | 奇美新田廠 |  | V_S |  | DELETE | MvMoment | S相電壓 |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 奇美新田廠(仁德K461)太陽光電S相電壓 |  |  | kV_-18_18(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.2CS1#5BUS_KV | 2CS1 #5BUS KV | BUS | [5 empty] | 538 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 11 | 11kV | 5BUS | 奇美新田廠 |  | V_T |  | DELETE | MvMoment | T相電壓 |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 奇美新田廠(仁德K461)太陽光電T相電壓 |  |  | kV_-18_18(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.2CT1#5BUS_KV | 2CT1 #5BUS KV | BUS | [5 empty] | 539 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 奇美實業B廠(二甲K645)太陽光電乏 |  |  | KVAR_-9000_9000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠KVAR | 11KVCM_B廠 KVAR | FEEDER | [5 empty] | 540 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 奇美實業B廠(二甲K645)太陽光電R相電流 |  |  | A_-300_300(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠A1 | 11KVCM_B廠 R相AMP | FEEDER | [5 empty] | 541 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 奇美實業B廠(二甲K645)太陽光電S相電流 |  |  | A_-300_300(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠A2 | 11KVCM_B廠 S相AMP | FEEDER | [5 empty] | 542 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 奇美實業B廠(二甲K645)太陽光電T相電流 |  |  | A_-300_300(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠A3 | 11KVCM_B廠 T相AMP | FEEDER | [5 empty] | 543 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | KVAR |  | DELETE | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 奇美新田廠(仁德K461)太陽光電乏 |  |  | KVAR_-6000_6000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田KVAR | 23KVCM新田 KVAR | FEEDER | [5 empty] | 544 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 奇美新田廠(仁德K461)太陽光電R相電流 |  |  | A_-100_100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田A1 | 23KVCM新田 R相AMP | FEEDER | [5 empty] | 545 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 奇美新田廠(仁德K461)太陽光電S相電流 |  |  | A_-100_100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田A2 | 23KVCM新田 S相AMP | FEEDER | [5 empty] | 546 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 奇美新田廠(仁德K461)太陽光電T相電流 |  |  | A_-100_100(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田A3 | 23KVCM新田 T相AMP | FEEDER | [5 empty] | 547 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | KW |  | DELETE | MvMoment | KW |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 奇美新田廠(仁德K461)太陽光電瓦 |  |  | KW_-6000_6000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田_KW | 23KVCM新田 KW | OTHER | [5 empty] | 548 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_KW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | KW |  | DELETE | MvMoment | KW |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 奇美實業B廠(二甲K645)太陽光電瓦 |  |  | KW_-9000_9000(-2000_2000) |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠_KW | 11KVCM_B廠 KW | OTHER | [5 empty] | 549 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [5 empty] | LG_KW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ABS2 | gggggggggggb | INSERT | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0021 | 1-3B-02 | 1-3B-03 | 1-15 | 保安歸仁線 (662) ABS |  |  |  |  | B2/S65_A1 | [8 empty] | 保安SS.662_ABS | 662(歸仁保安線) ABS | LINE69 | [5 empty] | 550 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 三甲線(F6) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM21_LOA | 三甲線 復閉失敗閉鎖 | OTHER | [5 empty] | 551 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 仁工線(F7) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM22_LOA | 仁工線 復閉失敗閉鎖 | OTHER | [5 empty] | 552 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 保安線(F8) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM23_LOA | 保安線 復閉失敗閉鎖 | OTHER | [5 empty] | 553 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 二行線(F9) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM24_LOA | 二行線 復閉失敗閉鎖 | OTHER | [5 empty] | 554 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 豐和線(F10) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM25_LOA | 豐和線 復閉失敗閉鎖 | OTHER | [5 empty] | 555 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | 安廟線(F11) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM26_LOA | 安廟線 復閉失敗閉鎖 | OTHER | [5 empty] | 556 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0503 |  |  | 1-3F-07 |  |  | 上崙線(F12) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM27_LOA | 上崙線 復閉失敗閉鎖 | OTHER | [5 empty] | 557 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0504 |  |  | 1-3F-08 |  |  | 藥專線(F13) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM28_LOA | 藥專線 復閉失敗閉鎖 | OTHER | [5 empty] | 558 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-3F-09 |  |  | 保29線(F14) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM29_LOA | 保29線 復閉失敗閉鎖 | OTHER | [5 empty] | 559 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0506 |  |  | 1-3F-10 |  |  | 仁七線(F15) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM30_LOA | 仁七線 復閉失敗閉鎖 | OTHER | [5 empty] | 560 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0507 |  |  | 1-3F-11 |  |  | 保51線(F16) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM51_LOA | 保51線 復閉失敗閉鎖 | OTHER | [5 empty] | 561 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0508 |  |  | 1-3F-12 |  |  | 保52線(F17) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM52_LOA | 保52線 復閉失敗閉鎖 | OTHER | [5 empty] | 562 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0509 |  |  | 1-3F-13 |  |  | 保53線(F18) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM53_LOA | 保53線 復閉失敗閉鎖 | OTHER | [5 empty] | 563 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0510 |  |  | 1-3F-14 |  |  | 備54線(F19) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM54_LOA | 備54線 復閉失敗閉鎖 | OTHER | [5 empty] | 564 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0511 |  |  | 1-3F-15 |  |  | 備55線(F20) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM55_LOA | 備55線 復閉失敗閉鎖 | OTHER | [5 empty] | 565 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1DTR 63Q |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 566 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1DTR 96B1 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 567 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1DTR 96B2 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 568 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1DTR 96D |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 569 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1DTR 96P |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 570 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2DTR 63Q |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | [5 empty] | 571 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2DTR 96B1 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | [5 empty] | 572 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2DTR 96B2 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | [5 empty] | 573 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2DTR 96D |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | [5 empty] | 574 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2DTR 96P |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | [5 empty] | 575 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | #3DTR 63Q |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | [5 empty] | 576 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | #3DTR 96B1 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | [5 empty] | 577 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | #3DTR 96B2 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | [5 empty] | 578 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | #3DTR 96D |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | [5 empty] | 579 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | #3DTR 96P |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | [5 empty] | 580 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | #4DTR 63Q |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | [5 empty] | 581 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | #4DTR 96B1 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | [5 empty] | 582 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | #4DTR 96B2 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | [5 empty] | 583 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | #4DTR 96D |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | [5 empty] | 584 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | #4DTR 96P |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | [5 empty] | 585 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 586 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #1DTR 86A |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 587 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 588 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2DTR 51ZLS |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | [5 empty] | 589 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | #2DTR 86A |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 590 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 591 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3DTR 51ZLS |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | [5 empty] | 592 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | #3DTR 86A |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 593 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3DTR 87LS2S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | [5 empty] | 594 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0487 |  |  | 1-3E-07 |  |  | #4DTR 51ZLS |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_51ZUL | #4MTR 51Z U/L | OTHER | [5 empty] | 595 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS |  |  | 4MTR | #4MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | #4DTR 86A |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_86A | #4MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 596 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS |  |  | 4MTR | #4MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | #4DTR 87LS2S |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.#4MTR_87UL2 | #4MTR 第二套87RY U/L | OTHER | [5 empty] | 597 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S65 | 保安SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S65_D1 | [8 empty] | 保安SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 598 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | 保甲線 (F1) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM31_LOA | 保甲線 復閉失敗閉鎖 | OTHER | [5 empty] | 599 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | 中生線 (F2) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM32_LOA | 中生線 復閉失敗閉鎖 | OTHER | [5 empty] | 600 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | 新崙線 (F3) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM33_LOA | 新崙線 復閉失敗閉鎖 | OTHER | [5 empty] | 601 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | 保34線 (F4) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM34_LOA | 保34線 復閉失敗閉鎖 | OTHER | [5 empty] | 602 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | 中洲線 (F5) LOA |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.KM35_LOA | 中洲線 復閉失敗閉鎖 | OTHER | [5 empty] | 603 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | UVA |  | DELETE | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 奇美實業B廠(二甲K645)太陽光電 27/59RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠27 | 奇美實業B廠 27/59A | OTHER | [5 empty] | 604 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | 奇美實業B廠(二甲K645)太陽光電 50/51RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠51 | 奇美實業B廠 50/51A | OTHER | [5 empty] | 605 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 奇美實業B廠(二甲K645)太陽光電 50N/51NRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠51N | 奇美實業B廠 50N/51NA | OTHER | [5 empty] | 606 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | 59A_V0 |  | DELETE | Status | 59RY 0相 | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | 奇美實業B廠(二甲K645)太陽光電 59VoRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠59 | 奇美實業B廠 59V0A | OTHER | [5 empty] | 607 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 奇美實業B廠(二甲K645)太陽光電 81LRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠81L | 奇美實業B廠 81LA | OTHER | [5 empty] | 608 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 奇美實業B廠(二甲K645)太陽光電 CB |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠CB | 奇美實業B廠 CB | OTHER | [5 empty] | 609 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | CFA | 通訊故障 | DELETE | [12 empty] | 0393 |  |  | 1-38-09 |  |  | 奇美實業B廠(二甲K645)太陽光電通訊警報 |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠CFA | 奇美實業B廠通訊故障 | OTHER | [5 empty] | 610 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | D1 |  | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | 奇美實業B廠(二甲K645)太陽光電DS |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM_B廠DS | 奇美實業B廠 DS | OTHER | [5 empty] | 611 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | UVA |  | DELETE | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 奇美新田廠(仁德K461)太陽光電 27/59/RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田27 | 奇美新田廠 27/59A | OTHER | [5 empty] | 612 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 奇美新田廠(仁德K461)太陽光電 50/51RY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田51 | 奇美新田廠 50/51A | OTHER | [5 empty] | 613 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 奇美新田廠(仁德K461)太陽光電 50N/51NRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田51N | 奇美新田廠 50N/51NA | OTHER | [5 empty] | 614 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | 59A_V0 |  | DELETE | Status | 59RY 0相 | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 奇美新田廠(仁德K461)太陽光電 59VoRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田59 | 奇美新田廠 59V0A | OTHER | [5 empty] | 615 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | 81A |  | DELETE | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 奇美新田廠(仁德K461)太陽光電 81LRY |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田81L | 奇美新田廠 81LA | OTHER | [5 empty] | 616 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | 奇美新田廠(仁德K461)太陽光電 CB |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田CB | 奇美新田廠 CB | OTHER | [5 empty] | 617 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | CFA | 通訊故障 | DELETE | [12 empty] | 0392 |  |  | 1-38-08 |  |  | 奇美新田廠(仁德K461)太陽光電通訊警報 |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田CFA | 奇美新田廠通訊故障 | OTHER | [5 empty] | 618 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | CM_XT | 奇美新田廠 |  | D1 |  | DELETE | Status | DS1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0440 |  |  | 1-3B-08 |  |  | 奇美新田廠(仁德K461)太陽光電DS |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.CM新田DS | 奇美新田廠 DS | OTHER | [5 empty] | 619 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 保甲線 (F1) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 620 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 中生線 (F2) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 621 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 新崙線 (F3) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 622 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 中洲線 (F5) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 623 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 三甲線 (F6) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 624 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 仁工線 (F7) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 625 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 保安線 (F8) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 626 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 二行線 (F9) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 627 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 豐和線 (F10) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 628 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | 安廟線 (F11) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 629 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | 上崙線 (F12) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 630 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | 藥專線 (F13) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 631 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | 仁七線 (F15) KWH(+) |  |  |  |  | B2/S65_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 632 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | DS2 | 2BR_ (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.2BR_DS | 2BR_DS (非取樣點) | TIE | [5 empty] | 633 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 2ABUS | #2ABUS |  | BE0 | #2A BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 634 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 2BBUS | #2BBUS |  | BE0 | #2B BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 635 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 3BUS | #3BUS |  | BE0 | #3 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 636 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | 1BUS | #1BUS |  | BE0 | #1 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.#1_BE | #1 BE(非取樣點) | OTHER | [5 empty] | 637 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 1BR | #1BR |  | DS | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | BayFdrF | B/2ABUS | [13 empty] | adhb | B2/S65_D1 | [8 empty] | 保安SS.1BR_DS | 1BR_DS (非取樣點) | TIE | [5 empty] | 638 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 1BR | #1BR |  | ES | (非取樣點) | INSERT | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.1BR_ES | 1BR_ES(非取樣點) | OTHER | [5 empty] | 639 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 640 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 641 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | 3AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值3 |  | Y |  | AI | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 642 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | 4AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值4 |  | Y |  | AI | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 643 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1SSTR |  |  | 0181 |  | 0127 | 1-16-05 |  | 1-7F | Locate Empty |  |  |  | not found | B2/S65_D1 | [8 empty] | 保安SS.390_CB | 390(#1SSTR) CB | OTHER |  |  |  |  | CDC | 644 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | Locate Empty |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 645 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | Locate Empty |  |  |  |  | B2/S65_D1 | [8 empty] | 保安SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  |  |  |  | CDC | 646 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 390 | #1SSTR(390) |  | DS | 391(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 647 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S65 | 保安SS | 11 | 11kV | 390 | #1SSTR(390) |  | ES | 391E(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S65_D1 | [8 empty] | 保安SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 648 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S65 | 保安SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S65_D1 | [12 empty] | 保安SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S65/69/1BUS/V
S65 | 保安SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S65_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S65/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S65 | 保安SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S65_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_7 | OPRD1: S65/11/M1/MW; OPRD2: S65/11/M2A/MW; OPRD3: S65/11/M3/MW; OPRD4: S65/22/M4/MW; OPRD5: S65/69/610/MW; OPRD6: S65/69/620/MW; OPRD7: S65/69/660/MW
S65 | 保安SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S65_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S65/0/CalcPoint/OPRN2_MW
S65 | 保安SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S65_D1 | [17 empty] | none
S65 | 保安SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S65_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S65/0/CalcPoint/OPRN1; OPRD2: S65/0/CalcPoint/OPRN2; OPRD3: S65/0/CalcPoint/PRFL_UL
S65 | 保安SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S65_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S65/11/M1/MW; OPRD2: S65/11/M1/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S65_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S65/11/M2A/MW; OPRD2: S65/11/M2A/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S65_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S65/11/M3/MW; OPRD2: S65/11/M3/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S65_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S65/22/M4/MW; OPRD2: S65/22/M4/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S65_A1 | [12 empty] | 保安SS.610_AMP | 備用線 AMP | LINE69 | AMP_CAL | C06R0500 | amp_cal | OPRD1: S65/69/610/MW; OPRD2: S65/69/610/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS | 69 | 69kV | 620 | 台南～保安線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S65_A1 | [12 empty] | 保安SS.620_AMP | 台南保安線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: S65/69/620/MW; OPRD2: S65/69/620/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S65_A1 | [12 empty] | 保安SS.660_AMP | 歸仁保安線 AMP | LINE69 | AMP_CAL | C10R0800 | amp_cal | OPRD1: S65/69/660/MW; OPRD2: S65/69/660/MVAR; OPRD3: S65/0/CalcPoint/Vbs1
S65 | 保安SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S65_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 保安SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S65/11/M1/MW; OPRD2: S65/11/M1/MVAR
S65 | 保安SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S65_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 保安SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S65/11/M2A/MW; OPRD2: S65/11/M2A/MVAR
S65 | 保安SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S65_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 保安SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S65/11/M3/MW; OPRD2: S65/11/M3/MVAR
S65 | 保安SS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S65_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 保安SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S65/22/M4/MW; OPRD2: S65/22/M4/MVAR
S65 | 保安SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S65_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S65//1MTR/MVA; OPRD2: 0
S65 | 保安SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S65_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S65//2MTR/MVA; OPRD2: 0
S65 | 保安SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S65_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S65//3MTR/MVA; OPRD2: 0
S65 | 保安SS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/S65_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S65//4MTR/MVA; OPRD2: 0
S65 | 保安SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S65_D1 | [12 empty] | 保安SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S65/11/M1/MW; OPRD2: S65/11/M1/MVAR
S65 | 保安SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S65_D1 | [12 empty] | 保安SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S65/11/M2A/MW; OPRD2: S65/11/M2A/MVAR
S65 | 保安SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S65_D1 | [12 empty] | 保安SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S65/11/M3/MW; OPRD2: S65/11/M3/MVAR
S65 | 保安SS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/S65_D1 | [12 empty] | 保安SS.#4MTR_PF | #4MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S65/22/M4/MW; OPRD2: S65/22/M4/MVAR
S65 | 保安SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S65_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S65//1MTR/SupLocal; OPRD2: S65//1MTR/Tap Chan; OPRD3: NULL
S65 | 保安SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S65_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S65//2MTR/SupLocal; OPRD2: S65//2MTR/Tap Chan; OPRD3: NULL
S65 | 保安SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S65_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S65//3MTR/SupLocal; OPRD2: S65//3MTR/Tap Chan; OPRD3: NULL
S65 | 保安SS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/S65_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S65//4MTR/SupLocal; OPRD2: S65//4MTR/Tap Chan; OPRD3: NULL
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/CM_B/I_R; OPRD3: S65/11/CM_B/I_S; OPRD4: S65/11/CM_B/I_T
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM21/I_R; OPRD3: S65/11/KM21/I_S; OPRD4: S65/11/KM21/I_T
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM22/I_R; OPRD3: S65/11/KM22/I_S; OPRD4: S65/11/KM22/I_T
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM23/I_R; OPRD3: S65/11/KM23/I_S; OPRD4: S65/11/KM23/I_T
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM24/I_R; OPRD3: S65/11/KM24/I_S; OPRD4: S65/11/KM24/I_T
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM25/I_R; OPRD3: S65/11/KM25/I_S; OPRD4: S65/11/KM25/I_T
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM26/I_R; OPRD3: S65/11/KM26/I_S; OPRD4: S65/11/KM26/I_T
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM27/I_R; OPRD3: S65/11/KM27/I_S; OPRD4: S65/11/KM27/I_T
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM28/I_R; OPRD3: S65/11/KM28/I_S; OPRD4: S65/11/KM28/I_T
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM29/I_R; OPRD3: S65/11/KM29/I_S; OPRD4: S65/11/KM29/I_T
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM30/I_R; OPRD3: S65/11/KM30/I_S; OPRD4: S65/11/KM30/I_T
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM31/I_R; OPRD3: S65/11/KM31/I_S; OPRD4: S65/11/KM31/I_T
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM32/I_R; OPRD3: S65/11/KM32/I_S; OPRD4: S65/11/KM32/I_T
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM33/I_R; OPRD3: S65/11/KM33/I_S; OPRD4: S65/11/KM33/I_T
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM34/I_R; OPRD3: S65/11/KM34/I_S; OPRD4: S65/11/KM34/I_T
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/11/KM35/I_R; OPRD3: S65/11/KM35/I_S; OPRD4: S65/11/KM35/I_T
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/22/KM51/I_R; OPRD3: S65/22/KM51/I_S; OPRD4: S65/22/KM51/I_T
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/22/KM52/I_R; OPRD3: S65/22/KM52/I_S; OPRD4: S65/22/KM52/I_T
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/22/KM53/I_R; OPRD3: S65/22/KM53/I_S; OPRD4: S65/22/KM53/I_T
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/22/KM54/I_R; OPRD3: S65/22/KM54/I_S; OPRD4: S65/22/KM54/I_T
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S65/22/KM55/I_R; OPRD3: S65/22/KM55/I_S; OPRD4: S65/22/KM55/I_T
S65 | 保安SS | 11 | 11kV | CM_B | 奇美實業B廠 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/CM_B/kVA; OPRD2: S65/11/CM_B/KVAR
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM21/kVA; OPRD2: S65/11/KM21/KVAR
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM22/kVA; OPRD2: S65/11/KM22/KVAR
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM23/kVA; OPRD2: S65/11/KM23/KVAR
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM24/kVA; OPRD2: S65/11/KM24/KVAR
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM25/kVA; OPRD2: S65/11/KM25/KVAR
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM26/kVA; OPRD2: S65/11/KM26/KVAR
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM27/kVA; OPRD2: S65/11/KM27/KVAR
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM28/kVA; OPRD2: S65/11/KM28/KVAR
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM29/kVA; OPRD2: S65/11/KM29/KVAR
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM30/kVA; OPRD2: S65/11/KM30/KVAR
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM31/kVA; OPRD2: S65/11/KM31/KVAR
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM32/kVA; OPRD2: S65/11/KM32/KVAR
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM33/kVA; OPRD2: S65/11/KM33/KVAR
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM34/kVA; OPRD2: S65/11/KM34/KVAR
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/11/KM35/kVA; OPRD2: S65/11/KM35/KVAR
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/22/KM51/kVA; OPRD2: S65/22/KM51/KVAR
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/22/KM52/kVA; OPRD2: S65/22/KM52/KVAR
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/22/KM53/kVA; OPRD2: S65/22/KM53/KVAR
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/22/KM54/kVA; OPRD2: S65/22/KM54/KVAR
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S65/22/KM55/kVA; OPRD2: S65/22/KM55/KVAR
S65 | 保安SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S65_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_4 | OPRD1: S65/11/M1/MW; OPRD2: S65/11/M2A/MW; OPRD3: S65/11/M3/MW; OPRD4: S65/22/M4/MW
S65 | 保安SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S65_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_4 | OPRD1: S65/11/M1/MVAR; OPRD2: S65/11/M2A/MVAR; OPRD3: S65/11/M3/MVAR; OPRD4: S65/22/M4/MVAR
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S65_D1 | [12 empty] | 保安SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S65/11/210/CB; OPRD2: 6.9; OPRD3: 0
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S65_D1 | [12 empty] | 保安SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S65/11/220/CB; OPRD2: 6.9; OPRD3: 0
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S65_D1 | [12 empty] | 保安SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S65/11/230/CB; OPRD2: 6.9; OPRD3: 0
S65 | 保安SS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S65_D1 | [15 empty] | SC_CAL_11 |  | sc_mvar | OPRD1: S65/11/240/CB; OPRD2: 6.9; OPRD3: 0
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S65_A1 | [12 empty] | 保安SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S65/69/810/CB; OPRD2: 69; OPRD3: 0
S65 | 保安SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S65_D1 | [12 empty] | 保安SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_16 |  | com_alarm_32 | S65//1MTR/TRA | S65//1MTR/96B2 | S65//1MTR/96D | S65//1MTR/96PA | S65//1MTR/63Q | S65//1MTR/96B1 | S65//1MTR/87A | S65//1MTR/51ZA | S65//2MTR/96PA | S65//2MTR/96D | S65//2MTR/63Q | S65//2MTR/96B1 | S65//2MTR/96B2 | S65//2MTR/51ZA | S65//2MTR/TRA | S65//2MTR/87A | S65//3MTR/51ZA | S65//3MTR/96B2 | S65//3MTR/96D | S65//3MTR/63Q | S65//3MTR/96B1 | S65//3MTR/TRA | S65//3MTR/96PA | S65//3MTR/87A | S65//4MTR/96B1 | S65//4MTR/63Q | S65//4MTR/96B2 | S65//4MTR/96D | S65//4MTR/87A | S65//4MTR/51ZA | S65//4MTR/96PA | S65//4MTR/TRA
S65 | 保安SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S65_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: S65//1MTR/TRF; OPRD2: S65//2MTR/TRF; OPRD3: S65//3MTR/TRF; OPRD4: S65//4MTR/TRF
S65 | 保安SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/RTU/RTU_R_L
S65 | 保安SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/StaDev/PSF
S65 | 保安SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/StaDev/DCE
S65 | 保安SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S65_D1 | [17 empty] | lamp2CC | OPRD1: S65/69/ComPoint/CBA
S65 | 保安SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S65_D1 | [17 empty] | lamp2CC | OPRD1: S65/69/ComPoint/CBF
S65 | 保安SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S65_D1 | [17 empty] | lamp2CC | OPRD1: S65/69/ComPoint/ABS_89A
S65 | 保安SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/StaDev/DCA
S65 | 保安SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/StaDev/Fire
S65 | 保安SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S65_A1 | [17 empty] | lamp2CC | OPRD1: S65/0/StaDev/PMA
S65 | 保安SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S65_D1 | [17 empty] | lamp2CC | OPRD1: S65/69/ComPoint/CFA
S65 | 保安SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S65_D1 | [17 empty] | lamp2CC | OPRD1: S65/69/ComPoint/IRFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S65 | 保安SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 保安SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S65/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | I | [25 empty] | ADCS_S | [8 empty] | 保安SS.610_AMP | 備用線 AMP | LINE69 | S65/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C06R0500 | 450.000000 | 450.000000 | 500.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 保安SS.620_AMP | 台南保安線 AMP | LINE69 | S65/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | I | [25 empty] | ADCS_S | [8 empty] | 保安SS.640_AMP | 保安大湖線 AMP | LINE69 | [5 empty] | 5 | CalcAIPoint | [21 empty] | C06R0500 | 450.000000 | 450.000000 | 500.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | I | [25 empty] | ADCS_S | [8 empty] | 保安SS.660_AMP | 歸仁保安線 AMP | LINE69 | S65/69/660/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C10R0800 | 650.000000 | 720.000000 | 800.000000 | 1000.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S65 | 保安SS | 0 |  |  |  |  | 二行線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.二行線KVA | 11KV二行線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 二行線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.二行線KW | 11KV二行線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 三甲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.三甲線KVA | 11KV三甲線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 三甲線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.三甲線KW | 11KV三甲線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 上崙線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.上崙線KVA | 11KV上崙線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 上崙線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.上崙線KW | 11KV上崙線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 中生線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.中生線KVA | 11KV中生線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 中生線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.中生線KW | 11KV中生線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 中洲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.中洲線KVA | 11KV中洲線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 中洲線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.中洲線KW | 11KV中洲線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 仁七線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.仁七線KVA | 11KV仁七線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 仁七線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.仁七線KW | 11KV仁七線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 仁工線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.仁工線KVA | 11KV仁工線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 仁工線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.仁工線KW | 11KV仁工線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 安廟線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.安廟線KVA | 11KV安廟線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 安廟線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.安廟線KW | 11KV安廟線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保甲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保甲線KVA | 11KV保甲線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保甲線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保甲線KW | 11KV保甲線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保安線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保安線KVA | 11KV保安線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保安線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保安線KW | 11KV保安線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 新崙線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.新崙線KVA | 11KV新崙線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 新崙線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.新崙線KW | 11KV新崙線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 豐和線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.豐和線KVA | 11KV豐和線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 豐和線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.豐和線KW | 11KV豐和線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 藥專線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.藥專線KVA | 11KV藥專線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 藥專線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.藥專線KW | 11KV藥專線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S65//1MTR/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_PF | #1MTR 功率因素 | DTR | S65//1MTR/PF |  | RPDC_PF_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S65//2MTR/MVA |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_PF | #2MTR 功率因素 | DTR | S65//2MTR/PF |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S65//3MTR/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_PF | #3MTR 功率因素 | DTR | S65//3MTR/PF |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | S65//4MTR/MVA |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_PF | #4MTR 功率因素 | DTR | S65//4MTR/PF |  | RPDC_PF_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S65 | 保安SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S65/11/210/MVAR |  | SC_CAL_11 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S65/11/220/MVAR |  | SC_CAL_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S65/11/230/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 22 | 22kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.240_SC_MVAR | 23KV#4SC MVAR | SC |  |  | SC_CAL_23 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S65/69/810/MVAR |  | SC_CAL_69 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保29線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保29線KVA | 11KV保29線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保29線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保29線KW | 11KV保29線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保34線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保34線KVA | 11KV保34線KVA | FEEDER |  |  | KVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保34線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保34線KW | 11KV保34線KW | FEEDER |  |  | KW_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保51線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保51線KVA | 23KV保51線KVA | FEEDER |  |  | KVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保51線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保51線KW | 23KV保51線KW | FEEDER |  |  | KW_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保52線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保52線KVA | 23KV保52線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保52線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保52線KW | 23KV保52線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保53線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保53線KVA | 23KV保53線KVA | FEEDER |  |  | KVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 保53線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.保53線KW | 23KV保53線KW | FEEDER |  |  | KW_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 備54線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.備54線KVA | 23KV備54線KVA | FEEDER |  |  | KVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 備54線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.備54線KW | 23KV備54線KW | FEEDER |  |  | KW_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 備55線KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.備55線KVA | 23KV備55線KVA | FEEDER |  |  | KVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | 備55線KW | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.備55線KW | 23KV備55線KW | FEEDER |  |  | KW_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  | CM | CM |  | B廠KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠KVA | 11KVCM_B廠KVA | FEEDER |  |  | KVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 0 |  |  |  |  | CM新田KVA | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田KVA | 23KVCM新田KVA | FEEDER |  |  | KVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 69 | 69kV | 610_CB | 備用線(610_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.610_CB_4 | 610(備用線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 62 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 620_CB | 台南保安線(620_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.620_CB_4 | 620(台南保安線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 63 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 660_CB | 歸仁保安線(660_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.660_CB_4 | 660(歸仁保安線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 64 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 65 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_S | [8 empty] | 保安SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 66 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_S | [8 empty] | 保安SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 67 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_S | [8 empty] | 保安SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 68 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_S | [8 empty] | 保安SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 69 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 保安SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S65/0/CalcPoint/SUBA |  | STATION_FAULT_16 |  |  | 70 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 71 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_4 |  |  | 72 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610_AMP | 備用線 | [27 empty] | ADCS_S | [8 empty] | 保安SS.610_AMP_A | 備用線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 73 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 69 | 69kV | 610_AMP | 備用線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.610_AMP_4 | 備用線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 69 | 69kV | 620_AMP | 台南保安線 | [27 empty] | ADCS_S | [8 empty] | 保安SS.620_AMP_A | 台南保安線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 69 | 69kV | 620_AMP | 台南保安線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.620_AMP_4 | 台南保安線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 69 | 69kV | 660_AMP | 歸仁保安線 | [27 empty] | ADCS_S | [8 empty] | 保安SS.660_AMP_A | 歸仁保安線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 69 | 69kV | 660_AMP | 歸仁保安線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.660_AMP_4 | 歸仁保安線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 3MTR_MVA | #3MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_MVA_4 | #3MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 4MTR_MVA | #4MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_MVA_4 | #4MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 保安SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 87 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S65/0/RTU/ADCH1 |  |  |  | CDC | 88 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S65/0/RTU/ADCH2 |  |  |  | CDC | 89 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S65/0/RTU/ADCH3 |  |  |  | CDC | 90 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S65/0/RTU/ADCL1 |  |  |  | CDC | 91 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S65/0/RTU/ADCL2 |  |  |  | CDC | 92 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S65/0/RTU/ADCL3 |  |  |  | CDC | 93 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S65 | 保安SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S65/69/1BUS/V |  |  |  | CDC | 94 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S65 | 保安SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S65/11/1BUS/V_R |  |  |  | CDC | 95 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S65/11/3BUS/V_R |  |  |  | CDC | 96 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.610_MW | 備用線 MW | LINE69 | S65/69/610/MW |  |  |  | CDC | 97 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.610_MVAR | 備用線 MVAR | LINE69 | S65/69/610/MVAR |  |  |  | CDC | 98 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.620_MW | 台南保安線 MW | LINE69 | S65/69/620/MW |  |  |  | CDC | 99 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.620_MVAR | 台南保安線 MVAR | LINE69 | S65/69/620/MVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.640_MW | 保安大湖線 MW | LINE69 |  |  |  |  | CDC | 101 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.640_MVAR | 保安大湖線 MVAR | LINE69 |  |  |  |  | CDC | 102 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.660_MW | 歸仁保安線 MW | LINE69 | S65/69/660/MW |  |  |  | CDC | 103 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 保安SS.660_MVAR | 歸仁保安線 MVAR | LINE69 | S65/69/660/MVAR |  |  |  | CDC | 104 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S65 | 保安SS | 11 | 11kV | 二行線 | 二行線 |  | 二行線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.二行線KVAR | 11KV二行線 KVAR | FEEDER | S65/11/KM24/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 二行線 | 二行線 |  | 二行線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.二行線A1 | 11KV二行線 R相AMP | FEEDER | S65/11/KM24/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 二行線 | 二行線 |  | 二行線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.二行線A2 | 11KV二行線 S相AMP | FEEDER | S65/11/KM24/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 二行線 | 二行線 |  | 二行線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.二行線A3 | 11KV二行線 T相AMP | FEEDER | S65/11/KM24/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 二行線 | 二行線 |  | 二行線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.二行線A0 | 11KV二行線 N相AMP | FEEDER | S65/11/KM24/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 三甲線 | 三甲線 |  | 三甲線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.三甲線KVAR | 11KV三甲線 KVAR | FEEDER | S65/11/KM21/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 三甲線 | 三甲線 |  | 三甲線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.三甲線A1 | 11KV三甲線 R相AMP | FEEDER | S65/11/KM21/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 三甲線 | 三甲線 |  | 三甲線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.三甲線A2 | 11KV三甲線 S相AMP | FEEDER | S65/11/KM21/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 三甲線 | 三甲線 |  | 三甲線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.三甲線A3 | 11KV三甲線 T相AMP | FEEDER | S65/11/KM21/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 三甲線 | 三甲線 |  | 三甲線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.三甲線A0 | 11KV三甲線 N相AMP | FEEDER | S65/11/KM21/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 上崙線 | 上崙線 |  | 上崙線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.上崙線KVAR | 11KV上崙線 KVAR | FEEDER | S65/11/KM27/KVAR |  |  |  | CDC | 115 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 上崙線 | 上崙線 |  | 上崙線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.上崙線A1 | 11KV上崙線 R相AMP | FEEDER | S65/11/KM27/I_R |  |  |  | CDC | 116 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 上崙線 | 上崙線 |  | 上崙線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.上崙線A2 | 11KV上崙線 S相AMP | FEEDER | S65/11/KM27/I_S |  |  |  | CDC | 117 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 上崙線 | 上崙線 |  | 上崙線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.上崙線A3 | 11KV上崙線 T相AMP | FEEDER | S65/11/KM27/I_T |  |  |  | CDC | 118 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 上崙線 | 上崙線 |  | 上崙線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.上崙線A0 | 11KV上崙線 N相AMP | FEEDER | S65/11/KM27/I_N |  |  |  | CDC | 119 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中生線 | 中生線 |  | 中生線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中生線KVAR | 11KV中生線 KVAR | FEEDER | S65/11/KM32/KVAR |  |  |  | CDC | 120 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中生線 | 中生線 |  | 中生線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中生線A1 | 11KV中生線 R相AMP | FEEDER | S65/11/KM32/I_R |  |  |  | CDC | 121 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中生線 | 中生線 |  | 中生線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中生線A2 | 11KV中生線 S相AMP | FEEDER | S65/11/KM32/I_S |  |  |  | CDC | 122 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中生線 | 中生線 |  | 中生線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中生線A3 | 11KV中生線 T相AMP | FEEDER | S65/11/KM32/I_T |  |  |  | CDC | 123 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中生線 | 中生線 |  | 中生線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中生線A0 | 11KV中生線 N相AMP | FEEDER | S65/11/KM32/I_N |  |  |  | CDC | 124 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中洲線KVAR | 11KV中洲線 KVAR | FEEDER | S65/11/KM35/KVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中洲線A1 | 11KV中洲線 R相AMP | FEEDER | S65/11/KM35/I_R |  |  |  | CDC | 126 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中洲線A2 | 11KV中洲線 S相AMP | FEEDER | S65/11/KM35/I_S |  |  |  | CDC | 127 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中洲線A3 | 11KV中洲線 T相AMP | FEEDER | S65/11/KM35/I_T |  |  |  | CDC | 128 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 中洲線 | 中洲線 |  | 中洲線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.中洲線A0 | 11KV中洲線 N相AMP | FEEDER | S65/11/KM35/I_N |  |  |  | CDC | 129 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁七線 | 仁七線 |  | 仁七線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁七線KVAR | 11KV仁七線 KVAR | FEEDER | S65/11/KM30/KVAR |  |  |  | CDC | 130 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁七線 | 仁七線 |  | 仁七線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁七線A1 | 11KV仁七線 R相AMP | FEEDER | S65/11/KM30/I_R |  |  |  | CDC | 131 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁七線 | 仁七線 |  | 仁七線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁七線A2 | 11KV仁七線 S相AMP | FEEDER | S65/11/KM30/I_S |  |  |  | CDC | 132 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁七線 | 仁七線 |  | 仁七線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁七線A3 | 11KV仁七線 T相AMP | FEEDER | S65/11/KM30/I_T |  |  |  | CDC | 133 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁七線 | 仁七線 |  | 仁七線A0 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁七線A0 | 11KV仁七線 N相AMP | FEEDER | S65/11/KM30/I_N |  |  |  | CDC | 134 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁工線 | 仁工線 |  | 仁工線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁工線KVAR | 11KV仁工線 KVAR | FEEDER | S65/11/KM22/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁工線 | 仁工線 |  | 仁工線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁工線A1 | 11KV仁工線 R相AMP | FEEDER | S65/11/KM22/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁工線 | 仁工線 |  | 仁工線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁工線A2 | 11KV仁工線 S相AMP | FEEDER | S65/11/KM22/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁工線 | 仁工線 |  | 仁工線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁工線A3 | 11KV仁工線 T相AMP | FEEDER | S65/11/KM22/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 仁工線 | 仁工線 |  | 仁工線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.仁工線A0 | 11KV仁工線 N相AMP | FEEDER | S65/11/KM22/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 安廟線 | 安廟線 |  | 安廟線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.安廟線KVAR | 11KV安廟線 KVAR | FEEDER | S65/11/KM26/KVAR |  |  |  | CDC | 140 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 安廟線 | 安廟線 |  | 安廟線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.安廟線A1 | 11KV安廟線 R相AMP | FEEDER | S65/11/KM26/I_R |  |  |  | CDC | 141 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 安廟線 | 安廟線 |  | 安廟線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.安廟線A2 | 11KV安廟線 S相AMP | FEEDER | S65/11/KM26/I_S |  |  |  | CDC | 142 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 安廟線 | 安廟線 |  | 安廟線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.安廟線A3 | 11KV安廟線 T相AMP | FEEDER | S65/11/KM26/I_T |  |  |  | CDC | 143 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 安廟線 | 安廟線 |  | 安廟線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.安廟線A0 | 11KV安廟線 N相AMP | FEEDER | S65/11/KM26/I_N |  |  |  | CDC | 144 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保甲線 | 保甲線 |  | 保甲線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保甲線KVAR | 11KV保甲線 KVAR | FEEDER | S65/11/KM31/KVAR |  |  |  | CDC | 145 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保甲線 | 保甲線 |  | 保甲線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保甲線A1 | 11KV保甲線 R相AMP | FEEDER | S65/11/KM31/I_R |  |  |  | CDC | 146 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保甲線 | 保甲線 |  | 保甲線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保甲線A2 | 11KV保甲線 S相AMP | FEEDER | S65/11/KM31/I_S |  |  |  | CDC | 147 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保甲線 | 保甲線 |  | 保甲線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保甲線A3 | 11KV保甲線 T相AMP | FEEDER | S65/11/KM31/I_T |  |  |  | CDC | 148 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保甲線 | 保甲線 |  | 保甲線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保甲線A0 | 11KV保甲線 N相AMP | FEEDER | S65/11/KM31/I_N |  |  |  | CDC | 149 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保安線 | 保安線 |  | 保安線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保安線KVAR | 11KV保安線 KVAR | FEEDER | S65/11/KM23/KVAR |  |  |  | CDC | 150 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保安線 | 保安線 |  | 保安線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保安線A1 | 11KV保安線 R相AMP | FEEDER | S65/11/KM23/I_R |  |  |  | CDC | 151 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保安線 | 保安線 |  | 保安線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保安線A2 | 11KV保安線 S相AMP | FEEDER | S65/11/KM23/I_S |  |  |  | CDC | 152 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保安線 | 保安線 |  | 保安線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保安線A3 | 11KV保安線 T相AMP | FEEDER | S65/11/KM23/I_T |  |  |  | CDC | 153 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保安線 | 保安線 |  | 保安線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保安線A0 | 11KV保安線 N相AMP | FEEDER | S65/11/KM23/I_N |  |  |  | CDC | 154 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 新崙線 | 新崙線 |  | 新崙線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.新崙線KVAR | 11KV新崙線 KVAR | FEEDER | S65/11/KM33/KVAR |  |  |  | CDC | 155 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 新崙線 | 新崙線 |  | 新崙線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.新崙線A1 | 11KV新崙線 R相AMP | FEEDER | S65/11/KM33/I_R |  |  |  | CDC | 156 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 新崙線 | 新崙線 |  | 新崙線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.新崙線A2 | 11KV新崙線 S相AMP | FEEDER | S65/11/KM33/I_S |  |  |  | CDC | 157 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 新崙線 | 新崙線 |  | 新崙線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.新崙線A3 | 11KV新崙線 T相AMP | FEEDER | S65/11/KM33/I_T |  |  |  | CDC | 158 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 新崙線 | 新崙線 |  | 新崙線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.新崙線A0 | 11KV新崙線 N相AMP | FEEDER | S65/11/KM33/I_N |  |  |  | CDC | 159 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 豐和線 | 豐和線 |  | 豐和線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.豐和線KVAR | 11KV豐和線 KVAR | FEEDER | S65/11/KM25/KVAR |  |  |  | CDC | 160 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 豐和線 | 豐和線 |  | 豐和線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.豐和線A1 | 11KV豐和線 R相AMP | FEEDER | S65/11/KM25/I_R |  |  |  | CDC | 161 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 豐和線 | 豐和線 |  | 豐和線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.豐和線A2 | 11KV豐和線 S相AMP | FEEDER | S65/11/KM25/I_S |  |  |  | CDC | 162 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 豐和線 | 豐和線 |  | 豐和線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.豐和線A3 | 11KV豐和線 T相AMP | FEEDER | S65/11/KM25/I_T |  |  |  | CDC | 163 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 豐和線 | 豐和線 |  | 豐和線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.豐和線A0 | 11KV豐和線 N相AMP | FEEDER | S65/11/KM25/I_N |  |  |  | CDC | 164 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 藥專線 | 藥專線 |  | 藥專線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.藥專線KVAR | 11KV藥專線 KVAR | FEEDER | S65/11/KM28/KVAR |  |  |  | CDC | 165 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 藥專線 | 藥專線 |  | 藥專線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.藥專線A1 | 11KV藥專線 R相AMP | FEEDER | S65/11/KM28/I_R |  |  |  | CDC | 166 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 藥專線 | 藥專線 |  | 藥專線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.藥專線A2 | 11KV藥專線 S相AMP | FEEDER | S65/11/KM28/I_S |  |  |  | CDC | 167 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 藥專線 | 藥專線 |  | 藥專線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.藥專線A3 | 11KV藥專線 T相AMP | FEEDER | S65/11/KM28/I_T |  |  |  | CDC | 168 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 藥專線 | 藥專線 |  | 藥專線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.藥專線A0 | 11KV藥專線 N相AMP | FEEDER | S65/11/KM28/I_N |  |  |  | CDC | 169 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S65/11/TIE1/I_R |  |  |  | CDC | 170 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S65/11/TIE1/I_S |  |  |  | CDC | 171 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S65/11/TIE1/I_T |  |  |  | CDC | 172 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S65/11/TIE2/I_R |  |  |  | CDC | 173 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S65/11/TIE2/I_S |  |  |  | CDC | 174 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S65/11/TIE2/I_T |  |  |  | CDC | 175 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE | S65/11/TIE3/I_R |  |  |  | CDC | 176 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE | S65/11/TIE3/I_S |  |  |  | CDC | 177 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE | S65/11/TIE3/I_T |  |  |  | CDC | 178 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_MW | #1MTR二次側 MW | DTR | S65/11/M1/MW |  |  |  | CDC | 179 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S65/11/M1/MVAR |  |  |  | CDC | 180 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S65/11/M1/I_R |  |  |  | CDC | 181 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S65/11/M1/I_S |  |  |  | CDC | 182 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S65/11/M1/I_T |  |  |  | CDC | 183 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_OIL | #1MTR 油溫 | DTR | S65//1MTR/OilTemp |  |  |  | CDC | 184 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_COIL | #1MTR 線溫 | DTR | S65//1MTR/CoilTemp |  |  |  | CDC | 185 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-27 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S65//1MTR/TapPosMv |  |  |  | CDC | 186 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_MW | #2MTR二次側 MW | DTR | S65/11/M2A/MW |  |  |  | CDC | 187 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S65/11/M2A/MVAR |  |  |  | CDC | 188 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S65/11/M2A/I_R |  |  |  | CDC | 189 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S65/11/M2A/I_S |  |  |  | CDC | 190 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S65/11/M2A/I_T |  |  |  | CDC | 191 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_OIL | #2MTR 油溫 | DTR | S65//2MTR/OilTemp |  |  |  | CDC | 192 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_COIL | #2MTR 線溫 | DTR | S65//2MTR/CoilTemp |  |  |  | CDC | 193 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-3A |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S65//2MTR/TapPosMv |  |  |  | CDC | 194 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_MW | #3MTR二次側 MW | DTR | S65/11/M3/MW |  |  |  | CDC | 195 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S65/11/M3/MVAR |  |  |  | CDC | 196 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S65/11/M3/I_R |  |  |  | CDC | 197 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S65/11/M3/I_S |  |  |  | CDC | 198 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S65/11/M3/I_T |  |  |  | CDC | 199 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_OIL | #3MTR 油溫 | DTR | S65//3MTR/OilTemp |  |  |  | CDC | 200 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_COIL | #3MTR 線溫 | DTR | S65//3MTR/CoilTemp |  |  |  | CDC | 201 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-4D |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S65//3MTR/TapPosMv |  |  |  | CDC | 202 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 2-8D | [5 empty] | MW_-39.6_39.6(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_MW | #4MTR二次側 MW | DTR | S65/22/M4/MW |  |  |  | CDC | 203 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.079200 | 0.010000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 2-8E | [5 empty] | MVAR_-39.6_39.6(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR | S65/22/M4/MVAR |  |  |  | CDC | 204 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.079200 | 0.010000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-1100_1100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR | S65/22/M4/I_R |  |  |  | CDC | 205 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-1100_1100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR | S65/22/M4/I_S |  |  |  | CDC | 206 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 4MTR | #4MTR二次側 |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-1100_1100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR | S65/22/M4/I_T |  |  |  | CDC | 207 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 2-8B | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_OIL | #4MTR 油溫 | DTR | S65//4MTR/OilTemp |  |  |  | CDC | 208 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 2-8A | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_COIL | #4MTR 線溫 | DTR | S65//4MTR/CoilTemp |  |  |  | CDC | 209 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 2-8C |  | 1-5F |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 保安SS.#4MTR_TAP | #4MTR OLTC TAP | DTR | S65//4MTR/TapPosMv |  |  |  | CDC | 210 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S65 | 保安SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.直流電源電壓 | 直流電源電壓 | OTHER | S65/0/StaDev/DCV |  |  |  | CDC | 211 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保29線 | 保29線 |  | 保29線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保29線KVAR | 11KV保29線 KVAR | FEEDER | S65/11/KM29/KVAR |  |  |  | CDC | 212 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保29線 | 保29線 |  | 保29線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保29線A1 | 11KV保29線 R相AMP | FEEDER | S65/11/KM29/I_R |  |  |  | CDC | 213 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保29線 | 保29線 |  | 保29線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保29線A2 | 11KV保29線 S相AMP | FEEDER | S65/11/KM29/I_S |  |  |  | CDC | 214 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保29線 | 保29線 |  | 保29線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保29線A3 | 11KV保29線 T相AMP | FEEDER | S65/11/KM29/I_T |  |  |  | CDC | 215 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保29線 | 保29線 |  | 保29線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保29線A0 | 11KV保29線 N相AMP | FEEDER | S65/11/KM29/I_N |  |  |  | CDC | 216 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保34線 | 保34線 |  | 保34線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保34線KVAR | 11KV保34線 KVAR | FEEDER | S65/11/KM34/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保34線 | 保34線 |  | 保34線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保34線A1 | 11KV保34線 R相AMP | FEEDER | S65/11/KM34/I_R |  |  |  | CDC | 218 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保34線 | 保34線 |  | 保34線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保34線A2 | 11KV保34線 S相AMP | FEEDER | S65/11/KM34/I_S |  |  |  | CDC | 219 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保34線 | 保34線 |  | 保34線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保34線A3 | 11KV保34線 T相AMP | FEEDER | S65/11/KM34/I_T |  |  |  | CDC | 220 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 保34線 | 保34線 |  | 保34線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保34線A0 | 11KV保34線 N相AMP | FEEDER | S65/11/KM34/I_N |  |  |  | CDC | 221 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | S65/11/2ABUS/V_R |  |  |  | CDC | 222 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-91 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | S65/11/2BBUS/V_R |  |  |  | CDC | 223 | GENERICAIPoint | SS407_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 22 | 22kV | 4BUS | #4BUS |  | V | [17 empty] | 2-89 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | S65/22/4BUS/V_R |  |  |  | CDC | 224 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 22 | 22kV | 保51線 | 保51線 |  | 保51線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保51線KVAR | 23KV保51線 KVAR | FEEDER | S65/22/KM51/KVAR |  |  |  | CDC | 225 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保51線 | 保51線 |  | 保51線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保51線A1 | 23KV保51線 R相AMP | FEEDER | S65/22/KM51/I_R |  |  |  | CDC | 226 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保51線 | 保51線 |  | 保51線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保51線A2 | 23KV保51線 S相AMP | FEEDER | S65/22/KM51/I_S |  |  |  | CDC | 227 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保51線 | 保51線 |  | 保51線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保51線A3 | 23KV保51線 T相AMP | FEEDER | S65/22/KM51/I_T |  |  |  | CDC | 228 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保51線 | 保51線 |  | 保51線A0 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保51線A0 | 23KV保51線 N相AMP | FEEDER | S65/22/KM51/I_N |  |  |  | CDC | 229 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保52線 | 保52線 |  | 保52線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保52線KVAR | 23KV保52線 KVAR | FEEDER | S65/22/KM52/KVAR |  |  |  | CDC | 230 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保52線 | 保52線 |  | 保52線A1 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保52線A1 | 23KV保52線 R相AMP | FEEDER | S65/22/KM52/I_R |  |  |  | CDC | 231 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保52線 | 保52線 |  | 保52線A2 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保52線A2 | 23KV保52線 S相AMP | FEEDER | S65/22/KM52/I_S |  |  |  | CDC | 232 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保52線 | 保52線 |  | 保52線A3 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保52線A3 | 23KV保52線 T相AMP | FEEDER | S65/22/KM52/I_T |  |  |  | CDC | 233 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保52線 | 保52線 |  | 保52線A0 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保52線A0 | 23KV保52線 N相AMP | FEEDER | S65/22/KM52/I_N |  |  |  | CDC | 234 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保53線 | 保53線 |  | 保53線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保53線KVAR | 23KV保53線 KVAR | FEEDER | S65/22/KM53/KVAR |  |  |  | CDC | 235 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保53線 | 保53線 |  | 保53線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保53線A1 | 23KV保53線 R相AMP | FEEDER | S65/22/KM53/I_R |  |  |  | CDC | 236 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保53線 | 保53線 |  | 保53線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保53線A2 | 23KV保53線 S相AMP | FEEDER | S65/22/KM53/I_S |  |  |  | CDC | 237 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保53線 | 保53線 |  | 保53線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保53線A3 | 23KV保53線 T相AMP | FEEDER | S65/22/KM53/I_T |  |  |  | CDC | 238 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 保53線 | 保53線 |  | 保53線A0 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.保53線A0 | 23KV保53線 N相AMP | FEEDER | S65/22/KM53/I_N |  |  |  | CDC | 239 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備54線 | 備54線 |  | 備54線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備54線KVAR | 23KV備54線 KVAR | FEEDER | S65/22/KM54/KVAR |  |  |  | CDC | 240 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備54線 | 備54線 |  | 備54線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備54線A1 | 23KV備54線 R相AMP | FEEDER | S65/22/KM54/I_R |  |  |  | CDC | 241 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備54線 | 備54線 |  | 備54線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備54線A2 | 23KV備54線 S相AMP | FEEDER | S65/22/KM54/I_S |  |  |  | CDC | 242 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備54線 | 備54線 |  | 備54線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備54線A3 | 23KV備54線 T相AMP | FEEDER | S65/22/KM54/I_T |  |  |  | CDC | 243 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備54線 | 備54線 |  | 備54線A0 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備54線A0 | 23KV備54線 N相AMP | FEEDER | S65/22/KM54/I_N |  |  |  | CDC | 244 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備55線 | 備55線 |  | 備55線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備55線KVAR | 23KV備55線 KVAR | FEEDER | S65/22/KM55/KVAR |  |  |  | CDC | 245 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備55線 | 備55線 |  | 備55線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備55線A1 | 23KV備55線 R相AMP | FEEDER | S65/22/KM55/I_R |  |  |  | CDC | 246 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備55線 | 備55線 |  | 備55線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備55線A2 | 23KV備55線 S相AMP | FEEDER | S65/22/KM55/I_S |  |  |  | CDC | 247 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備55線 | 備55線 |  | 備55線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備55線A3 | 23KV備55線 T相AMP | FEEDER | S65/22/KM55/I_T |  |  |  | CDC | 248 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | 備55線 | 備55線 |  | 備55線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.備55線A0 | 23KV備55線 N相AMP | FEEDER | S65/22/KM55/I_N |  |  |  | CDC | 249 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 0 |  | 11S12ABUS | 11S1 |  | V | [17 empty] | 2-AA | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11S1#2ABUS_KV | 11S1 #2ABUS KV | BUS | S65/11/2ABUS/V_S |  |  |  | CDC | 250 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11S12BBUS | 11S1 |  | V | [17 empty] | 2-AC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11S1#2BBUS_KV | 11S1 #2BBUS KV | BUS | S65/11/2BBUS/V_S |  |  |  | CDC | 251 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11S13BUS | 11S1 |  | V | [17 empty] | 2-AE | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | S65/11/3BUS/V_S |  |  |  | CDC | 252 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11T12ABUS | 11T1 |  | V | [17 empty] | 2-AB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11T1#2ABUS_KV | 11T1 #2ABUS KV | BUS | S65/11/2ABUS/V_T |  |  |  | CDC | 253 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11T12BBUS | 11T1 |  | V | [17 empty] | 2-AD | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11T1#2BBUS_KV | 11T1 #2BBUS KV | BUS | S65/11/2BBUS/V_T |  |  |  | CDC | 254 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11T13BUS | 11T1 |  | V | [17 empty] | 2-AF | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | S65/11/3BUS/V_T |  |  |  | CDC | 255 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11S11BUS | 11S1 |  | V | [17 empty] | 2-A8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | S65/11/1BUS/V_S |  |  |  | CDC | 256 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 11T11BUS | 11T1 |  | V | [17 empty] | 2-A9 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | S65/11/1BUS/V_T |  |  |  | CDC | 257 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 23S14BUS | 23S1 |  | V | [17 empty] | 2-B0 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.23S1#4BUS_KV | 23S1 #4BUS KV | BUS | S65/22/4BUS/V_S |  |  |  | CDC | 258 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 0 |  | 23T14BUS | 23T1 |  | V | [17 empty] | 2-B1 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.23T1#4BUS_KV | 23T1 #4BUS KV | BUS | S65/22/4BUS/V_T |  |  |  | CDC | 259 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 0 |  | 1CR16BUS | 1CR1 |  | V | [17 empty] | 2-D7 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.1CR1#6BUS_KV | 1CR1 #6BUS KV | BUS | S65/11/6BUS/V_R |  |  |  | CDC | 260 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 1CS16BUS | 1CS1 |  | V | [17 empty] | 2-D8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.1CS1#6BUS_KV | 1CS1 #6BUS KV | BUS | S65/11/6BUS/V_S |  |  |  | CDC | 261 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 1CT16BUS | 1CT1 |  | V | [17 empty] | 2-D9 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.1CT1#6BUS_KV | 1CT1 #6BUS KV | BUS | S65/11/6BUS/V_T |  |  |  | CDC | 262 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S65 | 保安SS | 0 |  | 2CR15BUS | 2CR1 |  | V | [17 empty] | 2-B5 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.2CR1#5BUS_KV | 2CR1 #5BUS KV | BUS | S65/11/5BUS/V_R |  |  |  | CDC | 263 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 0 |  | 2CS15BUS | 2CS1 |  | V | [17 empty] | 2-B6 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.2CS1#5BUS_KV | 2CS1 #5BUS KV | BUS | S65/11/5BUS/V_S |  |  |  | CDC | 264 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 0 |  | 2CT15BUS | 2CT1 |  | V | [17 empty] | 2-B7 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.2CT1#5BUS_KV | 2CT1 #5BUS KV | BUS | S65/11/5BUS/V_T |  |  |  | CDC | 265 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
S65 | 保安SS | 11 | 11kV | CM | CM_B廠 |  | B廠KVAR | [17 empty] | 2-DB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM_B廠KVAR | 11KVCM_B廠 KVAR | FEEDER | S65/11/CM_B/KVAR |  |  |  | CDC | 266 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM | CM_B廠 |  | B廠A1 | [17 empty] | 2-D4 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM_B廠A1 | 11KVCM_B廠 R相AMP | FEEDER | S65/11/CM_B/I_R |  |  |  | CDC | 267 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM | CM_B廠 |  | B廠A2 | [17 empty] | 2-D5 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM_B廠A2 | 11KVCM_B廠 S相AMP | FEEDER | S65/11/CM_B/I_S |  |  |  | CDC | 268 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM | CM_B廠 |  | B廠A3 | [17 empty] | 2-D6 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM_B廠A3 | 11KVCM_B廠 T相AMP | FEEDER | S65/11/CM_B/I_T |  |  |  | CDC | 269 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM新田 | CM新田 |  | CM新田KVAR | [17 empty] | 2-B9 | [5 empty] | KVAR_-6000_6000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM新田KVAR | 23KVCM新田 KVAR | FEEDER | S65/22/CM_XT/KVAR |  |  |  | CDC | 270 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM新田 | CM新田 |  | CM新田A1 | [17 empty] | 2-B2 | [5 empty] | A_-100_100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM新田A1 | 23KVCM新田 R相AMP | FEEDER | S65/22/CM_XT/I_R |  |  |  | CDC | 271 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM新田 | CM新田 |  | CM新田A2 | [17 empty] | 2-B3 | [5 empty] | A_-100_100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM新田A2 | 23KVCM新田 S相AMP | FEEDER | S65/22/CM_XT/I_S |  |  |  | CDC | 272 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM新田 | CM新田 |  | CM新田A3 | [17 empty] | 2-B4 | [5 empty] | A_-100_100(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM新田A3 | 23KVCM新田 T相AMP | FEEDER | S65/22/CM_XT/I_T |  |  |  | CDC | 273 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S65 | 保安SS | 22 | 22kV | CM新田 | CM新田 |  | KW | [17 empty] | 2-B8 | [5 empty] | KW_-6000_6000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM新田_KW | 23KVCM新田 KW | OTHER | S65/22/CM_XT/KW |  |  |  | CDC | 274 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 11 | 11kV | CM_B廠 | CM_B廠 |  | KW | [17 empty] | 2-DA | [5 empty] | KW_-9000_9000(-2000_2000) |  | DDCS4_2 | [8 empty] | 保安SS.CM_B廠_KW | 11KVCM_B廠 KW | OTHER | S65/11/CM_B/KW |  |  |  | CDC | 275 | GENERICAIPoint | SS407_L2 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_S | [8 empty] | 保安SS.610_PHA | 備用線(610) 相間RY | LINE69 | S65/69/610/PHA |  |  |  | CDC | 276 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_S | [8 empty] | 保安SS.610_GDA | 備用線(610) 接地RY | LINE69 | S65/69/610/GDA |  |  |  | CDC | 277 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 85A | [17 empty] | 1-08-01 | [7 empty] | 69KV_S | [8 empty] | 保安SS.610_85A | 備用線(610) 85RY | LINE69 | S65/69/610/85A |  |  |  | CDC | 278 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 74A | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 保安SS.610_74A | 備用線(610) 74RY | LINE69 | S65/69/610/74A |  |  |  | CDC | 279 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | 85UL | [17 empty] | 1-32-00 |  | 1-06 | [5 empty] | ADCS_S | [8 empty] | 保安SS.610_85UL | 備用線(610) 85RY U/L | LINE69 | S65/69/610/85UL |  |  |  | CDC | 280 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_S | [8 empty] | 保安SS.610_CB | 610(備用線) CB | LINE69 | S65/69/610/CB |  |  |  | CDC | 281 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | ABS1 | 611 | [16 empty] | 1-39-10 | 1-39-11 | 1-0B | [5 empty] | ADCS_S | [8 empty] | 保安SS.611_ABS | 611(備用線) ABS | LINE69 | S65/69/610/ABS1 |  |  |  | CDC | 282 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | ABS2 | 612 | [16 empty] | 1-39-12 | 1-39-13 | 1-0C | [5 empty] | ADCS_S | [8 empty] | 保安SS.612_ABS | 612(備用線) ABS | LINE69 | S65/69/610/ABS2 |  |  |  | CDC | 283 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | E2 | 612E | [16 empty] | 1-39-14 | 1-39-15 | 1-0D | [5 empty] | ADCS_S | [8 empty] | 保安SS.612E_ES | 612E(備用線) ES | LINE69 | S65/69/610/ES2 |  |  |  | CDC | 284 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_S | [8 empty] | 保安SS.620_PHA | 台南保安線(620) 相間RY | LINE69 | S65/69/620/PHA |  |  |  | CDC | 285 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_S | [8 empty] | 保安SS.620_GDA | 台南保安線(620) 接地RY | LINE69 | S65/69/620/GDA |  |  |  | CDC | 286 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_S | [8 empty] | 保安SS.620_CB | 620(台南保安線) CB | LINE69 | S65/69/620/CB |  |  |  | CDC | 287 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | ABS1 | 621 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-11 | [5 empty] | ADCS_S | [8 empty] | 保安SS.621_ABS | 621(台南保安線) ABS | LINE69 | S65/69/620/ABS1 |  |  |  | CDC | 288 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | ABS2 | 622 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 保安SS.622_ABS | 622(台南保安線) ABS | LINE69 | S65/69/620/ABS2 |  |  |  | CDC | 289 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | E2 | 622E | [16 empty] | 1-3A-10 | 1-3A-11 | 1-13 | [5 empty] | ADCS_S | [8 empty] | 保安SS.622E_ES | 622E(台南保安線) ES | LINE69 | S65/69/620/ES2 |  |  |  | CDC | 290 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_S | [8 empty] | 保安SS.640_PHA | 保安大湖線(640) 相間RY | LINE69 |  |  |  |  | CDC | 291 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_S | [8 empty] | 保安SS.640_GDA | 保安大湖線(640) 接地RY | LINE69 |  |  |  |  | CDC | 292 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 640 | 保安大湖線(640) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_S | [8 empty] | 保安SS.640_CB | 640(保安大湖線) CB | LINE69 |  |  |  |  | CDC | 293 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_S | [8 empty] | 保安SS.660_PHA | 歸仁保安線(660) 相間RY | LINE69 | S65/69/660/PHA |  |  |  | CDC | 294 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_S | [8 empty] | 保安SS.660_GDA | 歸仁保安線(660) 接地RY | LINE69 | S65/69/660/GDA |  |  |  | CDC | 295 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_S | [8 empty] | 保安SS.660_CB | 660(歸仁保安線) CB | LINE69 | S65/69/660/CB |  |  |  | CDC | 296 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | ABS1 | 661 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-14 | [5 empty] | ADCS_S | [8 empty] | 保安SS.661_ABS | 661(歸仁保安線) ABS | LINE69 | S65/69/660/ABS1 |  |  |  | CDC | 297 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | ABS2 | 662 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 保安SS.662_ABS | 662(歸仁保安線) ABS | LINE69 | S65/69/660/ABS2 |  |  |  | CDC | 298 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | E2 | 662E | [16 empty] | 1-3B-00 | 1-3B-01 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 保安SS.662E_ES | 662E(歸仁保安線) ES | LINE69 | S65/69/660/ES2 |  |  |  | CDC | 299 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_PHA | 11KV三甲線(KM21) 相間RY | FEEDER | S65/11/KM21/PHA |  |  |  | CDC | 300 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_GDA | 11KV三甲線(KM21) 接地RY | FEEDER | S65/11/KM21/GDA |  |  |  | CDC | 301 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-3D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_79UL | 11KV三甲線(KM21) 79RY U/L | FEEDER | S65/11/KM21/79UL |  |  |  | CDC | 302 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM21 | 三甲線(KM21) LCO分流器 |  | ADJ | [17 empty] | 1-37-05 |  | 1-6D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_ADJ | 11KV三甲線(KM21) LCO分流器 U/L | FEEDER | S65/11/KM21/ADJ |  |  |  | CDC | 303 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM21 | KM21(11KV三甲線) |  | CB | [17 empty] | 1-0E-06 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_CB | KM21(11KV三甲線) CB | FEEDER | S65/11/KM21/CB |  |  |  | CDC | 304 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_PHA | 11KV仁工線(KM22) 相間RY | FEEDER | S65/11/KM22/PHA |  |  |  | CDC | 305 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_GDA | 11KV仁工線(KM22) 接地RY | FEEDER | S65/11/KM22/GDA |  |  |  | CDC | 306 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-3E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_79UL | 11KV仁工線(KM22) 79RY U/L | FEEDER | S65/11/KM22/79UL |  |  |  | CDC | 307 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM22 | 仁工線(KM22) LCO分流器 |  | ADJ | [17 empty] | 1-37-06 |  | 1-6E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_ADJ | 11KV仁工線(KM22) LCO分流器 U/L | FEEDER | S65/11/KM22/ADJ |  |  |  | CDC | 308 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM22 | KM22(11KV仁工線) |  | CB | [17 empty] | 1-0E-07 |  | 1-36 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_CB | KM22(11KV仁工線) CB | FEEDER | S65/11/KM22/CB |  |  |  | CDC | 309 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_PHA | 11KV保安線(KM23) 相間RY | FEEDER | S65/11/KM23/PHA |  |  |  | CDC | 310 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_GDA | 11KV保安線(KM23) 接地RY | FEEDER | S65/11/KM23/GDA |  |  |  | CDC | 311 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-3F | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_79UL | 11KV保安線(KM23) 79RY U/L | FEEDER | S65/11/KM23/79UL |  |  |  | CDC | 312 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM23 | 保安線(KM23) LCO分流器 |  | ADJ | [17 empty] | 1-37-07 |  | 1-6F | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_ADJ | 11KV保安線(KM23) LCO分流器 U/L | FEEDER | S65/11/KM23/ADJ |  |  |  | CDC | 313 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM23 | KM23(11KV保安線) |  | CB | [17 empty] | 1-0F-00 |  | 1-37 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_CB | KM23(11KV保安線) CB | FEEDER | S65/11/KM23/CB |  |  |  | CDC | 314 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_PHA | 11KV二行線(KM24) 相間RY | FEEDER | S65/11/KM24/PHA |  |  |  | CDC | 315 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_GDA | 11KV二行線(KM24) 接地RY | FEEDER | S65/11/KM24/GDA |  |  |  | CDC | 316 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_79UL | 11KV二行線(KM24) 79RY U/L | FEEDER | S65/11/KM24/79UL |  |  |  | CDC | 317 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM24 | 二行線(KM24) LCO分流器 |  | ADJ | [17 empty] | 1-37-08 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_ADJ | 11KV二行線(KM24) LCO分流器 U/L | FEEDER | S65/11/KM24/ADJ |  |  |  | CDC | 318 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM24 | KM24(11KV二行線) |  | CB | [17 empty] | 1-0F-01 |  | 1-38 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_CB | KM24(11KV二行線) CB | FEEDER | S65/11/KM24/CB |  |  |  | CDC | 319 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_PHA | 11KV豐和線(KM25) 相間RY | FEEDER | S65/11/KM25/PHA |  |  |  | CDC | 320 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_GDA | 11KV豐和線(KM25) 接地RY | FEEDER | S65/11/KM25/GDA |  |  |  | CDC | 321 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_79UL | 11KV豐和線(KM25) 79RY U/L | FEEDER | S65/11/KM25/79UL |  |  |  | CDC | 322 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM25 | 豐和線(KM25) LCO分流器 |  | ADJ | [17 empty] | 1-37-09 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_ADJ | 11KV豐和線(KM25) LCO分流器 U/L | FEEDER | S65/11/KM25/ADJ |  |  |  | CDC | 323 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM25 | KM25(11KV豐和線) |  | CB | [17 empty] | 1-0F-02 |  | 1-39 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_CB | KM25(11KV豐和線) CB | FEEDER | S65/11/KM25/CB |  |  |  | CDC | 324 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_PHA | 11KV安廟線(KM26) 相間RY | FEEDER | S65/11/KM26/PHA |  |  |  | CDC | 325 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_GDA | 11KV安廟線(KM26) 接地RY | FEEDER | S65/11/KM26/GDA |  |  |  | CDC | 326 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_79UL | 11KV安廟線(KM26) 79RY U/L | FEEDER | S65/11/KM26/79UL |  |  |  | CDC | 327 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM26 | 安廟線(KM26) LCO分流器 |  | ADJ | [17 empty] | 1-37-10 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_ADJ | 11KV安廟線(KM26) LCO分流器 U/L | FEEDER | S65/11/KM26/ADJ |  |  |  | CDC | 328 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM26 | KM26(11KV安廟線) |  | CB | [17 empty] | 1-11-04 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_CB | KM26(11KV安廟線) CB | FEEDER | S65/11/KM26/CB |  |  |  | CDC | 329 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | PHA | [17 empty] | 1-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_PHA | 11KV上崙線(KM27) 相間RY | FEEDER | S65/11/KM27/PHA |  |  |  | CDC | 330 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) |  | GDA | [17 empty] | 1-13-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_GDA | 11KV上崙線(KM27) 接地RY | FEEDER | S65/11/KM27/GDA |  |  |  | CDC | 331 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_79UL | 11KV上崙線(KM27) 79RY U/L | FEEDER | S65/11/KM27/79UL |  |  |  | CDC | 332 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM27 | 上崙線(KM27) LCO分流器 |  | ADJ | [17 empty] | 1-37-11 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_ADJ | 11KV上崙線(KM27) LCO分流器 U/L | FEEDER | S65/11/KM27/ADJ |  |  |  | CDC | 333 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM27 | KM27(11KV上崙線) |  | CB | [17 empty] | 1-11-05 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_CB | KM27(11KV上崙線) CB | FEEDER | S65/11/KM27/CB |  |  |  | CDC | 334 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_PHA | 11KV藥專線(KM28) 相間RY | FEEDER | S65/11/KM28/PHA |  |  |  | CDC | 335 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_GDA | 11KV藥專線(KM28) 接地RY | FEEDER | S65/11/KM28/GDA |  |  |  | CDC | 336 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_79UL | 11KV藥專線(KM28) 79RY U/L | FEEDER | S65/11/KM28/79UL |  |  |  | CDC | 337 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM28 | 藥專線(KM28) LCO分流器 |  | ADJ | [17 empty] | 1-37-12 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_ADJ | 11KV藥專線(KM28) LCO分流器 U/L | FEEDER | S65/11/KM28/ADJ |  |  |  | CDC | 338 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM28 | KM28(11KV藥專線) |  | CB | [17 empty] | 1-11-06 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_CB | KM28(11KV藥專線) CB | FEEDER | S65/11/KM28/CB |  |  |  | CDC | 339 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | PHA | [17 empty] | 1-13-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_PHA | 11KV保29線(KM29) 相間RY | FEEDER | S65/11/KM29/PHA |  |  |  | CDC | 340 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) |  | GDA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_GDA | 11KV保29線(KM29) 接地RY | FEEDER | S65/11/KM29/GDA |  |  |  | CDC | 341 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_79UL | 11KV保29線(KM29) 79RY U/L | FEEDER | S65/11/KM29/79UL |  |  |  | CDC | 342 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM29 | 保29線(KM29) LCO分流器 |  | ADJ | [17 empty] | 1-37-13 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_ADJ | 11KV保29線(KM29) LCO分流器 U/L | FEEDER | S65/11/KM29/ADJ |  |  |  | CDC | 343 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM29 | KM29(11KV保29線) |  | CB | [17 empty] | 1-11-07 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_CB | KM29(11KV保29線) CB | FEEDER | S65/11/KM29/CB |  |  |  | CDC | 344 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | PHA | [17 empty] | 1-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_PHA | 11KV仁七線(KM30) 相間RY | FEEDER | S65/11/KM30/PHA |  |  |  | CDC | 345 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) |  | GDA | [17 empty] | 1-13-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_GDA | 11KV仁七線(KM30) 接地RY | FEEDER | S65/11/KM30/GDA |  |  |  | CDC | 346 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_79UL | 11KV仁七線(KM30) 79RY U/L | FEEDER | S65/11/KM30/79UL |  |  |  | CDC | 347 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM30 | 仁七線(KM30) LCO分流器 |  | ADJ | [17 empty] | 1-37-14 |  | 1-76 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_ADJ | 11KV仁七線(KM30) LCO分流器 U/L | FEEDER | S65/11/KM30/ADJ |  |  |  | CDC | 348 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM30 | KM30(11KV仁七線) |  | CB | [17 empty] | 1-12-00 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_CB | KM30(11KV仁七線) CB | FEEDER | S65/11/KM30/CB |  |  |  | CDC | 349 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_PHA | 11KV保甲線(KM31) 相間RY | FEEDER | S65/11/KM31/PHA |  |  |  | CDC | 350 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_GDA | 11KV保甲線(KM31) 接地RY | FEEDER | S65/11/KM31/GDA |  |  |  | CDC | 351 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_79UL | 11KV保甲線(KM31) 79RY U/L | FEEDER | S65/11/KM31/79UL |  |  |  | CDC | 352 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM31 | 保甲線(KM31) LCO分流器 |  | ADJ | [17 empty] | 1-37-00 |  | 1-68 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_ADJ | 11KV保甲線(KM31) LCO分流器 U/L | FEEDER | S65/11/KM31/ADJ |  |  |  | CDC | 353 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM31 | KM31(11KV保甲線) |  | CB | [17 empty] | 1-0C-00 |  | 1-22 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_CB | KM31(11KV保甲線) CB | FEEDER | S65/11/KM31/CB |  |  |  | CDC | 354 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_PHA | 11KV中生線(KM32) 相間RY | FEEDER | S65/11/KM32/PHA |  |  |  | CDC | 355 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_GDA | 11KV中生線(KM32) 接地RY | FEEDER | S65/11/KM32/GDA |  |  |  | CDC | 356 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-2B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_79UL | 11KV中生線(KM32) 79RY U/L | FEEDER | S65/11/KM32/79UL |  |  |  | CDC | 357 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM32 | 中生線(KM32) LCO分流器 |  | ADJ | [17 empty] | 1-37-01 |  | 1-69 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_ADJ | 11KV中生線(KM32) LCO分流器 U/L | FEEDER | S65/11/KM32/ADJ |  |  |  | CDC | 358 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM32 | KM32(11KV中生線) |  | CB | [17 empty] | 1-0C-01 |  | 1-23 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_CB | KM32(11KV中生線) CB | FEEDER | S65/11/KM32/CB |  |  |  | CDC | 359 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_PHA | 11KV新崙線(KM33) 相間RY | FEEDER | S65/11/KM33/PHA |  |  |  | CDC | 360 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_GDA | 11KV新崙線(KM33) 接地RY | FEEDER | S65/11/KM33/GDA |  |  |  | CDC | 361 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-2C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_79UL | 11KV新崙線(KM33) 79RY U/L | FEEDER | S65/11/KM33/79UL |  |  |  | CDC | 362 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM33 | 新崙線(KM33) LCO分流器 |  | ADJ | [17 empty] | 1-37-02 |  | 1-6A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_ADJ | 11KV新崙線(KM33) LCO分流器 U/L | FEEDER | S65/11/KM33/ADJ |  |  |  | CDC | 363 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM33 | KM33(11KV新崙線) |  | CB | [17 empty] | 1-0C-02 |  | 1-24 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_CB | KM33(11KV新崙線) CB | FEEDER | S65/11/KM33/CB |  |  |  | CDC | 364 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_PHA | 11KV保34線(KM34) 相間RY | FEEDER | S65/11/KM34/PHA |  |  |  | CDC | 365 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_GDA | 11KV保34線(KM34) 接地RY | FEEDER | S65/11/KM34/GDA |  |  |  | CDC | 366 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_79UL | 11KV保34線(KM34) 79RY U/L | FEEDER | S65/11/KM34/79UL |  |  |  | CDC | 367 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM34 | 保34線(KM34) LCO分流器 |  | ADJ | [17 empty] | 1-37-03 |  | 1-6B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_ADJ | 11KV保34線(KM34) LCO分流器 U/L | FEEDER | S65/11/KM34/ADJ |  |  |  | CDC | 368 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM34 | KM34(11KV保34線) |  | CB | [17 empty] | 1-0C-03 |  | 1-25 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_CB | KM34(11KV保34線) CB | FEEDER | S65/11/KM34/CB |  |  |  | CDC | 369 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_PHA | 11KV中洲線(KM35) 相間RY | FEEDER | S65/11/KM35/PHA |  |  |  | CDC | 370 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_GDA | 11KV中洲線(KM35) 接地RY | FEEDER | S65/11/KM35/GDA |  |  |  | CDC | 371 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_79UL | 11KV中洲線(KM35) 79RY U/L | FEEDER | S65/11/KM35/79UL |  |  |  | CDC | 372 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 11 | 11kV | KM35 | 中洲線(KM35) LCO分流器 |  | ADJ | [17 empty] | 1-37-04 |  | 1-6C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_ADJ | 11KV中洲線(KM35) LCO分流器 U/L | FEEDER | S65/11/KM35/ADJ |  |  |  | CDC | 373 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 11 | 11kV | KM35 | KM35(11KV中洲線) |  | CB | [17 empty] | 1-0C-04 |  | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_CB | KM35(11KV中洲線) CB | FEEDER | S65/11/KM35/CB |  |  |  | CDC | 374 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-20 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE1_CB | 11KV TIE1 CB | TIE | S65/11/TIE1/CB |  |  |  | CDC | 375 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE1_51A | 11KV TIE1 51RY | TIE | S65/11/TIE1/51A |  |  |  | CDC | 376 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S65/11/TIE1/51NA |  |  |  | CDC | 377 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE2_CB | 11KV TIE2 CB | TIE | S65/11/TIE2/CB |  |  |  | CDC | 378 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE2_51A | 11KV TIE2 51RY | TIE | S65/11/TIE2/51A |  |  |  | CDC | 379 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S65/11/TIE2/51NA |  |  |  | CDC | 380 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-12-01 |  | 1-46 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE3_CB | 11KV TIE3 CB | TIE | S65/11/TIE3/CB |  |  |  | CDC | 381 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 11 | 11kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-13-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE3_51A | 11KV TIE3 51RY | TIE | S65/11/TIE3/51A |  |  |  | CDC | 382 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-14-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE3_51NA | 11KV TIE3 51N RY | TIE | S65/11/TIE3/51NA |  |  |  | CDC | 383 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-1E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.750_CB | 750(#1MTR) CB | DTR | S65/69/750/CB |  |  |  | CDC | 384 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-1F | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.1M_CB | 1M(#1MTR) CB | DTR | S65/11/M1/CB |  |  |  | CDC | 385 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_51A | #1MTR 51RY | DTR | S65/69/750/51A |  |  |  | CDC | 386 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_51NA | #1MTR 51N RY | DTR | S65/69/750/51NA |  |  |  | CDC | 387 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S65//1MTR/51ZA |  |  |  | CDC | 388 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_87A | #1MTR 87RY | DTR | S65//1MTR/87A |  |  |  | CDC | 389 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-2F | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR | S65/69/750/81AS |  |  |  | CDC | 390 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S65 | 保安SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S65/11/M1/51A |  |  |  | CDC | 391 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_TRA | #1MTR 重故障 | DTR | S65//1MTR/TRA |  |  |  | CDC | 392 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S65//1MTR/TRF |  |  |  | CDC | 393 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S65//1MTR/SupLocal |  |  |  | CDC | 394 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-28 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S65//1MTR/Tap Chan |  |  |  | CDC | 395 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S65 | 保安SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-39-00 | 1-39-01 | 1-18 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.751_ABS | 751(#1MTR) ABS | DTR | S65/69/750/ABS1 |  |  |  | CDC | 396 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S65//1MTR/OLTC_DLY |  |  |  | CDC | 397 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S65//1MTR/AC_Fault |  |  |  | CDC | 398 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.760_CB | 760(#2MTR) CB | DTR | S65/69/760/CB |  |  |  | CDC | 399 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_51A | #2MTR 51RY | DTR | S65/69/760/51A |  |  |  | CDC | 400 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_51NA | #2MTR 51N RY | DTR | S65/69/760/51NA |  |  |  | CDC | 401 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S65//2MTR/51ZA |  |  |  | CDC | 402 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_87A | #2MTR 87RY | DTR | S65//2MTR/87A |  |  |  | CDC | 403 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #760 |  | 81AS | [17 empty] | 1-0F-04 |  | 1-42 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_81A/S | #760 81RY A/S | DTR | S65/69/760/81AS |  |  |  | CDC | 404 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_TRA | #2MTR 重故障 | DTR | S65//2MTR/TRA |  |  |  | CDC | 405 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S65//2MTR/TRF |  |  |  | CDC | 406 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S65//2MTR/SupLocal |  |  |  | CDC | 407 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S65//2MTR/Tap Chan |  |  |  | CDC | 408 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S65 | 保安SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-39-02 | 1-39-03 | 1-19 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.761_ABS | 761(#2MTR) ABS | DTR | S65/69/760/ABS1 |  |  |  | CDC | 409 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S65//2MTR/OLTC_DLY |  |  |  | CDC | 410 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S65//2MTR/AC_Fault |  |  |  | CDC | 411 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-43 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.770_CB | 770(#3MTR) CB | DTR | S65/69/770/CB |  |  |  | CDC | 412 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.3M_CB | 3M(#3MTR) CB | DTR | S65/11/M3/CB |  |  |  | CDC | 413 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_51A | #3MTR 51RY | DTR | S65/69/770/51A |  |  |  | CDC | 414 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_51NA | #3MTR 51N RY | DTR | S65/69/770/51NA |  |  |  | CDC | 415 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S65//3MTR/51ZA |  |  |  | CDC | 416 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_87A | #3MTR 87RY | DTR | S65//3MTR/87A |  |  |  | CDC | 417 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #770 |  | 81AS | [17 empty] | 1-12-02 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_81A/S | #770 81RY A/S | DTR | S65/69/770/81AS |  |  |  | CDC | 418 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S65 | 保安SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S65/11/M3/51A |  |  |  | CDC | 419 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_TRA | #3MTR 重故障 | DTR | S65//3MTR/TRA |  |  |  | CDC | 420 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S65//3MTR/TRF |  |  |  | CDC | 421 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S65//3MTR/SupLocal |  |  |  | CDC | 422 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-4E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S65//3MTR/Tap Chan |  |  |  | CDC | 423 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S65 | 保安SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-39-04 | 1-39-05 | 1-1A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.771_ABS | 771(#3MTR) ABS | DTR | S65/69/770/ABS1 |  |  |  | CDC | 424 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S65//3MTR/OLTC_DLY |  |  |  | CDC | 425 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-35-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S65//3MTR/AC_Fault |  |  |  | CDC | 426 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 1-04-02 |  | 1-56 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.780_CB | 780(#4MTR) CB | DTR | S65/69/780/CB |  |  |  | CDC | 427 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 4M | #4MTR |  | CB | [17 empty] | 1-04-03 |  | 1-57 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.4M_CB | 4M(#4MTR) CB | DTR | S65/22/M4/CB |  |  |  | CDC | 428 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 51A | [17 empty] | 1-04-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_51A | #4MTR 51RY | DTR | S65/69/780/51A |  |  |  | CDC | 429 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 51NA | [17 empty] | 1-04-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_51NA | #4MTR 51N RY | DTR | S65/69/780/51NA |  |  |  | CDC | 430 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 1-05-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_51ZA | #4MTR 51Z RY | DTR | S65//4MTR/51ZA |  |  |  | CDC | 431 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-05-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_87A | #4MTR 87RY | DTR | S65//4MTR/87A |  |  |  | CDC | 432 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4M | #4MTR二次側(4M) |  | 51A | [17 empty] | 1-05-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.4M_51A | #4MTR二次側(4M) 51RY | DTR | S65/22/M4/51A |  |  |  | CDC | 433 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 1-36-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_TRA | #4MTR 重故障 | DTR | S65//4MTR/TRA |  |  |  | CDC | 434 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 1-36-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_TRF | #4MTR 輕故障 | DTR | S65//4MTR/TRF |  |  |  | CDC | 435 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 1-36-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_S/L | #4MTR OLTC S/L | DTR | S65//4MTR/SupLocal |  |  |  | CDC | 436 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 1-36-05 |  | 1-60 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_A/M | #4MTR OLTC A/M | DTR | S65//4MTR/Tap Chan |  |  |  | CDC | 437 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S65 | 保安SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | [16 empty] | 1-39-06 | 1-39-07 | 1-1B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.781_ABS | 781(#4MTR) ABS | DTR | S65/69/780/ABS1 |  |  |  | CDC | 438 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | OLTC_DLY | [17 empty] | 1-36-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR | S65//4MTR/OLTC_DLY |  |  |  | CDC | 439 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR_AC | #4MTR |  | FAULT | [17 empty] | 1-36-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR | S65//4MTR/AC_Fault |  |  |  | CDC | 440 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-21 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.210_CB | 210(11KV #1SC) CB | SC | S65/11/210/CB |  |  |  | CDC | 441 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-29 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S65/11/210/SC_A_M |  |  |  | CDC | 442 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.210_SCA | 11KV #1SC 51,51N RY | SC | S65/11/210/SCA |  |  |  | CDC | 443 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S65/11/210/UVA |  |  |  | CDC | 444 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.220_CB | 220(11KV #2SC) CB | SC | S65/11/220/CB |  |  |  | CDC | 445 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-3C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S65/11/220/SC_A_M |  |  |  | CDC | 446 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.220_SCA | 11KV #2SC 51,51N RY | SC | S65/11/220/SCA |  |  |  | CDC | 447 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S65/11/220/UVA |  |  |  | CDC | 448 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-47 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.230_CB | 230(11KV #3SC) CB | SC | S65/11/230/CB |  |  |  | CDC | 449 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S65/11/230/SC_A_M |  |  |  | CDC | 450 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.230_SCA | 11KV #3SC 51,51N RY | SC | S65/11/230/SCA |  |  |  | CDC | 451 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S65/11/230/UVA |  |  |  | CDC | 452 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-14-01 |  | 1-59 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.240_CB | 240(23KV #4SC) CB | SC | S65/11/240/CB |  |  |  | CDC | 453 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 1-36-06 |  | 1-61 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.240_A/M | 23KV #4SC 乏控器 A/M | SC | S65/22/240/SC_A_M |  |  |  | CDC | 454 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.240_SCA | 23KV #4SC 51,51N RY | SC | S65/22/240/SCA |  |  |  | CDC | 455 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-15-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | S65/22/240/UVA |  |  |  | CDC | 456 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-05 | [5 empty] | 69KV_S | [8 empty] | 保安SS.810_CB | 810(69KV #1SC) CB | SC | S65/69/810/CB |  |  |  | CDC | 457 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-39-08 | 1-39-09 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 保安SS.811_ABS | 811(69KV #1SC) ABS | SC | S65/69/810/ABS1 |  |  |  | CDC | 458 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_S | [8 empty] | 保安SS.810_SCA | 69KV #1SC 51,51N RY | SC | S65/69/810/SCA |  |  |  | CDC | 459 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_S | [8 empty] | 保安SS.810_OUVA | 69KV #1SC 27,59RY | SC | S65/69/810/UVA |  |  |  | CDC | 460 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | 69BUS | BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 保安SS.69BUS_VUA | 69KV BUS 衡相RY | BUS | S65/69/1BUS/BUS_VUA |  |  |  | CDC | 461 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S65/11/ComPoint/CBA |  |  |  | CDC | 462 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S65/11/ComPoint/CBF |  |  |  | CDC | 463 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S65/69/ComPoint/ABS_89A |  |  |  | CDC | 464 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S65/69/ComPoint/CBA |  |  |  | CDC | 465 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S65/69/ComPoint/CBF |  |  |  | CDC | 466 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S65/0/RTU/RTU_R_L |  |  |  | CDC | 467 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S65 | 保安SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.TEST_CB | TEST CB | OTHER | S65/0/RTU/Test_CB |  |  |  | CDC | 468 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S65/0/StaDev/PSF |  |  |  | CDC | 469 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S65/0/StaDev/ACB1 |  |  |  | CDC | 470 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S65 | 保安SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S65/0/StaDev/ACB2 |  |  |  | CDC | 471 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S65 | 保安SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S65/0/StaDev/STUV |  |  |  | CDC | 472 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.直流充電機故障 | 直流充電機故障 | OTHER | S65/0/StaDev/CHG1 |  |  |  | CDC | 473 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S65/0/StaDev/DCA |  |  |  | CDC | 474 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S65/0/StaDev/DCE |  |  |  | CDC | 475 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S65/0/StaDev/OilLeak |  |  |  | CDC | 476 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-38-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S65/0/StaDev/5A5Other |  |  |  | CDC | 477 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-38-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S65/0/StaDev/6A5Other |  |  |  | CDC | 478 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-38-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S65/0/StaDev/7A5Other |  |  |  | CDC | 479 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S65/0/StaDev/CHG2 |  |  |  | CDC | 480 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-38-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S65/0/StaDev/CommACF |  |  |  | CDC | 481 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S65/0/StaDev/Door1 |  |  |  | CDC | 482 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S65 | 保安SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-1C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S65/0/StaDev/Lights1 |  |  |  | CDC | 483 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S65 | 保安SS | 0 |  | 1_MAIN | #1MCB |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1_MAIN_51NA | #1MCB GDA | OTHER | S65/11/M1/51NA |  |  |  | CDC | 484 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3_MAIN | #3MCB |  | 51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3_MAIN_51NA | #3MCB GDA | OTHER | S65/11/M3/51NA |  |  |  | CDC | 485 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4_MAIN | #4MCB |  | 51NA | [17 empty] | 1-05-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4_MAIN_51NA | #4MCB GDA | OTHER | S65/22/M4/51NA |  |  |  | CDC | 486 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.69KVSC警報 | 69KVSC警報 | OTHER | S65/69/810/60A |  |  |  | CDC | 487 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S65 | 保安SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.RTU_DC故障 | RTU DC故障 | OTHER | S65/0/RTU/DCA |  |  |  | CDC | 488 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.水氣霧故障 | 水氣霧故障 | OTHER | S65/0/StaDev/2A5Other |  |  |  | CDC | 489 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.水氣霧警報 | 水氣霧警報 | OTHER | S65/0/StaDev/3A5Other |  |  |  | CDC | 490 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.火災警報 | 火警 | OTHER | S65/0/StaDev/Fire |  |  |  | CDC | 491 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.安全監控 | 保全設定 | OTHER | S65/0/StaDev/1A5Other |  |  |  | CDC | 492 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.門禁小門 | 門禁小門 | OTHER | S65/0/StaDev/Door2 |  |  |  | CDC | 493 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-1D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S65/0/StaDev/Lights |  |  |  | CDC | 494 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-07 |  | 1-67 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S65/0/StaDev/4A5Other |  |  |  | CDC | 495 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S65 | 保安SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.11KV_IED_FA | 11KV IED故障 | OTHER | S65/11/ComPoint/IRFA |  |  |  | CDC | 496 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 保安SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S65/69/ComPoint/CFA |  |  |  | CDC | 497 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 保安SS.69KV_IED_FA | 69KV IED故障 | OTHER | S65/69/ComPoint/IRFA |  |  |  | CDC | 498 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-17-00 |  | 1-7C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.490_CB | 490(#2SSTR) CB | OTHER | S65/11/490/CB |  |  |  | CDC | 499 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-17-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2SSTR_51A | #2SSTR 51RY | OTHER | S65/11/490/PHA |  |  |  | CDC | 500 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-17-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | S65/11/490/GDA |  |  |  | CDC | 501 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 590 | #3SSTR(590) |  | CB | [17 empty] | 1-17-03 |  | 1-7D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.590_CB | 590(#3SSTR) CB | OTHER | S65/11/590/CB |  |  |  | CDC | 502 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 1-17-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3SSTR_51A | #3SSTR 51RY | OTHER | S65/11/590/PHA |  |  |  | CDC | 503 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3SSTR_51NA | #3SSTR 51N RY | OTHER | S65/11/590/GDA |  |  |  | CDC | 504 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.2MA_CB | 2MA(#2MTR) CB | DTR | S65/11/M2A/CB |  |  |  | CDC | 505 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.2MB_CB | 2MB(#2MTR) CB | DTR | S65/11/M2B/CB |  |  |  | CDC | 506 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S65/11/M2A/51A |  |  |  | CDC | 507 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S65/11/M2B/51A |  |  |  | CDC | 508 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2_MA | #2MA |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2_MA_51NA | #2MA GDA | OTHER | S65/11/M2A/51NA |  |  |  | CDC | 509 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2_MB | #2MB |  | 51NA | [17 empty] | 1-02-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2_MB_51NA | #2MB GDA | OTHER | S65/11/M2B/51NA |  |  |  | CDC | 510 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.PM_CFA | PM通訊故障 | OTHER | S65/0/StaDev/PMA |  |  |  | CDC | 511 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.81RY_IED_FA | 低頻IED故障 | OTHER | S65/0/StaDev/81A_RYFA |  |  |  | CDC | 512 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_PHA | 22KV保51線(KM51) 相間RY | FEEDER | S65/22/KM51/PHA |  |  |  | CDC | 513 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_GDA | 22KV保51線(KM51) 接地RY | FEEDER | S65/22/KM51/GDA |  |  |  | CDC | 514 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) 79RY |  | 79UL | [17 empty] | 1-36-07 |  | 1-62 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_79UL | 22KV保51線(KM51) 79RY U/L | FEEDER | S65/22/KM51/79UL |  |  |  | CDC | 515 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM51 | 保51線(KM51) LCO分流器 |  | ADJ | [17 empty] | 1-37-15 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_ADJ | 22KV保51線(KM51) LCO分流器 U/L | FEEDER | S65/22/KM51/ADJ |  |  |  | CDC | 516 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM51 | KM51(22KV保51線) |  | CB | [17 empty] | 1-14-02 |  | 1-5A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_CB | KM51(22KV保51線) CB | FEEDER | S65/22/KM51/CB |  |  |  | CDC | 517 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | PHA | [17 empty] | 1-15-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_PHA | 22KV保52線(KM52) 相間RY | FEEDER | S65/22/KM52/PHA |  |  |  | CDC | 518 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) |  | GDA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_GDA | 22KV保52線(KM52) 接地RY | FEEDER | S65/22/KM52/GDA |  |  |  | CDC | 519 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) 79RY |  | 79UL | [17 empty] | 1-36-08 |  | 1-63 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_79UL | 22KV保52線(KM52) 79RY U/L | FEEDER | S65/22/KM52/79UL |  |  |  | CDC | 520 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM52 | 保52線(KM52) LCO分流器 |  | ADJ | [17 empty] | 1-38-00 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_ADJ | 22KV保52線(KM52) LCO分流器 U/L | FEEDER | S65/22/KM52/ADJ |  |  |  | CDC | 521 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM52 | KM52(22KV保52線) |  | CB | [17 empty] | 1-14-03 |  | 1-5B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_CB | KM52(22KV保52線) CB | FEEDER | S65/22/KM52/CB |  |  |  | CDC | 522 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_PHA | 22KV保53線(KM53) 相間RY | FEEDER | S65/22/KM53/PHA |  |  |  | CDC | 523 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_GDA | 22KV保53線(KM53) 接地RY | FEEDER | S65/22/KM53/GDA |  |  |  | CDC | 524 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) 79RY |  | 79UL | [17 empty] | 1-36-09 |  | 1-64 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_79UL | 22KV保53線(KM53) 79RY U/L | FEEDER | S65/22/KM53/79UL |  |  |  | CDC | 525 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM53 | 保53線(KM53) LCO分流器 |  | ADJ | [17 empty] | 1-38-01 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_ADJ | 22KV保53線(KM53) LCO分流器 U/L | FEEDER | S65/22/KM53/ADJ |  |  |  | CDC | 526 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM53 | KM53(22KV保53線) |  | CB | [17 empty] | 1-14-04 |  | 1-5C | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_CB | KM53(22KV保53線) CB | FEEDER | S65/22/KM53/CB |  |  |  | CDC | 527 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_PHA | 22KV備54線(KM54) 相間RY | FEEDER | S65/22/KM54/PHA |  |  |  | CDC | 528 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_GDA | 22KV備54線(KM54) 接地RY | FEEDER | S65/22/KM54/GDA |  |  |  | CDC | 529 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) 79RY |  | 79UL | [17 empty] | 1-36-10 |  | 1-65 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_79UL | 22KV備54線(KM54) 79RY U/L | FEEDER | S65/22/KM54/79UL |  |  |  | CDC | 530 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM54 | 備54線(KM54) LCO分流器 |  | ADJ | [17 empty] | 1-38-02 |  | 1-7A | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_ADJ | 22KV備54線(KM54) LCO分流器 U/L | FEEDER | S65/22/KM54/ADJ |  |  |  | CDC | 531 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM54 | KM54(22KV備54線) |  | CB | [17 empty] | 1-14-05 |  | 1-5D | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_CB | KM54(22KV備54線) CB | FEEDER | S65/22/KM54/CB |  |  |  | CDC | 532 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | PHA | [17 empty] | 1-16-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_PHA | 22KV備55線(KM55) 相間RY | FEEDER | S65/22/KM55/PHA |  |  |  | CDC | 533 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) |  | GDA | [17 empty] | 1-16-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_GDA | 22KV備55線(KM55) 接地RY | FEEDER | S65/22/KM55/GDA |  |  |  | CDC | 534 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) 79RY |  | 79UL | [17 empty] | 1-36-11 |  | 1-66 | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_79UL | 22KV備55線(KM55) 79RY U/L | FEEDER | S65/22/KM55/79UL |  |  |  | CDC | 535 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 22 | 22kV | KM55 | 備55線(KM55) LCO分流器 |  | ADJ | [17 empty] | 1-38-03 |  | 1-7B | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_ADJ | 22KV備55線(KM55) LCO分流器 U/L | FEEDER | S65/22/KM55/ADJ |  |  |  | CDC | 536 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S65 | 保安SS | 22 | 22kV | KM55 | KM55(22KV備55線) |  | CB | [17 empty] | 1-14-06 |  | 1-5E | [5 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_CB | KM55(22KV備55線) CB | FEEDER | S65/22/KM55/CB |  |  |  | CDC | 537 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 620 | 台南保安線(620) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 保安SS.620_87A | 620台南保安線87RY | OTHER | S65/69/620/87A |  |  |  | CDC | 538 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 620 | 台南保安線(620) |  | 87UL | [17 empty] | 1-32-04 |  | 1-08 | [5 empty] | ADCS_S | [8 empty] | 保安SS.620_87UL | 620台南保安線87RY UL | OTHER | S65/69/620/87UL |  |  |  | CDC | 539 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | KM21 | 三甲線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_LOA | 三甲線 復閉失敗閉鎖 | OTHER | S65/11/KM21/LOA |  |  |  | CDC | 540 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM22 | 仁工線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_LOA | 仁工線 復閉失敗閉鎖 | OTHER | S65/11/KM22/LOA |  |  |  | CDC | 541 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM23 | 保安線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_LOA | 保安線 復閉失敗閉鎖 | OTHER | S65/11/KM23/LOA |  |  |  | CDC | 542 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM24 | 二行線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_LOA | 二行線 復閉失敗閉鎖 | OTHER | S65/11/KM24/LOA |  |  |  | CDC | 543 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM25 | 豐和線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_LOA | 豐和線 復閉失敗閉鎖 | OTHER | S65/11/KM25/LOA |  |  |  | CDC | 544 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM26 | 安廟線 |  | LOA | [17 empty] | 1-3F-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_LOA | 安廟線 復閉失敗閉鎖 | OTHER | S65/11/KM26/LOA |  |  |  | CDC | 545 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM27 | 上崙線 |  | LOA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_LOA | 上崙線 復閉失敗閉鎖 | OTHER | S65/11/KM27/LOA |  |  |  | CDC | 546 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM28 | 藥專線 |  | LOA | [17 empty] | 1-3F-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_LOA | 藥專線 復閉失敗閉鎖 | OTHER | S65/11/KM28/LOA |  |  |  | CDC | 547 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM29 | 保29線 |  | LOA | [17 empty] | 1-3F-09 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_LOA | 保29線 復閉失敗閉鎖 | OTHER | S65/11/KM29/LOA |  |  |  | CDC | 548 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM30 | 仁七線 |  | LOA | [17 empty] | 1-3F-10 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_LOA | 仁七線 復閉失敗閉鎖 | OTHER | S65/11/KM30/LOA |  |  |  | CDC | 549 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM51 | 保51線 |  | LOA | [17 empty] | 1-3F-11 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_LOA | 保51線 復閉失敗閉鎖 | OTHER | S65/22/KM51/LOA |  |  |  | CDC | 550 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM52 | 保52線 |  | LOA | [17 empty] | 1-3F-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_LOA | 保52線 復閉失敗閉鎖 | OTHER | S65/22/KM52/LOA |  |  |  | CDC | 551 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM53 | 保53線 |  | LOA | [17 empty] | 1-3F-13 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_LOA | 保53線 復閉失敗閉鎖 | OTHER | S65/22/KM53/LOA |  |  |  | CDC | 552 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM54 | 備54線 |  | LOA | [17 empty] | 1-3F-14 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_LOA | 備54線 復閉失敗閉鎖 | OTHER | S65/22/KM54/LOA |  |  |  | CDC | 553 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM55 | 備55線 |  | LOA | [17 empty] | 1-3F-15 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_LOA | 備55線 復閉失敗閉鎖 | OTHER | S65/22/KM55/LOA |  |  |  | CDC | 554 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S65//1MTR/63Q |  |  |  | CDC | 555 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S65//1MTR/96B1 |  |  |  | CDC | 556 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S65//1MTR/96B2 |  |  |  | CDC | 557 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S65//1MTR/96D |  |  |  | CDC | 558 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S65//1MTR/96P |  |  |  | CDC | 559 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S65//2MTR/63Q |  |  |  | CDC | 560 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S65//2MTR/96B1 |  |  |  | CDC | 561 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S65//2MTR/96B2 |  |  |  | CDC | 562 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S65//2MTR/96D |  |  |  | CDC | 563 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S65//2MTR/96P |  |  |  | CDC | 564 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-19-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | S65//3MTR/63Q |  |  |  | CDC | 565 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-19-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | S65//3MTR/96B1 |  |  |  | CDC | 566 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-19-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | S65//3MTR/96B2 |  |  |  | CDC | 567 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-19-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | S65//3MTR/96D |  |  |  | CDC | 568 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-19-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | S65//3MTR/96P |  |  |  | CDC | 569 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 63Q | [17 empty] | 1-1A-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | S65//4MTR/63Q |  |  |  | CDC | 570 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 96B1 | [17 empty] | 1-1A-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | S65//4MTR/96B1 |  |  |  | CDC | 571 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 96B2 | [17 empty] | 1-1A-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | S65//4MTR/96B2 |  |  |  | CDC | 572 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 96D | [17 empty] | 1-19-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | S65//4MTR/96D |  |  |  | CDC | 573 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 96P | [17 empty] | 1-1A-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | S65//4MTR/96P |  |  |  | CDC | 574 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.變電所低水位 | 變電所低水位 | OTHER | S65/0/StaDev/Water1 |  |  |  | CDC | 575 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.變電所高水位 | 變電所高水位 | OTHER | S65/0/StaDev/Water2 |  |  |  | CDC | 576 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 660 | 歸仁保安線(660) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_S | [8 empty] | 保安SS.660_87A | 660歸仁保安線87RY | OTHER | S65/69/660/87A |  |  |  | CDC | 577 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 660 | 歸仁保安線(660) |  | 87UL | [17 empty] | 1-32-06 |  | 1-09 | [5 empty] | ADCS_S | [8 empty] | 保安SS.660_87UL | 660歸仁保安線87RY UL | OTHER | S65/69/660/87UL |  |  |  | CDC | 578 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S65//1MTR/96PA |  |  |  | CDC | 579 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S65//2MTR/96PA |  |  |  | CDC | 580 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR | S65//3MTR/96PA |  |  |  | CDC | 581 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 1-04-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR | S65//4MTR/96PA |  |  |  | CDC | 582 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | S65//1MTR/51Z_UL |  |  |  | CDC | 583 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | S65//1MTR/MTR_86A |  |  |  | CDC | 584 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER | S65//1MTR/87UL |  |  |  | CDC | 585 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | S65//1MTR/1_87UL2 |  |  |  | CDC | 586 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3E-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | S65//2MTR/51Z_UL |  |  |  | CDC | 587 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | S65//2MTR/MTR_86A |  |  |  | CDC | 588 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-34-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER | S65//2MTR/87UL |  |  |  | CDC | 589 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-3E-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | S65//2MTR/1_87UL2 |  |  |  | CDC | 590 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3E-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | S65//3MTR/51Z_UL |  |  |  | CDC | 591 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | S65//3MTR/MTR_86A |  |  |  | CDC | 592 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 1-35-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER | S65//3MTR/87UL |  |  |  | CDC | 593 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 1-3E-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | S65//3MTR/1_87UL2 |  |  |  | CDC | 594 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 51Z_UL | [17 empty] | 1-3E-07 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_51ZUL | #4MTR 51Z U/L | OTHER | S65//4MTR/51Z_UL |  |  |  | CDC | 595 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | MTR_86A | [17 empty] | 1-1B-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_86A | #4MTR 86(51Z/87/96)RY | OTHER | S65//4MTR/MTR_86A |  |  |  | CDC | 596 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 1_87UL1 | [17 empty] | 1-36-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_87UL1 | #4MTR 第一套87RY U/L | OTHER | S65//4MTR/87UL |  |  |  | CDC | 597 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | 4MTR | #4MTR |  | 1_87UL2 | [17 empty] | 1-3E-09 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.#4MTR_87UL2 | #4MTR 第二套87RY U/L | OTHER | S65//4MTR/1_87UL2 |  |  |  | CDC | 598 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | MTR | MTR |  | IEDGA | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.MTR_IED故障 | MTR IED故障 | OTHER | S65/0/MTR/IRFA |  |  |  | CDC | 599 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM31 | 保甲線 |  | LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_LOA | 保甲線 復閉失敗閉鎖 | OTHER | S65/11/KM31/LOA |  |  |  | CDC | 600 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM32 | 中生線 |  | LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_LOA | 中生線 復閉失敗閉鎖 | OTHER | S65/11/KM32/LOA |  |  |  | CDC | 601 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM33 | 新崙線 |  | LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_LOA | 新崙線 復閉失敗閉鎖 | OTHER | S65/11/KM33/LOA |  |  |  | CDC | 602 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM34 | 保34線 |  | LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_LOA | 保34線 復閉失敗閉鎖 | OTHER | S65/11/KM34/LOA |  |  |  | CDC | 603 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | KM35 | 中洲線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_LOA | 中洲線 復閉失敗閉鎖 | OTHER | S65/11/KM35/LOA |  |  |  | CDC | 604 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠27 | [17 empty] | 1-07-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠27 | 奇美實業B廠 27/59A | OTHER | S65/11/CM_B/UVA |  |  |  | CDC | 605 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠51 | [17 empty] | 1-07-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠51 | 奇美實業B廠 50/51A | OTHER | S65/11/CM_B/PHA |  |  |  | CDC | 606 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠51N | [17 empty] | 1-07-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠51N | 奇美實業B廠 50N/51NA | OTHER | S65/11/CM_B/GDA |  |  |  | CDC | 607 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠59 | [17 empty] | 1-07-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠59 | 奇美實業B廠 59V0A | OTHER | S65/11/CM_B/59A_V0 |  |  |  | CDC | 608 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠81L | [17 empty] | 1-07-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠81L | 奇美實業B廠 81LA | OTHER | S65/11/CM_B/81A |  |  |  | CDC | 609 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠CB | [17 empty] | 1-07-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠CB | 奇美實業B廠 CB | OTHER | S65/11/CM_B/CB |  |  |  | CDC | 610 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | CM | CM |  | B廠CFA | [17 empty] | 1-38-09 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠CFA | 奇美實業B廠通訊故障 | OTHER | S65/11/CM_B/CFA |  |  |  | CDC | 611 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | CM | 奇美實業B廠 |  | B廠DS | [17 empty] | 1-3C-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM_B廠DS | 奇美實業B廠 DS | OTHER | S65/11/CM_B/D1 |  |  |  | CDC | 612 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田27 | [17 empty] | 1-06-01 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田27 | 奇美新田廠 27/59A | OTHER | S65/22/CM_XT/UVA |  |  |  | CDC | 613 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田51 | [17 empty] | 1-06-03 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田51 | 奇美新田廠 50/51A | OTHER | S65/22/CM_XT/PHA |  |  |  | CDC | 614 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田51N | [17 empty] | 1-06-04 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田51N | 奇美新田廠 50N/51NA | OTHER | S65/22/CM_XT/GDA |  |  |  | CDC | 615 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田59 | [17 empty] | 1-06-02 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田59 | 奇美新田廠 59V0A | OTHER | S65/22/CM_XT/59A_V0 |  |  |  | CDC | 616 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田81L | [17 empty] | 1-06-05 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田81L | 奇美新田廠 81LA | OTHER | S65/22/CM_XT/81A |  |  |  | CDC | 617 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田CB | [17 empty] | 1-06-00 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田CB | 奇美新田廠 CB | OTHER | S65/22/CM_XT/CB |  |  |  | CDC | 618 | GENERICDIPoint | SS407_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  |  |  |  | CM新田CFA | [17 empty] | 1-38-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田CFA | 奇美新田廠通訊故障 | OTHER | S65/22/CM_XT/CFA |  |  |  | CDC | 619 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S65 | 保安SS | 0 |  | 奇美新田廠 | 奇美新田廠 |  | CM新田DS | [17 empty] | 1-3B-08 | [7 empty] | DDCS4_2 | [8 empty] | 保安SS.CM新田DS | 奇美新田廠 DS | OTHER | S65/22/CM_XT/D1 |  |  |  | CDC | 620 | GENERICDIPoint | SS407_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.210_SC_CAP | 11KV#1SC 容量 | SC | S65/11/210/1AI_Oth |  |  |  |  | 621 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.220_SC_CAP | 11KV#2SC 容量 | SC | S65/11/220/2AI_Oth |  |  |  |  | 622 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.230_SC_CAP | 11KV#3SC 容量 | SC | S65/11/230/3AI_Oth |  |  |  |  | 623 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 22 | 22kV | 240_SC | #4SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 624 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 保安SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 625 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S65 | 保安SS | 69 | 69kV | 610 | 備用線(610) |  | LE0 | 610LE | [24 empty] | ADCS_S | [8 empty] | 保安SS.610LE | 610LE (非取樣點) | LINE69 | S65/69/610/LE0 |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 保安SS.620LE | 620LE (非取樣點) | LINE69 | S65/69/620/LE0 |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | LE0 | 660LE | [24 empty] | ADCS_S | [8 empty] | 保安SS.660LE | 660LE (非取樣點) | LINE69 | S65/69/660/LE0 |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM21 | KM21_ES |  | LE0 | KM21_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_ES | KM21_ES (非取樣點) | FEEDER | S65/11/KM21/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM22 | KM22_ES |  | LE0 | KM22_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_ES | KM22_ES (非取樣點) | FEEDER | S65/11/KM22/ES |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM23 | KM23_ES |  | LE0 | KM23_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_ES | KM23_ES (非取樣點) | FEEDER | S65/11/KM23/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM24 | KM24_ES |  | LE0 | KM24_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_ES | KM24_ES (非取樣點) | FEEDER | S65/11/KM24/ES |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM25DS1 | KM25DS1 |  | KM25DS1 | KM25DS1 | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25DS1 | KM25DS1 (非取樣點) | FEEDER | [5 empty] | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM25DS2 | KM25DS2 |  | KM25DS2 | KM25DS2 | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25DS2 | KM25DS2 (非取樣點) | FEEDER | [5 empty] | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM25 | KM25_ES |  | LE0 | KM25_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_ES | KM25_ES (非取樣點) | FEEDER | S65/11/KM25/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM26 | KM26_ES |  | LE0 | KM26_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_ES | KM26_ES (非取樣點) | FEEDER | S65/11/KM26/ES |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM27 | KM27_ES |  | LE0 | KM27_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_ES | KM27_ES (非取樣點) | FEEDER | S65/11/KM27/ES |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM28 | KM28_ES |  | LE0 | KM28_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_ES | KM28_ES (非取樣點) | FEEDER | S65/11/KM28/ES |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM29_KM30 | KM29_KM30_DS |  | DS1 | KM29_KM30_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_KM30_DS | KM29_KM30_DS (非取樣點) | FEEDER | [5 empty] | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM29 | KM29_ES |  | LE0 | KM29_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_ES | KM29_ES (非取樣點) | FEEDER | S65/11/KM29/ES |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM30 | KM30_ES |  | LE0 | KM30_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_ES | KM30_ES (非取樣點) | FEEDER | S65/11/KM30/ES |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM31 | KM31_DS |  | DS1 | KM31_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_DS | KM31_DS (非取樣點) | FEEDER | S65/11/KM31/DS |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM31 | KM31_ES |  | LE0 | KM31_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM31_ES | KM31_ES (非取樣點) | FEEDER | S65/11/KM31/ES |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM32 | KM32_DS |  | DS1 | KM32_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_DS | KM32_DS (非取樣點) | FEEDER | S65/11/KM32/DS |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM32 | KM32_ES |  | LE0 | KM32_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM32_ES | KM32_ES (非取樣點) | FEEDER | S65/11/KM32/ES |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM33 | KM33_DS |  | DS1 | KM33_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_DS | KM33_DS (非取樣點) | FEEDER | S65/11/KM33/DS |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM33 | KM33_ES |  | LE0 | KM33_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM33_ES | KM33_ES (非取樣點) | FEEDER | S65/11/KM33/ES |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM34 | KM34_DS |  | DS1 | KM34_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_DS | KM34_DS (非取樣點) | FEEDER | S65/11/KM34/DS |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM34 | KM34_ES |  | LE0 | KM34_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM34_ES | KM34_ES (非取樣點) | FEEDER | S65/11/KM34/ES |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM35 | KM35_DS |  | DS1 | KM35_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_DS | KM35_DS (非取樣點) | FEEDER | S65/11/KM35/DS |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM35 | KM35_ES |  | LE0 | KM35_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM35_ES | KM35_ES (非取樣點) | FEEDER | S65/11/KM35/ES |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S65/11/TIE1/D1 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S65/11/TIE2/D1 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S65/11/TIE3/D1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.1M_DS | 1M_DS (非取樣點) | DTR | S65/11/M1/DS |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.1M_ES | 1M_ES (非取樣點) | DTR | S65/11/M1/ES |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.3M_DS | 3M_DS (非取樣點) | DTR | S65/11/M3/DS |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.3M_ES | 3M_ES (非取樣點) | DTR | S65/11/M3/ES |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 4M | 4M_DS |  | DS1 | 4M_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.4M_DS | 4M_DS (非取樣點) | DTR | S65/22/M4/DS |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 4M | 4M_ES |  | M0 | 4M_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.4M_ES | 4M_ES (非取樣點) | DTR | S65/22/M4/ES |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.210_ES | 210_ES (非取樣點) | SC | S65/11/210/ES |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.210_DS | 210_DS (非取樣點) | SC | S65/11/210/DS |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.220_ES | 220_ES (非取樣點) | SC | S65/11/220/ES |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.230_ES | 230_ES (非取樣點) | SC | S65/11/230/ES |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.240_ES | 240_ES (非取樣點) | SC | S65/11/240/ES |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.240_DS | 240_DS (非取樣點) | SC | S65/22/240/DS |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 保安SS.69B1E | 69B1E (非取樣點) | BUS | S65/69/1BUS/BE1 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 668 | NotelDIPoint | [38 empty] | START/STOP | STOP
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PW1UL | 660_PW1UL | [24 empty] | ADCS_S | [8 empty] | 保安SS.660_PW1UL | 歸仁線(660)PW1_UL(非取樣點) | LINE69 | [5 empty] | 669 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PW2UL | 660_PW2UL | [24 empty] | ADCS_S | [8 empty] | 保安SS.660_PW2UL | 歸仁線(660)PW2_UL(非取樣點) | LINE69 | [5 empty] | 670 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S65 | 保安SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | HCBUL | 660_HCBUL | [24 empty] | ADCS_S | [8 empty] | 保安SS.660_HCBUL | 歸仁線(660)HCB_UL(非取樣點) | LINE69 | [5 empty] | 671 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_S | [8 empty] | 保安SS.620_PW1UL | 台南線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 672 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_S | [8 empty] | 保安SS.620_PW2UL | 台南線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 673 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S65 | 保安SS | 69 | 69kV | 620 | 台南保安線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_S | [8 empty] | 保安SS.620_HCBUL | 台南線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 674 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S65 | 保安SS | 0 |  | KM26 | KM26_DS |  | DS1 | KM26_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM26_DS | KM26_DS (非取樣點) | FEEDER | S65/11/KM26/DS |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM27 | KM27_DS |  | DS1 | KM27_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM27_DS | KM27_DS (非取樣點) | FEEDER | S65/11/KM27/DS |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM30 | KM30_DS |  | DS1 | KM30_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM30_DS | KM30_DS (非取樣點) | FEEDER | S65/11/KM30/DS |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM28 | KM28_DS |  | DS1 | KM28_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM28_DS | KM28_DS (非取樣點) | FEEDER | S65/11/KM28/DS |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM29 | KM29_DS |  | DS1 | KM29_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM29_DS | KM29_DS (非取樣點) | FEEDER | S65/11/KM29/DS |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM21 | KM21_DS |  | DS1 | KM21_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM21_DS | KM21_DS (非取樣點) | FEEDER | S65/11/KM21/DS |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM22 | KM22_DS |  | DS1 | KM22_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM22_DS | KM22_DS (非取樣點) | FEEDER | S65/11/KM22/DS |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM23 | KM23_DS |  | DS1 | KM23_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM23_DS | KM23_DS (非取樣點) | FEEDER | S65/11/KM23/DS |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM24 | KM24_DS |  | DS1 | KM24_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM24_DS | KM24_DS (非取樣點) | FEEDER | S65/11/KM24/DS |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM25 | KM25_DS |  | DS1 | KM25_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM25_DS | KM25_DS (非取樣點) | FEEDER | S65/11/KM25/DS |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2BR | 2BR_DS |  | DS1 | 2BR_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2BR_DS | 2BR_DS (非取樣點) | TIE | S65/11/2BR/DS |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.491 | 491 (非取樣點) | OTHER | S65/11/490/DS |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.491E | 491E (非取樣點) | OTHER | S65/11/490/ES |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 591 | 591 |  | 591 | 591 | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.591 | 591 (非取樣點) | OTHER | S65/11/590/DS |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 591E | 591E |  | 591E | 591E | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.591E | 591E (非取樣點) | OTHER | S65/11/590/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S65/11/M2A/DS |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S65/11/M2B/DS |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S65/11/M2A/ES |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S65/11/M2B/ES |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.220_DS | 220_DS (非取樣點) | SC | S65/11/220/DS |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.230_DS | 230_DS (非取樣點) | SC | S65/11/230/DS |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | 2BR | 2BR |  | BR0 | 2BR_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.2BR_ES | 2BR ES(非取樣點) | OTHER | S65/11/2BR/ES |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | TIE1 | TIE1 |  | LE0 | TIE1_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE1_ES | TIE1 ES(非取樣點) | OTHER | S65/11/TIE1/E1 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | TIE2 | TIE2 |  | LE0 | TIE2_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.TIE2_ES | TIE2 ES(非取樣點) | OTHER | S65/11/TIE2/E1 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM51 | KM51_DS |  | DS1 | KM51_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_DS | KM51_DS (非取樣點) | FEEDER | S65/22/KM51/DS |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM51 | KM51_ES |  | LE0 | KM51_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM51_ES | KM51_ES (非取樣點) | FEEDER | S65/22/KM51/ES |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM52 | KM52_DS |  | DS1 | KM52_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_DS | KM52_DS (非取樣點) | FEEDER | S65/22/KM52/DS |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM52 | KM52_ES |  | LE0 | KM52_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM52_ES | KM52_ES (非取樣點) | FEEDER | S65/22/KM52/ES |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM53 | KM53_DS |  | DS1 | KM53_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_DS | KM53_DS (非取樣點) | FEEDER | S65/22/KM53/DS |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM53 | KM53_ES |  | LE0 | KM53_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM53_ES | KM53_ES (非取樣點) | FEEDER | S65/22/KM53/ES |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM54 | KM54_DS |  | DS1 | KM54_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_DS | KM54_DS (非取樣點) | FEEDER | S65/22/KM54/DS |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM54 | KM54_ES |  | LE0 | KM54_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM54_ES | KM54_ES (非取樣點) | FEEDER | S65/22/KM54/ES |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | KM55 | KM55_DS |  | DS1 | KM55_DS | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_DS | KM55_DS (非取樣點) | FEEDER | S65/22/KM55/DS |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S65 | 保安SS | 0 |  | KM55 | KM55_ES |  | LE0 | KM55_ES | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.KM55_ES | KM55_ES (非取樣點) | FEEDER | S65/22/KM55/ES |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.#2A_BE | #2A BE(非取樣點) | OTHER | S65/11/2ABUS/BE0 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.#2B_BE | #2B BE(非取樣點) | OTHER | S65/11/2BBUS/BE0 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S65 | 保安SS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | DDCS4_2 | [8 empty] | 保安SS.#3_BE | #3 BE(非取樣點) | OTHER | S65/11/3BUS/BE0 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo