## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS 1 電壓（R相） |  |  | kV_-90_90(-2000_2000) | aaa | B2/S66_A1 | [8 empty] | 大灣SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S66 | 大灣SS | 69 | 69kV | #2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV BUS 2 電壓（R相） |  |  | kV_-90_90(-2000_2000) | aab | B2/S66_A1 | [8 empty] | 大灣SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S66 | 大灣SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S66_D1 | [8 empty] | 大灣SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0059 |  |  | 1-BB |  |  | #2A 11KV 電壓（R相） |  |  | kV_-9_9(-2000_2000) | aba | B2/S66_D1 | [8 empty] | 大灣SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2B 11KV 電壓（R相） |  |  | kV_-9_9(-2000_2000) | aca | B2/S66_D1 | [8 empty] | 大灣SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 3BUS | #3BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | #3 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S66_D1 | [8 empty] | 大灣SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 8 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 9 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 69KV #1BUS 87A |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER |  |  |  |  | CDC | 10 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | #2BUS | #2BUS |  | BE2 | 69B2E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 11 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | #2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV BUS #2 衡相監視 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | #2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 69KV #2BUS 87A |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 69KV 大灣永康一路（630）瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.630_MW | 大灣永康一路 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 69KV 大灣永康一路（630）乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.630_MVAR | 大灣永康一路 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 69KV 大灣永康一路（630）MWH(+) |  |  |  |  | B2/S66_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 69KV 後甲大灣線（620）瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.620_MW | 後甲大灣線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 69KV 後甲大灣線（620）乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.620_MVAR | 後甲大灣線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 69KV 後甲大灣線（620）MWH(+) |  |  |  |  | B2/S66_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 69KV 台南大灣一路（670）瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.670_MW | 台南大灣一路 MW | LINE69 |  |  |  |  | CDC | 20 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 69KV 台南大灣一路（670）乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.670_MVAR | 台南大灣一路 MVAR | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 69KV 台南大灣一路（670）MWH(+) |  |  |  |  | B2/S66_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 22 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 69KV 大灣永康二路（640）瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.640_MW | 大灣永康二路 MW | LINE69 |  |  |  |  | CDC | 23 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 69KV 大灣永康二路（640）乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.640_MVAR | 大灣永康二路 MVAR | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 69KV 大灣永康二路（640）MWH(+) |  |  |  |  | B2/S66_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 25 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 69KV 台南大灣二路（720）瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.720_MW | 台南大灣二路 MW | LINE69 |  |  |  |  | CDC | 26 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 69KV 台南大灣二路（720）乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.720_MVAR | 台南大灣二路 MVAR | LINE69 |  |  |  |  | CDC | 27 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0032 |  |  | 2-40 |  |  | 69KV 台南大灣二路（720）MWH(+) |  |  |  |  | B2/S66_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 28 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 大灣永康一路（630）67 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.630_PHA | 永康線(630) 相間RY | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 大灣永康一路（630）67N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.630_GDA | 大灣永康一路(630) 接地RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 大灣永康一路（630）87 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.630_87A | 630大灣永康一路87RY | OTHER |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 後甲大灣線（620）67 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.620_PHA | 後甲大灣線(620) 相間RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 後甲大灣線（620）67N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.620_GDA | 後甲大灣線(620) 接地RY | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 後甲大灣線（620）87 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.620_87A | 620後甲大灣線87RY | OTHER |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | I台南大灣一路（670）67 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.670_PHA | 台南大灣一路(670) 相間RY | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 台南大灣一路（670）67N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.670_GDA | 台南大灣一路(670) 接地RY | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 台南大灣一路（670）87 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.670_87A | 670台南大灣一路87RY | OTHER |  |  |  |  | CDC | 37 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | I大灣永康二路（640） 67 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.640_PHA | 大灣永康二路(640) 相間RY | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 大灣永康二路（640） 67N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.640_GDA | 大灣永康二路(640) 接地RY | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | I台南大灣二路（720） 21 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.720_PHA | 台南大灣二路(720) 相間RY | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 台南大灣二路（720） 21N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.720_GDA | 台南大灣二路(720) 接地RY | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 大灣永康一路（630） 87RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.630_87UL | 630大灣永康一路87RY UL | OTHER |  |  |  |  | CDC | 42 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 後甲大灣線（620）87RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.620_87UL | 620後甲大灣線87RY UL | OTHER |  |  |  |  | CDC | 43 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 台南大灣一路（670） 87RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.670_87UL | 670台南大灣一路87RY UL | OTHER |  |  |  |  | CDC | 44 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S66S631/T1 |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 大灣永康一路（630）CB |  |  |  | aaaa | B2/S66_A1 | [8 empty] | 大灣SS.630_CB | 630(大灣永康一路) CB | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S62S66/T2 |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 後甲大灣線（620）CB |  |  |  | aada | B2/S66_A1 | [8 empty] | 大灣SS.620_CB | 620(後甲大灣線) CB | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/P07S661/T2 |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 台南大灣一路（670）CB |  |  |  | aaga | B2/S66_A1 | [8 empty] | 大灣SS.670_CB | 670(台南大灣一路) CB | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S66S632/T1 |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 大灣永康二路（640） CB |  |  |  | aaia | B2/S66_A1 | [8 empty] | 大灣SS.640_CB | 640(大灣永康二路) CB | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/P07S662/T2 |  | 0080 |  | 0005 | 1-0A-00 |  | 1-05 | 台南大灣二路（720） CB |  |  |  | aaja | B2/S66_A1 | [8 empty] | 大灣SS.720_CB | 720(台南大灣二路) CB | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | DS1 | 631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0016 | 1-38-00 | 1-38-01 | 1-10 | 大灣永康一路（631）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.631_DS | 631(大灣永康一路) DS | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | DS2 | 632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0017 | 1-38-02 | 1-38-03 | 1-11 | 大灣永康一路（632）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.632_DS | 632(大灣永康一路) DS | LINE69 |  |  |  |  | CDC | 51 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | DS1 | 621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0020 | 1-38-08 | 1-38-09 | 1-14 | 後甲大灣線（621）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.621_DS | 621(後甲大灣線) DS | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | DS2 | 622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0021 | 1-38-10 | 1-38-11 | 1-15 | 後甲大灣線（622）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.622_DS | 622(後甲大灣線) DS | LINE69 |  |  |  |  | CDC | 53 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | DS1 | 671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0024 | 1-39-00 | 1-39-01 | 1-18 | 台南大灣一路（671）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.671_DS | 671(台南大灣一路) DS | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | DS2 | 672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0402 | 403 | 0025 | 1-39-02 | 1-39-03 | 1-19 | 台南大灣一路（672）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.672_DS | 672(台南大灣一路) DS | LINE69 |  |  |  |  | CDC | 55 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0408 | 409 | 0028 | 1-39-08 | 1-39-09 | 1-1C | 大灣永康二路（641） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.641_DS | 641(大灣永康二路) DS | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0029 | 1-39-10 | 1-39-11 | 1-1D | 大灣永康二路（642） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.642_DS | 642(大灣永康二路) DS | LINE69 |  |  |  |  | CDC | 57 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | DS1 | 721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0416 | 417 | 0032 | 1-3A-00 | 1-3A-01 | 1-20 | 大灣永康二路（721） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.721_DS | 721(台南大灣二路) DS | LINE69 |  |  |  |  | CDC | 58 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | DS2 | 722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0418 | 419 | 0033 | 1-3A-02 | 1-3A-03 | 1-21 | 大灣永康二路（722） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.722_DS | 722(台南大灣二路) DS | LINE69 |  |  |  |  | CDC | 59 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | DS3 | 633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0018 | 1-38-04 | 1-38-05 | 1-12 | 大灣永康一路（633）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.633_DS | 633(大灣永康一路) DS | LINE69 |  |  |  |  | CDC | 60 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | ES3 | 633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0390 | 391 | 0019 | 1-38-06 | 1-38-07 | 1-13 | 大灣永康一路（633E）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.633E_ES | 633E(大灣永康一路) ES | LINE69 |  |  |  |  | CDC | 61 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | LE0 | 630LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 62 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | BE0 | 630BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 63 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | DS3 | 623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0396 | 397 | 0022 | 1-38-12 | 1-38-13 | 1-16 | 後甲大灣線（623）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.623_DS | 623(後甲大灣線) DS | LINE69 |  |  |  |  | CDC | 64 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | ES3 | 623E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0398 | 399 | 0023 | 1-38-14 | 1-38-15 | 1-17 | 後甲大灣線（623E）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.623E_ES | 623E(後甲大灣線) ES | LINE69 |  |  |  |  | CDC | 65 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | LE0 | 620LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 66 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | BE0 | 620BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 67 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | DS3 | 673 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0026 | 1-39-04 | 1-39-05 | 1-1A | 台南大灣一路（673）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.673_DS | 673(台南大灣一路) DS | LINE69 |  |  |  |  | CDC | 68 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | ES3 | 673E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0406 | 407 | 0027 | 1-39-06 | 1-39-07 | 1-1B | 台南大灣一路（673E）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.673E_ES | 673E(台南大灣一路) ES | LINE69 |  |  |  |  | CDC | 69 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | LE0 | 670LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 70 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | BE0 | 670BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 71 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0030 | 1-39-12 | 1-39-13 | 1-1E | 大灣永康二路（643） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.643_DS | 643(大灣永康二路) DS | LINE69 |  |  |  |  | CDC | 72 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | ES3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0031 | 1-39-14 | 1-39-15 | 1-1F | 大灣永康二路（643E） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.643E_ES | 643E(大灣永康二路) ES | LINE69 |  |  |  |  | CDC | 73 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | LE0 | 640LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 74 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | BE0 | 640BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 75 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | DS3 | 723 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0420 | 421 | 0034 | 1-3A-04 | 1-3A-05 | 1-22 | 大灣永康二路（723） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.723_DS | 723(台南大灣二路) DS | LINE69 |  |  |  |  | CDC | 76 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | ES3 | 723E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0422 | 423 | 0035 | 1-3A-06 | 1-3A-07 | 1-23 | 大灣永康二路（723E） ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.723E_ES | 723E(台南大灣二路) ES | LINE69 |  |  |  |  | CDC | 77 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | LE0 | 720LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.720LE | 720LE (非取樣點) | LINE69 | [5 empty] | 78 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | BE0 | 720BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 79 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 灣26線（KZ26）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣26線KVAR | 11KV灣26線 KVAR | FEEDER |  |  |  |  | CDC | 80 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 灣26線（KZ26）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣26線A1 | 11KV灣26線 R相AMP | FEEDER |  |  |  |  | CDC | 81 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 灣26線（KZ26）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣26線A2 | 11KV灣26線 S相AMP | FEEDER |  |  |  |  | CDC | 82 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 灣26線（KZ26）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣26線A3 | 11KV灣26線 T相AMP | FEEDER |  |  |  |  | CDC | 83 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 灣26線（KZ26）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣26線A0 | 11KV灣26線 N相AMP | FEEDER |  |  |  |  | CDC | 84 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 灣26線（KZ26）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 85 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 灣27線（KZ27）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣27線KVAR | 11KV灣27線 KVAR | FEEDER |  |  |  |  | CDC | 86 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 灣27線（KZ27）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣27線A1 | 11KV灣27線 R相AMP | FEEDER |  |  |  |  | CDC | 87 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 灣27線（KZ27）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣27線A2 | 11KV灣27線 S相AMP | FEEDER |  |  |  |  | CDC | 88 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 灣27線（KZ27）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣27線A3 | 11KV灣27線 T相AMP | FEEDER |  |  |  |  | CDC | 89 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 灣27線（KZ27）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣27線A0 | 11KV灣27線 N相AMP | FEEDER |  |  |  |  | CDC | 90 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 灣27線（KZ27）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 91 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 灣28線（KZ28）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣28線KVAR | 11KV灣28線 KVAR | FEEDER |  |  |  |  | CDC | 92 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 灣28線（KZ28）R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣28線A1 | 11KV灣28線 R相AMP | FEEDER |  |  |  |  | CDC | 93 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 灣28線（KZ28）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣28線A2 | 11KV灣28線 S相AMP | FEEDER |  |  |  |  | CDC | 94 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 灣28線（KZ28）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣28線A3 | 11KV灣28線 T相AMP | FEEDER |  |  |  |  | CDC | 95 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 灣28線（KZ28）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣28線A0 | 11KV灣28線 N相AMP | FEEDER |  |  |  |  | CDC | 96 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 灣28線（KZ28）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 97 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 灣29線（KZ29）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣29線KVAR | 11KV灣29線 KVAR | FEEDER |  |  |  |  | CDC | 98 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 灣29線（KZ29）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣29線A1 | 11KV灣29線 R相AMP | FEEDER |  |  |  |  | CDC | 99 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 灣29線（KZ29）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣29線A2 | 11KV灣29線 S相AMP | FEEDER |  |  |  |  | CDC | 100 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 灣29線（KZ29）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣29線A3 | 11KV灣29線 T相AMP | FEEDER |  |  |  |  | CDC | 101 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 灣29線（KZ29）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣29線A0 | 11KV灣29線 N相AMP | FEEDER |  |  |  |  | CDC | 102 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 灣29線（KZ29）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 103 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 灣30線（KZ30）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣30線KVAR | 11KV灣30線 KVAR | FEEDER |  |  |  |  | CDC | 104 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 灣30線（KZ30）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣30線A1 | 11KV灣30線 R相AMP | FEEDER |  |  |  |  | CDC | 105 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 灣30線（KZ30）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣30線A2 | 11KV灣30線 S相AMP | FEEDER |  |  |  |  | CDC | 106 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 灣30線（KZ30）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣30線A3 | 11KV灣30線 T相AMP | FEEDER |  |  |  |  | CDC | 107 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 灣30線（KZ30）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.灣30線A0 | 11KV灣30線 N相AMP | FEEDER |  |  |  |  | CDC | 108 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 灣30線（KZ30）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 109 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 國光線（KZ21）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_PHA | 11KV國光線(KZ21) 相間RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 國光線（KZ21）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_GDA | 11KV國光線(KZ21) 接地RY | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0310 |  | 0062 | 1-33-06 |  | 1-3E | 國光線（KZ21）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_79UL | 11KV國光線(KZ21) 79RY U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | 國光線（KZ21）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_ADJ | 11KV國光線(KZ21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 大新線（KZ22）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_PHA | 11KV大新線(KZ22) 相間RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | 大新線（KZ22）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_GDA | 11KV大新線(KZ22) 接地RY | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0063 | 1-33-07 |  | 1-3F | 大新線（KZ22）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_79UL | 11KV大新線(KZ22) 79RY U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | 大新線（KZ22）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_ADJ | 11KV大新線(KZ22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | 美好線（KZ23）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_PHA | 11KV美好線(KZ23) 相間RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | 美好線（KZ23）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_GDA | 11KV美好線(KZ23) 接地RY | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0064 | 1-33-08 |  | 1-40 | 美好線（KZ23）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_79UL | 11KV美好線(KZ23) 79RY U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | 美好線（KZ23）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_ADJ | 11KV美好線(KZ23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 北灣線（KZ24）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_PHA | 11KV北灣線(KZ24) 相間RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 北灣線（KZ24）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_GDA | 11KV北灣線(KZ24) 接地RY | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0065 | 1-33-09 |  | 1-41 | 北灣線（KZ24）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_79UL | 11KV北灣線(KZ24) 79RY U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | 北灣線（KZ24）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_ADJ | 11KV北灣線(KZ24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 王厝線（KZ25）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_PHA | 11KV王厝線(KZ25) 相間RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 王厝線（KZ25）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_GDA | 11KV王厝線(KZ25) 接地RY | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0066 | 1-33-10 |  | 1-42 | 王厝線（KZ25）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_79UL | 11KV王厝線(KZ25) 79RY U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | 王厝線（KZ25）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_ADJ | 11KV王厝線(KZ25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | 灣26線（KZ26）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_PHA | 11KV灣26(KZ26) 相間RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | 灣26線（KZ26）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_GDA | 11KV灣26(KZ26) 接地RY | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0081 | 1-34-06 |  | 1-51 | 灣26線（KZ26）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_79UL | 11KV灣26(KZ26) 79RY U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | 灣26線（KZ26）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_ADJ | 11KV灣26(KZ26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0F-01 |  |  | 灣27線（KZ27）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_PHA | 11KV灣27(KZ27) 相間RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0122 |  |  | 1-0F-02 |  |  | 灣27線（KZ27）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_GDA | 11KV灣27(KZ27) 接地RY | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0082 | 1-34-07 |  | 1-52 | 灣27線（KZ27）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_79UL | 11KV灣27(KZ27) 79RY U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | 灣27線（KZ27）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_ADJ | 11KV灣27(KZ27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 灣28線（KZ28）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_PHA | 11KV灣28(KZ28) 相間RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | 灣28線（KZ28）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_GDA | 11KV灣28(KZ28) 接地RY | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0083 | 1-34-08 |  | 1-53 | 灣28線（KZ28）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_79UL | 11KV灣28(KZ28) 79RY U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | 灣28線（KZ28）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_ADJ | 11KV灣28(KZ28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 灣29線（KZ29）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_PHA | 11KV灣29(KZ29) 相間RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 灣29線（KZ29）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_GDA | 11KV灣29(KZ29) 接地RY | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0084 | 1-34-09 |  | 1-54 | 灣29線（KZ29）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_79UL | 11KV灣29(KZ29) 79RY U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | 灣29線（KZ29）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_ADJ | 11KV灣29(KZ29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 灣30線（KZ30）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_PHA | 11KV灣30(KZ30) 相間RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 灣30線（KZ30）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_GDA | 11KV灣30(KZ30) 接地RY | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0085 | 1-34-10 |  | 1-55 | 灣30線（KZ30）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_79UL | 11KV灣30(KZ30) 79RY U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | 灣30線（KZ30）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_ADJ | 11KV灣30(KZ30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-04 |  |  | 西灣線（KZ35）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_PHA | 11KV西灣線(KZ35) 相間RY | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 西灣線（KZ35）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_GDA | 11KV西灣線(KZ35) 接地RY | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0342 |  | 0100 | 1-35-06 |  | 1-64 | 西灣線（KZ35）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_79UL | 11KV西灣線(KZ35) 79RY U/L | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | 西灣線（KZ35）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_ADJ | 11KV西灣線(KZ35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | 文化線（KZ34）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_PHA | 11KV文化線(KZ34) 相間RY | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | 文化線（KZ34）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_GDA | 11KV文化線(KZ34) 接地RY | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0101 | 1-35-07 |  | 1-65 | 文化線（KZ34）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_79UL | 11KV文化線(KZ34) 79RY U/L | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | 文化線（KZ34）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_ADJ | 11KV文化線(KZ34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | 崑技線（KZ33）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_PHA | 11KV崑技線(KZ33) 相間RY | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | 崑技線（KZ33）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_GDA | 11KV崑技線(KZ33) 接地RY | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0102 | 1-35-08 |  | 1-66 | 崑技線（KZ33）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_79UL | 11KV崑技線(KZ33) 79RY U/L | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | 崑技線（KZ33）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_ADJ | 11KV崑技線(KZ33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | 南興線（KZ32）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_PHA | 11KV南興線(KZ32) 相間RY | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 南興線（KZ32）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_GDA | 11KV南興線(KZ32) 接地RY | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0103 | 1-35-09 |  | 1-67 | 南興線（KZ32）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_79UL | 11KV南興線(KZ32) 79RY U/L | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | 南興線（KZ32）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_ADJ | 11KV南興線(KZ32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | 市場線（KZ31）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_PHA | 11KV市場線(KZ31) 相間RY | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | 市場線（KZ31）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_GDA | 11KV市場線(KZ31) 接地RY | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0104 | 1-35-10 |  | 1-68 | 市場線（KZ31）79S |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_79UL | 11KV市場線(KZ31) 79RY U/L | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | 市場線（KZ31）LCO ADJ U/L |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_ADJ | 11KV市場線(KZ31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KZ21/T1 |  |  | 0095 |  | 0053 | 1-0B-07 |  | 1-35 | 國光線（KZ21）CB |  |  |  | aabb | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_CB | KZ21(11KV國光線) CB | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_DS | KZ21_DS (非取樣點) | FEEDER | [5 empty] | 171 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | ES | KZ21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_ES | KZ21_ES (非取樣點) | FEEDER | [5 empty] | 172 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KZ22/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | 大新線（KZ22）CB |  |  |  | aadb | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_CB | KZ22(11KV大新線) CB | FEEDER |  |  |  |  | CDC | 173 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_DS | KZ22_DS (非取樣點) | FEEDER | [5 empty] | 174 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | ES | KZ22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_ES | KZ22_ES (非取樣點) | FEEDER | [5 empty] | 175 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KZ23/T1 |  |  | 0101 |  | 0055 | 1-0C-05 |  | 1-37 | 美好線（KZ23）CB |  |  |  | aaeb | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_CB | KZ23(11KV美好線) CB | FEEDER |  |  |  |  | CDC | 176 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_DS | KZ23_DS (非取樣點) | FEEDER | [5 empty] | 177 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | ES | KZ23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_ES | KZ23_ES (非取樣點) | FEEDER | [5 empty] | 178 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KZ24/T1 |  |  | 0104 |  | 0056 | 1-0D-00 |  | 1-38 | 北灣線（KZ24）CB |  |  |  | aafb | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_CB | KZ24(11KV北灣線) CB | FEEDER |  |  |  |  | CDC | 179 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_DS | KZ24_DS (非取樣點) | FEEDER | [5 empty] | 180 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | ES | KZ24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_ES | KZ24_ES (非取樣點) | FEEDER | [5 empty] | 181 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | L/KZ25/T1 |  |  | 0107 |  | 0057 | 1-0D-03 |  | 1-39 | 王厝線（KZ25）CB |  |  |  | aagb | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_CB | KZ25(11KV王厝線) CB | FEEDER |  |  |  |  | CDC | 182 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_DS | KZ25_DS (非取樣點) | FEEDER | [5 empty] | 183 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | ES | KZ25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_ES | KZ25_ES (非取樣點) | FEEDER | [5 empty] | 184 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/KZ26/T1 |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | 灣26線（KZ26）CB |  |  |  | abab | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_CB | KZ26(11KV灣26) CB | FEEDER |  |  |  |  | CDC | 185 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_DS | KZ26_DS (非取樣點) | FEEDER | [5 empty] | 186 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | ES | KZ26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_ES | KZ26_ES (非取樣點) | FEEDER | [5 empty] | 187 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/KZ27/T1 |  |  | 0120 |  | 0073 | 1-0F-00 |  | 1-49 | 灣27線（KZ27）CB |  |  |  | abbb | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_CB | KZ27(11KV灣27) CB | FEEDER |  |  |  |  | CDC | 188 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_DS | KZ27_DS (非取樣點) | FEEDER | [5 empty] | 189 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | ES | KZ27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_ES | KZ27_ES (非取樣點) | FEEDER | [5 empty] | 190 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | L/KZ28/T1 |  |  | 0123 |  | 0074 | 1-0F-03 |  | 1-4A | 灣28線（KZ28）CB |  |  |  | abcb | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_CB | KZ28(11KV灣28) CB | FEEDER |  |  |  |  | CDC | 191 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_DS | KZ28_DS (非取樣點) | FEEDER | [5 empty] | 192 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | ES | KZ28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_ES | KZ28_ES (非取樣點) | FEEDER | [5 empty] | 193 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | L/KZ29/T1 |  |  | 0126 |  | 0075 | 1-0F-06 |  | 1-4B | 灣29線（KZ29）CB |  |  |  | acbb | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_CB | KZ29(11KV灣29) CB | FEEDER |  |  |  |  | CDC | 194 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_DS | KZ29_DS (非取樣點) | FEEDER | [5 empty] | 195 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | ES | KZ29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_ES | KZ29_ES (非取樣點) | FEEDER | [5 empty] | 196 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | L/KZ30/T1 |  |  | 0129 |  | 0076 | 1-10-01 |  | 1-4C | 灣30線（KZ30）CB |  |  |  | accb | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_CB | KZ30(11KV灣30) CB | FEEDER |  |  |  |  | CDC | 197 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_DS | KZ30_DS (非取樣點) | FEEDER | [5 empty] | 198 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | ES | KZ30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_ES | KZ30_ES (非取樣點) | FEEDER | [5 empty] | 199 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KZ35/T1 |  |  | 0139 |  | 0092 | 1-11-03 |  | 1-5C | 西灣線（KZ35）CB |  |  |  | adab | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_CB | KZ35(11KV西灣線) CB | FEEDER |  |  |  |  | CDC | 200 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_DS | KZ35_DS (非取樣點) | FEEDER | [5 empty] | 201 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | ES | KZ35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_ES | KZ35_ES (非取樣點) | FEEDER | [5 empty] | 202 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KZ34/T1 |  |  | 0142 |  | 0093 | 1-11-06 |  | 1-5D | 文化線（KZ34）CB |  |  |  | adbb | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_CB | KZ34(11KV文化線) CB | FEEDER |  |  |  |  | CDC | 203 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_DS | KZ34_DS (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | ES | KZ34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_ES | KZ34_ES (非取樣點) | FEEDER | [5 empty] | 205 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KZ33/T1 |  |  | 0145 |  | 0094 | 1-12-01 |  | 1-5E | 崑技線（KZ33）CB |  |  |  | adcb | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_CB | KZ33(11KV崑技線) CB | FEEDER |  |  |  |  | CDC | 206 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_DS | KZ33_DS (非取樣點) | FEEDER | [5 empty] | 207 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | ES | KZ33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_ES | KZ33_ES (非取樣點) | FEEDER | [5 empty] | 208 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KZ32/T1 |  |  | 0148 |  | 0095 | 1-12-04 |  | 1-5F | 南興線（KZ32）CB |  |  |  | adeb | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_CB | KZ32(11KV南興線) CB | FEEDER |  |  |  |  | CDC | 209 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_DS | KZ32_DS (非取樣點) | FEEDER | [5 empty] | 210 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | ES | KZ32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_ES | KZ32_ES (非取樣點) | FEEDER | [5 empty] | 211 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KZ31/T1 |  |  | 0151 |  | 0096 | 1-12-07 |  | 1-60 | 市場線（KZ31）CB |  |  |  | adfb | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_CB | KZ31(11KV市場線) CB | FEEDER |  |  |  |  | CDC | 212 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_DS | KZ31_DS (非取樣點) | FEEDER | [5 empty] | 213 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | ES | KZ31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_ES | KZ31_ES (非取樣點) | FEEDER | [5 empty] | 214 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | TIE（600）R 相電流 |  |  | A_-1200_1200(-2000_2000) |  | B2/S66_A1 | [8 empty] | 大灣SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 215 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R | #1-#2MA | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1-#2MA TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 216 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S | #1-#2MA | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1-#2MA TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 217 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T | #1-#2MA | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1-#2MA TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 218 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R | #2MB-#3 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2MB-#3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 219 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S | #2MB-#3 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2MB-#3 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 220 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T | #2MB-#3 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2MB-#3 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 221 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | CouplerA | B/1BUS | B/2BUS |  |  | 0034 |  | 0007 | 1-04-02 |  | 1-07 | TIE（600）CB |  |  |  | aafz | B2/S66_A1 | [8 empty] | 大灣SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 222 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB | #1-#2MA |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2ABUS |  |  | 0113 |  | 0058 | 1-0E-01 |  | 1-3A | #1-#2MA TIE CB |  |  |  | zzzz | B2/S66_D1 | [8 empty] | 大灣SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 223 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A | #1-#2MA |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #1-#2MA TIE 51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 224 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA | #1-#2MA |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1-#2MA TIE 51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 225 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB | #2MB-#3 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BBUS | B/3BUS |  |  | 0135 |  | 0077 | 1-10-07 |  | 1-4D | #2MB-#3 TIE CB |  |  |  | zzzz | B2/S66_D1 | [8 empty] | 大灣SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 226 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A | #2MB-#3 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | #2MB-#3 TIE 51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 227 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA | #2MB-#3 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2MB-#3 TIE 51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 228 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | 433 | 0042 | 1-3B-00 | 1-3B-01 | 1-2A | 600 TIE（601）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 229 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0043 | 1-3B-02 | 1-3B-03 | 1-2B | 600 TIE（602）ABS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 230 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | #1-#2MA(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 231 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | #2MB-#3(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 232 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 233 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 234 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 235 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 236 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 237 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 238 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 239 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 240 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 241 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 242 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 243 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 244 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 245 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 246 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 247 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 248 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 249 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0059 | 1-9B |  | 1-3B | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 250 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1 TR MWH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 251 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 252 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 253 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 254 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 255 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2 TR MWH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 256 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 257 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 258 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 259 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 260 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3 TR MWH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 261 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3 TR MVARH(+) |  |  |  |  | B1/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 262 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/1MTR |  | 0001 |  | 0050 | 1-00-01 |  | 1-32 | #1TR 一次（750）CB |  |  |  | aabb | B3/S66_D1 | [8 empty] | 大灣SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 263 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 264 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 265 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/2MTR |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | #2TR 一次（760）CB |  |  |  | aaeb | B3/S66_D1 | [8 empty] | 大灣SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 266 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 267 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 268 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/3MTR |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | #3TR 一次（770）CB |  |  |  | aahb | B3/S66_D1 | [8 empty] | 大灣SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 269 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 270 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S66_D1 | [8 empty] | 大灣SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 271 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0007 |  | 0051 | 1-00-07 |  | 1-33 | #1TR 二次（#1MT）CB |  |  |  | aaca | B2/S66_D1 | [8 empty] | 大灣SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 272 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABUS | T/2MTR |  |  | 0016 |  | 0069 | 1-02-00 |  | 1-45 | #2TR 二次（A）CB |  |  |  | abda | B2/S66_D1 | [8 empty] | 大灣SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 273 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M2B | #2MTR(M2B) |  | CB |  | B2,B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | T/2MTR |  |  | 0017 |  | 0070 | 1-02-01 |  | 1-46 | #2TR 二次（B）CB |  |  |  | acaa | B2/S66_D1 | [8 empty] | 大灣SS.2MB_CB | 2MB(#2MTR) CB | DTR |  |  |  |  | CDC | 274 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0028 |  | 0089 | 1-03-04 |  | 1-59 | #3TR 二次（#3MT）CB |  |  |  | adda | B2/S66_D1 | [8 empty] | 大灣SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 275 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | #1TR 一次（750）51 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 276 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次（750）51N RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 277 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 51Z RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 278 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 87 RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 279 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 280 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  | 0067 | 1-0E-04 |  | 1-43 | #750 #760 81 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#1MTR_81A/S | #750 81RY A/S | DTR |  |  |  |  | CDC | 281 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | #2TR 一次（760）51 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 282 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | #2TR 一次（760）51N RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 283 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 51Z RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 284 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 87 RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 285 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2TR 87 LS1S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 286 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  | 0086 | 1-11-02 |  | 1-56 | 81 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#2MTR_81A/S | #760 81RY A/S | DTR |  |  |  |  | CDC | 287 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | #3TR 一次（770）51 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 288 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | #3TR 一次（770）51N RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 289 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3TR 51Z RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 290 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3TR 87 RY |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 291 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3TR 87 LS1S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 292 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  | 0105 | 1-13-05 |  | 1-69 | 81 RY |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.#3MTR_81A/S | #770 81RY A/S | DTR |  |  |  |  | CDC | 293 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次（#1MT）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 294 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 295 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 296 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 297 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0060 | 1-33-05 |  | 1-3C | #1TR OLTC A/M |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 298 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 二次（A）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 299 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51A |  | B2,B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | #2TR 二次（B）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR |  |  |  |  | CDC | 300 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 301 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 302 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 303 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2TR OLTC A/M |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 304 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #3TR 二次（#3MT）51 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 305 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0336 |  |  | 1-35-00 |  |  | #3TR 重故障 |  |  |  | a | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 306 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3TR 輕故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 307 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3TR OLTC R/L |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 308 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3TR OLTC A/M |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 309 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0368 | 369 | 0044 | 1-37-00 | 1-37-01 | 1-2C | #1TR（751）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.751_DS | 751(#1MTR) DS | DTR |  |  |  |  | CDC | 310 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0370 | 371 | 0045 | 1-37-02 | 1-37-03 | 1-2D | #1TR（752）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.752_DS | 752(#1MTR) DS | DTR |  |  |  |  | CDC | 311 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0372 | 373 | 0046 | 1-37-04 | 1-37-05 | 1-2E | #2TR（761）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 312 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0374 | 375 | 0047 | 1-37-06 | 1-37-07 | 1-2F | #2TR（762）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 313 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0376 | 377 | 0048 | 1-37-08 | 1-37-09 | 1-30 | #3TR（771）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.771_DS | 771(#3MTR) DS | DTR |  |  |  |  | CDC | 314 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0378 | 379 | 0049 | 1-37-10 | 1-37-11 | 1-31 | #3TR（772）ABS |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.772_DS | 772(#3MTR) DS | DTR |  |  |  |  | CDC | 315 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 316 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 機械保護動作(96PA) |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 317 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 318 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #1TR 冷卻電源故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 319 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 320 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | ES | 2MA_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 321 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | M2B | #2MTR(M2B) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 322 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | M2B | #2MTR(M2B) |  | ES | 2MB_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 323 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 324 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 325 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0333 |  |  | 1-34-13 |  |  | #2TR 冷卻電源故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 326 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 327 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3TR 機械保護動作(96PA) |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR |  |  |  |  | CDC | 328 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3TR OLTC 遲滯 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 329 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0367 |  |  | 1-36-15 |  |  | #3TR 冷卻電源故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 330 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | C/1SC |  |  | 0110 |  | 0052 | 1-0D-06 |  | 1-34 | #1 11KV SC CB |  |  |  | aaab | B2/S66_D1 | [8 empty] | 大灣SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 331 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0315 |  | 0061 | 1-33-11 |  | 1-3D | #1SC Q-CTL A/M |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 332 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 333 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BBUS | C/2SC |  |  | 0132 |  | 0071 | 1-10-04 |  | 1-47 | #2 11KV SC CB |  |  |  | acdb | B2/S66_D1 | [8 empty] | 大灣SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 334 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0331 |  | 0080 | 1-34-11 |  | 1-50 | #2SC Q-CTL A/M |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 335 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 336 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | C/3SC |  |  | 0154 |  | 0091 | 1-13-02 |  | 1-5B | #3 11KV SC CB |  |  |  | adgb | B2/S66_D1 | [8 empty] | 大灣SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 337 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0347 |  | 0099 | 1-35-11 |  | 1-63 | #3SC Q-CTL A/M |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 338 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 339 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 340 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 341 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 342 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 343 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | #3SC 51,51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 344 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | #3SC 27,59 RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 345 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 346 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 347 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 348 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 349 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 350 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 351 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 352 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 353 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 354 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCL4 |  | B2 | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 國光線 (F1) 瓦 |  |  |  |  | B3/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 355 | AI_ADC | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 0 |  | RTU | RTU |  | ADCH4 |  | B2 | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 大新線 (F2) 瓦 |  |  |  |  | B3/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 356 | AI_ADC | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 大灣SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0106 | 1-30-06 |  | 1-6A | 開關場照明 C/T |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1S |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2S |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 所內用電警報 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.所內電源警報 | 所內電源警報 | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電欠壓 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 372 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 373 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 374 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 375 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 1-35-12 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 376 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0349 |  |  | 1-35-13 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 377 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0350 |  |  | 1-35-14 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 378 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0351 |  |  | 1-35-15 |  |  | 博碼調變器故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 379 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S66_D1 | [8 empty] | 大灣SS.火災警報(1) | 火警 | OTHER |  |  |  |  | CDC | 380 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 381 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 382 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | ComPoint |  |  | FDR_60A | SC_60A | Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | SC 60 A |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.11KV_SC_60A | 11KV電容器組 60RY | OTHER |  |  |  |  | CDC | 383 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M2A | #2MTR(M2A) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2TR 二次（A）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.#2M(A)_GDA | #2MA GDA | OTHER |  |  |  |  | CDC | 384 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2TR 二次（B）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.#2M(B)_GDA | #2MB GDA | OTHER |  |  |  |  | CDC | 385 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 386 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0107 | 1-30-07 |  | 1-6B | 開關場照明 A/M |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 387 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 388 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 389 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-32-10 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 390 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 緊急發電機故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.緊急發電機啟動 | 緊急發電機啟動 | OTHER |  |  |  |  | CDC | 391 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | FDR_60A | #1SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | #1 SC 60 A |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER |  |  |  |  | CDC | 392 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | FDR_60A | #2SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | #2 SC 60 A |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_#2SC_60A | 11KV #2SC 60A | OTHER |  |  |  |  | CDC | 393 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | FDR_60A | #3SC_60A | B3,Element | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | #3 SC 60 A |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER |  |  |  |  | CDC | 394 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | CO2故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.CO2故障 | CO2故障 | OTHER |  |  |  |  | CDC | 395 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | CO2警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.CO2警報 | CO2警報 | OTHER |  |  |  |  | CDC | 396 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0161 |  | 0108 | 1-14-01 |  | 1-6C | 全所故障指示器復歸點 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 397 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 600CB-67-1 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | TIE |  |  |  |  | CDC | 398 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 600CB-67N-1 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | TIE |  |  |  |  | CDC | 399 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 600CB -67-2 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | TIE |  |  |  |  | CDC | 400 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 600CB-67N-2 |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | TIE |  |  |  |  | CDC | 401 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | [13 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 402 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 403 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 404 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 405 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 大灣永康二路（640） 87 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.640_87A | 大灣永康二路(640) 87RY | LINE69 |  |  |  |  | CDC | 406 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 大灣永康二路（640） 87RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.640_87UL | 大灣永康二路(640) 87RY U/L | LINE69 |  |  |  |  | CDC | 407 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 台南大灣二路（720） 87 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.720_87A | 台南大灣二路(720) 87RY | LINE69 |  |  |  |  | CDC | 408 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0013 | 1-32-08 |  | 1-0D | 台南大灣二路（720） 87RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.720_87UL | 台南大灣二路(720) 87RY U/L | LINE69 |  |  |  |  | CDC | 409 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 南興線（KZ32）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.南興線A0 | 11KV南興線 N相AMP | FEEDER |  |  |  |  | CDC | 410 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 美好線（KZ23）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.美好線KVAR | 11KV美好線 KVAR | FEEDER |  |  |  |  | CDC | 411 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 美好線（KZ23）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.美好線A1 | 11KV美好線 R相AMP | FEEDER |  |  |  |  | CDC | 412 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 美好線（KZ23）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.美好線A2 | 11KV美好線 S相AMP | FEEDER |  |  |  |  | CDC | 413 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 美好線（KZ23）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.美好線A3 | 11KV美好線 T相AMP | FEEDER |  |  |  |  | CDC | 414 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 美好線（KZ23）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.美好線A0 | 11KV美好線 N相AMP | FEEDER |  |  |  |  | CDC | 415 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 國光線（KZ21）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.國光線KVAR | 11KV國光線 KVAR | FEEDER |  |  |  |  | CDC | 416 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 國光線（KZ21）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.國光線A1 | 11KV國光線 R相AMP | FEEDER |  |  |  |  | CDC | 417 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 國光線（KZ21）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.國光線A2 | 11KV國光線 S相AMP | FEEDER |  |  |  |  | CDC | 418 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 國光線（KZ21）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.國光線A3 | 11KV國光線 T相AMP | FEEDER |  |  |  |  | CDC | 419 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 國光線（KZ21）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.國光線A0 | 11KV國光線 N相AMP | FEEDER |  |  |  |  | CDC | 420 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 崑技線（KZ33）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.崑技線KVAR | 11KV崑技線 KVAR | FEEDER |  |  |  |  | CDC | 421 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 崑技線（KZ33）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.崑技線A1 | 11KV崑技線 R相AMP | FEEDER |  |  |  |  | CDC | 422 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 崑技線（KZ33）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.崑技線A2 | 11KV崑技線 S相AMP | FEEDER |  |  |  |  | CDC | 423 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 崑技線（KZ33）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.崑技線A3 | 11KV崑技線 T相AMP | FEEDER |  |  |  |  | CDC | 424 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 崑技線（KZ33）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 | [8 empty] | 大灣SS.崑技線A0 | 11KV崑技線 N相AMP | FEEDER |  |  |  |  | CDC | 425 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | DC 電壓 |  |  | DCVolt_-150_150(-2000_2000) |  | B3/S66_D1 | [8 empty] | 大灣SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 426 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_125 | 135 | 136 | 140 | 150 | 0.2 | 120 | 119 | 100 | -150 | 0.1 | 0.01 | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 1BUS | #1BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0168 |  |  | 2-A8 |  |  | #1 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S66_D1 | [8 empty] | 大灣SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | [5 empty] | 427 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0170 |  |  | 2-AA |  |  | #2A TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S66_D1 | [8 empty] | 大灣SS.11S1#2ABUS_KV | 11S1 #2ABUS KV | BUS | [5 empty] | 428 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0172 |  |  | 2-AC |  |  | #2B TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S66_D1 | [8 empty] | 大灣SS.11S1#2BBUS_KV | 11S1 #2BBUS KV | BUS | [5 empty] | 429 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 3BUS | #3BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0174 |  |  | 2-AE |  |  | #3 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S66_D1 | [8 empty] | 大灣SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | [5 empty] | 430 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 1BUS | #1BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | #1 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S66_D1 | [8 empty] | 大灣SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | [5 empty] | 431 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0171 |  |  | 2-AB |  |  | #2A TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S66_D1 | [8 empty] | 大灣SS.11T1#2ABUS_KV | 11T1 #2ABUS KV | BUS | [5 empty] | 432 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0173 |  |  | 2-AD |  |  | #2B TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S66_D1 | [8 empty] | 大灣SS.11T1#2BBUS_KV | 11T1 #2BBUS KV | BUS | [5 empty] | 433 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 3BUS | #3BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0175 |  |  | 2-AF |  |  | #3 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S66_D1 | [8 empty] | 大灣SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | [5 empty] | 434 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | C/1SC |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 69SC CB |  |  |  | aacb | B2/S66_A1 | [8 empty] | 大灣SS.810_CB | 810(69KV #1SC) CB | SC | [5 empty] | 435 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0380 | 381 | 0040 | 1-37-12 | 1-37-13 | 1-28 | 69KV SC 1AS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.811_DS | 811(69KV #1SC) DS | SC | [5 empty] | 436 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0382 | 383 | 0041 | 1-37-14 | 1-37-15 | 1-29 | 69KV SC 2AS |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.812_DS | 812(69KV #1SC) DS | SC | [5 empty] | 437 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  | INSERT | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 69SC 51,51N RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.810_SCA | 69KV #1SC 51,51N RY | SC | [5 empty] | 438 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  | INSERT | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 69SC 27,59 RY |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.810_OUVA | 69KV #1SC 27,59RY | SC | [5 empty] | 439 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1DTR 63Q |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 440 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1DTR 96B1 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 441 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1DTR 96B2 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 442 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1DTR 96D |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 443 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1DTR 96P |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 444 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2DTR 63Q |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | [5 empty] | 445 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2DTR 96B1 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | [5 empty] | 446 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2DTR 96B2 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | [5 empty] | 447 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2DTR 96D |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | [5 empty] | 448 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2DTR 96P |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | [5 empty] | 449 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | #3DTR 63Q |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | [5 empty] | 450 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | #3DTR 96B1 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | [5 empty] | 451 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | #3DTR 96B2 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | [5 empty] | 452 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | #3DTR 96D |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | [5 empty] | 453 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | #3DTR 96P |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | [5 empty] | 454 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | 國光線（KZ21）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ21_LOA | 國光線 復閉失敗閉鎖 | OTHER | [5 empty] | 455 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | 大新線（KZ22）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ22_LOA | 大新線 復閉失敗閉鎖 | OTHER | [5 empty] | 456 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | 美好線（KZ23）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ23_LOA | 美好線 復閉失敗閉鎖 | OTHER | [5 empty] | 457 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | 北灣線（KZ24）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ24_LOA | 北灣線 復閉失敗閉鎖 | OTHER | [5 empty] | 458 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | 王厝線（KZ25）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ25_LOA | 王厝線 復閉失敗閉鎖 | OTHER | [5 empty] | 459 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 灣26線（KZ26）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ26_LOA | 灣26線 復閉失敗閉鎖 | OTHER | [5 empty] | 460 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 灣27線（KZ27）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ27_LOA | 灣27線 復閉失敗閉鎖 | OTHER | [5 empty] | 461 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 灣28線（KZ28）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ28_LOA | 灣28線 復閉失敗閉鎖 | OTHER | [5 empty] | 462 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 灣29線（KZ29）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ29_LOA | 灣29線 復閉失敗閉鎖 | OTHER | [5 empty] | 463 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 灣30線（KZ30）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ30_LOA | 灣30線 復閉失敗閉鎖 | OTHER | [5 empty] | 464 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0506 |  |  | 1-3F-10 |  |  | 市場線（KZ31）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ31_LOA | 市場線 復閉失敗閉鎖 | OTHER | [5 empty] | 465 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-3F-09 |  |  | 南興線（KZ32）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ32_LOA | 南興線 復閉失敗閉鎖 | OTHER | [5 empty] | 466 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0504 |  |  | 1-3F-08 |  |  | 崑技線（KZ33）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ33_LOA | 崑技線 復閉失敗閉鎖 | OTHER | [5 empty] | 467 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0503 |  |  | 1-3F-07 |  |  | 文化線（KZ34）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ34_LOA | 文化線 復閉失敗閉鎖 | OTHER | [5 empty] | 468 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | 西灣線（KZ35）LOA |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.KZ35_LOA | 西灣線 復閉失敗閉鎖 | OTHER | [5 empty] | 469 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | #3TR 二次（#3MT）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.#3_MAIN_51NA | #3MCB GDA | OTHER | [5 empty] | 470 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 二次（#1MT）51N RY |  |  |  |  | B2/S66_D1 | [8 empty] | 大灣SS.#1_MAIN_51NA | #1MCB GDA | OTHER | [5 empty] | 471 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | StaDev | 所內設施 |  | 1A3U_L | CO2 使用/閉鎖 | INSERT | Status | USE_LOCK動作1 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0511 |  |  | 1-3F-15 |  |  | CO2 使用/閉鎖 |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.CO2_UL | CO2 UL | OTHER | [5 empty] | 472 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 473 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #1DTR 86A |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 474 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 475 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2DTR 51ZLS |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | [5 empty] | 476 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | #2DTR 86A |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 477 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 478 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3DTR 51ZLS |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | [5 empty] | 479 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | #3DTR 86A |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 480 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3DTR 87LS2S |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | [5 empty] | 481 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS |  |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S66_D1 | [8 empty] | 大灣SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 482 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0443 |  | 0110 | 1-3B-11 |  | 1-6E | 69KV #1BUS RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER | [5 empty] | 483 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | #2BUS | #2BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0444 |  | 0111 | 1-3B-12 |  | 1-6F | 69KV #2BUS RY U/L |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER | [5 empty] | 484 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | 12B_CTFA | 69KV BUS CT迴路故障 | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0446 |  |  | 1-3B-14 |  |  | 69KV BUS RY CTFA |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 485 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | ComPoint |  |  | BUS_RYFA | 69KV BUS IED故障 | INSERT | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0445 |  |  | 1-3B-13 |  |  | 69KV BUS RY RYFA |  |  |  |  | B3/S66_D1 | [8 empty] | 大灣SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER | [5 empty] | 486 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | RYFA | 69KV TIE IED故障 | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0447 |  |  | 1-3B-15 |  |  | 69KV TIE RYFA |  |  |  |  | B2/S66_A1 | [8 empty] | 大灣SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER | [5 empty] | 487 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 國光線（KZ21）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 488 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 大新線（KZ22）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.大新線KVAR | 11KV大新線 KVAR | FEEDER |  |  |  |  | CDC | 489 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 大新線（KZ22）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.大新線A1 | 11KV大新線 R相AMP | FEEDER |  |  |  |  | CDC | 490 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 大新線（KZ22）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.大新線A2 | 11KV大新線 S相AMP | FEEDER |  |  |  |  | CDC | 491 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 大新線（KZ22）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.大新線A3 | 11KV大新線 T相AMP | FEEDER |  |  |  |  | CDC | 492 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 大新線（KZ22）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.大新線A0 | 11KV大新線 N相AMP | FEEDER |  |  |  |  | CDC | 493 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 大新線（KZ22）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 494 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 美好線（KZ23）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 495 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 北灣線（KZ24）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.北灣線KVAR | 11KV北灣線 KVAR | FEEDER |  |  |  |  | CDC | 496 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 北灣線（KZ24）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.北灣線A1 | 11KV北灣線 R相AMP | FEEDER |  |  |  |  | CDC | 497 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 北灣線（KZ24）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.北灣線A2 | 11KV北灣線 S相AMP | FEEDER |  |  |  |  | CDC | 498 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 北灣線（KZ24）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.北灣線A3 | 11KV北灣線 T相AMP | FEEDER |  |  |  |  | CDC | 499 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 北灣線（KZ24）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.北灣線A0 | 11KV北灣線 N相AMP | FEEDER |  |  |  |  | CDC | 500 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 北灣線（KZ24）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 501 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 王厝線（KZ25）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.王厝線KVAR | 11KV王厝線 KVAR | FEEDER |  |  |  |  | CDC | 502 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 王厝線（KZ25）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.王厝線A1 | 11KV王厝線 R相AMP | FEEDER |  |  |  |  | CDC | 503 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 王厝線（KZ25）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.王厝線A2 | 11KV王厝線 S相AMP | FEEDER |  |  |  |  | CDC | 504 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 王厝線（KZ25）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.王厝線A3 | 11KV王厝線 T相AMP | FEEDER |  |  |  |  | CDC | 505 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 王厝線（KZ25）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.王厝線A0 | 11KV王厝線 N相AMP | FEEDER |  |  |  |  | CDC | 506 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 王厝線（KZ25）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 507 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 西灣線（KZ35）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.西灣線KVAR | 11KV西灣線 KVAR | FEEDER |  |  |  |  | CDC | 508 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 西灣線（KZ35）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.西灣線A1 | 11KV西灣線 R相AMP | FEEDER |  |  |  |  | CDC | 509 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 西灣線（KZ35）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.西灣線A2 | 11KV西灣線 S相AMP | FEEDER |  |  |  |  | CDC | 510 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 西灣線（KZ35）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.西灣線A3 | 11KV西灣線 T相AMP | FEEDER |  |  |  |  | CDC | 511 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 西灣線（KZ35）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.西灣線A0 | 11KV西灣線 N相AMP | FEEDER |  |  |  |  | CDC | 512 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | 西灣線（KZ35）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 513 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 文化線（KZ34）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.文化線KVAR | 11KV文化線 KVAR | FEEDER |  |  |  |  | CDC | 514 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 文化線（KZ34）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.文化線A1 | 11KV文化線 R相AMP | FEEDER |  |  |  |  | CDC | 515 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 文化線（KZ34）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.文化線A2 | 11KV文化線 S相AMP | FEEDER |  |  |  |  | CDC | 516 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 文化線（KZ34）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.文化線A3 | 11KV文化線 T相AMP | FEEDER |  |  |  |  | CDC | 517 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 文化線（KZ34）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.文化線A0 | 11KV文化線 N相AMP | FEEDER |  |  |  |  | CDC | 518 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | 文化線（KZ34）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 519 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | 崑技線（KZ33）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 520 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 南興線（KZ32）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.南興線KVAR | 11KV南興線 KVAR | FEEDER |  |  |  |  | CDC | 521 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 南興線（KZ32）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.南興線A1 | 11KV南興線 R相AMP | FEEDER |  |  |  |  | CDC | 522 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 南興線（KZ32）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.南興線A2 | 11KV南興線 S相AMP | FEEDER |  |  |  |  | CDC | 523 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 南興線（KZ32）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.南興線A3 | 11KV南興線 T相AMP | FEEDER |  |  |  |  | CDC | 524 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | 南興線（KZ32）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 525 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 市場線（KZ31）乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.市場線KVAR | 11KV市場線 KVAR | FEEDER |  |  |  |  | CDC | 526 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 市場線（KZ31）R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.市場線A1 | 11KV市場線 R相AMP | FEEDER |  |  |  |  | CDC | 527 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 市場線（KZ31）S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.市場線A2 | 11KV市場線 S相AMP | FEEDER |  |  |  |  | CDC | 528 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 市場線（KZ31）T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.市場線A3 | 11KV市場線 T相AMP | FEEDER |  |  |  |  | CDC | 529 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 市場線（KZ31）N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S66_D1 |  |  | 600 | [5 empty] | 大灣SS.市場線A0 | 11KV市場線 N相AMP | FEEDER |  |  |  |  | CDC | 530 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | 市場線（KZ31）KWH(+) |  |  |  |  | B2/S66_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 531 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | E1 | 810E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.810E | 810E (非取樣點) | SC | [5 empty] | 532 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.810BE | 810BE(非取樣點) | OTHER | [5 empty] | 533 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.810LE | 810LE(非取樣點) | OTHER | [5 empty] | 534 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.601E | 601E (非取樣點) | TIE | [5 empty] | 535 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S66_A1 | [8 empty] | 大灣SS.602E | 602E (非取樣點) | TIE | [5 empty] | 536 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 537 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 538 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | 3AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值3 |  | Y |  | AI | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 539 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 540 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S66 | 大灣SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S66_D1 | [8 empty] | 大灣SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 541 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S66 | 大灣SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S66_D1 | [12 empty] | 大灣SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S66/69/1BUS/V; OPRD2: S66/69/2BUS/V
S66 | 大灣SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S66_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S66/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S66 | 大灣SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S66_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_8 | OPRD1: S66/11/M1/MW; OPRD2: S66/11/M2A/MW; OPRD3: S66/11/M3/MW; OPRD4: S66/69/620/MW; OPRD5: S66/69/630/MW; OPRD6: S66/69/640/MW; OPRD7: S66/69/670/MW; OPRD8: S66/69/720/MW
S66 | 大灣SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S66_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S66/0/CalcPoint/OPRN2_MW
S66 | 大灣SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S66_D1 | [17 empty] | none
S66 | 大灣SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S66_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S66/0/CalcPoint/OPRN1; OPRD2: S66/0/CalcPoint/OPRN2; OPRD3: S66/0/CalcPoint/PRFL_UL
S66 | 大灣SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S66_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S66/11/M1/MW; OPRD2: S66/11/M1/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S66_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S66/11/M2A/MW; OPRD2: S66/11/M2A/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S66_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S66/11/M3/MW; OPRD2: S66/11/M3/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS | 69 | 69kV | 620 | 後甲～大灣線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S66_A1 | [12 empty] | 大灣SS.620_AMP | 後甲大灣線 AMP | LINE69 | AMP_CAL | C12R0876 | amp_cal | OPRD1: S66/69/620/MW; OPRD2: S66/69/620/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS | 69 | 69kV | 630 | 大灣～永康一路(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S66_A1 | [12 empty] | 大灣SS.630_AMP | 大灣永康一路 AMP | LINE69 | AMP_CAL | C12R0800 | amp_cal | OPRD1: S66/69/630/MW; OPRD2: S66/69/630/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS | 69 | 69kV | 640 | 大灣～永康二路(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S66_A1 | [12 empty] | 大灣SS.640_AMP | 大灣永康二路 AMP | LINE69 | AMP_CAL | C12R0899 | amp_cal | OPRD1: S66/69/640/MW; OPRD2: S66/69/640/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS | 69 | 69kV | 670 | 台南～大灣一路(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S66_A1 | [12 empty] | 大灣SS.670_AMP | 台南大灣一路 AMP | LINE69 | AMP_CAL | C12R0800 | amp_cal | OPRD1: S66/69/670/MW; OPRD2: S66/69/670/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS | 69 | 69kV | 720 | 台南～大灣二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S66_A1 | [12 empty] | 大灣SS.720_AMP | 台南大灣二路 AMP | LINE69 | AMP_CAL | C12R0899 | amp_cal | OPRD1: S66/69/720/MW; OPRD2: S66/69/720/MVAR; OPRD3: S66/0/CalcPoint/Vbs2
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S66_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大灣SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S66/11/M1/MW; OPRD2: S66/11/M1/MVAR
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S66_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大灣SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S66/11/M2A/MW; OPRD2: S66/11/M2A/MVAR
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S66_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 大灣SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S66/11/M3/MW; OPRD2: S66/11/M3/MVAR
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S66_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S66//1MTR/MVA; OPRD2: 0
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S66_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S66//2MTR/MVA; OPRD2: 0
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S66_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S66//3MTR/MVA; OPRD2: 0
S66 | 大灣SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S66_D1 | [12 empty] | 大灣SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S66/11/M1/MW; OPRD2: S66/11/M1/MVAR
S66 | 大灣SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S66_D1 | [12 empty] | 大灣SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S66/11/M2A/MW; OPRD2: S66/11/M2A/MVAR
S66 | 大灣SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S66_D1 | [12 empty] | 大灣SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S66/11/M3/MW; OPRD2: S66/11/M3/MVAR
S66 | 大灣SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S66_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S66//1MTR/SupLocal; OPRD2: S66//1MTR/Tap Chan; OPRD3: NULL
S66 | 大灣SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S66_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S66//2MTR/SupLocal; OPRD2: S66//2MTR/Tap Chan; OPRD3: NULL
S66 | 大灣SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S66_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S66//3MTR/SupLocal; OPRD2: S66//3MTR/Tap Chan; OPRD3: NULL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ21/I_R; OPRD3: S66/11/KZ21/I_S; OPRD4: S66/11/KZ21/I_T
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ22/I_R; OPRD3: S66/11/KZ22/I_S; OPRD4: S66/11/KZ22/I_T
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ23/I_R; OPRD3: S66/11/KZ23/I_S; OPRD4: S66/11/KZ23/I_T
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ24/I_R; OPRD3: S66/11/KZ24/I_S; OPRD4: S66/11/KZ24/I_T
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ25/I_R; OPRD3: S66/11/KZ25/I_S; OPRD4: S66/11/KZ25/I_T
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ26/I_R; OPRD3: S66/11/KZ26/I_S; OPRD4: S66/11/KZ26/I_T
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ27/I_R; OPRD3: S66/11/KZ27/I_S; OPRD4: S66/11/KZ27/I_T
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ28/I_R; OPRD3: S66/11/KZ28/I_S; OPRD4: S66/11/KZ28/I_T
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ29/I_R; OPRD3: S66/11/KZ29/I_S; OPRD4: S66/11/KZ29/I_T
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ30/I_R; OPRD3: S66/11/KZ30/I_S; OPRD4: S66/11/KZ30/I_T
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ31/I_R; OPRD3: S66/11/KZ31/I_S; OPRD4: S66/11/KZ31/I_T
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ32/I_R; OPRD3: S66/11/KZ32/I_S; OPRD4: S66/11/KZ32/I_T
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ33/I_R; OPRD3: S66/11/KZ33/I_S; OPRD4: S66/11/KZ33/I_T
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ34/I_R; OPRD3: S66/11/KZ34/I_S; OPRD4: S66/11/KZ34/I_T
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S66/11/KZ35/I_R; OPRD3: S66/11/KZ35/I_S; OPRD4: S66/11/KZ35/I_T
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ21/kVA; OPRD2: S66/11/KZ21/KVAR
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ22/kVA; OPRD2: S66/11/KZ22/KVAR
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ23/kVA; OPRD2: S66/11/KZ23/KVAR
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ24/kVA; OPRD2: S66/11/KZ24/KVAR
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ25/kVA; OPRD2: S66/11/KZ25/KVAR
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26線(KZ26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ26/kVA; OPRD2: S66/11/KZ26/KVAR
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27線(KZ27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ27/kVA; OPRD2: S66/11/KZ27/KVAR
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28線(KZ28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ28/kVA; OPRD2: S66/11/KZ28/KVAR
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29線(KZ29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ29/kVA; OPRD2: S66/11/KZ29/KVAR
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30線(KZ30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ30/kVA; OPRD2: S66/11/KZ30/KVAR
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ31/kVA; OPRD2: S66/11/KZ31/KVAR
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ32/kVA; OPRD2: S66/11/KZ32/KVAR
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ33/kVA; OPRD2: S66/11/KZ33/KVAR
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ34/kVA; OPRD2: S66/11/KZ34/KVAR
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S66_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S66/11/KZ35/kVA; OPRD2: S66/11/KZ35/KVAR
S66 | 大灣SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S66_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S66/11/M1/MW; OPRD2: S66/11/M2A/MW; OPRD3: S66/11/M3/MW
S66 | 大灣SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S66_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: S66/11/M1/MVAR; OPRD2: S66/11/M2A/MVAR; OPRD3: S66/11/M3/MVAR
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S66_D1 | [12 empty] | 大灣SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S66/11/210/CB; OPRD2: 6.9; OPRD3: 0
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S66_D1 | [12 empty] | 大灣SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S66/11/220/CB; OPRD2: 6.9; OPRD3: 0
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S66_D1 | [12 empty] | 大灣SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S66/11/230/CB; OPRD2: 6.9; OPRD3: 0
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S66_A1 | [15 empty] | SC_CAL_11 |  | sc_mvar | OPRD1: S66/69/810/CB; OPRD2: 69; OPRD3: 0
S66 | 大灣SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S66_D1 | [12 empty] | 大灣SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_27 | OPRD1: S66//1MTR/63Q; OPRD2: S66//1MTR/96B1; OPRD3: S66//1MTR/96PA; OPRD4: S66//1MTR/TRA; OPRD5: S66//1MTR/96B2; OPRD6: S66//1MTR/96D; OPRD7: S66//1MTR/51ZA; OPRD8: S66//1MTR/87A; OPRD9: S66//2MTR/96PA; OPRD10: S66//2MTR/63Q; OPRD11: S66//2MTR/96B1; OPRD12: S66//2MTR/96B2; OPRD13: S66//2MTR/51ZA; OPRD14: S66//2MTR/87A; OPRD15: S66//2MTR/96D; OPRD16: S66//2MTR/TRA; OPRD17: S66//3MTR/96D; OPRD18: S66//3MTR/96B2; OPRD19: S66//3MTR/63Q; OPRD20: S66//3MTR/96B1; OPRD21: S66//3MTR/87A; OPRD22: S66//3MTR/51ZA; OPRD23: S66//3MTR/TRA; OPRD24: S66//3MTR/96PA; OPRD25: S66/11/M2A/GDA; OPRD26: S66/69/1BUS/87A; OPRD27: S66/69/2BUS/87A
S66 | 大灣SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S66_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_3 | OPRD1: S66//1MTR/TRF; OPRD2: S66//2MTR/TRF; OPRD3: S66//3MTR/TRF
S66 | 大灣SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/RTU/RTU_R_L
S66 | 大灣SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/StaDev/PSF
S66 | 大灣SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/StaDev/PMA
S66 | 大灣SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/StaDev/DCE
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/CBA
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/CBF
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/ABS_89A
S66 | 大灣SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/StaDev/DCA
S66 | 大灣SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S66_A1 | [17 empty] | lamp2CC | OPRD1: S66/0/StaDev/Fire
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/CFA
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/IRFA
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | 12B_CTFA | 69KV BUS CT迴路故障 |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/12B_CTFA
S66 | 大灣SS | 69 | 69kV | ComPoint_D1 |  |  | BUS_RYFA | 69KV BUS IED故障 |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S66_D1 | [17 empty] | lamp2CC | OPRD1: S66/69/ComPoint/BUS_RYFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S66 | 大灣SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S66/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 大灣SS.620_AMP | 後甲大灣線 AMP | LINE69 | S66/69/620/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0876 | 788.400024 | 788.400024 | 876.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 大灣SS.630_AMP | 大灣永康一路 AMP | LINE69 | S66/69/630/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0800 | 720.000000 | 720.000000 | 800.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | I | [25 empty] | ADCS_S | [8 empty] | 大灣SS.670_AMP | 台南大灣一路 AMP | LINE69 | S66/69/670/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0800 | 720.000000 | 720.000000 | 800.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S66 | 大灣SS | 0 |  |  |  |  | 大新線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.大新線KVA | 11KV大新線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 大新線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.大新線KW | 11KV大新線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 文化線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.文化線KVA | 11KV文化線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 文化線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.文化線KW | 11KV文化線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 王厝線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.王厝線KVA | 11KV王厝線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 王厝線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.王厝線KW | 11KV王厝線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 北灣線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.北灣線KVA | 11KV北灣線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 北灣線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.北灣線KW | 11KV北灣線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 市場線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.市場線KVA | 11KV市場線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 市場線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.市場線KW | 11KV市場線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 西灣線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.西灣線KVA | 11KV西灣線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 西灣線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.西灣線KW | 11KV西灣線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 南興線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.南興線KVA | 11KV南興線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 南興線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.南興線KW | 11KV南興線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 美好線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.美好線KVA | 11KV美好線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 美好線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.美好線KW | 11KV美好線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 國光線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.國光線KVA | 11KV國光線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 國光線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.國光線KW | 11KV國光線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 崑技線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.崑技線KVA | 11KV崑技線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 崑技線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.崑技線KW | 11KV崑技線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣26線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣26線KVA | 11KV灣26線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣26線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣26線KW | 11KV灣26線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣27線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣27線KVA | 11KV灣27線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣27線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣27線KW | 11KV灣27線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣28線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣28線KVA | 11KV灣28線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣28線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣28線KW | 11KV灣28線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣29線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣29線KVA | 11KV灣29線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣29線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣29線KW | 11KV灣29線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣30線KVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣30線KVA | 11KV灣30線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  |  |  |  | 灣30線KW | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.灣30線KW | 11KV灣30線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S66//1MTR/MVA |  | MVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_PF | #1MTR 功率因素 | DTR | S66//1MTR/PF |  | RPDC_PF_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S66//2MTR/MVA |  | MVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_PF | #2MTR 功率因素 | DTR | S66//2MTR/PF |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S66//3MTR/MVA |  | MVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_PF | #3MTR 功率因素 | DTR | S66//3MTR/PF |  | RPDC_PF_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S66 | 大灣SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S66/11/210/MVAR |  | SC_CAL_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S66/11/220/MVAR |  | SC_CAL_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S66/11/230/MVAR |  | SC_CAL_11 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | I | [25 empty] | ADCS_S | [8 empty] | 大灣SS.640_AMP | 大灣永康二路 AMP | LINE69 | S66/69/640/I |  | AMP_CAL |  |  | 45 | CalcAIPoint | [21 empty] | C12R0899 | 806.400024 | 806.400024 | 899.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | I | [25 empty] | ADCS_S | [8 empty] | 大灣SS.720_AMP | 台南大灣二路 AMP | LINE69 | S66/69/720/I |  | AMP_CAL |  |  | 46 | CalcAIPoint | [21 empty] | C12R0899 | 806.400024 | 806.400024 | 899.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S66 | 大灣SS | 69 | 69kV | 620_CB | 後甲大灣線(620_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.620_CB_4 | 620(後甲大灣線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 630_CB | 大灣永康一路(630_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.630_CB_4 | 630(大灣永康一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 48 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 670_CB | 台南大灣一路(670_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.670_CB_4 | 670(台南大灣一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 49 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 600_CB | 600(600_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.600_CB_4 | 600 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 50 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 51 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 52 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_S | [8 empty] | 大灣SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 53 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 大灣SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S66/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_3 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620_AMP | 後甲大灣線 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.620_AMP_A | 後甲大灣線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 57 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 620_AMP | 後甲大灣線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.620_AMP_4 | 後甲大灣線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 58 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 630_AMP | 大灣永康一路 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.630_AMP_A | 大灣永康一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 59 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 630_AMP | 大灣永康一路 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.630_AMP_4 | 大灣永康一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 60 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 670_AMP | 台南大灣一路 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.670_AMP_A | 台南大灣一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 670_AMP | 台南大灣一路 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.670_AMP_4 | 台南大灣一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 63 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 66 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 3MTR_MVA | #3MTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_MVA_4 | #3MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 68 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 640_AMP | 大灣永康二路 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.640_AMP_A | 大灣永康二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 69 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 720_AMP | 台南大灣二路 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.720_AMP_A | 台南大灣二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 70 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 69 | 69kV | 640_CB | 大灣永康二路(640_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.640_CB_4 | 640(大灣永康二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 71 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 720_CB | 台南大灣二路(720_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.720_CB_4 | 720(台南大灣二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 72 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 大灣SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 73 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S66/0/RTU/ADCH1 |  |  |  | CDC | 75 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S66/0/RTU/ADCH2 |  |  |  | CDC | 76 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S66/0/RTU/ADCH3 |  |  |  | CDC | 77 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S66/0/RTU/ADCL1 |  |  |  | CDC | 78 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S66/0/RTU/ADCL2 |  |  |  | CDC | 79 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S66/0/RTU/ADCL3 |  |  |  | CDC | 80 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S66/69/1BUS/V |  |  |  | CDC | 81 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S66 | 大灣SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S66/69/2BUS/V |  |  |  | CDC | 82 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S66 | 大灣SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S66/11/1BUS/V_R |  |  |  | CDC | 83 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-BB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | S66/11/2ABUS/V_R |  |  |  | CDC | 84 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | S66/11/2BBUS/V_R |  |  |  | CDC | 85 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S66/11/3BUS/V_R |  |  |  | CDC | 86 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.620_MW | 後甲大灣線 MW | LINE69 | S66/69/620/MW |  |  |  | CDC | 87 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.620_MVAR | 後甲大灣線 MVAR | LINE69 | S66/69/620/MVAR |  |  |  | CDC | 88 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.630_MW | 大灣永康一路 MW | LINE69 | S66/69/630/MW |  |  |  | CDC | 89 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.630_MVAR | 大灣永康一路 MVAR | LINE69 | S66/69/630/MVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.670_MW | 台南大灣一路 MW | LINE69 | S66/69/670/MW |  |  |  | CDC | 91 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.670_MVAR | 台南大灣一路 MVAR | LINE69 | S66/69/670/MVAR |  |  |  | CDC | 92 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.大新線KVAR | 11KV大新線 KVAR | FEEDER | S66/11/KZ22/KVAR |  |  |  | CDC | 93 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.大新線A1 | 11KV大新線 R相AMP | FEEDER | S66/11/KZ22/I_R |  |  |  | CDC | 94 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.大新線A2 | 11KV大新線 S相AMP | FEEDER | S66/11/KZ22/I_S |  |  |  | CDC | 95 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.大新線A3 | 11KV大新線 T相AMP | FEEDER | S66/11/KZ22/I_T |  |  |  | CDC | 96 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 大新線 | 大新線 |  | 大新線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.大新線A0 | 11KV大新線 N相AMP | FEEDER | S66/11/KZ22/I_N |  |  |  | CDC | 97 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.文化線KVAR | 11KV文化線 KVAR | FEEDER | S66/11/KZ34/KVAR |  |  |  | CDC | 98 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.文化線A1 | 11KV文化線 R相AMP | FEEDER | S66/11/KZ34/I_R |  |  |  | CDC | 99 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.文化線A2 | 11KV文化線 S相AMP | FEEDER | S66/11/KZ34/I_S |  |  |  | CDC | 100 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.文化線A3 | 11KV文化線 T相AMP | FEEDER | S66/11/KZ34/I_T |  |  |  | CDC | 101 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 文化線 | 文化線 |  | 文化線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.文化線A0 | 11KV文化線 N相AMP | FEEDER | S66/11/KZ34/I_N |  |  |  | CDC | 102 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 王厝線 | 王厝線 |  | 王厝線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.王厝線KVAR | 11KV王厝線 KVAR | FEEDER | S66/11/KZ25/KVAR |  |  |  | CDC | 103 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 王厝線 | 王厝線 |  | 王厝線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.王厝線A1 | 11KV王厝線 R相AMP | FEEDER | S66/11/KZ25/I_R |  |  |  | CDC | 104 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 王厝線 | 王厝線 |  | 王厝線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.王厝線A2 | 11KV王厝線 S相AMP | FEEDER | S66/11/KZ25/I_S |  |  |  | CDC | 105 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 王厝線 | 王厝線 |  | 王厝線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.王厝線A3 | 11KV王厝線 T相AMP | FEEDER | S66/11/KZ25/I_T |  |  |  | CDC | 106 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 王厝線 | 王厝線 |  | 王厝線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.王厝線A0 | 11KV王厝線 N相AMP | FEEDER | S66/11/KZ25/I_N |  |  |  | CDC | 107 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 北灣線 | 北灣線 |  | 北灣線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.北灣線KVAR | 11KV北灣線 KVAR | FEEDER | S66/11/KZ24/KVAR |  |  |  | CDC | 108 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 北灣線 | 北灣線 |  | 北灣線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.北灣線A1 | 11KV北灣線 R相AMP | FEEDER | S66/11/KZ24/I_R |  |  |  | CDC | 109 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 北灣線 | 北灣線 |  | 北灣線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.北灣線A2 | 11KV北灣線 S相AMP | FEEDER | S66/11/KZ24/I_S |  |  |  | CDC | 110 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 北灣線 | 北灣線 |  | 北灣線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.北灣線A3 | 11KV北灣線 T相AMP | FEEDER | S66/11/KZ24/I_T |  |  |  | CDC | 111 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 北灣線 | 北灣線 |  | 北灣線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.北灣線A0 | 11KV北灣線 N相AMP | FEEDER | S66/11/KZ24/I_N |  |  |  | CDC | 112 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 市場線 | 市場線 |  | 市場線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.市場線KVAR | 11KV市場線 KVAR | FEEDER | S66/11/KZ31/KVAR |  |  |  | CDC | 113 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 市場線 | 市場線 |  | 市場線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.市場線A1 | 11KV市場線 R相AMP | FEEDER | S66/11/KZ31/I_R |  |  |  | CDC | 114 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 市場線 | 市場線 |  | 市場線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.市場線A2 | 11KV市場線 S相AMP | FEEDER | S66/11/KZ31/I_S |  |  |  | CDC | 115 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 市場線 | 市場線 |  | 市場線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.市場線A3 | 11KV市場線 T相AMP | FEEDER | S66/11/KZ31/I_T |  |  |  | CDC | 116 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 市場線 | 市場線 |  | 市場線A0 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.市場線A0 | 11KV市場線 N相AMP | FEEDER | S66/11/KZ31/I_N |  |  |  | CDC | 117 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 西灣線 | 西灣線 |  | 西灣線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.西灣線KVAR | 11KV西灣線 KVAR | FEEDER | S66/11/KZ35/KVAR |  |  |  | CDC | 118 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 西灣線 | 西灣線 |  | 西灣線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.西灣線A1 | 11KV西灣線 R相AMP | FEEDER | S66/11/KZ35/I_R |  |  |  | CDC | 119 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 西灣線 | 西灣線 |  | 西灣線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.西灣線A2 | 11KV西灣線 S相AMP | FEEDER | S66/11/KZ35/I_S |  |  |  | CDC | 120 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 西灣線 | 西灣線 |  | 西灣線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.西灣線A3 | 11KV西灣線 T相AMP | FEEDER | S66/11/KZ35/I_T |  |  |  | CDC | 121 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 西灣線 | 西灣線 |  | 西灣線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.西灣線A0 | 11KV西灣線 N相AMP | FEEDER | S66/11/KZ35/I_N |  |  |  | CDC | 122 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 南興線 | 南興線 |  | 南興線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.南興線KVAR | 11KV南興線 KVAR | FEEDER | S66/11/KZ32/KVAR |  |  |  | CDC | 123 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 南興線 | 南興線 |  | 南興線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.南興線A1 | 11KV南興線 R相AMP | FEEDER | S66/11/KZ32/I_R |  |  |  | CDC | 124 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 南興線 | 南興線 |  | 南興線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.南興線A2 | 11KV南興線 S相AMP | FEEDER | S66/11/KZ32/I_S |  |  |  | CDC | 125 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 南興線 | 南興線 |  | 南興線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.南興線A3 | 11KV南興線 T相AMP | FEEDER | S66/11/KZ32/I_T |  |  |  | CDC | 126 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 南興線 | 南興線 |  | 南興線A0 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.南興線A0 | 11KV南興線 N相AMP | FEEDER | S66/11/KZ32/I_N |  |  |  | CDC | 127 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 美好線 | 美好線 |  | 美好線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.美好線KVAR | 11KV美好線 KVAR | FEEDER | S66/11/KZ23/KVAR |  |  |  | CDC | 128 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 美好線 | 美好線 |  | 美好線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.美好線A1 | 11KV美好線 R相AMP | FEEDER | S66/11/KZ23/I_R |  |  |  | CDC | 129 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 美好線 | 美好線 |  | 美好線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.美好線A2 | 11KV美好線 S相AMP | FEEDER | S66/11/KZ23/I_S |  |  |  | CDC | 130 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 美好線 | 美好線 |  | 美好線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.美好線A3 | 11KV美好線 T相AMP | FEEDER | S66/11/KZ23/I_T |  |  |  | CDC | 131 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 美好線 | 美好線 |  | 美好線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.美好線A0 | 11KV美好線 N相AMP | FEEDER | S66/11/KZ23/I_N |  |  |  | CDC | 132 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 國光線 | 國光線 |  | 國光線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.國光線KVAR | 11KV國光線 KVAR | FEEDER | S66/11/KZ21/KVAR |  |  |  | CDC | 133 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 國光線 | 國光線 |  | 國光線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.國光線A1 | 11KV國光線 R相AMP | FEEDER | S66/11/KZ21/I_R |  |  |  | CDC | 134 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 國光線 | 國光線 |  | 國光線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.國光線A2 | 11KV國光線 S相AMP | FEEDER | S66/11/KZ21/I_S |  |  |  | CDC | 135 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 國光線 | 國光線 |  | 國光線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.國光線A3 | 11KV國光線 T相AMP | FEEDER | S66/11/KZ21/I_T |  |  |  | CDC | 136 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 國光線 | 國光線 |  | 國光線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.國光線A0 | 11KV國光線 N相AMP | FEEDER | S66/11/KZ21/I_N |  |  |  | CDC | 137 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 崑技線 | 崑技線 |  | 崑技線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.崑技線KVAR | 11KV崑技線 KVAR | FEEDER | S66/11/KZ33/KVAR |  |  |  | CDC | 138 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 崑技線 | 崑技線 |  | 崑技線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.崑技線A1 | 11KV崑技線 R相AMP | FEEDER | S66/11/KZ33/I_R |  |  |  | CDC | 139 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 崑技線 | 崑技線 |  | 崑技線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.崑技線A2 | 11KV崑技線 S相AMP | FEEDER | S66/11/KZ33/I_S |  |  |  | CDC | 140 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 崑技線 | 崑技線 |  | 崑技線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.崑技線A3 | 11KV崑技線 T相AMP | FEEDER | S66/11/KZ33/I_T |  |  |  | CDC | 141 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 崑技線 | 崑技線 |  | 崑技線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.崑技線A0 | 11KV崑技線 N相AMP | FEEDER | S66/11/KZ33/I_N |  |  |  | CDC | 142 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣26線 | 灣26線 |  | 灣26線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣26線KVAR | 11KV灣26線 KVAR | FEEDER | S66/11/KZ26/KVAR |  |  |  | CDC | 143 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣26線 | 灣26線 |  | 灣26線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣26線A1 | 11KV灣26線 R相AMP | FEEDER | S66/11/KZ26/I_R |  |  |  | CDC | 144 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣26線 | 灣26線 |  | 灣26線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣26線A2 | 11KV灣26線 S相AMP | FEEDER | S66/11/KZ26/I_S |  |  |  | CDC | 145 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣26線 | 灣26線 |  | 灣26線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣26線A3 | 11KV灣26線 T相AMP | FEEDER | S66/11/KZ26/I_T |  |  |  | CDC | 146 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣26線 | 灣26線 |  | 灣26線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣26線A0 | 11KV灣26線 N相AMP | FEEDER | S66/11/KZ26/I_N |  |  |  | CDC | 147 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣27線 | 灣27線 |  | 灣27線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣27線KVAR | 11KV灣27線 KVAR | FEEDER | S66/11/KZ27/KVAR |  |  |  | CDC | 148 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣27線 | 灣27線 |  | 灣27線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣27線A1 | 11KV灣27線 R相AMP | FEEDER | S66/11/KZ27/I_R |  |  |  | CDC | 149 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣27線 | 灣27線 |  | 灣27線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣27線A2 | 11KV灣27線 S相AMP | FEEDER | S66/11/KZ27/I_S |  |  |  | CDC | 150 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣27線 | 灣27線 |  | 灣27線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣27線A3 | 11KV灣27線 T相AMP | FEEDER | S66/11/KZ27/I_T |  |  |  | CDC | 151 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣27線 | 灣27線 |  | 灣27線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣27線A0 | 11KV灣27線 N相AMP | FEEDER | S66/11/KZ27/I_N |  |  |  | CDC | 152 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣28線 | 灣28線 |  | 灣28線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣28線KVAR | 11KV灣28線 KVAR | FEEDER | S66/11/KZ28/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣28線 | 灣28線 |  | 灣28線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣28線A1 | 11KV灣28線 R相AMP | FEEDER | S66/11/KZ28/I_R |  |  |  | CDC | 154 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣28線 | 灣28線 |  | 灣28線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣28線A2 | 11KV灣28線 S相AMP | FEEDER | S66/11/KZ28/I_S |  |  |  | CDC | 155 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣28線 | 灣28線 |  | 灣28線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣28線A3 | 11KV灣28線 T相AMP | FEEDER | S66/11/KZ28/I_T |  |  |  | CDC | 156 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣28線 | 灣28線 |  | 灣28線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣28線A0 | 11KV灣28線 N相AMP | FEEDER | S66/11/KZ28/I_N |  |  |  | CDC | 157 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣29線 | 灣29線 |  | 灣29線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣29線KVAR | 11KV灣29線 KVAR | FEEDER | S66/11/KZ29/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣29線 | 灣29線 |  | 灣29線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣29線A1 | 11KV灣29線 R相AMP | FEEDER | S66/11/KZ29/I_R |  |  |  | CDC | 159 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣29線 | 灣29線 |  | 灣29線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣29線A2 | 11KV灣29線 S相AMP | FEEDER | S66/11/KZ29/I_S |  |  |  | CDC | 160 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣29線 | 灣29線 |  | 灣29線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣29線A3 | 11KV灣29線 T相AMP | FEEDER | S66/11/KZ29/I_T |  |  |  | CDC | 161 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣29線 | 灣29線 |  | 灣29線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣29線A0 | 11KV灣29線 N相AMP | FEEDER | S66/11/KZ29/I_N |  |  |  | CDC | 162 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣30線 | 灣30線 |  | 灣30線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣30線KVAR | 11KV灣30線 KVAR | FEEDER | S66/11/KZ30/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣30線 | 灣30線 |  | 灣30線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣30線A1 | 11KV灣30線 R相AMP | FEEDER | S66/11/KZ30/I_R |  |  |  | CDC | 164 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣30線 | 灣30線 |  | 灣30線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣30線A2 | 11KV灣30線 S相AMP | FEEDER | S66/11/KZ30/I_S |  |  |  | CDC | 165 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣30線 | 灣30線 |  | 灣30線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣30線A3 | 11KV灣30線 T相AMP | FEEDER | S66/11/KZ30/I_T |  |  |  | CDC | 166 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | 灣30線 | 灣30線 |  | 灣30線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.灣30線A0 | 11KV灣30線 N相AMP | FEEDER | S66/11/KZ30/I_N |  |  |  | CDC | 167 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-90 | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.600TIE_AMP | 600TIE AMP | TIE | S66/69/600/I |  |  |  | CDC | 168 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S66/11/TIE1/I_R |  |  |  | CDC | 169 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S66/11/TIE1/I_S |  |  |  | CDC | 170 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S66/11/TIE1/I_T |  |  |  | CDC | 171 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S66/11/TIE2/I_R |  |  |  | CDC | 172 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S66/11/TIE2/I_S |  |  |  | CDC | 173 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S66/11/TIE2/I_T |  |  |  | CDC | 174 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_MW | #1MTR二次側 MW | DTR | S66/11/M1/MW |  |  |  | CDC | 175 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S66/11/M1/MVAR |  |  |  | CDC | 176 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S66/11/M1/I_R |  |  |  | CDC | 177 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S66/11/M1/I_S |  |  |  | CDC | 178 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S66/11/M1/I_T |  |  |  | CDC | 179 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_OIL | #1MTR 油溫 | DTR | S66//1MTR/OilTemp |  |  |  | CDC | 180 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_COIL | #1MTR 線溫 | DTR | S66//1MTR/CoilTemp |  |  |  | CDC | 181 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-3B |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S66//1MTR/TapPosMv |  |  |  | CDC | 182 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_MW | #2MTR二次側 MW | DTR | S66/11/M2A/MW |  |  |  | CDC | 183 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S66/11/M2A/MVAR |  |  |  | CDC | 184 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S66/11/M2A/I_R |  |  |  | CDC | 185 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S66/11/M2A/I_S |  |  |  | CDC | 186 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S66/11/M2A/I_T |  |  |  | CDC | 187 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_OIL | #2MTR 油溫 | DTR | S66//2MTR/OilTemp |  |  |  | CDC | 188 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_COIL | #2MTR 線溫 | DTR | S66//2MTR/CoilTemp |  |  |  | CDC | 189 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S66//2MTR/TapPosMv |  |  |  | CDC | 190 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_MW | #3MTR二次側 MW | DTR | S66/11/M3/MW |  |  |  | CDC | 191 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S66/11/M3/MVAR |  |  |  | CDC | 192 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S66/11/M3/I_R |  |  |  | CDC | 193 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S66/11/M3/I_S |  |  |  | CDC | 194 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S66/11/M3/I_T |  |  |  | CDC | 195 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_OIL | #3MTR 油溫 | DTR | S66//3MTR/OilTemp |  |  |  | CDC | 196 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_COIL | #3MTR 線溫 | DTR | S66//3MTR/CoilTemp |  |  |  | CDC | 197 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S66//3MTR/TapPosMv |  |  |  | CDC | 198 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S66 | 大灣SS | 0 |  |  |  |  | DCV | [17 empty] | 2-82 | [5 empty] | DCVolt_-150_150(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.直流電源電壓 | 直流電源電壓 | OTHER | S66/0/StaDev/DCV |  |  |  | CDC | 199 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_125 | 135.000000 | 135.000000 | 140.000000 | 150.000000 | 0.200000 | 120.000000 | 120.000000 | 100.000000 | -150.000000 | 0.100000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.640_MW | 大灣永康二路 MW | LINE69 | S66/69/640/MW |  |  |  | CDC | 200 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.640_MVAR | 大灣永康二路 MVAR | LINE69 | S66/69/640/MVAR |  |  |  | CDC | 201 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.720_MW | 台南大灣二路 MW | LINE69 | S66/69/720/MW |  |  |  | CDC | 202 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 大灣SS.720_MVAR | 台南大灣二路 MVAR | LINE69 | S66/69/720/MVAR |  |  |  | CDC | 203 | GENERICAIPoint | SS408_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S66 | 大灣SS | 0 |  | 11S11BUS | 11S1 |  | V | [17 empty] | 2-A8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | S66/11/1BUS/V_S |  |  |  | CDC | 204 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11S12ABUS | 11S1 |  | V | [17 empty] | 2-AA | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11S1#2ABUS_KV | 11S1 #2ABUS KV | BUS | S66/11/2ABUS/V_S |  |  |  | CDC | 205 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11S12BBUS | 11S1 |  | V | [17 empty] | 2-AC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11S1#2BBUS_KV | 11S1 #2BBUS KV | BUS | S66/11/2BBUS/V_S |  |  |  | CDC | 206 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11S13BUS | 11S1 |  | V | [17 empty] | 2-AE | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | S66/11/3BUS/V_S |  |  |  | CDC | 207 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11T11BUS | 11T1 |  | V | [17 empty] | 2-A9 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | S66/11/1BUS/V_T |  |  |  | CDC | 208 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11T12ABUS | 11T1 |  | V | [17 empty] | 2-AB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11T1#2ABUS_KV | 11T1 #2ABUS KV | BUS | S66/11/2ABUS/V_T |  |  |  | CDC | 209 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11T12BBUS | 11T1 |  | V | [17 empty] | 2-AD | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11T1#2BBUS_KV | 11T1 #2BBUS KV | BUS | S66/11/2BBUS/V_T |  |  |  | CDC | 210 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 0 |  | 11T13BUS | 11T1 |  | V | [17 empty] | 2-AF | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 大灣SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | S66/11/3BUS/V_T |  |  |  | CDC | 211 | GENERICAIPoint | SS408_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.620_PHA | 後甲大灣線(620) 相間RY | LINE69 | S66/69/620/PHA |  |  |  | CDC | 212 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.620_GDA | 後甲大灣線(620) 接地RY | LINE69 | S66/69/620/GDA |  |  |  | CDC | 213 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.620_CB | 620(後甲大灣線) CB | LINE69 | S66/69/620/CB |  |  |  | CDC | 214 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | DS1 | 621 | [16 empty] | 1-38-08 | 1-38-09 | 1-14 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.621_DS | 621(後甲大灣線) DS | LINE69 | S66/69/620/DS1 |  |  |  | CDC | 215 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | DS2 | 622 | [16 empty] | 1-38-10 | 1-38-11 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.622_DS | 622(後甲大灣線) DS | LINE69 | S66/69/620/DS2 |  |  |  | CDC | 216 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | DS3 | 623 | [16 empty] | 1-38-12 | 1-38-13 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.623_DS | 623(後甲大灣線) DS | LINE69 | S66/69/620/DS3 |  |  |  | CDC | 217 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | E3 | 623E | [16 empty] | 1-38-14 | 1-38-15 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.623E_ES | 623E(後甲大灣線) ES | LINE69 | S66/69/620/ES3 |  |  |  | CDC | 218 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 630 | 永康線(630) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.630_PHA | 永康線(630) 相間RY | LINE69 | S66/69/630/PHA |  |  |  | CDC | 219 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.630_GDA | 大灣永康一路(630) 接地RY | LINE69 | S66/69/630/GDA |  |  |  | CDC | 220 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | CB | [17 empty] | 1-08-00 |  | 1-01 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.630_CB | 630(大灣永康一路) CB | LINE69 | S66/69/630/CB |  |  |  | CDC | 221 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | DS1 | 631 | [16 empty] | 1-38-00 | 1-38-01 | 1-10 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.631_DS | 631(大灣永康一路) DS | LINE69 | S66/69/630/DS1 |  |  |  | CDC | 222 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | DS2 | 632 | [16 empty] | 1-38-02 | 1-38-03 | 1-11 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.632_DS | 632(大灣永康一路) DS | LINE69 | S66/69/630/DS2 |  |  |  | CDC | 223 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | DS3 | 633 | [16 empty] | 1-38-04 | 1-38-05 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.633_DS | 633(大灣永康一路) DS | LINE69 | S66/69/630/DS3 |  |  |  | CDC | 224 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | E3 | 633E | [16 empty] | 1-38-06 | 1-38-07 | 1-13 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.633E_ES | 633E(大灣永康一路) ES | LINE69 | S66/69/630/ES3 |  |  |  | CDC | 225 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.670_PHA | 台南大灣一路(670) 相間RY | LINE69 | S66/69/670/PHA |  |  |  | CDC | 226 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.670_GDA | 台南大灣一路(670) 接地RY | LINE69 | S66/69/670/GDA |  |  |  | CDC | 227 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.670_CB | 670(台南大灣一路) CB | LINE69 | S66/69/670/CB |  |  |  | CDC | 228 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | DS1 | 671 | [16 empty] | 1-39-00 | 1-39-01 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.671_DS | 671(台南大灣一路) DS | LINE69 | S66/69/670/DS1 |  |  |  | CDC | 229 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | DS2 | 672 | [16 empty] | 1-39-02 | 1-39-03 | 1-19 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.672_DS | 672(台南大灣一路) DS | LINE69 | S66/69/670/DS2 |  |  |  | CDC | 230 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | DS3 | 673 | [16 empty] | 1-39-04 | 1-39-05 | 1-1A | [5 empty] | ADCS_S | [8 empty] | 大灣SS.673_DS | 673(台南大灣一路) DS | LINE69 | S66/69/670/DS3 |  |  |  | CDC | 231 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | E3 | 673E | [16 empty] | 1-39-06 | 1-39-07 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 大灣SS.673E_ES | 673E(台南大灣一路) ES | LINE69 | S66/69/670/ES3 |  |  |  | CDC | 232 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | PHA | [17 empty] | 1-0C-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_PHA | 11KV國光線(KZ21) 相間RY | FEEDER | S66/11/KZ21/PHA |  |  |  | CDC | 233 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) |  | GDA | [17 empty] | 1-0C-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_GDA | 11KV國光線(KZ21) 接地RY | FEEDER | S66/11/KZ21/GDA |  |  |  | CDC | 234 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) 79RY |  | 79UL | [17 empty] | 1-33-06 |  | 1-3E | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_79UL | 11KV國光線(KZ21) 79RY U/L | FEEDER | S66/11/KZ21/79UL |  |  |  | CDC | 235 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ21 | 國光線(KZ21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_ADJ | 11KV國光線(KZ21) LCO分流器 U/L | FEEDER | S66/11/KZ21/ADJ |  |  |  | CDC | 236 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ21 | KZ21(11KV國光線) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_CB | KZ21(11KV國光線) CB | FEEDER | S66/11/KZ21/CB |  |  |  | CDC | 237 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | PHA | [17 empty] | 1-0C-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_PHA | 11KV大新線(KZ22) 相間RY | FEEDER | S66/11/KZ22/PHA |  |  |  | CDC | 238 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_GDA | 11KV大新線(KZ22) 接地RY | FEEDER | S66/11/KZ22/GDA |  |  |  | CDC | 239 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3F | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_79UL | 11KV大新線(KZ22) 79RY U/L | FEEDER | S66/11/KZ22/79UL |  |  |  | CDC | 240 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ22 | 大新線(KZ22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_ADJ | 11KV大新線(KZ22) LCO分流器 U/L | FEEDER | S66/11/KZ22/ADJ |  |  |  | CDC | 241 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ22 | KZ22(11KV大新線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_CB | KZ22(11KV大新線) CB | FEEDER | S66/11/KZ22/CB |  |  |  | CDC | 242 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | PHA | [17 empty] | 1-0C-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_PHA | 11KV美好線(KZ23) 相間RY | FEEDER | S66/11/KZ23/PHA |  |  |  | CDC | 243 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_GDA | 11KV美好線(KZ23) 接地RY | FEEDER | S66/11/KZ23/GDA |  |  |  | CDC | 244 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-40 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_79UL | 11KV美好線(KZ23) 79RY U/L | FEEDER | S66/11/KZ23/79UL |  |  |  | CDC | 245 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ23 | 美好線(KZ23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_ADJ | 11KV美好線(KZ23) LCO分流器 U/L | FEEDER | S66/11/KZ23/ADJ |  |  |  | CDC | 246 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ23 | KZ23(11KV美好線) |  | CB | [17 empty] | 1-0C-05 |  | 1-37 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_CB | KZ23(11KV美好線) CB | FEEDER | S66/11/KZ23/CB |  |  |  | CDC | 247 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_PHA | 11KV北灣線(KZ24) 相間RY | FEEDER | S66/11/KZ24/PHA |  |  |  | CDC | 248 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_GDA | 11KV北灣線(KZ24) 接地RY | FEEDER | S66/11/KZ24/GDA |  |  |  | CDC | 249 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-41 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_79UL | 11KV北灣線(KZ24) 79RY U/L | FEEDER | S66/11/KZ24/79UL |  |  |  | CDC | 250 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ24 | 北灣線(KZ24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_ADJ | 11KV北灣線(KZ24) LCO分流器 U/L | FEEDER | S66/11/KZ24/ADJ |  |  |  | CDC | 251 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ24 | KZ24(11KV北灣線) |  | CB | [17 empty] | 1-0D-00 |  | 1-38 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_CB | KZ24(11KV北灣線) CB | FEEDER | S66/11/KZ24/CB |  |  |  | CDC | 252 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | PHA | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_PHA | 11KV王厝線(KZ25) 相間RY | FEEDER | S66/11/KZ25/PHA |  |  |  | CDC | 253 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_GDA | 11KV王厝線(KZ25) 接地RY | FEEDER | S66/11/KZ25/GDA |  |  |  | CDC | 254 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-42 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_79UL | 11KV王厝線(KZ25) 79RY U/L | FEEDER | S66/11/KZ25/79UL |  |  |  | CDC | 255 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ25 | 王厝線(KZ25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_ADJ | 11KV王厝線(KZ25) LCO分流器 U/L | FEEDER | S66/11/KZ25/ADJ |  |  |  | CDC | 256 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ25 | KZ25(11KV王厝線) |  | CB | [17 empty] | 1-0D-03 |  | 1-39 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_CB | KZ25(11KV王厝線) CB | FEEDER | S66/11/KZ25/CB |  |  |  | CDC | 257 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26(KZ26) |  | PHA | [17 empty] | 1-0E-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_PHA | 11KV灣26(KZ26) 相間RY | FEEDER | S66/11/KZ26/PHA |  |  |  | CDC | 258 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26(KZ26) |  | GDA | [17 empty] | 1-0E-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_GDA | 11KV灣26(KZ26) 接地RY | FEEDER | S66/11/KZ26/GDA |  |  |  | CDC | 259 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26(KZ26) 79RY |  | 79UL | [17 empty] | 1-34-06 |  | 1-51 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_79UL | 11KV灣26(KZ26) 79RY U/L | FEEDER | S66/11/KZ26/79UL |  |  |  | CDC | 260 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ26 | 灣26(KZ26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_ADJ | 11KV灣26(KZ26) LCO分流器 U/L | FEEDER | S66/11/KZ26/ADJ |  |  |  | CDC | 261 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ26 | KZ26(11KV灣26) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_CB | KZ26(11KV灣26) CB | FEEDER | S66/11/KZ26/CB |  |  |  | CDC | 262 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27(KZ27) |  | PHA | [17 empty] | 1-0F-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_PHA | 11KV灣27(KZ27) 相間RY | FEEDER | S66/11/KZ27/PHA |  |  |  | CDC | 263 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27(KZ27) |  | GDA | [17 empty] | 1-0F-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_GDA | 11KV灣27(KZ27) 接地RY | FEEDER | S66/11/KZ27/GDA |  |  |  | CDC | 264 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27(KZ27) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-52 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_79UL | 11KV灣27(KZ27) 79RY U/L | FEEDER | S66/11/KZ27/79UL |  |  |  | CDC | 265 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ27 | 灣27(KZ27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_ADJ | 11KV灣27(KZ27) LCO分流器 U/L | FEEDER | S66/11/KZ27/ADJ |  |  |  | CDC | 266 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ27 | KZ27(11KV灣27) |  | CB | [17 empty] | 1-0F-00 |  | 1-49 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_CB | KZ27(11KV灣27) CB | FEEDER | S66/11/KZ27/CB |  |  |  | CDC | 267 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28(KZ28) |  | PHA | [17 empty] | 1-0F-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_PHA | 11KV灣28(KZ28) 相間RY | FEEDER | S66/11/KZ28/PHA |  |  |  | CDC | 268 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28(KZ28) |  | GDA | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_GDA | 11KV灣28(KZ28) 接地RY | FEEDER | S66/11/KZ28/GDA |  |  |  | CDC | 269 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28(KZ28) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-53 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_79UL | 11KV灣28(KZ28) 79RY U/L | FEEDER | S66/11/KZ28/79UL |  |  |  | CDC | 270 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ28 | 灣28(KZ28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_ADJ | 11KV灣28(KZ28) LCO分流器 U/L | FEEDER | S66/11/KZ28/ADJ |  |  |  | CDC | 271 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ28 | KZ28(11KV灣28) |  | CB | [17 empty] | 1-0F-03 |  | 1-4A | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_CB | KZ28(11KV灣28) CB | FEEDER | S66/11/KZ28/CB |  |  |  | CDC | 272 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29(KZ29) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_PHA | 11KV灣29(KZ29) 相間RY | FEEDER | S66/11/KZ29/PHA |  |  |  | CDC | 273 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29(KZ29) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_GDA | 11KV灣29(KZ29) 接地RY | FEEDER | S66/11/KZ29/GDA |  |  |  | CDC | 274 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29(KZ29) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-54 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_79UL | 11KV灣29(KZ29) 79RY U/L | FEEDER | S66/11/KZ29/79UL |  |  |  | CDC | 275 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ29 | 灣29(KZ29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_ADJ | 11KV灣29(KZ29) LCO分流器 U/L | FEEDER | S66/11/KZ29/ADJ |  |  |  | CDC | 276 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ29 | KZ29(11KV灣29) |  | CB | [17 empty] | 1-0F-06 |  | 1-4B | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_CB | KZ29(11KV灣29) CB | FEEDER | S66/11/KZ29/CB |  |  |  | CDC | 277 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30(KZ30) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_PHA | 11KV灣30(KZ30) 相間RY | FEEDER | S66/11/KZ30/PHA |  |  |  | CDC | 278 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30(KZ30) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_GDA | 11KV灣30(KZ30) 接地RY | FEEDER | S66/11/KZ30/GDA |  |  |  | CDC | 279 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30(KZ30) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-55 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_79UL | 11KV灣30(KZ30) 79RY U/L | FEEDER | S66/11/KZ30/79UL |  |  |  | CDC | 280 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ30 | 灣30(KZ30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_ADJ | 11KV灣30(KZ30) LCO分流器 U/L | FEEDER | S66/11/KZ30/ADJ |  |  |  | CDC | 281 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ30 | KZ30(11KV灣30) |  | CB | [17 empty] | 1-10-01 |  | 1-4C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_CB | KZ30(11KV灣30) CB | FEEDER | S66/11/KZ30/CB |  |  |  | CDC | 282 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_PHA | 11KV市場線(KZ31) 相間RY | FEEDER | S66/11/KZ31/PHA |  |  |  | CDC | 283 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_GDA | 11KV市場線(KZ31) 接地RY | FEEDER | S66/11/KZ31/GDA |  |  |  | CDC | 284 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-68 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_79UL | 11KV市場線(KZ31) 79RY U/L | FEEDER | S66/11/KZ31/79UL |  |  |  | CDC | 285 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ31 | 市場線(KZ31) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_ADJ | 11KV市場線(KZ31) LCO分流器 U/L | FEEDER | S66/11/KZ31/ADJ |  |  |  | CDC | 286 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ31 | KZ31(11KV市場線) |  | CB | [17 empty] | 1-12-07 |  | 1-60 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_CB | KZ31(11KV市場線) CB | FEEDER | S66/11/KZ31/CB |  |  |  | CDC | 287 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | PHA | [17 empty] | 1-12-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_PHA | 11KV南興線(KZ32) 相間RY | FEEDER | S66/11/KZ32/PHA |  |  |  | CDC | 288 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) |  | GDA | [17 empty] | 1-12-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_GDA | 11KV南興線(KZ32) 接地RY | FEEDER | S66/11/KZ32/GDA |  |  |  | CDC | 289 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-67 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_79UL | 11KV南興線(KZ32) 79RY U/L | FEEDER | S66/11/KZ32/79UL |  |  |  | CDC | 290 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ32 | 南興線(KZ32) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_ADJ | 11KV南興線(KZ32) LCO分流器 U/L | FEEDER | S66/11/KZ32/ADJ |  |  |  | CDC | 291 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ32 | KZ32(11KV南興線) |  | CB | [17 empty] | 1-12-04 |  | 1-5F | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_CB | KZ32(11KV南興線) CB | FEEDER | S66/11/KZ32/CB |  |  |  | CDC | 292 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | PHA | [17 empty] | 1-12-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_PHA | 11KV崑技線(KZ33) 相間RY | FEEDER | S66/11/KZ33/PHA |  |  |  | CDC | 293 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) |  | GDA | [17 empty] | 1-12-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_GDA | 11KV崑技線(KZ33) 接地RY | FEEDER | S66/11/KZ33/GDA |  |  |  | CDC | 294 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-66 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_79UL | 11KV崑技線(KZ33) 79RY U/L | FEEDER | S66/11/KZ33/79UL |  |  |  | CDC | 295 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ33 | 崑技線(KZ33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_ADJ | 11KV崑技線(KZ33) LCO分流器 U/L | FEEDER | S66/11/KZ33/ADJ |  |  |  | CDC | 296 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ33 | KZ33(11KV崑技線) |  | CB | [17 empty] | 1-12-01 |  | 1-5E | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_CB | KZ33(11KV崑技線) CB | FEEDER | S66/11/KZ33/CB |  |  |  | CDC | 297 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | PHA | [17 empty] | 1-11-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_PHA | 11KV文化線(KZ34) 相間RY | FEEDER | S66/11/KZ34/PHA |  |  |  | CDC | 298 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) |  | GDA | [17 empty] | 1-12-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_GDA | 11KV文化線(KZ34) 接地RY | FEEDER | S66/11/KZ34/GDA |  |  |  | CDC | 299 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-65 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_79UL | 11KV文化線(KZ34) 79RY U/L | FEEDER | S66/11/KZ34/79UL |  |  |  | CDC | 300 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ34 | 文化線(KZ34) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_ADJ | 11KV文化線(KZ34) LCO分流器 U/L | FEEDER | S66/11/KZ34/ADJ |  |  |  | CDC | 301 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ34 | KZ34(11KV文化線) |  | CB | [17 empty] | 1-11-06 |  | 1-5D | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_CB | KZ34(11KV文化線) CB | FEEDER | S66/11/KZ34/CB |  |  |  | CDC | 302 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | PHA | [17 empty] | 1-11-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_PHA | 11KV西灣線(KZ35) 相間RY | FEEDER | S66/11/KZ35/PHA |  |  |  | CDC | 303 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) |  | GDA | [17 empty] | 1-11-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_GDA | 11KV西灣線(KZ35) 接地RY | FEEDER | S66/11/KZ35/GDA |  |  |  | CDC | 304 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) 79RY |  | 79UL | [17 empty] | 1-35-06 |  | 1-64 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_79UL | 11KV西灣線(KZ35) 79RY U/L | FEEDER | S66/11/KZ35/79UL |  |  |  | CDC | 305 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 11 | 11kV | KZ35 | 西灣線(KZ35) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_ADJ | 11KV西灣線(KZ35) LCO分流器 U/L | FEEDER | S66/11/KZ35/ADJ |  |  |  | CDC | 306 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 11 | 11kV | KZ35 | KZ35(11KV西灣線) |  | CB | [17 empty] | 1-11-03 |  | 1-5C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_CB | KZ35(11KV西灣線) CB | FEEDER | S66/11/KZ35/CB |  |  |  | CDC | 307 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-04-02 |  | 1-07 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.600_CB | 600(TIE) CB | TIE | S66/69/600/CB |  |  |  | CDC | 308 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-2A | [5 empty] | ADCS_S | [8 empty] | 大灣SS.601_DS | 601(TIE) DS | TIE | S66/69/600/DS1 |  |  |  | CDC | 309 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-2B | [5 empty] | ADCS_S | [8 empty] | 大灣SS.602_DS | 602(TIE) DS | TIE | S66/69/600/DS2 |  |  |  | CDC | 310 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0E-01 |  | 1-3A | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE1_CB | 11KV TIE1 CB | TIE | S66/11/TIE1/CB |  |  |  | CDC | 311 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE1_51A | 11KV TIE1 51RY | TIE | S66/11/TIE1/51A |  |  |  | CDC | 312 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S66/11/TIE1/51NA |  |  |  | CDC | 313 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-10-07 |  | 1-4D | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE2_CB | 11KV TIE2 CB | TIE | S66/11/TIE2/CB |  |  |  | CDC | 314 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE2_51A | 11KV TIE2 51RY | TIE | S66/11/TIE2/51A |  |  |  | CDC | 315 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S66/11/TIE2/51NA |  |  |  | CDC | 316 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-32 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.750_CB | 750(#1MTR) CB | DTR | S66/69/750/CB |  |  |  | CDC | 317 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-07 |  | 1-33 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.1M_CB | 1M(#1MTR) CB | DTR | S66/11/M1/CB |  |  |  | CDC | 318 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_51A | #1MTR 51RY | DTR | S66/69/750/51A |  |  |  | CDC | 319 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_51NA | #1MTR 51N RY | DTR | S66/69/750/51NA |  |  |  | CDC | 320 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-00-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S66//1MTR/51ZA |  |  |  | CDC | 321 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_87A | #1MTR 87RY | DTR | S66//1MTR/87A |  |  |  | CDC | 322 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #750 |  | 81AS | [17 empty] | 1-0E-04 |  | 1-43 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_81A/S | #750 81RY A/S | DTR | S66/69/750/81AS |  |  |  | CDC | 323 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S66 | 大灣SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-01-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S66/11/M1/51A |  |  |  | CDC | 324 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_TRA | #1MTR 重故障 | DTR | S66//1MTR/TRA |  |  |  | CDC | 325 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S66//1MTR/TRF |  |  |  | CDC | 326 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S66//1MTR/SupLocal |  |  |  | CDC | 327 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S66//1MTR/Tap Chan |  |  |  | CDC | 328 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-37-00 | 1-37-01 | 1-2C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.751_DS | 751(#1MTR) DS | DTR | S66/69/750/DS1 |  |  |  | CDC | 329 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-37-02 | 1-37-03 | 1-2D | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.752_DS | 752(#1MTR) DS | DTR | S66/69/750/DS2 |  |  |  | CDC | 330 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S66//1MTR/OLTC_DLY |  |  |  | CDC | 331 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S66//1MTR/AC_Fault |  |  |  | CDC | 332 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.760_CB | 760(#2MTR) CB | DTR | S66/69/760/CB |  |  |  | CDC | 333 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-02-00 |  | 1-45 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MA_CB | 2MA(#2MTR) CB | DTR | S66/11/M2A/CB |  |  |  | CDC | 334 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-02-01 |  | 1-46 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MB_CB | 2MB(#2MTR) CB | DTR | S66/11/M2B/CB |  |  |  | CDC | 335 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_51A | #2MTR 51RY | DTR | S66/69/760/51A |  |  |  | CDC | 336 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_51NA | #2MTR 51N RY | DTR | S66/69/760/51NA |  |  |  | CDC | 337 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S66//2MTR/51ZA |  |  |  | CDC | 338 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_87A | #2MTR 87RY | DTR | S66//2MTR/87A |  |  |  | CDC | 339 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #760 |  | 81AS | [17 empty] | 1-11-02 |  | 1-56 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_81A/S | #760 81RY A/S | DTR | S66/69/760/81AS |  |  |  | CDC | 340 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S66 | 大灣SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S66/11/M2A/51A |  |  |  | CDC | 341 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S66/11/M2B/51A |  |  |  | CDC | 342 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_TRA | #2MTR 重故障 | DTR | S66//2MTR/TRA |  |  |  | CDC | 343 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S66//2MTR/TRF |  |  |  | CDC | 344 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S66//2MTR/SupLocal |  |  |  | CDC | 345 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S66//2MTR/Tap Chan |  |  |  | CDC | 346 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-37-04 | 1-37-05 | 1-2E | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.761_DS | 761(#2MTR) DS | DTR | S66/69/760/DS1 |  |  |  | CDC | 347 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-37-06 | 1-37-07 | 1-2F | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.762_DS | 762(#2MTR) DS | DTR | S66/69/760/DS2 |  |  |  | CDC | 348 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S66//2MTR/OLTC_DLY |  |  |  | CDC | 349 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S66//2MTR/AC_Fault |  |  |  | CDC | 350 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.770_CB | 770(#3MTR) CB | DTR | S66/69/770/CB |  |  |  | CDC | 351 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-03-04 |  | 1-59 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.3M_CB | 3M(#3MTR) CB | DTR | S66/11/M3/CB |  |  |  | CDC | 352 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-02-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_51A | #3MTR 51RY | DTR | S66/69/770/51A |  |  |  | CDC | 353 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_51NA | #3MTR 51N RY | DTR | S66/69/770/51NA |  |  |  | CDC | 354 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-03-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S66//3MTR/51ZA |  |  |  | CDC | 355 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_87A | #3MTR 87RY | DTR | S66//3MTR/87A |  |  |  | CDC | 356 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #770 |  | 81AS | [17 empty] | 1-13-05 |  | 1-69 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_81A/S | #770 81RY A/S | DTR | S66/69/770/81AS |  |  |  | CDC | 357 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S66 | 大灣SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S66/11/M3/51A |  |  |  | CDC | 358 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_TRA | #3MTR 重故障 | DTR | S66//3MTR/TRA |  |  |  | CDC | 359 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S66//3MTR/TRF |  |  |  | CDC | 360 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S66//3MTR/SupLocal |  |  |  | CDC | 361 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S66//3MTR/Tap Chan |  |  |  | CDC | 362 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-37-08 | 1-37-09 | 1-30 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.771_DS | 771(#3MTR) DS | DTR | S66/69/770/DS1 |  |  |  | CDC | 363 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-37-10 | 1-37-11 | 1-31 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.772_DS | 772(#3MTR) DS | DTR | S66/69/770/DS2 |  |  |  | CDC | 364 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S66//3MTR/OLTC_DLY |  |  |  | CDC | 365 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-36-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S66//3MTR/AC_Fault |  |  |  | CDC | 366 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0D-06 |  | 1-34 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_CB | 210(11KV #1SC) CB | SC | S66/11/210/CB |  |  |  | CDC | 367 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-11 |  | 1-3D | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S66/11/210/SC_A_M |  |  |  | CDC | 368 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_SCA | 11KV #1SC 51,51N RY | SC | S66/11/210/SCA |  |  |  | CDC | 369 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S66/11/210/UVA |  |  |  | CDC | 370 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-10-04 |  | 1-47 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_CB | 220(11KV #2SC) CB | SC | S66/11/220/CB |  |  |  | CDC | 371 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-11 |  | 1-50 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S66/11/220/SC_A_M |  |  |  | CDC | 372 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_SCA | 11KV #2SC 51,51N RY | SC | S66/11/220/SCA |  |  |  | CDC | 373 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-10-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S66/11/220/UVA |  |  |  | CDC | 374 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-13-02 |  | 1-5B | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_CB | 230(11KV #3SC) CB | SC | S66/11/230/CB |  |  |  | CDC | 375 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-11 |  | 1-63 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S66/11/230/SC_A_M |  |  |  | CDC | 376 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-13-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_SCA | 11KV #3SC 51,51N RY | SC | S66/11/230/SCA |  |  |  | CDC | 377 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S66/11/230/UVA |  |  |  | CDC | 378 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S66/69/1BUS/BUS_VUA |  |  |  | CDC | 379 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S66/69/2BUS/BUS_VUA |  |  |  | CDC | 380 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S66/11/ComPoint/CBA |  |  |  | CDC | 381 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S66/11/ComPoint/CBF |  |  |  | CDC | 382 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | _SC | 電容器組 |  | 60A | [17 empty] | 1-33-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_SC_60A | 11KV電容器組 60RY | OTHER | S66/11/ComPoint/FDR_60A |  |  |  | CDC | 383 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S66/69/ComPoint/ABS_89A |  |  |  | CDC | 384 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S66/69/ComPoint/CBA |  |  |  | CDC | 385 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S66/69/ComPoint/CBF |  |  |  | CDC | 386 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S66/0/RTU/RTU_R_L |  |  |  | CDC | 387 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S66 | 大灣SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.TEST_CB | TEST CB | OTHER | S66/0/RTU/Test_CB |  |  |  | CDC | 388 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.火災警報(1) | 火警 | OTHER | S66/0/StaDev/Fire |  |  |  | CDC | 389 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S66/0/StaDev/PSF |  |  |  | CDC | 390 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S66/0/StaDev/ACB1 |  |  |  | CDC | 391 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S66 | 大灣SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S66/0/StaDev/ACB2 |  |  |  | CDC | 392 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S66 | 大灣SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S66/0/StaDev/STUV |  |  |  | CDC | 393 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.直流充電機故障 | 直流充電機故障 | OTHER | S66/0/StaDev/CHG1 |  |  |  | CDC | 394 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S66/0/StaDev/DCA |  |  |  | CDC | 395 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S66/0/StaDev/DCE |  |  |  | CDC | 396 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S66/0/StaDev/OilLeak |  |  |  | CDC | 397 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-35-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S66/0/StaDev/5A5Other |  |  |  | CDC | 398 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-35-14 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S66/0/StaDev/6A5Other |  |  |  | CDC | 399 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-35-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S66/0/StaDev/7A5Other |  |  |  | CDC | 400 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S66/0/StaDev/CHG2 |  |  |  | CDC | 401 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-35-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S66/0/StaDev/CommACF |  |  |  | CDC | 402 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S66/0/StaDev/Door1 |  |  |  | CDC | 403 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S66 | 大灣SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-6A | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S66/0/StaDev/Lights1 |  |  |  | CDC | 404 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S66 | 大灣SS | 0 |  | 2M(A) | #2MA |  | GDA | [17 empty] | 1-02-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2M(A)_GDA | #2MA GDA | OTHER | S66/11/M2A/GDA |  |  |  | CDC | 405 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2M(B) | #2MB |  | GDA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2M(B)_GDA | #2MB GDA | OTHER | S66/11/M2B/51NA |  |  |  | CDC | 406 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | _1SC | #1SC |  | 60A | [17 empty] | 1-33-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_#1SC_60A | 11KV #1SC 60A | OTHER | S66/11/210/FDR_60A |  |  |  | CDC | 407 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | _2SC | #2SC |  | 60A | [17 empty] | 1-33-14 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_#2SC_60A | 11KV #2SC 60A | OTHER | S66/11/220/FDR_60A |  |  |  | CDC | 408 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | _3SC | #3SC |  | 60A | [17 empty] | 1-33-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_#3SC_60A | 11KV #3SC 60A | OTHER | S66/11/230/FDR_60A |  |  |  | CDC | 409 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-10 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.RTU_DC故障 | RTU DC故障 | OTHER | S66/0/RTU/DCA |  |  |  | CDC | 410 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 水位警報 | 水位警報 |  | 1 | [17 empty] | 1-34-14 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.水位警報_1 | 水位警報 1 | OTHER |  |  |  |  | CDC | 411 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 水位警報 | 水位警報 | [19 empty] | 1-34-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.水位警報_2 | 水位警報 2 | OTHER |  |  |  |  | CDC | 412 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.安全監控 | 保全設定 | OTHER | S66/0/StaDev/1A5Other |  |  |  | CDC | 413 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.門禁小門 | 門禁小門 | OTHER | S66/0/StaDev/Door2 |  |  |  | CDC | 414 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-6B | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S66/0/StaDev/Lights |  |  |  | CDC | 415 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  |  |  |  | 緊急發電機啟動 | [17 empty] | 1-32-11 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.緊急發電機啟動 | 緊急發電機啟動 | OTHER | S66/0/StaDev/8A5Other |  |  |  | CDC | 416 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-01 |  | 1-6C | [5 empty] | DDCS4_1 | [8 empty] | 大灣SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S66/0/StaDev/4A5Other |  |  |  | CDC | 417 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 600GDA(1) | [17 empty] | 1-04-04 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.600GDA(1) | 69KV #1BUS TIE(600) 67NA | TIE | S66/69/600/GDA1 |  |  |  | CDC | 418 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 2BUS | #2BUS |  | 600GDA(2) | [17 empty] | 1-04-01 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.600GDA(2) | 69KV #2BUS TIE(600) 67NA | TIE | S66/69/600/GDA2 |  |  |  | CDC | 419 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 600PHA(1) | [17 empty] | 1-04-03 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.600PHA(1) | 69KV #1BUS TIE(600) 67A | TIE | S66/69/600/PHA1 |  |  |  | CDC | 420 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 2BUS | #2BUS |  | 600PHA(2) | [17 empty] | 1-04-00 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.600PHA(2) | 69KV #2BUS TIE(600) 67A | TIE | S66/69/600/PHA2 |  |  |  | CDC | 421 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.640_PHA | 大灣永康二路(640) 相間RY | LINE69 | S66/69/640/PHA |  |  |  | CDC | 422 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.640_GDA | 大灣永康二路(640) 接地RY | LINE69 | S66/69/640/GDA |  |  |  | CDC | 423 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.640_87A | 大灣永康二路(640) 87RY | LINE69 | S66/69/640/87A |  |  |  | CDC | 424 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_S | [8 empty] | 大灣SS.640_87UL | 大灣永康二路(640) 87RY U/L | LINE69 | S66/69/640/87UL |  |  |  | CDC | 425 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.640_CB | 640(大灣永康二路) CB | LINE69 | S66/69/640/CB |  |  |  | CDC | 426 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | DS1 | 641 | [16 empty] | 1-39-08 | 1-39-09 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 大灣SS.641_DS | 641(大灣永康二路) DS | LINE69 | S66/69/640/DS1 |  |  |  | CDC | 427 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | DS2 | 642 | [16 empty] | 1-39-10 | 1-39-11 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 大灣SS.642_DS | 642(大灣永康二路) DS | LINE69 | S66/69/640/DS2 |  |  |  | CDC | 428 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | DS3 | 643 | [16 empty] | 1-39-12 | 1-39-13 | 1-1E | [5 empty] | ADCS_S | [8 empty] | 大灣SS.643_DS | 643(大灣永康二路) DS | LINE69 | S66/69/640/DS3 |  |  |  | CDC | 429 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | E3 | 643E | [16 empty] | 1-39-14 | 1-39-15 | 1-1F | [5 empty] | ADCS_S | [8 empty] | 大灣SS.643E_ES | 643E(大灣永康二路) ES | LINE69 | S66/69/640/ES3 |  |  |  | CDC | 430 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.720_PHA | 台南大灣二路(720) 相間RY | LINE69 | S66/69/720/PHA |  |  |  | CDC | 431 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.720_GDA | 台南大灣二路(720) 接地RY | LINE69 | S66/69/720/GDA |  |  |  | CDC | 432 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.720_87A | 台南大灣二路(720) 87RY | LINE69 | S66/69/720/87A |  |  |  | CDC | 433 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_S | [8 empty] | 大灣SS.720_87UL | 台南大灣二路(720) 87RY U/L | LINE69 | S66/69/720/87UL |  |  |  | CDC | 434 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | CB | [17 empty] | 1-0A-00 |  | 1-05 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.720_CB | 720(台南大灣二路) CB | LINE69 | S66/69/720/CB |  |  |  | CDC | 435 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | DS1 | 721 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-20 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.721_DS | 721(台南大灣二路) DS | LINE69 | S66/69/720/DS1 |  |  |  | CDC | 436 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | DS2 | 722 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-21 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.722_DS | 722(台南大灣二路) DS | LINE69 | S66/69/720/DS2 |  |  |  | CDC | 437 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | DS3 | 723 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-22 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.723_DS | 723(台南大灣二路) DS | LINE69 | S66/69/720/DS3 |  |  |  | CDC | 438 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | E3 | 723E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-23 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.723E_ES | 723E(台南大灣二路) ES | LINE69 | S66/69/720/ES3 |  |  |  | CDC | 439 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.11KV_IED_FA | 11KV IED故障 | OTHER | S66/11/ComPoint/IRFA |  |  |  | CDC | 440 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S66/69/ComPoint/CFA |  |  |  | CDC | 441 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_IED_FA | 69KV IED故障 | OTHER | S66/69/ComPoint/IRFA |  |  |  | CDC | 442 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.81RY_IED_FA | 低頻IED故障 | OTHER | S66/0/StaDev/81A_RYFA |  |  |  | CDC | 443 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.PM_CFA | PM通訊故障 | OTHER | S66/0/StaDev/PMA |  |  |  | CDC | 444 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_S | [8 empty] | 大灣SS.810_CB | 810(69KV #1SC) CB | SC | S66/69/810/CB |  |  |  | CDC | 445 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 1-37-12 | 1-37-13 | 1-28 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.811_DS | 811(69KV #1SC) DS | SC | S66/69/810/DS1 |  |  |  | CDC | 446 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 1-37-14 | 1-37-15 | 1-29 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.812_DS | 812(69KV #1SC) DS | SC | S66/69/810/DS2 |  |  |  | CDC | 447 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.810_SCA | 69KV #1SC 51,51N RY | SC | S66/69/810/SCA |  |  |  | CDC | 448 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.810_OUVA | 69KV #1SC 27,59RY | SC | S66/69/810/UVA |  |  |  | CDC | 449 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 670 | 台南大灣一路(670) |  | 87A | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.670_87A | 670台南大灣一路87RY | OTHER | S66/69/670/87A |  |  |  | CDC | 450 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 670 | 台南大灣一路(670) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_S | [8 empty] | 大灣SS.670_87UL | 670台南大灣一路87RY UL | OTHER | S66/69/670/87UL |  |  |  | CDC | 451 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-18-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S66//1MTR/63Q |  |  |  | CDC | 452 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-18-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S66//1MTR/96B1 |  |  |  | CDC | 453 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-18-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S66//1MTR/96B2 |  |  |  | CDC | 454 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-18-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S66//1MTR/96D |  |  |  | CDC | 455 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-18-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S66//1MTR/96P |  |  |  | CDC | 456 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-18-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S66//2MTR/63Q |  |  |  | CDC | 457 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-19-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S66//2MTR/96B1 |  |  |  | CDC | 458 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-19-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S66//2MTR/96B2 |  |  |  | CDC | 459 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-18-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S66//2MTR/96D |  |  |  | CDC | 460 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-18-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S66//2MTR/96P |  |  |  | CDC | 461 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-19-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | S66//3MTR/63Q |  |  |  | CDC | 462 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-19-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | S66//3MTR/96B1 |  |  |  | CDC | 463 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-19-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | S66//3MTR/96B2 |  |  |  | CDC | 464 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-19-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | S66//3MTR/96D |  |  |  | CDC | 465 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-19-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | S66//3MTR/96P |  |  |  | CDC | 466 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.變電所低水位 | 變電所低水位 | OTHER | S66/0/StaDev/Water1 |  |  |  | CDC | 467 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.變電所高水位 | 變電所高水位 | OTHER | S66/0/StaDev/Water2 |  |  |  | CDC | 468 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ21 | 國光線 |  | LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_LOA | 國光線 復閉失敗閉鎖 | OTHER | S66/11/KZ21/LOA |  |  |  | CDC | 469 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ22 | 大新線 |  | LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_LOA | 大新線 復閉失敗閉鎖 | OTHER | S66/11/KZ22/LOA |  |  |  | CDC | 470 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ23 | 美好線 |  | LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_LOA | 美好線 復閉失敗閉鎖 | OTHER | S66/11/KZ23/LOA |  |  |  | CDC | 471 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ24 | 北灣線 |  | LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_LOA | 北灣線 復閉失敗閉鎖 | OTHER | S66/11/KZ24/LOA |  |  |  | CDC | 472 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ25 | 王厝線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_LOA | 王厝線 復閉失敗閉鎖 | OTHER | S66/11/KZ25/LOA |  |  |  | CDC | 473 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ26 | 灣26線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_LOA | 灣26線 復閉失敗閉鎖 | OTHER | S66/11/KZ26/LOA |  |  |  | CDC | 474 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ27 | 灣27線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_LOA | 灣27線 復閉失敗閉鎖 | OTHER | S66/11/KZ27/LOA |  |  |  | CDC | 475 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ28 | 灣28線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_LOA | 灣28線 復閉失敗閉鎖 | OTHER | S66/11/KZ28/LOA |  |  |  | CDC | 476 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ29 | 灣29線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_LOA | 灣29線 復閉失敗閉鎖 | OTHER | S66/11/KZ29/LOA |  |  |  | CDC | 477 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ30 | 灣30線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_LOA | 灣30線 復閉失敗閉鎖 | OTHER | S66/11/KZ30/LOA |  |  |  | CDC | 478 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ31 | 市場線 |  | LOA | [17 empty] | 1-3F-10 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_LOA | 市場線 復閉失敗閉鎖 | OTHER | S66/11/KZ31/LOA |  |  |  | CDC | 479 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ32 | 南興線 |  | LOA | [17 empty] | 1-3F-09 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_LOA | 南興線 復閉失敗閉鎖 | OTHER | S66/11/KZ32/LOA |  |  |  | CDC | 480 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ33 | 崑技線 |  | LOA | [17 empty] | 1-3F-08 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_LOA | 崑技線 復閉失敗閉鎖 | OTHER | S66/11/KZ33/LOA |  |  |  | CDC | 481 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ34 | 文化線 |  | LOA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_LOA | 文化線 復閉失敗閉鎖 | OTHER | S66/11/KZ34/LOA |  |  |  | CDC | 482 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | KZ35 | 西灣線 |  | LOA | [17 empty] | 1-3F-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_LOA | 西灣線 復閉失敗閉鎖 | OTHER | S66/11/KZ35/LOA |  |  |  | CDC | 483 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3_MAIN | #3MCB |  | 51NA | [17 empty] | 1-03-07 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3_MAIN_51NA | #3MCB GDA | OTHER | S66/11/M3/51NA |  |  |  | CDC | 484 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 620 | 後甲大灣線(620) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.620_87A | 620後甲大灣線87RY | OTHER | S66/69/620/87A |  |  |  | CDC | 485 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 620 | 後甲大灣線(620) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_S | [8 empty] | 大灣SS.620_87UL | 620後甲大灣線87RY UL | OTHER | S66/69/620/87UL |  |  |  | CDC | 486 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 1_MAIN | #1MCB |  | 51NA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1_MAIN_51NA | #1MCB GDA | OTHER | S66/11/M1/51NA |  |  |  | CDC | 487 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 630 | 大灣永康一路(630) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | 69KV_S | [8 empty] | 大灣SS.630_87A | 630大灣永康一路87RY | OTHER | S66/69/630/87A |  |  |  | CDC | 488 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 630 | 大灣永康一路(630) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_S | [8 empty] | 大灣SS.630_87UL | 630大灣永康一路87RY UL | OTHER | S66/69/630/87UL |  |  |  | CDC | 489 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  |  |  |  | CO2故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.CO2故障 | CO2故障 | OTHER | S66/0/StaDev/2A5Other |  |  |  | CDC | 490 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  |  |  |  | CO2警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.CO2警報 | CO2警報 | OTHER | S66/0/StaDev/3A5Other |  |  |  | CDC | 491 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S66//1MTR/96PA |  |  |  | CDC | 492 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S66//2MTR/96PA |  |  |  | CDC | 493 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR | S66//3MTR/96PA |  |  |  | CDC | 494 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | CO2 | CO2 |  | UL | [17 empty] | 1-3F-15 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.CO2_UL | CO2 UL | OTHER | S66/0/StaDev/1A3U_L |  |  |  | CDC | 495 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  |  |  |  | 所內電源警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.所內電源警報 | 所內電源警報 | OTHER | S66/0/StaDev/ACBA |  |  |  | CDC | 496 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | S66//1MTR/51Z_UL |  |  |  | CDC | 497 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | S66//1MTR/MTR_86A |  |  |  | CDC | 498 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER | S66//1MTR/87UL |  |  |  | CDC | 499 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | S66//1MTR/1_87UL2 |  |  |  | CDC | 500 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3E-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | S66//2MTR/51Z_UL |  |  |  | CDC | 501 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | S66//2MTR/MTR_86A |  |  |  | CDC | 502 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-34-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER | S66//2MTR/87UL |  |  |  | CDC | 503 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-3E-02 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | S66//2MTR/1_87UL2 |  |  |  | CDC | 504 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3E-05 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | S66//3MTR/51Z_UL |  |  |  | CDC | 505 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | S66//3MTR/MTR_86A |  |  |  | CDC | 506 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 1-35-03 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER | S66//3MTR/87UL |  |  |  | CDC | 507 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 1-3E-04 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | S66//3MTR/1_87UL2 |  |  |  | CDC | 508 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 0 |  | MTR | MTR |  | IEDGA | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_1 | [8 empty] | 大灣SS.MTR_IED故障 | MTR IED故障 | OTHER | S66//MTR/IRFA |  |  |  | CDC | 509 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 87A | [17 empty] | 1-04-05 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER | S66/69/1BUS/87A |  |  |  | CDC | 510 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL | [17 empty] | 1-3B-11 |  | 1-6E | [5 empty] | ADCS_S | [8 empty] | 大灣SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER | S66/69/1BUS/87UL |  |  |  | CDC | 511 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 2BUS | #2BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER | S66/69/2BUS/87A |  |  |  | CDC | 512 | GENERICDIPoint | SS408_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL | [17 empty] | 1-3B-12 |  | 1-6F | [5 empty] | ADCS_S | [8 empty] | 大灣SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER | S66/69/2BUS/87UL |  |  |  | CDC | 513 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-3B-14 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | S66/69/ComPoint/12B_CTFA |  |  |  | CDC | 514 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-3B-13 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER | S66/69/ComPoint/BUS_RYFA |  |  |  | CDC | 515 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 69 | 69kV | _TIE | TIE |  | RYFA | [17 empty] | 1-3B-15 | [7 empty] | ADCS_S | [8 empty] | 大灣SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER | S66/69/600/RYFA |  |  |  | CDC | 516 | GENERICDIPoint | SS408_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S66 | 大灣SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_SC_CAP | 11KV#1SC 容量 | SC | S66/11/210/1AI_Oth |  |  |  |  | 517 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_SC_CAP | 11KV#2SC 容量 | SC | S66/11/220/2AI_Oth |  |  |  |  | 518 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_SC_CAP | 11KV#3SC 容量 | SC | S66/11/230/3AI_Oth |  |  |  |  | 519 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.620LE | 620LE (非取樣點) | LINE69 | S66/69/620/LE0 |  |  |  |  | 520 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | BE0 | 620BE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.620BE | 620BE (非取樣點) | LINE69 | S66/69/620/BE0 |  |  |  |  | 521 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.630LE | 630LE (非取樣點) | LINE69 | S66/69/630/LE0 |  |  |  |  | 522 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | BE0 | 630BE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.630BE | 630BE (非取樣點) | LINE69 | S66/69/630/BE0 |  |  |  |  | 523 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | LE0 | 670LE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.670LE | 670LE (非取樣點) | LINE69 | S66/69/670/LE0 |  |  |  |  | 524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | BE0 | 670BE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.670BE | 670BE (非取樣點) | LINE69 | S66/69/670/BE0 |  |  |  |  | 525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ21 | KZ21_DS |  | DS1 | KZ21_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_DS | KZ21_DS (非取樣點) | FEEDER | S66/11/KZ21/DS |  |  |  |  | 526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ21 | KZ21_ES |  | LE0 | KZ21_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ21_ES | KZ21_ES (非取樣點) | FEEDER | S66/11/KZ21/ES |  |  |  |  | 527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ22 | KZ22_DS |  | DS1 | KZ22_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_DS | KZ22_DS (非取樣點) | FEEDER | S66/11/KZ22/DS |  |  |  |  | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ22 | KZ22_ES |  | LE0 | KZ22_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ22_ES | KZ22_ES (非取樣點) | FEEDER | S66/11/KZ22/ES |  |  |  |  | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ23 | KZ23_DS |  | DS1 | KZ23_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_DS | KZ23_DS (非取樣點) | FEEDER | S66/11/KZ23/DS |  |  |  |  | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ23 | KZ23_ES |  | LE0 | KZ23_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ23_ES | KZ23_ES (非取樣點) | FEEDER | S66/11/KZ23/ES |  |  |  |  | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ24 | KZ24_DS |  | DS1 | KZ24_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_DS | KZ24_DS (非取樣點) | FEEDER | S66/11/KZ24/DS |  |  |  |  | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ24 | KZ24_ES |  | LE0 | KZ24_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ24_ES | KZ24_ES (非取樣點) | FEEDER | S66/11/KZ24/ES |  |  |  |  | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ25 | KZ25_DS |  | DS1 | KZ25_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_DS | KZ25_DS (非取樣點) | FEEDER | S66/11/KZ25/DS |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ25 | KZ25_ES |  | LE0 | KZ25_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ25_ES | KZ25_ES (非取樣點) | FEEDER | S66/11/KZ25/ES |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ26 | KZ26_DS |  | DS1 | KZ26_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_DS | KZ26_DS (非取樣點) | FEEDER | S66/11/KZ26/DS |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ26 | KZ26_ES |  | LE0 | KZ26_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ26_ES | KZ26_ES (非取樣點) | FEEDER | S66/11/KZ26/ES |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ27 | KZ27_DS |  | DS1 | KZ27_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_DS | KZ27_DS (非取樣點) | FEEDER | S66/11/KZ27/DS |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ27 | KZ27_ES |  | LE0 | KZ27_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ27_ES | KZ27_ES (非取樣點) | FEEDER | S66/11/KZ27/ES |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ28 | KZ28_DS |  | DS1 | KZ28_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_DS | KZ28_DS (非取樣點) | FEEDER | S66/11/KZ28/DS |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ28 | KZ28_ES |  | LE0 | KZ28_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ28_ES | KZ28_ES (非取樣點) | FEEDER | S66/11/KZ28/ES |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ29 | KZ29_DS |  | DS1 | KZ29_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_DS | KZ29_DS (非取樣點) | FEEDER | S66/11/KZ29/DS |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ29 | KZ29_ES |  | LE0 | KZ29_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ29_ES | KZ29_ES (非取樣點) | FEEDER | S66/11/KZ29/ES |  |  |  |  | 543 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ30 | KZ30_DS |  | DS1 | KZ30_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_DS | KZ30_DS (非取樣點) | FEEDER | S66/11/KZ30/DS |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ30 | KZ30_ES |  | LE0 | KZ30_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ30_ES | KZ30_ES (非取樣點) | FEEDER | S66/11/KZ30/ES |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ31 | KZ31_DS |  | DS1 | KZ31_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_DS | KZ31_DS (非取樣點) | FEEDER | S66/11/KZ31/DS |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ31 | KZ31_ES |  | LE0 | KZ31_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ31_ES | KZ31_ES (非取樣點) | FEEDER | S66/11/KZ31/ES |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ32 | KZ32_DS |  | DS1 | KZ32_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_DS | KZ32_DS (非取樣點) | FEEDER | S66/11/KZ32/DS |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ32 | KZ32_ES |  | LE0 | KZ32_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ32_ES | KZ32_ES (非取樣點) | FEEDER | S66/11/KZ32/ES |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ33 | KZ33_DS |  | DS1 | KZ33_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_DS | KZ33_DS (非取樣點) | FEEDER | S66/11/KZ33/DS |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ33 | KZ33_ES |  | LE0 | KZ33_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ33_ES | KZ33_ES (非取樣點) | FEEDER | S66/11/KZ33/ES |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ34 | KZ34_DS |  | DS1 | KZ34_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_DS | KZ34_DS (非取樣點) | FEEDER | S66/11/KZ34/DS |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ34 | KZ34_ES |  | LE0 | KZ34_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ34_ES | KZ34_ES (非取樣點) | FEEDER | S66/11/KZ34/ES |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | KZ35 | KZ35_DS |  | DS1 | KZ35_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_DS | KZ35_DS (非取樣點) | FEEDER | S66/11/KZ35/DS |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | KZ35 | KZ35_ES |  | LE0 | KZ35_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.KZ35_ES | KZ35_ES (非取樣點) | FEEDER | S66/11/KZ35/ES |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S66/11/TIE1/D1 |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S66/11/TIE2/D1 |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.750TE | 750TE (非取樣點) | DTR | S66/69/750/TE0 |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.750BE | 750BE (非取樣點) | DTR | S66/69/750/BE0 |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.1M_DS | 1M_DS (非取樣點) | DTR | S66/11/M1/DS |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.760TE | 760TE (非取樣點) | DTR | S66/69/760/TE0 |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.760BE | 760BE (非取樣點) | DTR | S66/69/760/BE0 |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S66/11/M2A/DS |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S66/11/M2B/DS |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S66/11/M2A/ES |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S66/11/M2B/ES |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.770TE | 770TE (非取樣點) | DTR | S66/69/770/TE0 |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.770BE | 770BE (非取樣點) | DTR | S66/69/770/BE0 |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.3M_DS | 3M_DS (非取樣點) | DTR | S66/11/M3/DS |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_ES | 210_ES (非取樣點) | SC | S66/11/210/ES |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.210_DS | 210_DS (非取樣點) | SC | S66/11/210/DS |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_ES | 220_ES (非取樣點) | SC | S66/11/220/ES |  |  |  |  | 572 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.220_DS | 220_DS (非取樣點) | SC | S66/11/220/DS |  |  |  |  | 573 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_ES | 230_ES (非取樣點) | SC | S66/11/230/ES |  |  |  |  | 574 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.230_DS | 230_DS (非取樣點) | SC | S66/11/230/DS |  |  |  |  | 575 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S66 | 大灣SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 大灣SS.69B1E | 69B1E (非取樣點) | BUS | S66/69/1BUS/BE1 |  |  |  |  | 576 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_S | [8 empty] | 大灣SS.69B2E | 69B2E (非取樣點) | BUS | S66/69/2BUS/BE2 |  |  |  |  | 577 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 578 | NotelDIPoint | [38 empty] | START/STOP | STOP
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.620_PW1UL | 后甲線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 579 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.620_PW2UL | 后甲線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 580 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 69 | 69kV | 620 | 後甲大灣線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.620_HCBUL | 后甲線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 581 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | PW1UL | 630_PW1UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.630_PW1UL | 永康線(630)PW1_UL(非取樣點) | LINE69 | [5 empty] | 582 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | PW2UL | 630_PW2UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.630_PW2UL | 永康線(630)PW2_UL(非取樣點) | LINE69 | [5 empty] | 583 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 69 | 69kV | 630 | 大灣永康一路(630) |  | HCBUL | 630_HCBUL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.630_HCBUL | 永康線(630)HCB_UL(非取樣點) | LINE69 | [5 empty] | 584 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PW1UL | 670_PW1UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.670_PW1UL | 台南線(670)PW1_UL(非取樣點) | LINE69 | [5 empty] | 585 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | PW2UL | 670_PW2UL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.670_PW2UL | 台南線(670)PW2_UL(非取樣點) | LINE69 | [5 empty] | 586 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S66 | 大灣SS | 69 | 69kV | 670 | 台南大灣一路(670) |  | HCBUL | 670_HCBUL | [24 empty] | ADCS_S | [8 empty] | 大灣SS.670_HCBUL | 台南線(670)HCB_UL(非取樣點) | LINE69 | [5 empty] | 587 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | LE0 | 640LE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.640LE | 640LE (非取樣點) | LINE69 | S66/69/640/LE0 |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 640 | 大灣永康二路(640) |  | BE0 | 640BE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.640BE | 640BE (非取樣點) | LINE69 | S66/69/640/BE0 |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | LE0 | 720LE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.720LE | 720LE (非取樣點) | LINE69 | S66/69/720/LE0 |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 720 | 台南大灣二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_S | [8 empty] | 大灣SS.720BE | 720BE (非取樣點) | LINE69 | S66/69/720/BE0 |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  | 810E | 810E |  | 810E | 810E | [24 empty] | ADCS_S | [8 empty] | 大灣SS.810E | 810E (非取樣點) | SC | S66/69/810/E1 |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  |  |  |  | 810BE | 810BE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.810BE | 810BE(非取樣點) | OTHER | S66/69/810/BE0 |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 0 |  |  |  |  | 810LE | 810LE | [24 empty] | DDCS4_1 | [8 empty] | 大灣SS.810LE | 810LE(非取樣點) | OTHER | S66/69/810/LE0 |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_S | [8 empty] | 大灣SS.601E | 601E (非取樣點) | TIE | S66/69/600/E1 |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S66 | 大灣SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_S | [8 empty] | 大灣SS.602E | 602E (非取樣點) | TIE | S66/69/600/E2 |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo