## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S67 | 歸仁SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV #1 BUS 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S67_A1 | [8 empty] | 歸仁SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S67 | 歸仁SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S67_D1 | [8 empty] | 歸仁SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 1BUS | #1BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0206 |  |  | 2-CE |  |  | 11KV S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S67_D1 | [8 empty] | 歸仁SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 1BUS | #1BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0207 |  |  | 2-CF |  |  | 11KV T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S67_D1 | [8 empty] | 歸仁SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 2BUS | #2BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S67_D1 | [8 empty] | 歸仁SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 2BUS | #2BUS |  | V_S |  |  | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0208 |  |  | 2-D0 |  |  | 11KV S相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S67_D1 | [8 empty] | 歸仁SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 2BUS | #2BUS |  | V_T |  |  | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0209 |  |  | 2-D1 |  |  | 11KV T相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S67_D1 | [8 empty] | 歸仁SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS |  |  |  |  | CDC | 8 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 3BUS | #3BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | #3 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S67_D1 | [8 empty] | 歸仁SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 9 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 4BUS | #4BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0137 |  |  | 2-89 |  |  | #4 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S67_D1 | [8 empty] | 歸仁SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS |  |  |  |  | CDC | 10 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 6BUS | #6BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0173 |  |  | 2-AD |  |  | #6 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aea | B2/S67_D1 | [8 empty] | 歸仁SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS |  |  |  |  | CDC | 11 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | LOA |  | Element | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0888 |  |  | 2-37-08 |  |  | 看西線 (F9) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_LOA | 看西線 復閉失敗閉鎖 | OTHER |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S67_A1 | [8 empty] | 歸仁SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 13 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 新市歸仁線 (670) 瓦 |  |  | MW_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_MW | 新市歸仁線 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 新市歸仁線 (670) 乏 |  |  | MVAR_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_MVAR | 新市歸仁線 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0040 |  |  | 2-48 |  |  | 新市歸仁線 (670) MWH(+) |  |  |  |  | B2/S67_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 山上歸仁線 (680) 瓦 |  |  | MW_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_MW | 山上歸仁線 MW | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 山上歸仁線 (680) 乏 |  |  | MVAR_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_MVAR | 山上歸仁線 MVAR | LINE69 |  |  |  |  | CDC | 19 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0042 |  |  | 2-4A |  |  | 山上歸仁線 (680) MWH(+) |  |  |  |  | B2/S67_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 20 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 歸仁大亞線 (630) 瓦 |  |  | MW_-72_72(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.630_MW | 歸仁大亞線 MW | LINE69 |  |  |  |  | CDC | 21 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 歸仁大亞線 (630) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.630_MVAR | 歸仁大亞線 MVAR | LINE69 |  |  |  |  | CDC | 22 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0044 |  |  | 2-4C |  |  | 歸仁大亞線 (630) MWH(+) |  |  |  |  | B2/S67_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 23 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 歸仁保安線 (660)瓦 |  |  | MW_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_MW | 歸仁保安線 MW | LINE69 |  |  |  |  | CDC | 24 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 歸仁保安線 (660) 乏 |  |  | MVAR_-120_120(-2000_2000) |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_MVAR | 歸仁保安線 MVAR | LINE69 |  |  |  |  | CDC | 25 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0046 |  |  | 2-4E |  |  | 歸仁保安線 (660) MWH(+) |  |  |  |  | B2/S67_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 26 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 新市歸仁線 (670) 67 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_PHA | 新市歸仁線(670) 相間RY | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 新市歸仁線 (670) 67N RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_GDA | 新市歸仁線(670) 接地RY | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 山上歸仁線 (680) 67 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_PHA | 山上歸仁線(680) 相間RY | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 山上歸仁線 (680) 67N RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_GDA | 山上歸仁線(680) 接地RY | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | 歸仁大亞線 (630) 67 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.630_PHA | 歸仁大亞線(630) 相間RY | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | 歸仁大亞線 (630) 67N RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.630_GDA | 歸仁大亞線(630) 接地RY | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | 歸仁保安線 (660) 67 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_PHA | 歸仁保安線(660) 相間RY | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | 歸仁保安線 (660) 67N RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_GDA | 歸仁保安線(660) 接地RY | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 歸仁保安線 (660) 87 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_87A | 660歸仁保安線87RY | OTHER |  |  |  |  | CDC | 35 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 歸仁大亞線 (630) 85RY U/L |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.630_85UL | 歸仁大亞線(630) 85RY U/L | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 歸仁保安線 (660) 87RY U/L |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.660_87UL | 660歸仁保安線87RY UL | OTHER |  |  |  |  | CDC | 37 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0128 |  | 0001 | 1-10-00 |  | 1-01 | 新市歸仁線 (670) CB |  |  |  | aaba | B2/S67_A1 | [8 empty] | 歸仁SS.670_CB | 670(新市歸仁線) CB | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0132 |  | 0002 | 1-10-04 |  | 1-02 | 山上歸仁線 (680) CB |  |  |  | aafa | B2/S67_A1 | [8 empty] | 歸仁SS.680_CB | 680(山上歸仁線) CB | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0136 |  | 0003 | 1-11-00 |  | 1-03 | 歸仁大亞線 (630) CB |  |  |  | aada | B2/S67_A1 | [8 empty] | 歸仁SS.630_CB | 630(歸仁大亞線) CB | LINE69 |  |  |  |  | CDC | 40 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0140 |  | 0004 | 1-11-04 |  | 1-04 | 歸仁保安線 (660) CB |  |  |  | aaga | B2/S67_A1 | [8 empty] | 歸仁SS.660_CB | 660(歸仁保安線) CB | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | ABS1 | 671 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0332 | 333 | 0018 | 1-34-12 | 1-34-13 | 1-12 | 新市歸仁線 (671) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.671_ABS | 671(新市歸仁線) ABS | LINE69 |  |  |  |  | CDC | 42 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | ABS2 | 672 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0334 | 335 | 0019 | 1-34-14 | 1-34-15 | 1-13 | 新市歸仁線 (672) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.672_ABS | 672(新市歸仁線) ABS | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ABS1 | 681 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0338 | 339 | 0021 | 1-35-02 | 1-35-03 | 1-15 | 山上歸仁線 (681) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.681_ABS | 681(山上歸仁線) ABS | LINE69 |  |  |  |  | CDC | 44 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ABS2 | 682 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0340 | 341 | 0022 | 1-35-04 | 1-35-05 | 1-16 | 山上歸仁線 (682) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.682_ABS | 682(山上歸仁線) ABS | LINE69 |  |  |  |  | CDC | 45 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | ABS1 | 631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0344 | 345 | 0024 | 1-35-08 | 1-35-09 | 1-18 | 歸仁大亞線 (631) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.631_ABS | 631(歸仁大亞線) ABS | LINE69 |  |  |  |  | CDC | 46 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | ABS2 | 632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0346 | 347 | 0025 | 1-35-10 | 1-35-11 | 1-19 | 歸仁大亞線 (632) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.632_ABS | 632(歸仁大亞線) ABS | LINE69 |  |  |  |  | CDC | 47 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ABS1 | 661 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0350 | 351 | 0027 | 1-35-14 | 1-35-15 | 1-1B | 歸仁保安線 (661) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.661_ABS | 661(歸仁保安線) ABS | LINE69 |  |  |  |  | CDC | 48 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ABS2 | 662 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0864 | 865 | 0028 | 2-36-00 | 2-36-01 | 1-1C | 歸仁保安線 (662) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.662_ABS | 662(歸仁保安線) ABS | LINE69 |  |  |  |  | CDC | 49 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | ES2 | 672E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0336 | 337 | 0020 | 1-35-00 | 1-35-01 | 1-14 | 新市歸仁線 (672E) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.672E_ES | 672E(新市歸仁線) ES | LINE69 |  |  |  |  | CDC | 50 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | LE0 | 670LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_A1 | [8 empty] | 歸仁SS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 51 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | ES2 | 682E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0342 | 343 | 0023 | 1-35-06 | 1-35-07 | 1-17 | 山上歸仁線 (682E) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.682E_ES | 682E(山上歸仁線) ES | LINE69 |  |  |  |  | CDC | 52 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | LE0 | 680LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_A1 | [8 empty] | 歸仁SS.680LE | 680LE (非取樣點) | LINE69 | [5 empty] | 53 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0348 | 349 | 0026 | 1-35-12 | 1-35-13 | 1-1A | 歸仁大亞線 (632E) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.632E_ES | 632E(歸仁大亞線) ES | LINE69 |  |  |  |  | CDC | 54 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | LE0 | 630LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_A1 | [8 empty] | 歸仁SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 55 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | ES2 | 662E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0866 | 867 | 0029 | 2-36-02 | 2-36-03 | 1-1D | 歸仁保安線 (662E) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.662E_ES | 662E(歸仁保安線) ES | LINE69 |  |  |  |  | CDC | 56 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | LE0 | 660LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_A1 | [8 empty] | 歸仁SS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 57 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 歸33線 (F13) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸33線KVAR | 11KV歸33線 KVAR | FEEDER |  |  |  |  | CDC | 58 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 歸33線 (F13) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸33線A1 | 11KV歸33線 R相AMP | FEEDER |  |  |  |  | CDC | 59 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 歸33線 (F13) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸33線A2 | 11KV歸33線 S相AMP | FEEDER |  |  |  |  | CDC | 60 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 歸33線 (F13) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸33線A3 | 11KV歸33線 T相AMP | FEEDER |  |  |  |  | CDC | 61 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 歸33線 (F13) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸33線A0 | 11KV歸33線 N相AMP | FEEDER |  |  |  |  | CDC | 62 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | 歸33線 (F13) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 63 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 歸38線 (F18) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸38線KVAR | 11KV歸38線 KVAR | FEEDER |  |  |  |  | CDC | 64 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 歸38線 (F18) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸38線A1 | 11KV歸38線 R相AMP | FEEDER |  |  |  |  | CDC | 65 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 歸38線 (F18) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸38線A2 | 11KV歸38線 S相AMP | FEEDER |  |  |  |  | CDC | 66 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 歸38線 (F18) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸38線A3 | 11KV歸38線 T相AMP | FEEDER |  |  |  |  | CDC | 67 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | KR38 (F18) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸38線A0 | 11KV歸38線 N相AMP | FEEDER |  |  |  |  | CDC | 68 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0017 |  |  | 1-51 |  |  | 歸38線 (F18) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 69 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 歸仁線 (F1) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_PHA | 11KV歸仁線(KR21) 相間RY | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 歸仁線 (F1) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_GDA | 11KV歸仁線(KR21) 接地RY | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | 歸仁線 (F1) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_79UL | 11KV歸仁線(KR21) 79RY U/L | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0832 |  | 0152 | 2-34-00 |  | 2-18 | 歸仁線 (F1) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_ADJ | 11KV歸仁線(KR21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 新田線 (F2) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_PHA | 11KV新田線(KR22) 相間RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 新田線 (F2) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_GDA | 11KV新田線(KR22) 接地RY | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | 新田線 (F2) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_79UL | 11KV新田線(KR22) 79RY U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0833 |  | 0153 | 2-34-01 |  | 2-19 | 新田線 (F2) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_ADJ | 11KV新田線(KR22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | 媽廟線 (F3) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_PHA | 11KV媽廟線(KR23) 相間RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 媽廟線 (F3) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_GDA | 11KV媽廟線(KR23) 接地RY | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | 媽廟線 (F3) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_79UL | 11KV媽廟線(KR23) 79RY U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0834 |  | 0154 | 2-34-02 |  | 2-1A | 媽廟線 (F3) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_ADJ | 11KV媽廟線(KR23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | 南保線 (F4) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_PHA | 11KV南保線(KR24) 相間RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | 南保線 (F4) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_GDA | 11KV南保線(KR24) 接地RY | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | 南保線 (F4) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_79UL | 11KV南保線(KR24) 79RY U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0835 |  | 0155 | 2-34-03 |  | 2-1B | 南保線 (F4) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_ADJ | 11KV南保線(KR24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 貝汝線 (F5) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_PHA | 11KV貝汝線(KR25) 相間RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | 貝汝線 (F5) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_GDA | 11KV貝汝線(KR25) 接地RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | 貝汝線 (F5) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_79UL | 11KV貝汝線(KR25) 79RY U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0836 |  | 0156 | 2-34-04 |  | 2-1C | 貝汝線 (F5) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_ADJ | 11KV貝汝線(KR25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | 東盈線 (F6) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_PHA | 11KV東盈線(KR26) 相間RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | 東盈線 (F6) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_GDA | 11KV東盈線(KR26) 接地RY | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0081 | 2-30-07 |  | 1-51 | 東盈線 (F6) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_79UL | 11KV東盈線(KR26) 79RY U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0837 |  | 0157 | 2-34-05 |  | 2-1D | 東盈線 (F6) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_ADJ | 11KV東盈線(KR26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 豐中線 (F7) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_PHA | 11KV豐中線(KR27) 相間RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 豐中線 (F7) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_GDA | 11KV豐中線(KR27) 接地RY | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0082 | 2-30-08 |  | 1-52 | 豐中線 (F7) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_79UL | 11KV豐中線(KR27) 79RY U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0838 |  | 0158 | 2-34-06 |  | 2-1E | 豐中線 (F7) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_ADJ | 11KV豐中線(KR27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 崙頂線 (F8) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_PHA | 11KV崙頂線(KR28) 相間RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 崙頂線 (F8) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_GDA | 11KV崙頂線(KR28) 接地RY | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0083 | 2-30-09 |  | 1-53 | 崙頂線 (F8) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_79UL | 11KV崙頂線(KR28) 79RY U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0839 |  | 0159 | 2-34-07 |  | 2-1F | 崙頂線 (F8) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_ADJ | 11KV崙頂線(KR28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 看西線 (F9) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_PHA | 11KV看西線(KR29) 相間RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 看西線 (F9) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_GDA | 11KV看西線(KR29) 接地RY | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0084 | 2-30-10 |  | 1-54 | 看西線 (F9) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_79UL | 11KV看西線(KR29) 79RY U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0840 |  | 0160 | 2-34-08 |  | 2-20 | 看西線 (F9) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_ADJ | 11KV看西線(KR29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 關廟線 (F10) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_PHA | 11KV關廟線(KR30) 相間RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 關廟線 (F10) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_GDA | 11KV關廟線(KR30) 接地RY | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0085 | 2-30-11 |  | 1-55 | 關廟線 (F10) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_79UL | 11KV關廟線(KR30) 79RY U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0841 |  | 0161 | 2-34-09 |  | 2-21 | 關廟線 (F10) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_ADJ | 11KV關廟線(KR30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 萬芳線 (F11) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_PHA | 11KV萬芳線(KR31) 相間RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 萬芳線 (F11) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_GDA | 11KV萬芳線(KR31) 接地RY | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0101 | 2-31-07 |  | 1-65 | 萬芳線 (F11) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_79UL | 11KV萬芳線(KR31) 79RY U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0842 |  | 0162 | 2-34-10 |  | 2-22 | 萬芳線 (F11) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_ADJ | 11KV萬芳線(KR31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 八甲線 (F12) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_PHA | 11KV八甲線(KR32) 相間RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 八甲線 (F12) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_GDA | 11KV八甲線(KR32) 接地RY | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0102 | 2-31-08 |  | 1-66 | 光裕線 (F12) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_79UL | 11KV八甲線(KR32) 79RY U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0843 |  | 0163 | 2-34-11 |  | 2-23 | 八甲線 (F12) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_ADJ | 11KV八甲線(KR32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 歸33線 (F13) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_PHA | 11KV歸33線(KR33) 相間RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 歸33線 (F13) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_GDA | 11KV歸33線(KR33) 接地RY | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0103 | 2-31-09 |  | 1-67 | 歸33線 (F13) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_79UL | 11KV歸33線(KR33) 79RY U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0844 |  | 0164 | 2-34-12 |  | 2-24 | 歸33線 (F13) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_ADJ | 11KV歸33線(KR33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 深坑線 (F14) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_PHA | 11KV深坑線(KR34) 相間RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 深坑線 (F14) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_GDA | 11KV深坑線(KR34) 接地RY | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0104 | 2-31-10 |  | 1-68 | 深坑線 (F14) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_79UL | 11KV深坑線(KR34) 79RY U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0845 |  | 0165 | 2-34-13 |  | 2-25 | 深坑線 (F14) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_ADJ | 11KV深坑線(KR34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 南潭線 (F15) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_PHA | 11KV南潭線(KR35) 相間RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 南潭線 (F15) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_GDA | 11KV南潭線(KR35) 接地RY | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0795 |  | 0105 | 2-31-11 |  | 1-69 | 南潭線 (F15) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_79UL | 11KV南潭線(KR35) 79RY U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0166 | 2-34-14 |  | 2-26 | 南潭線 (F15) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_ADJ | 11KV南潭線(KR35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 六合線 (F16) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_PHA | 11KV六合線(KR36) 相間RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 六合線 (F16) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_GDA | 11KV六合線(KR36) 接地RY | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0121 | 2-32-07 |  | 1-79 | 六合線 (F16) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_79UL | 11KV六合線(KR36) 79RY U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0167 | 2-34-15 |  | 2-27 | 六合線 (F16) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_ADJ | 11KV六合線(KR36) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 松根線 (F17) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_PHA | 11KV松根線(KR37) 相間RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 松根線 (F17) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_GDA | 11KV松根線(KR37) 接地RY | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0122 | 2-32-08 |  | 1-7A | 松根線 (F17) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_79UL | 11KV松根線(KR37) 79RY U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0848 |  | 0168 | 2-35-00 |  | 2-28 | 松根線 (F17) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_ADJ | 11KV松根線(KR37) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 歸38線 (F18) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_PHA | 11KV歸38線(KR38) 相間RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 歸38線 (F18) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_GDA | 11KV歸38線(KR38) 接地RY | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0809 |  | 0123 | 2-32-09 |  | 1-7B | 歸38線 (F18) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_79UL | 11KV歸38線(KR38) 79RY U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0849 |  | 0169 | 2-35-01 |  | 2-29 | 歸38線 (F18) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_ADJ | 11KV歸38線(KR38) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 沙崙線 (F19) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_PHA | 11KV沙崙線(KR39) 相間RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 沙崙線 (F19) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_GDA | 11KV沙崙線(KR39) 接地RY | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 |  | 0124 | 2-32-10 |  | 1-7C | 沙崙線 (F19) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_79UL | 11KV沙崙線(KR39) 79RY U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0850 |  | 0170 | 2-35-02 |  | 2-2A | 沙崙線 (F19) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_ADJ | 11KV沙崙線(KR39) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 漢平線 (F20) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_PHA | 11KV漢平線(KR40) 相間RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  |  | 1-1E-05 |  |  | 漢平線 (F20) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_GDA | 11KV漢平線(KR40) 接地RY | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0811 |  | 0125 | 2-32-11 |  | 1-7D | 漢平線 (F20) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_79UL | 11KV漢平線(KR40) 79RY U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0851 |  | 0171 | 2-35-03 |  | 2-2B | 漢平線 (F20) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_ADJ | 11KV漢平線(KR40) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0641 |  |  | 2-10-01 |  |  | 歸南線 (F21) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_PHA | 11KV歸南線(KR41) 相間RY | FEEDER |  |  |  |  | CDC | 150 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0642 |  |  | 2-10-02 |  |  | 歸南線 (F21) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_GDA | 11KV歸南線(KR41) 接地RY | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0140 | 2-33-07 |  | 2-0C | 歸南線 (F21) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_79UL | 11KV歸南線(KR41) 79RY U/L | FEEDER |  |  |  |  | CDC | 152 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0852 |  | 0172 | 2-35-04 |  | 2-2C | 歸南線 (F21) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_ADJ | 11KV歸南線(KR41) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0643 |  |  | 2-10-03 |  |  | 古厝線 (F22) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_PHA | 11KV古厝線(KR42) 相間RY | FEEDER |  |  |  |  | CDC | 154 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0644 |  |  | 2-10-04 |  |  | 古厝線 (F22) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_GDA | 11KV古厝線(KR42) 接地RY | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0824 |  | 0141 | 2-33-08 |  | 2-0D | 古厝線 (F22) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_79UL | 11KV古厝線(KR42) 79RY U/L | FEEDER |  |  |  |  | CDC | 156 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0853 |  | 0173 | 2-35-05 |  | 2-2D | 古厝線 (F22) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_ADJ | 11KV古厝線(KR42) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0645 |  |  | 2-10-05 |  |  | 龍崎線 (F23) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_PHA | 11KV龍崎線(KR43) 相間RY | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0646 |  |  | 2-10-06 |  |  | 龍崎線 (F23) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_GDA | 11KV龍崎線(KR43) 接地RY | FEEDER |  |  |  |  | CDC | 159 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0825 |  | 0142 | 2-33-09 |  | 2-0E | 龍崎線 (F23) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_79UL | 11KV龍崎線(KR43) 79RY U/L | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0854 |  | 0174 | 2-35-06 |  | 2-2E | 龍崎線 (F23) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_ADJ | 11KV龍崎線(KR43) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 161 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0647 |  |  | 2-10-07 |  |  | 關甲線 (F24) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_PHA | 11KV關甲線(KR44) 相間RY | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0648 |  |  | 2-11-00 |  |  | 關甲線 (F24) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_GDA | 11KV關甲線(KR44) 接地RY | FEEDER |  |  |  |  | CDC | 163 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0826 |  | 0143 | 2-33-10 |  | 2-0F | 關甲線 (F24) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_79UL | 11KV關甲線(KR44) 79RY U/L | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0855 |  | 0175 | 2-35-07 |  | 2-2F | 關甲線 (F24) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_ADJ | 11KV關甲線(KR44) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 165 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0649 |  |  | 2-11-01 |  |  | 仁傑線 (F25) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_PHA | 11KV仁傑線(KR45) 相間RY | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0650 |  |  | 2-11-02 |  |  | 仁傑線 (F25) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_GDA | 11KV仁傑線(KR45) 接地RY | FEEDER |  |  |  |  | CDC | 167 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0827 |  | 0144 | 2-33-11 |  | 2-10 | 仁傑線 (F25) 79RY U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_79UL | 11KV仁傑線(KR45) 79RY U/L | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0856 |  | 0176 | 2-35-08 |  | 2-30 | 仁傑線 (F25) LCO ADJ U/L |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_ADJ | 11KV仁傑線(KR45) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 169 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KR21/T1 |  |  | 0160 |  | 0052 | 1-14-00 |  | 1-34 | 歸仁線 (F1) CB |  |  |  | aabb | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_CB | KR21(11KV歸仁線) CB | FEEDER |  |  |  |  | CDC | 170 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_DS | KR21_DS (非取樣點) | FEEDER | [5 empty] | 171 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | ES | KR21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_ES | KR21_ES (非取樣點) | FEEDER | [5 empty] | 172 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KR22/T1 |  |  | 0161 |  | 0053 | 1-14-01 |  | 1-35 | 新田線 (F2) CB |  |  |  | aadb | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_CB | KR22(11KV新田線) CB | FEEDER |  |  |  |  | CDC | 173 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_DS | KR22_DS (非取樣點) | FEEDER | [5 empty] | 174 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | ES | KR22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_ES | KR22_ES (非取樣點) | FEEDER | [5 empty] | 175 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KR23/T1 |  |  | 0162 |  | 0054 | 1-14-02 |  | 1-36 | 媽廟線 (F3) CB |  |  |  | aaeb | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_CB | KR23(11KV媽廟線) CB | FEEDER |  |  |  |  | CDC | 176 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_DS | KR23_DS (非取樣點) | FEEDER | [5 empty] | 177 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | ES | KR23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_ES | KR23_ES (非取樣點) | FEEDER | [5 empty] | 178 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KR24/T1 |  |  | 0163 |  | 0055 | 1-14-03 |  | 1-37 | 南保線 (F4) CB |  |  |  | aafb | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_CB | KR24(11KV南保線) CB | FEEDER |  |  |  |  | CDC | 179 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_DS | KR24_DS (非取樣點) | FEEDER | [5 empty] | 180 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | ES | KR24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_ES | KR24_ES (非取樣點) | FEEDER | [5 empty] | 181 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KR25/T1 |  |  | 0164 |  | 0056 | 1-14-04 |  | 1-38 | 貝汝線 (F5) CB |  |  |  | aagb | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_CB | KR25(11KV貝汝線) CB | FEEDER |  |  |  |  | CDC | 182 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_DS | KR25_DS (非取樣點) | FEEDER | [5 empty] | 183 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | ES | KR25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_ES | KR25_ES (非取樣點) | FEEDER | [5 empty] | 184 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | L/KR26/T1 |  |  | 0182 |  | 0073 | 1-16-06 |  | 1-49 | 東盈線 (F6) CB |  |  |  | abab | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_CB | KR26(11KV東盈線) CB | FEEDER |  |  |  |  | CDC | 185 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_DS | KR26_DS (非取樣點) | FEEDER | [5 empty] | 186 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | ES | KR26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_ES | KR26_ES (非取樣點) | FEEDER | [5 empty] | 187 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | L/KR27/T1 |  |  | 0183 |  | 0074 | 1-16-07 |  | 1-4A | 豐中線 (F7) CB |  |  |  | abbb | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_CB | KR27(11KV豐中線) CB | FEEDER |  |  |  |  | CDC | 188 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_DS | KR27_DS (非取樣點) | FEEDER | [5 empty] | 189 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | ES | KR27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_ES | KR27_ES (非取樣點) | FEEDER | [5 empty] | 190 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | L/KR28/T1 |  |  | 0184 |  | 0075 | 1-17-00 |  | 1-4B | 崙頂線 (F8) CB |  |  |  | abcb | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_CB | KR28(11KV崙頂線) CB | FEEDER |  |  |  |  | CDC | 191 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_DS | KR28_DS (非取樣點) | FEEDER | [5 empty] | 192 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | ES | KR28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_ES | KR28_ES (非取樣點) | FEEDER | [5 empty] | 193 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | L/KR29/T1 |  |  | 0185 |  | 0076 | 1-17-01 |  | 1-4C | 看西線 (F9) CB |  |  |  | abeb | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_CB | KR29(11KV看西線) CB | FEEDER |  |  |  |  | CDC | 194 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_DS | KR29_DS (非取樣點) | FEEDER | [5 empty] | 195 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | ES | KR29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR29_ES | KR29_ES (非取樣點) | FEEDER | [5 empty] | 196 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | L/KR30/T1 |  |  | 0186 |  | 0077 | 1-17-02 |  | 1-4D | 關廟線 (F10) CB |  |  |  | abfb | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_CB | KR30(11KV關廟線) CB | FEEDER |  |  |  |  | CDC | 197 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_DS | KR30_DS (非取樣點) | FEEDER | [5 empty] | 198 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | ES | KR30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_ES | KR30_ES (非取樣點) | FEEDER | [5 empty] | 199 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KR31/T1 |  |  | 0204 |  | 0093 | 1-19-04 |  | 1-5D | 萬芳線 (F11) CB |  |  |  | acab | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_CB | KR31(11KV萬芳線) CB | FEEDER |  |  |  |  | CDC | 200 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_DS | KR31_DS (非取樣點) | FEEDER | [5 empty] | 201 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | ES | KR31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_ES | KR31_ES (非取樣點) | FEEDER | [5 empty] | 202 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KR32/T1 |  |  | 0205 |  | 0094 | 1-19-05 |  | 1-5E | 八甲線 (F12) CB |  |  |  | acbb | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_CB | KR32(11KV八甲線) CB | FEEDER |  |  |  |  | CDC | 203 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_DS | KR32_DS (非取樣點) | FEEDER | [5 empty] | 204 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | ES | KR32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_ES | KR32_ES (非取樣點) | FEEDER | [5 empty] | 205 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KR33/T1 |  |  | 0206 |  | 0095 | 1-19-06 |  | 1-5F | 歸33線 (F13) CB |  |  |  | acdb | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_CB | KR33(11KV歸33線) CB | FEEDER |  |  |  |  | CDC | 206 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_DS | KR33_DS (非取樣點) | FEEDER | [5 empty] | 207 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | ES | KR33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_ES | KR33_ES (非取樣點) | FEEDER | [5 empty] | 208 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KR34/T1 |  |  | 0207 |  | 0096 | 1-19-07 |  | 1-60 | 深坑線 (F14) CB |  |  |  | aceb | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_CB | KR34(11KV深坑線) CB | FEEDER |  |  |  |  | CDC | 209 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_DS | KR34_DS (非取樣點) | FEEDER | [5 empty] | 210 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | ES | KR34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_ES | KR34_ES (非取樣點) | FEEDER | [5 empty] | 211 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KR35/T1 |  |  | 0208 |  | 0097 | 1-1A-00 |  | 1-61 | 南潭線 (F15) CB |  |  |  | acfb | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_CB | KR35(11KV南潭線) CB | FEEDER |  |  |  |  | CDC | 212 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_DS | KR35_DS (非取樣點) | FEEDER | [5 empty] | 213 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | ES | KR35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_ES | KR35_ES (非取樣點) | FEEDER | [5 empty] | 214 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | L/KR36/T1 |  |  | 0227 |  | 0113 | 1-1C-03 |  | 1-71 | 六合線 (F16) CB |  |  |  | adcb | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_CB | KR36(11KV六合線) CB | FEEDER |  |  |  |  | CDC | 215 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_DS | KR36_DS (非取樣點) | FEEDER | [5 empty] | 216 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | ES | KR36_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_ES | KR36_ES (非取樣點) | FEEDER | [5 empty] | 217 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | L/KR37/T1 |  |  | 0228 |  | 0114 | 1-1C-04 |  | 1-72 | 松根線 (F17) CB |  |  |  | addb | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_CB | KR37(11KV松根線) CB | FEEDER |  |  |  |  | CDC | 218 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_DS | KR37_DS (非取樣點) | FEEDER | [5 empty] | 219 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | ES | KR37_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_ES | KR37_ES (非取樣點) | FEEDER | [5 empty] | 220 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | L/KR38/T1 |  |  | 0229 |  | 0115 | 1-1C-05 |  | 1-73 | 歸38線 (F18) CB |  |  |  | adfb | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_CB | KR38(11KV歸38線) CB | FEEDER |  |  |  |  | CDC | 221 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_DS | KR38_DS (非取樣點) | FEEDER | [5 empty] | 222 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | ES | KR38_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_ES | KR38_ES (非取樣點) | FEEDER | [5 empty] | 223 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | L/KR39/T1 |  |  | 0230 |  | 0116 | 1-1C-06 |  | 1-74 | 沙崙線 (F19) CB |  |  |  | adgb | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_CB | KR39(11KV沙崙線) CB | FEEDER |  |  |  |  | CDC | 224 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_DS | KR39_DS (非取樣點) | FEEDER | [5 empty] | 225 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | ES | KR39_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_ES | KR39_ES (非取樣點) | FEEDER | [5 empty] | 226 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | L/KR40/T1 |  |  | 0231 |  | 0117 | 1-1C-07 |  | 1-75 | 漢平線 (F20) CB |  |  |  | adhb | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_CB | KR40(11KV漢平線) CB | FEEDER |  |  |  |  | CDC | 227 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | DS1 | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_DS | KR40_DS (非取樣點) | FEEDER | [5 empty] | 228 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | ES | KR40_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_ES | KR40_ES (非取樣點) | FEEDER | [5 empty] | 229 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KR41/T1 |  |  | 0249 |  | 0132 | 1-1F-01 |  | 2-04 | 歸南線 (F21) CB |  |  |  | aeab | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_CB | KR41(11KV歸南線) CB | FEEDER |  |  |  |  | CDC | 230 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_DS | KR41_DS (非取樣點) | FEEDER | [5 empty] | 231 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | ES | KR41_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_ES | KR41_ES (非取樣點) | FEEDER | [5 empty] | 232 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KR42/T1 |  |  | 0250 |  | 0133 | 1-1F-02 |  | 2-05 | 古厝線 (F22) CB |  |  |  | aebb | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_CB | KR42(11KV古厝線) CB | FEEDER |  |  |  |  | CDC | 233 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_DS | KR42_DS (非取樣點) | FEEDER | [5 empty] | 234 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | ES | KR42_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_ES | KR42_ES (非取樣點) | FEEDER | [5 empty] | 235 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KR43/T1 |  |  | 0251 |  | 0134 | 1-1F-03 |  | 2-06 | 龍崎線 (F23) CB |  |  |  | aecb | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_CB | KR43(11KV龍崎線) CB | FEEDER |  |  |  |  | CDC | 236 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_DS | KR43_DS (非取樣點) | FEEDER | [5 empty] | 237 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | ES | KR43_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_ES | KR43_ES (非取樣點) | FEEDER | [5 empty] | 238 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KR44/T1 |  |  | 0252 |  | 0135 | 1-1F-04 |  | 2-07 | 關甲線 (F24) CB |  |  |  | aeeb | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_CB | KR44(11KV關甲線) CB | FEEDER |  |  |  |  | CDC | 239 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_DS | KR44_DS (非取樣點) | FEEDER | [5 empty] | 240 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | ES | KR44_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_ES | KR44_ES (非取樣點) | FEEDER | [5 empty] | 241 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KR45/T1 |  |  | 0253 |  | 0136 | 1-1F-05 |  | 2-08 | 仁傑線 (F25) CB |  |  |  | aefb | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_CB | KR45(11KV仁傑線) CB | FEEDER |  |  |  |  | CDC | 242 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_DS | KR45_DS (非取樣點) | FEEDER | [5 empty] | 243 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | ES | KR45_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_ES | KR45_ES (非取樣點) | FEEDER | [5 empty] | 244 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R | #1-#2 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1- #2 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE1_A1 | 11KV #1-#2 TIE R相AMP | TIE |  |  |  |  | CDC | 245 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S | #1-#2 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1- #2 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE1_A2 | 11KV #1-#2 TIE S相AMP | TIE |  |  |  |  | CDC | 246 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T | #1-#2 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1- #2 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE1_A3 | 11KV #1-#2 TIE T相AMP | TIE |  |  |  |  | CDC | 247 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R | #3-#2 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #3- #2 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE2_A1 | 11KV #3-#2 TIE R相AMP | TIE |  |  |  |  | CDC | 248 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S | #3-#2 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #3- #2 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE2_A2 | 11KV #3-#2 TIE S相AMP | TIE |  |  |  |  | CDC | 249 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T | #3-#2 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #3- #2 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE2_A3 | 11KV #3-#2 TIE T相AMP | TIE |  |  |  |  | CDC | 250 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R | #6-#3 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | #6- #3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE3_A1 | 11KV #6-#3 TIE R相AMP | TIE |  |  |  |  | CDC | 251 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S | #6-#3 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | #6- #3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE3_A2 | 11KV #6-#3 TIE S相AMP | TIE |  |  |  |  | CDC | 252 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T | #6-#3 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | #6- #3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE3_A3 | 11KV #6-#3 TIE T相AMP | TIE |  |  |  |  | CDC | 253 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_R | #4-#1 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | #4- #1 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE4_A1 | 11KV #4-#1 TIE R相AMP | TIE |  |  |  |  | CDC | 254 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_S | #4-#1 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | #4- #1 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE4_A2 | 11KV #4-#1 TIE S相AMP | TIE |  |  |  |  | CDC | 255 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_T | #4-#1 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | #4- #1 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.11KV_TIE4_A3 | 11KV #4-#1 TIE T相AMP | TIE |  |  |  |  | CDC | 256 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB | #1-#2 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2A | B/1BUS | B/2BUS |  |  | 0165 |  | 0050 | 1-14-05 |  | 1-32 | #1- #2 TIE CB |  |  |  | zzzz | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_CB | 11KV #1-#2 TIE CB | TIE |  |  |  |  | CDC | 257 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A | #1-#2 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | #1- #2 TIE 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_51A | 11KV #1-#2 TIE 51RY | TIE |  |  |  |  | CDC | 258 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA | #1-#2 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | #1- #2 TIE 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_51NA | 11KV #1-#2 TIE 51N RY | TIE |  |  |  |  | CDC | 259 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB | #3-#2 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BUS | B/3BUS |  |  | 0187 |  | 0071 | 1-17-03 |  | 1-47 | #3- #2 TIE CB |  |  |  | zzzz | B2/S67_D1 | [8 empty] | 歸仁SS.TIE2_CB | 11KV #3-#2 TIE CB | TIE |  |  |  |  | CDC | 260 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A | #3-#2 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #3- #2 TIE 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE2_51A | 11KV #3-#2 TIE 51RY | TIE |  |  |  |  | CDC | 261 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA | #3-#2 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | #3- #2 TIE 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE2_51NA | 11KV #3-#2 TIE 51N RY | TIE |  |  |  |  | CDC | 262 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB | #6-#3 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/6BUS | S |  |  | 0209 |  | 0091 | 1-1A-01 |  | 1-5B | #6- #3 TIE CB |  |  |  | zzzz | B2/S67_D1 | [8 empty] | 歸仁SS.TIE3_CB | 11KV #6-#3 TIE CB | TIE |  |  |  |  | CDC | 263 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A | #6-#3 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | #6- #3 TIE 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE3_51A | 11KV #6-#3 TIE 51RY | TIE |  |  |  |  | CDC | 264 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA | #6-#3 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | #6- #3 TIE 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE3_51NA | 11KV #6-#3 TIE 51N RY | TIE |  |  |  |  | CDC | 265 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | CB | #4-#1 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2A | B/4BUS | B/1BUS |  |  | 0232 |  | 0111 | 1-1D-00 |  | 1-6F | #4- #1 TIE CB |  |  |  | zzzz | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_CB | 11KV #4-#1 TIE CB | TIE |  |  |  |  | CDC | 266 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51A | #4-#1 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | #4- #1 TIE 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_51A | 11KV #4-#1 TIE 51RY | TIE |  |  |  |  | CDC | 267 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51NA | #4-#1 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | #4- #1 TIE 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_51NA | 11KV #4-#1 TIE 51N RY | TIE |  |  |  |  | CDC | 268 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | DS1 | #1-#2(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_DS | #1-#2 TIE_DS (非取樣點) | TIE | [5 empty] | 269 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 1BR | #1BR |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | B/2BUS | [13 empty] | abhb | B2/S67_D1 | [8 empty] | 歸仁SS.1BR_DS | 1BR_DS (非取樣點) | TIE | [5 empty] | 270 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | #3-#2(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE2_DS | #3-#2 TIE_DS (非取樣點) | TIE | [5 empty] | 271 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 2BR | #2BR |  | DS | 2BR_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.2BR_DS | 2BR_DS (非取樣點) | TIE | [5 empty] | 272 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | D1 | #6-#3(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE3_DS | #6-#3 TIE_DS (非取樣點) | TIE | [5 empty] | 273 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | DS1 | #4-#1(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_DS | #4-#1 TIE_DS (非取樣點) | TIE | [5 empty] | 274 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | E1 | #4-#1(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_ES | #4-#1 TIE_ES (非取樣點) | OTHER | [5 empty] | 275 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 276 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 277 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 278 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 279 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 280 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 281 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 282 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 283 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 284 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 285 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 286 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 287 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 288 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 289 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 290 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | #4 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4MTR_MW | #4MTR二次側 MW | DTR |  |  |  |  | CDC | 291 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | #4 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR |  |  |  |  | CDC | 292 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | #4 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 293 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | #4 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 294 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | #4 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 295 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | #6 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6MTR_MW | #6MTR二次側 MW | DTR |  |  |  |  | CDC | 296 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | #6 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6MTR_MVAR | #6MTR二次側 MVAR | DTR |  |  |  |  | CDC | 297 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | #6 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6MTR_A1 | #6MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 298 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | #6 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6MTR_A2 | #6MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 299 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | #6 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6MTR_A3 | #6MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 300 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 301 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 302 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 303 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0025 |  |  | 1-59 |  |  | #1 TR MWH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 304 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0026 |  |  | 1-5A |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 305 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 306 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 307 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 308 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | #2 TR MWH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 309 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0029 |  |  | 1-5D |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 310 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 311 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 312 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-62 | #3 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 313 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0031 |  |  | 1-5F |  |  | #3 TR MWH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 314 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0032 |  |  | 2-40 |  |  | #3 TR MVARH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 315 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | #4 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_OIL | #4MTR 油溫 | DTR |  |  |  |  | CDC | 316 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | #4 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_COIL | #4MTR 線溫 | DTR |  |  |  |  | CDC | 317 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0140 |  | 0118 | 2-8C |  | 1-76 | #4 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_TAP | #4MTR OLTC TAP | DTR |  |  |  |  | CDC | 318 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0034 |  |  | 2-42 |  |  | #4 TR MWH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 319 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | MVARH_P |  | Element | [12 empty] | 0035 |  |  | 2-43 |  |  | #4 TR MVARH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 320 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | #6 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_OIL | #6MTR 油溫 | DTR |  |  |  |  | CDC | 321 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | #6 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_COIL | #6MTR 線溫 | DTR |  |  |  |  | CDC | 322 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0176 |  | 0137 | 2-B0 |  | 2-09 | #6 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_TAP | #6MTR OLTC TAP | DTR |  |  |  |  | CDC | 323 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0037 |  |  | 2-45 |  |  | #6 TR MWH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 324 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | MVARH_P |  | Element | [12 empty] | 0038 |  |  | 2-46 |  |  | #6 TR MVARH(+) |  |  |  |  | B1/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 325 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | #1TR 一次 (750) CB |  |  |  | aaab | B3/S67_D1 | [8 empty] | 歸仁SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 326 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 327 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 328 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | #2TR 一次 (760) CB |  |  |  | aaeb | B3/S67_D1 | [8 empty] | 歸仁SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 329 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 330 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 331 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/3MTR |  |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | #3TR 一次 (770) CB |  |  |  | aahb | B3/S67_D1 | [8 empty] | 歸仁SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 332 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 333 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 334 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/4MTR |  |  | 0034 |  | 0108 | 1-04-02 |  | 1-6C | #4TR 一次 (780) CB |  |  |  | aaib | B3/S67_D1 | [8 empty] | 歸仁SS.780_CB | 780(#4MTR) CB | DTR |  |  |  |  | CDC | 335 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.780TE | 780TE (非取樣點) | DTR | [5 empty] | 336 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.780BE | 780BE (非取樣點) | DTR | [5 empty] | 337 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | L | T/6MTR |  |  | 0046 |  | 0128 | 1-05-06 |  | 2-00 | #6TR 一次 (790) CB |  |  |  | aajb | B3/S67_D1 | [8 empty] | 歸仁SS.790_CB | 790(#6MTR) CB | DTR |  |  |  |  | CDC | 338 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | TE0 | 790TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.790TE | 790TE (非取樣點) | DTR | [5 empty] | 339 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | BE0 | 790BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S67_D1 | [8 empty] | 歸仁SS.790BE | 790BE (非取樣點) | DTR | [5 empty] | 340 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1TR 二次 (#1MT) CB |  |  |  | aaca | B2/S67_D1 | [8 empty] | 歸仁SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 341 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2TR 二次 (#2MT) CB |  |  |  | abda | B2/S67_D1 | [8 empty] | 歸仁SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 342 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0023 |  | 0089 | 1-02-07 |  | 1-59 | #3TR 二次 (#3MT) CB |  |  |  | acca | B2/S67_D1 | [8 empty] | 歸仁SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 343 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | T/4MTR |  |  | 0035 |  | 0109 | 1-04-03 |  | 1-6D | #4TR 二次 (#4MT) CB |  |  |  | adea | B2/S67_D1 | [8 empty] | 歸仁SS.4M_CB | 4M(#4MTR) CB | DTR |  |  |  |  | CDC | 344 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | T/6MTR |  |  | 0047 |  | 0129 | 1-05-07 |  | 2-01 | #6TR 二次 (#6MT) CB |  |  |  | aeda | B2/S67_D1 | [8 empty] | 歸仁SS.6M_CB | 6M(#6MTR) CB | DTR |  |  |  |  | CDC | 345 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次 (750) 51 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 346 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 一次 (750) 51N RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 347 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 51Z RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 348 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 87 RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 349 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 350 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  | 0065 | 1-14-06 |  | 1-41 | 750 BUS 81 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#1MTR_81A/S | #750 81RY A/S | DTR |  |  |  |  | CDC | 351 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 一次 (760) 51 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 352 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 一次 (760) 51N RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 353 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2TR 51Z RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 354 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2TR 87 RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 355 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 2-30-03 |  |  | #2TR 87 LS1S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 356 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  | 0086 | 1-17-04 |  | 1-56 | 760 780 BUS 81 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#2MTR_81A/S | #760.#780 81RY A/S | DTR |  |  |  |  | CDC | 357 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3TR 一次 (770) 51 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 358 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3TR 一次 (770) 51N RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 359 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3TR 51Z RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 360 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3TR 87 RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 361 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 2-31-03 |  |  | #3TR 87 LS1S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 362 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  | 0106 | 1-1A-02 |  | 1-6A | 770 BUS 81 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#3MTR_81A/S | #770 81RY A/S | DTR |  |  |  |  | CDC | 363 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #4TR 一次 (780) 51 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#4MTR_51A | #4MTR 51RY | DTR |  |  |  |  | CDC | 364 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #4TR 一次 (780) 51N RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#4MTR_51NA | #4MTR 51N RY | DTR |  |  |  |  | CDC | 365 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #4TR 51Z RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_51ZA | #4MTR 51Z RY | DTR |  |  |  |  | CDC | 366 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | #4TR 87 RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_87A | #4MTR 87RY | DTR |  |  |  |  | CDC | 367 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 |  |  | 2-32-03 |  |  | #4TR 87 LS1S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_87UL1 | #4MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 368 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #6TR 一次 (790) 51 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#6MTR_51A | #6MTR 51RY | DTR |  |  |  |  | CDC | 369 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #6TR 一次 (790) 51N RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#6MTR_51NA | #6MTR 51N RY | DTR |  |  |  |  | CDC | 370 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #6TR 51Z RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_51ZA | #6MTR 51Z RY | DTR |  |  |  |  | CDC | 371 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #6TR 87 RY |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_87A | #6MTR 87RY | DTR |  |  |  |  | CDC | 372 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 2-33-03 |  |  | #6TR 87 LS1S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_87UL1 | #6MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 373 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  | 0145 | 1-1F-06 |  | 2-11 | 790 BUS 81 RY |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.#6MTR_81A/S | #790 81RY A/S | DTR |  |  |  |  | CDC | 374 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1TR 二次 (#1MT) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 375 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 376 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 377 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 378 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1TR OLTC A/M |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 379 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2TR 二次 (#2MT) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 380 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 381 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 382 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 2-30-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 383 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0079 | 2-30-05 |  | 1-4F | #2TR OLTC A/M |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 384 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3TR 二次 (#3MT) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 385 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0784 |  |  | 2-31-00 |  |  | #3TR 重故障 |  |  |  | a | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 386 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0785 |  |  | 2-31-01 |  |  | #3TR 輕故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 387 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0788 |  |  | 2-31-04 |  |  | #3TR OLTC R/L |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 388 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0099 | 2-31-05 |  | 1-63 | #3TR OLTC A/M |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 389 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | #4TR 二次 (#4MT) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.4M_51A | #4MTR二次側(4M) 51RY | DTR |  |  |  |  | CDC | 390 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 2-32-00 |  |  | #4TR 重故障 |  |  |  | a | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_TRA | #4MTR 重故障 | DTR |  |  |  |  | CDC | 391 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0801 |  |  | 2-32-01 |  |  | #4TR 輕故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_TRF | #4MTR 輕故障 | DTR |  |  |  |  | CDC | 392 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | #4TR OLTC R/L |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_S/L | #4MTR OLTC S/L | DTR |  |  |  |  | CDC | 393 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0805 |  | 0119 | 2-32-05 |  | 1-77 | #4TR OLTC A/M |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_A/M | #4MTR OLTC A/M | DTR |  |  |  |  | CDC | 394 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #6TR 二次 (#6MT) 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.6M_51A | #6MTR二次側(6M) 51RY | DTR |  |  |  |  | CDC | 395 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | #6TR 重故障 |  |  |  | a | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_TRA | #6MTR 重故障 | DTR |  |  |  |  | CDC | 396 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | #6TR 輕故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_TRF | #6MTR 輕故障 | DTR |  |  |  |  | CDC | 397 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 2-33-04 |  |  | #6TR OLTC R/L |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_S/L | #6MTR OLTC S/L | DTR |  |  |  |  | CDC | 398 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0821 |  | 0138 | 2-33-05 |  | 2-0A | #6TR OLTC A/M |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_A/M | #6MTR OLTC A/M | DTR |  |  |  |  | CDC | 399 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0320 | 321 | 0040 | 1-34-00 | 1-34-01 | 1-28 | #1TR (751) ABS |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 400 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0322 | 323 | 0041 | 1-34-02 | 1-34-03 | 1-29 | #2TR (761) ABS |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 401 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0324 | 325 | 0042 | 1-34-04 | 1-34-05 | 1-2A | #3TR (771) ABS |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.771_ABS | 771(#3MTR) ABS | DTR |  |  |  |  | CDC | 402 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0326 | 327 | 0043 | 1-34-06 | 1-34-07 | 1-2B | #4TR (781) ABS |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.781_ABS | 781(#4MTR) ABS | DTR |  |  |  |  | CDC | 403 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | ABS1 | 791 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0328 | 329 | 0044 | 1-34-08 | 1-34-09 | 1-2C | #6TR (791) ABS |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.791_ABS | 791(#6MTR) ABS | DTR |  |  |  |  | CDC | 404 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS1 | 1M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 405 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 406 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 機械保護動作 (96PA) |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 407 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 408 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1TR 冷卻電源故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 409 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS1 | 2M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 410 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 411 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 412 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 413 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 2-30-12 |  |  | #2TR 冷卻電源故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 414 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 415 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 416 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3TR 機械保護動作(96PA) |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR |  |  |  |  | CDC | 417 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 2-31-02 |  |  | #3TR OLTC 遲滯 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 418 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 2-31-12 |  |  | #3TR 冷卻電源故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 419 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | DS1 | 4M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.4M_DS | 4M_DS (非取樣點) | DTR | [5 empty] | 420 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | ES | 4M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.4M_ES | 4M_ES (非取樣點) | DTR | [5 empty] | 421 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #4TR 機械保護動作(96PA) |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR |  |  |  |  | CDC | 422 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0802 |  |  | 2-32-02 |  |  | #4TR OLTC 遲滯 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 423 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | #4TR 冷卻電源故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR |  |  |  |  | CDC | 424 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.6M_DS | 6M_DS (非取樣點) | DTR | [5 empty] | 425 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | ES | 6M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.6M_ES | 6M_ES (非取樣點) | DTR | [5 empty] | 426 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #6TR 機械保護動作(96PA) |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_96PA | #6MTR 機械保護動作 | DTR |  |  |  |  | CDC | 427 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | #6TR OLTC 遲滯 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_OLTC遲滯 | #6MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 428 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | #6TR 冷卻電源故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_AC_FAULT | #6MTR AC電源失效 | DTR |  |  |  |  | CDC | 429 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0156 |  | 0008 | 1-13-04 |  | 1-08 | 69KV (810) SC CB |  |  |  | aacb | B2/S67_A1 | [8 empty] | 歸仁SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 430 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0159 |  | 0051 | 1-13-07 |  | 1-33 | #1 11KV SC CB |  |  |  | aaab | B2/S67_D1 | [8 empty] | 歸仁SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 431 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1SC Q-CTL A/M |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 432 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 433 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | C/2SC |  |  | 0181 |  | 0072 | 1-16-05 |  | 1-48 | #2 11KV SC CB |  |  |  | abgb | B2/S67_D1 | [8 empty] | 歸仁SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 434 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0774 |  | 0080 | 2-30-06 |  | 1-50 | #2SC Q-CTL A/M |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 435 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 436 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | C/3SC |  |  | 0203 |  | 0092 | 1-19-03 |  | 1-5C | #3 11KV SC CB |  |  |  | acgb | B2/S67_D1 | [8 empty] | 歸仁SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 437 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0790 |  | 0100 | 2-31-06 |  | 1-64 | #3SC Q-CTL A/M |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 438 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 439 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/4BUS | C/4SC |  |  | 0226 |  | 0112 | 1-1C-02 |  | 1-70 | #4 11KV SC CB |  |  |  | adib | B2/S67_D1 | [8 empty] | 歸仁SS.240_CB | 240(11KV #4SC) CB | SC |  |  |  |  | CDC | 440 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0806 |  | 0120 | 2-32-06 |  | 1-78 | #4SC Q-CTL A/M |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.240_A/M | 11KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 441 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | ES | 240_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 442 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | C/6SC |  |  | 0248 |  | 0131 | 1-1F-00 |  | 2-03 | #6 11KV SC CB |  |  |  | aegb | B2/S67_D1 | [8 empty] | 歸仁SS.260_CB | 260(11KV #6SC) CB | SC |  |  |  |  | CDC | 443 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0822 |  | 0139 | 2-33-06 |  | 2-0B | #6SC Q-CTL A/M |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.260_A/M | 11KV #6SC 乏控器 A/M | SC |  |  |  |  | CDC | 444 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | ES | 260_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 445 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0330 | 331 | 0039 | 1-34-10 | 1-34-11 | 1-27 | 69KV SC (811) ABS |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 446 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 69KV (810) SC 51,51N RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 447 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0158 |  |  | 1-13-06 |  |  | 69KV (810) SC 27,59 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 448 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 449 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 450 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 451 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 452 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | #3SC 51,51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 453 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #3SC 27,59 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 454 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | #4SC 51,51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.240_SCA | 11KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 455 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | #4SC 27,59 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 456 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | #6SC 51,51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.260_SCA | 11KV #6SC 51,51N RY | SC |  |  |  |  | CDC | 457 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0640 |  |  | 2-10-00 |  |  | #6SC 27,59 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.260_UVA | 11KV #6SC 27RY(欠壓) | SC |  |  |  |  | CDC | 458 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.210_DS1 | 210_DS1 (非取樣點) | SC | [5 empty] | 459 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.220_DS1 | 220_DS1 (非取樣點) | SC | [5 empty] | 460 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 461 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 462 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 463 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 464 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 465 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 466 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 467 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 468 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 469 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCL4 |  | B2 | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 470 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | ADCH4 |  | B2 | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 471 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 歸仁SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 474 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 開關場照明 C/T |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 475 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 476 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | ACB 1S |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 477 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | ACB 2S |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 479 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 480 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 483 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 484 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 2-35-12 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0861 |  |  | 2-35-13 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 488 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0862 |  |  | 2-35-14 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 489 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0863 |  |  | 2-35-15 |  |  | 博碼調變器故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 490 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.火災警報(1) | 火警 | OTHER |  |  |  |  | CDC | 491 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 492 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 493 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 開關場照明 A/M |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 494 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 495 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.保全設定 | 保全設定 | OTHER |  |  |  |  | CDC | 496 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV (810) SC 警報 |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 497 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 498 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次 (#1MT) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER |  |  |  |  | CDC | 499 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 二次 (#2MT) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER |  |  |  |  | CDC | 500 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #3TR 二次 (#3MT) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#3_MAIN_51NA | #3 MAIN 51NA | OTHER |  |  |  |  | CDC | 501 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | #4TR 二次 (#4MT) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4_MAIN_51NA | #4 MAIN 51NA | OTHER |  |  |  |  | CDC | 502 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | M6 | #6MTR(M6) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #6TR 二次 (#6MT) 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#6_MAIN_51NA | #6 MAIN 51NA | OTHER |  |  |  |  | CDC | 503 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 504 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 505 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0233 |  | 0126 | 1-1D-01 |  | 1-7E | 全所故障指示器復歸 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 506 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 507 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | PSA | DTU通訊故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | DTU通訊故障 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.DTU通訊故障 | DTU通訊故障 | OTHER |  |  |  |  | CDC | 508 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | PSF | DTU內部故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | DTU內部故障 |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.DTU內部故障 | DTU內部故障 | OTHER |  |  |  |  | CDC | 509 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 | Element | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  |  |  |  | ELEM/S67_D1 | [8 empty] | 歸仁SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 510 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | [13 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 511 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 512 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 513 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S67_D1 | [8 empty] | 歸仁SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 514 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | 87A |  | B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 新市歸仁線 (670)87 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_87A | 670新市歸仁線87RY | OTHER |  |  |  |  | CDC | 515 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | 87UL |  | B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | 新市歸仁線 (670) 87RY U/L |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.670_87UL | 670新市歸仁線87RY UL | OTHER |  |  |  |  | CDC | 516 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | 87A |  | B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 山上歸仁線 (680) 87 RY |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_87A | 680山上歸仁線87RY | OTHER |  |  |  |  | CDC | 517 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | 87UL |  | B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 山上歸仁線 (680) 87RY U/L |  |  |  |  | B2/S67_A1 | [8 empty] | 歸仁SS.680_87UL | 680山上歸仁線87RY UL | OTHER |  |  |  |  | CDC | 518 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | #1-#2(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_ES | #1-#2 TIE ES(非取樣點) | OTHER | [5 empty] | 519 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 1BR | #1BR |  | ES | 1BR_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.1BR_ES | 1BR_ES(非取樣點) | OTHER | [5 empty] | 520 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | E1 | #3-#2(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE2_ES | #3-#2 TIE ES(非取樣點) | OTHER | [5 empty] | 521 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 2BR | #2BR |  | ES | 2BR_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.2BR_ES | 2BR_ES(非取樣點) | OTHER | [5 empty] | 522 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 八甲線 (F12) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.八甲線KVAR | 11KV八甲線 KVAR | FEEDER |  |  |  |  | CDC | 523 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 八甲線 (F12) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.八甲線A1 | 11KV八甲線 R相AMP | FEEDER |  |  |  |  | CDC | 524 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 八甲線 (F12) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.八甲線A2 | 11KV八甲線 S相AMP | FEEDER |  |  |  |  | CDC | 525 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 八甲線 (F12) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.八甲線A3 | 11KV八甲線 T相AMP | FEEDER |  |  |  |  | CDC | 526 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 八甲線 (F12) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.八甲線A0 | 11KV八甲線 N相AMP | FEEDER |  |  |  |  | CDC | 527 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 仁傑線(F25) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.仁傑線KVAR | 11KV仁傑線 KVAR | FEEDER |  |  |  |  | CDC | 528 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 仁傑線 (F25) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.仁傑線A1 | 11KV仁傑線 R相AMP | FEEDER |  |  |  |  | CDC | 529 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 仁傑線 (F25) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.仁傑線A2 | 11KV仁傑線 S相AMP | FEEDER |  |  |  |  | CDC | 530 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 仁傑線 (F25) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.仁傑線A3 | 11KV仁傑線 T相AMP | FEEDER |  |  |  |  | CDC | 531 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 仁傑線 (F25) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.仁傑線A0 | 11KV仁傑線 N相AMP | FEEDER |  |  |  |  | CDC | 532 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 六合線 (F16) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.六合線KVAR | 11KV六合線 KVAR | FEEDER |  |  |  |  | CDC | 533 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 六合線 (F16) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.六合線A1 | 11KV六合線 R相AMP | FEEDER |  |  |  |  | CDC | 534 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 六合線 (F16) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.六合線A2 | 11KV六合線 S相AMP | FEEDER |  |  |  |  | CDC | 535 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 六合線 (F16) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.六合線A3 | 11KV六合線 T相AMP | FEEDER |  |  |  |  | CDC | 536 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 六合線(F16) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.六合線A0 | 11KV六合線 N相AMP | FEEDER |  |  |  |  | CDC | 537 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 古厝線 (F22) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.古厝線KVAR | 11KV古厝線 KVAR | FEEDER |  |  |  |  | CDC | 538 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 古厝線 (F22) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.古厝線A1 | 11KV古厝線 R相AMP | FEEDER |  |  |  |  | CDC | 539 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 古厝線 (F22) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.古厝線A2 | 11KV古厝線 S相AMP | FEEDER |  |  |  |  | CDC | 540 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 古厝線 (F22) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.古厝線A3 | 11KV古厝線 T相AMP | FEEDER |  |  |  |  | CDC | 541 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 古厝線 (F22) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.古厝線A0 | 11KV古厝線 N相AMP | FEEDER |  |  |  |  | CDC | 542 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 沙崙線 (F19) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.沙崙線KVAR | 11KV沙崙線 KVAR | FEEDER |  |  |  |  | CDC | 543 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 沙崙線 (F19) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.沙崙線A1 | 11KV沙崙線 R相AMP | FEEDER |  |  |  |  | CDC | 544 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 沙崙線 (F19) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.沙崙線A2 | 11KV沙崙線 S相AMP | FEEDER |  |  |  |  | CDC | 545 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 沙崙線 (F19) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.沙崙線A3 | 11KV沙崙線 T相AMP | FEEDER |  |  |  |  | CDC | 546 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 沙崙線 (F19) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.沙崙線A0 | 11KV沙崙線 N相AMP | FEEDER |  |  |  |  | CDC | 547 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 貝汝線 (F5) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.貝汝線KVAR | 11KV貝汝線 KVAR | FEEDER |  |  |  |  | CDC | 548 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 貝汝線 (F5) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.貝汝線A1 | 11KV貝汝線 R相AMP | FEEDER |  |  |  |  | CDC | 549 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 貝汝線 (F5) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.貝汝線A2 | 11KV貝汝線 S相AMP | FEEDER |  |  |  |  | CDC | 550 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 貝汝線 (F5) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.貝汝線A3 | 11KV貝汝線 T相AMP | FEEDER |  |  |  |  | CDC | 551 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 貝汝線 (F5) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.貝汝線A0 | 11KV貝汝線 N相AMP | FEEDER |  |  |  |  | CDC | 552 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 東盈線 (F6) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.東盈線KVAR | 11KV東盈線 KVAR | FEEDER |  |  |  |  | CDC | 553 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 東盈線 (F6) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.東盈線A1 | 11KV東盈線 R相AMP | FEEDER |  |  |  |  | CDC | 554 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 東盈線 (F6) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.東盈線A2 | 11KV東盈線 S相AMP | FEEDER |  |  |  |  | CDC | 555 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 東盈線 (F6) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.東盈線A3 | 11KV東盈線 T相AMP | FEEDER |  |  |  |  | CDC | 556 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 東盈線 (F6) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.東盈線A0 | 11KV東盈線 N相AMP | FEEDER |  |  |  |  | CDC | 557 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 松根線 (F17) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.松根線KVAR | 11KV松根線 KVAR | FEEDER |  |  |  |  | CDC | 558 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 松根線 (F17) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.松根線A1 | 11KV松根線 R相AMP | FEEDER |  |  |  |  | CDC | 559 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 松根線 (F17) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.松根線A2 | 11KV松根線 S相AMP | FEEDER |  |  |  |  | CDC | 560 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 松根線 (F17) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.松根線A3 | 11KV松根線 T相AMP | FEEDER |  |  |  |  | CDC | 561 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 松根線 (F17) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.松根線A0 | 11KV松根線 N相AMP | FEEDER |  |  |  |  | CDC | 562 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 南保線 (F4) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南保線KVAR | 11KV南保線 KVAR | FEEDER |  |  |  |  | CDC | 563 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 南保線 (F4) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南保線A1 | 11KV南保線 R相AMP | FEEDER |  |  |  |  | CDC | 564 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 南保線 (F4) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南保線A2 | 11KV南保線 S相AMP | FEEDER |  |  |  |  | CDC | 565 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 南保線 (F4) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南保線A3 | 11KV南保線 T相AMP | FEEDER |  |  |  |  | CDC | 566 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 南保線 (F4) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南保線A0 | 11KV南保線 N相AMP | FEEDER |  |  |  |  | CDC | 567 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 南潭線 (F15) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南潭線KVAR | 11KV南潭線 KVAR | FEEDER |  |  |  |  | CDC | 568 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 南潭線 (F15) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南潭線A1 | 11KV南潭線 R相AMP | FEEDER |  |  |  |  | CDC | 569 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 南潭線 (F15) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南潭線A2 | 11KV南潭線 S相AMP | FEEDER |  |  |  |  | CDC | 570 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 南潭線 (F15) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南潭線A3 | 11KV南潭線 T相AMP | FEEDER |  |  |  |  | CDC | 571 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 南潭線 (F15) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.南潭線A0 | 11KV南潭線 N相AMP | FEEDER |  |  |  |  | CDC | 572 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 看西線 (F9) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.看西線KVAR | 11KV看西線 KVAR | FEEDER |  |  |  |  | CDC | 573 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 看西線 (F9) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.看西線A1 | 11KV看西線 R相AMP | FEEDER |  |  |  |  | CDC | 574 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 看西線 (F9) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.看西線A2 | 11KV看西線 S相AMP | FEEDER |  |  |  |  | CDC | 575 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 看西線 (F9) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.看西線A3 | 11KV看西線 T相AMP | FEEDER |  |  |  |  | CDC | 576 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 看西線 (F9) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.看西線A0 | 11KV看西線 N相AMP | FEEDER |  |  |  |  | CDC | 577 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 崙頂線 (F8) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.崙頂線KVAR | 11KV崙頂線 KVAR | FEEDER |  |  |  |  | CDC | 578 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 崙頂線 (F8) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.崙頂線A1 | 11KV崙頂線 R相AMP | FEEDER |  |  |  |  | CDC | 579 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 崙頂線 (F8) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.崙頂線A2 | 11KV崙頂線 S相AMP | FEEDER |  |  |  |  | CDC | 580 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 崙頂線 (F8) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.崙頂線A3 | 11KV崙頂線 T相AMP | FEEDER |  |  |  |  | CDC | 581 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 崙頂線 (F8) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.崙頂線A0 | 11KV崙頂線 N相AMP | FEEDER |  |  |  |  | CDC | 582 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 深坑線 (F14) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.深坑線KVAR | 11KV深坑線 KVAR | FEEDER |  |  |  |  | CDC | 583 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 深坑線 (F14) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.深坑線A1 | 11KV深坑線 R相AMP | FEEDER |  |  |  |  | CDC | 584 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 深坑線 (F14) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.深坑線A2 | 11KV深坑線 S相AMP | FEEDER |  |  |  |  | CDC | 585 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 深坑線 (F14) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.深坑線A3 | 11KV深坑線 T相AMP | FEEDER |  |  |  |  | CDC | 586 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 深坑線 (F14) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.深坑線A0 | 11KV深坑線 N相AMP | FEEDER |  |  |  |  | CDC | 587 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 媽廟線 (F3) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.媽廟線KVAR | 11KV媽廟線 KVAR | FEEDER |  |  |  |  | CDC | 588 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 媽廟線 (F3) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.媽廟線A1 | 11KV媽廟線 R相AMP | FEEDER |  |  |  |  | CDC | 589 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 媽廟線 (F3) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.媽廟線A2 | 11KV媽廟線 S相AMP | FEEDER |  |  |  |  | CDC | 590 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 媽廟線 (F3) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.媽廟線A3 | 11KV媽廟線 T相AMP | FEEDER |  |  |  |  | CDC | 591 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 媽廟線 (F3) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.媽廟線A0 | 11KV媽廟線 N相AMP | FEEDER |  |  |  |  | CDC | 592 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 新田線 (F2) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.新田線KVAR | 11KV新田線 KVAR | FEEDER |  |  |  |  | CDC | 593 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 新田線 (F2) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.新田線A1 | 11KV新田線 R相AMP | FEEDER |  |  |  |  | CDC | 594 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 新田線 (F2) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.新田線A2 | 11KV新田線 S相AMP | FEEDER |  |  |  |  | CDC | 595 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 新田線 (F2) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.新田線A3 | 11KV新田線 T相AMP | FEEDER |  |  |  |  | CDC | 596 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 新田線 (F2) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.新田線A0 | 11KV新田線 N相AMP | FEEDER |  |  |  |  | CDC | 597 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 萬芳線 (F11) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.萬芳線KVAR | 11KV萬芳線 KVAR | FEEDER |  |  |  |  | CDC | 598 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 萬芳線 (F11) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.萬芳線A1 | 11KV萬芳線 R相AMP | FEEDER |  |  |  |  | CDC | 599 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 萬芳線 (F11) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.萬芳線A2 | 11KV萬芳線 S相AMP | FEEDER |  |  |  |  | CDC | 600 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 萬芳線 (F11) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.萬芳線A3 | 11KV萬芳線 T相AMP | FEEDER |  |  |  |  | CDC | 601 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 萬芳線 (F11) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.萬芳線A0 | 11KV萬芳線 N相AMP | FEEDER |  |  |  |  | CDC | 602 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 漢平線 (F20) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.漢平線KVAR | 11KV漢平線 KVAR | FEEDER |  |  |  |  | CDC | 603 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 漢平線 (F20) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.漢平線A1 | 11KV漢平線 R相AMP | FEEDER |  |  |  |  | CDC | 604 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 漢平線 (F20) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.漢平線A2 | 11KV漢平線 S相AMP | FEEDER |  |  |  |  | CDC | 605 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 漢平線 (F20) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.漢平線A3 | 11KV漢平線 T相AMP | FEEDER |  |  |  |  | CDC | 606 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 漢平線 (F20) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.漢平線A0 | 11KV漢平線 N相AMP | FEEDER |  |  |  |  | CDC | 607 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 龍崎線 (F23) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.龍崎線KVAR | 11KV龍崎線 KVAR | FEEDER |  |  |  |  | CDC | 608 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 龍崎線 (F23) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.龍崎線A1 | 11KV龍崎線 R相AMP | FEEDER |  |  |  |  | CDC | 609 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 龍崎線 (F23) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.龍崎線A2 | 11KV龍崎線 S相AMP | FEEDER |  |  |  |  | CDC | 610 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 龍崎線 (F23) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.龍崎線A3 | 11KV龍崎線 T相AMP | FEEDER |  |  |  |  | CDC | 611 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 龍崎線 (F23) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.龍崎線A0 | 11KV龍崎線 N相AMP | FEEDER |  |  |  |  | CDC | 612 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 歸仁線 (F1) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸仁線KVAR | 11KV歸仁線 KVAR | FEEDER |  |  |  |  | CDC | 613 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 歸仁線 (F1) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸仁線A1 | 11KV歸仁線 R相AMP | FEEDER |  |  |  |  | CDC | 614 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 歸仁線 (F1) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸仁線A2 | 11KV歸仁線 S相AMP | FEEDER |  |  |  |  | CDC | 615 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 歸仁線 (F1) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸仁線A3 | 11KV歸仁線 T相AMP | FEEDER |  |  |  |  | CDC | 616 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 歸仁線 (F1) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸仁線A0 | 11KV歸仁線 N相AMP | FEEDER |  |  |  |  | CDC | 617 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 歸南線 (F21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸南線KVAR | 11KV歸南線 KVAR | FEEDER |  |  |  |  | CDC | 618 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 歸南線 (F21) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸南線A1 | 11KV歸南線 R相AMP | FEEDER |  |  |  |  | CDC | 619 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 歸南線 (F21) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸南線A2 | 11KV歸南線 S相AMP | FEEDER |  |  |  |  | CDC | 620 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 歸南線 (F21) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸南線A3 | 11KV歸南線 T相AMP | FEEDER |  |  |  |  | CDC | 621 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 歸南線 (F21) N電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.歸南線A0 | 11KV歸南線 N相AMP | FEEDER |  |  |  |  | CDC | 622 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 豐中線 (F7) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.豐中線KVAR | 11KV豐中線 KVAR | FEEDER |  |  |  |  | CDC | 623 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 豐中線 (F7) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.豐中線A1 | 11KV豐中線 R相AMP | FEEDER |  |  |  |  | CDC | 624 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 豐中線 (F7) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.豐中線A2 | 11KV豐中線 S相AMP | FEEDER |  |  |  |  | CDC | 625 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 豐中線 (F7) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.豐中線A3 | 11KV豐中線 T相AMP | FEEDER |  |  |  |  | CDC | 626 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 豐中線 (F7) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.豐中線A0 | 11KV豐中線 N相AMP | FEEDER |  |  |  |  | CDC | 627 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 關甲線 (F24) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關甲線KVAR | 11KV關甲線 KVAR | FEEDER |  |  |  |  | CDC | 628 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 關甲線 (F24) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關甲線A1 | 11KV關甲線 R相AMP | FEEDER |  |  |  |  | CDC | 629 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 關甲線 ( F24) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關甲線A2 | 11KV關甲線 S相AMP | FEEDER |  |  |  |  | CDC | 630 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 關甲線 (F24) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關甲線A3 | 11KV關甲線 T相AMP | FEEDER |  |  |  |  | CDC | 631 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 關甲線 (F24) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關甲線A0 | 11KV關甲線 N相AMP | FEEDER |  |  |  |  | CDC | 632 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 關廟線 (F10) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關廟線KVAR | 11KV關廟線 KVAR | FEEDER |  |  |  |  | CDC | 633 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 關廟線 (F10) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關廟線A1 | 11KV關廟線 R相AMP | FEEDER |  |  |  |  | CDC | 634 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 關廟線 (F10) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關廟線A2 | 11KV關廟線 S相AMP | FEEDER |  |  |  |  | CDC | 635 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 關廟線 (F10) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關廟線A3 | 11KV關廟線 T相AMP | FEEDER |  |  |  |  | CDC | 636 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 關廟線 (F10) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.關廟線A0 | 11KV關廟線 N相AMP | FEEDER |  |  |  |  | CDC | 637 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S67_D1 | [8 empty] | 歸仁SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 638 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 3BUS | #3BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0210 |  |  | 2-D2 |  |  | 11KV S相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S67_D1 | [8 empty] | 歸仁SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | [5 empty] | 639 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 6BUS | #6BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0214 |  |  | 2-D6 |  |  | 11KV S相電壓 |  |  | kV_-9_9(-2000_2000) | aea | B2/S67_D1 | [8 empty] | 歸仁SS.11S1#6BUS_KV | 11S1 #6BUS KV | BUS | [5 empty] | 640 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 3BUS | #3BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0211 |  |  | 2-D3 |  |  | 11KV T相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S67_D1 | [8 empty] | 歸仁SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | [5 empty] | 641 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 4BUS | #4BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0212 |  |  | 2-D4 |  |  | 11KV S相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S67_D1 | [8 empty] | 歸仁SS.11S1#4BUS_KV | 11S1 #4BUS KV | BUS | [5 empty] | 642 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 4BUS | #4BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0213 |  |  | 2-D5 |  |  | 11KV T相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S67_D1 | [8 empty] | 歸仁SS.11T1#4BUS_KV | 11T1 #4BUS KV | BUS | [5 empty] | 643 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 7BUS | #7BUS |  | V_R |  | DELETE | MvMoment | R相電壓 |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 大聚太陽光電 R相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.TAR1#7BUS_KV | TAR1 #7BUS KV | BUS | [5 empty] | 644 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 7BUS | #7BUS |  | V_S |  | DELETE | MvMoment | S相電壓 |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 大聚太陽光電 S相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.TAS1#7BUS_KV | TAS1 #7BUS KV | BUS | [5 empty] | 645 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 7BUS | #7BUS |  | V_T |  | DELETE | MvMoment | T相電壓 |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 大聚太陽光電 T相電壓 |  |  | kV_-9_9(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.TAT1#7BUS_KV | TAT1 #7BUS KV | BUS | [5 empty] | 646 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | 大聚太陽光電 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.大聚線KVAR | 11KV大聚線 KVAR | FEEDER | [5 empty] | 647 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 大聚太陽光電 R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.大聚線A1 | 11KV大聚線 R相AMP | FEEDER | [5 empty] | 648 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 大聚太陽光電 S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.大聚線A2 | 11KV大聚線 S相AMP | FEEDER | [5 empty] | 649 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 大聚太陽光電 T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.大聚線A3 | 11KV大聚線 T相AMP | FEEDER | [5 empty] | 650 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 大聚太陽光電 N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S67_D1 | [8 empty] | 歸仁SS.大聚線A0 | 11KV大聚線 N相AMP | FEEDER | [5 empty] | 651 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | #1TR 63Q |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 652 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | #1TR 96B1 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 653 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | #1TR 96B2 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 654 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | #1TR 96D |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 655 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | #1TR 96P |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 656 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #2TR 63Q |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | [5 empty] | 657 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #2TR 96B1 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | [5 empty] | 658 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | #2TR 96B2 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | [5 empty] | 659 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | #2TR 96D |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | [5 empty] | 660 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | #2TR 96P |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | [5 empty] | 661 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | #3TR 63Q |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | [5 empty] | 662 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | #3TR 96B1 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | [5 empty] | 663 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | #3TR 96B2 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | [5 empty] | 664 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #3TR 96D |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | [5 empty] | 665 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #3TR 96P |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | [5 empty] | 666 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | #4TR 63Q |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | [5 empty] | 667 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #4TR 96B1 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | [5 empty] | 668 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #4TR 96B2 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | [5 empty] | 669 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | #4TR 96D |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | [5 empty] | 670 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | #4TR 96P |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | [5 empty] | 671 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | #6TR 63Q |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_63Q | #6MTR ULTC電驛動作 | OTHER | [5 empty] | 672 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | #6TR 96B1 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_96B1 | #6MTR 撲氣電驛警報 | OTHER | [5 empty] | 673 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | #6TR 96B2 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_96B2 | #6MTR 撲氣電驛動作 | OTHER | [5 empty] | 674 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #6TR 96D |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_96D | #6MTR 放壓電驛動作 | OTHER | [5 empty] | 675 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | #6TR 96P |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_96P | #6MTR 突壓電驛動作 | OTHER | [5 empty] | 676 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 萬芳線 (F11) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR31_LOA | 萬芳線 復閉失敗閉鎖 | OTHER | [5 empty] | 677 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 八甲線 (F12) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR32_LOA | 八甲線 復閉失敗閉鎖 | OTHER | [5 empty] | 678 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 歸33線 (F13) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR33_LOA | 歸33線 復閉失敗閉鎖 | OTHER | [5 empty] | 679 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 深坑線 (F14) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR34_LOA | 深坑線 復閉失敗閉鎖 | OTHER | [5 empty] | 680 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 南潭線 (F15) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR35_LOA | 南潭線 復閉失敗閉鎖 | OTHER | [5 empty] | 681 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | 六合線 (F16) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR36_LOA | 六合線 復閉失敗閉鎖 | OTHER | [5 empty] | 682 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0503 |  |  | 1-3F-07 |  |  | 松根線 (F17) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR37_LOA | 松根線 復閉失敗閉鎖 | OTHER | [5 empty] | 683 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0504 |  |  | 1-3F-08 |  |  | 歸38線 (F18) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR38_LOA | 歸38線 復閉失敗閉鎖 | OTHER | [5 empty] | 684 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-3F-09 |  |  | 沙崙線 (F19) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR39_LOA | 沙崙線 復閉失敗閉鎖 | OTHER | [5 empty] | 685 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0506 |  |  | 1-3F-10 |  |  | 漢平線 (F20) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR40_LOA | 漢平線 復閉失敗閉鎖 | OTHER | [5 empty] | 686 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0507 |  |  | 1-3F-11 |  |  | 歸南線 (F21) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR41_LOA | 歸南線 復閉失敗閉鎖 | OTHER | [5 empty] | 687 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0508 |  |  | 1-3F-12 |  |  | 古厝線 (F22) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR42_LOA | 古厝線 復閉失敗閉鎖 | OTHER | [5 empty] | 688 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0509 |  |  | 1-3F-13 |  |  | 龍崎線 (F23) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR43_LOA | 龍崎線 復閉失敗閉鎖 | OTHER | [5 empty] | 689 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0510 |  |  | 1-3F-14 |  |  | 關甲線 (F24) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR44_LOA | 關甲線 復閉失敗閉鎖 | OTHER | [5 empty] | 690 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0511 |  |  | 1-3F-15 |  |  | 仁傑線 (F25) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR45_LOA | 仁傑線 復閉失敗閉鎖 | OTHER | [5 empty] | 691 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 692 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | #1DTR 86A |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 693 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 694 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2DTR 51ZLS |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | [5 empty] | 695 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | #2DTR 86A |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 696 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 697 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | #3DTR 51ZLS |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | [5 empty] | 698 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | #3DTR 86A |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 699 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3DTR 87LS2S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | [5 empty] | 700 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0487 |  |  | 1-3E-07 |  |  | #4DTR 51ZLS |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_51ZUL | #4MTR 51Z U/L | OTHER | [5 empty] | 701 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | #4DTR 86A |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_86A | #4MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 702 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0486 |  |  | 1-3E-06 |  |  | #4DTR 87LS2S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#4MTR_87UL2 | #4MTR 第二套87RY U/L | OTHER | [5 empty] | 703 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | #6DTR 51ZLS |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_51ZUL | #6MTR 51Z U/L | OTHER | [5 empty] | 704 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | #6DTR 86A |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_86A | #6MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 705 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | #6DTR 87LS2S |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.#6MTR_87UL2 | #6MTR 第二套87RY U/L | OTHER | [5 empty] | 706 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0490 |  |  | 1-3E-10 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S67_D1 | [8 empty] | 歸仁SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 707 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 4SSTR | #4SSTR |  | PHA |  | DELETE | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | #4 SSTR 51 RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4SSTR_51A | #4SSTR 51RY | OTHER | [5 empty] | 708 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 4SSTR | #4SSTR |  | GDA |  | DELETE | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | #4 SSTR 51N RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4SSTR_51NA | #4SSTR 51N RY | OTHER | [5 empty] | 709 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 4SSTR | #4SSTR |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0090 |  | 0127 | 1-0B-02 |  | 1-7F | #4 SSTR CB |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.#4SSTR_CB | #4SSTR CB | OTHER | [5 empty] | 710 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 27A |  | INSERT | Status | 27RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 大聚太陽光電 27RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_27A | 大聚太陽光電 27A | OTHER | [5 empty] | 711 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 50A |  | INSERT | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 大聚太陽光電 50RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_50A | 大聚太陽光電 50A | OTHER | [5 empty] | 712 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 1A3Other | 50NA | INSERT | Status | 警報等級3動作1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 大聚太陽光電 50NRY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_50NA | 大聚太陽光電 50NA | OTHER | [5 empty] | 713 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 大聚太陽光電 51RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_51A | 大聚太陽光電 51A | OTHER | [5 empty] | 714 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 大聚太陽光電 51NRY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_51NA | 大聚太陽光電 51NA | OTHER | [5 empty] | 715 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 59A |  | INSERT | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 大聚太陽光電 59RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_59A | 大聚太陽光電 59A | OTHER | [5 empty] | 716 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | 59A_V0 |  | INSERT | Status | 59RY 0相 | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 大聚太陽光電 59V0RY |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_59V0A | 大聚太陽光電 59V0A | OTHER | [5 empty] | 717 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | L/KR45/T1 |  |  |  | 0072 |  |  | 1-09-00 |  |  | 大聚太陽光電 CB |  |  |  | not found | B2/S67_D1 | [8 empty] | 歸仁SS.TA_CB | 大聚太陽光電 CB | OTHER | [5 empty] | 718 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | DS |  | INSERT | Status | DS1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0868 |  |  | 2-36-04 |  |  | 大聚太陽光電DS |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_DS | 大聚太陽光電 DS | OTHER | [5 empty] | 719 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TA | 大聚太陽光電 |  | ES |  | INSERT | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 2-36-06 |  |  | 大聚太陽光電ES |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.TA_ES | 大聚太陽光電 ES | OTHER | [5 empty] | 720 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0880 |  |  | 2-37-00 |  |  | 歸仁線 (F1) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR21_LOA | 歸仁線 復閉失敗閉鎖 | OTHER | [5 empty] | 721 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0881 |  |  | 2-37-01 |  |  | 新田線 (F2) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR22_LOA | 新田線 復閉失敗閉鎖 | OTHER | [5 empty] | 722 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0882 |  |  | 2-37-02 |  |  | 媽廟線 (F3) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR23_LOA | 媽廟線 復閉失敗閉鎖 | OTHER | [5 empty] | 723 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0883 |  |  | 2-37-03 |  |  | 南保線 (F4) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR24_LOA | 南保線 復閉失敗閉鎖 | OTHER | [5 empty] | 724 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0884 |  |  | 2-37-04 |  |  | 貝汝線 (F5) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR25_LOA | 貝汝線 復閉失敗閉鎖 | OTHER | [5 empty] | 725 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0885 |  |  | 2-37-05 |  |  | 東盈線 (F6) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR26_LOA | 東盈線 復閉失敗閉鎖 | OTHER | [5 empty] | 726 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0886 |  |  | 2-37-06 |  |  | 豐中線 (F7) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR27_LOA | 豐中線 復閉失敗閉鎖 | OTHER | [5 empty] | 727 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0887 |  |  | 2-37-07 |  |  | 崙頂線 (F8) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR28_LOA | 崙頂線 復閉失敗閉鎖 | OTHER | [5 empty] | 728 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 歸仁線 (F1) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 729 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 新田線 (F2) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 730 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 媽廟線 (F3) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 731 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 南保線 (F4) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 732 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 貝汝線 (F5) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 733 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 溪頂線 (F6) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 734 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 豐中線 (F7) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 735 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 崙頂線 (F8) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 736 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 看西線 (F9) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 737 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 關廟線 (F10) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 738 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | 萬芳線 (F11) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 739 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | 八甲線 (F12) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 740 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | 深坑線 (F14) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 741 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | 南潭線 (F15) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 742 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | 六合線 (F16) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 743 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0016 |  |  | 1-50 |  |  | 松根線 (F17) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 744 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | 沙崙線 (F19) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 745 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0019 |  |  | 1-53 |  |  | 漢平線 (F20) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 746 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0020 |  |  | 1-54 |  |  | 歸南線 (F21) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 747 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | 古厝線 (F22) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 748 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0022 |  |  | 1-56 |  |  | 龍崎線 (F23) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 749 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0023 |  |  | 1-57 |  |  | 關甲線 (F24) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 750 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 仁傑線 (F25) KWH(+) |  |  |  |  | B2/S67_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 751 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S67 | 歸仁SS | 11 | 11kV | 4SSTR | #4SSTR |  | DS | #4SSTR(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.#4SSTR_DS | #4SSTR DS(非取樣點) | OTHER | [5 empty] | 752 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 4SSTR | #4SSTR |  | ES | #4SSTR(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.#4SSTR_ES | #4SSTR ES(非取樣點) | OTHER | [5 empty] | 753 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 1BUS | #1BUS |  | BE0 | #1 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.#1_BE | #1 BE(非取樣點) | OTHER | [5 empty] | 754 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 2BUS | #2BUS |  | BE0 | #2 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.#2_BE | #2 BE(非取樣點) | OTHER | [5 empty] | 755 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | 4BUS | #4BUS |  | BE0 | #4 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.#4_BE | #4 BE(非取樣點) | OTHER | [5 empty] | 756 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0889 |  |  | 2-37-09 |  |  | 關廟線 (F10) LOA |  |  |  |  | B2/S67_D1 | [8 empty] | 歸仁SS.KR30_LOA | 關廟線 復閉失敗閉鎖 | OTHER | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 758 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 759 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | 3AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值3 |  | Y |  | AI | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 760 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | 4AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值4 |  | Y |  | AI | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 761 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | 6AI_Oth | (非取樣點) | INSERT | [23 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 762 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 6BUS | #6BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0215 |  |  | 2-D7 |  |  | 11KV T相電壓 |  |  | kV_-9_9(-2000_2000) | aea | B2/S67_D1 | [8 empty] | 歸仁SS.11T1#6BUS_KV | 11T1 #6BUS KV | BUS | [5 empty] | 763 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | DS2 | #1-#2(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE1_DS | #1-#2 TIE_DS (非取樣點) | TIE | [5 empty] | 269 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | DS2 | #4-#1(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S67_D1 | [8 empty] | 歸仁SS.TIE4_DS | #4-#1 TIE_DS (非取樣點) | TIE | [5 empty] | 274 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S67/69/1BUS/V
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S67_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S67/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S67_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_9 | OPRD1: S67/11/M1/MW; OPRD2: S67/11/M2/MW; OPRD3: S67/11/M3/MW; OPRD4: S67/11/M4/MW; OPRD5: S67/11/M6/MW; OPRD6: S67/69/630/MW; OPRD7: S67/69/660/MW; OPRD8: S67/69/670/MW; OPRD9: S67/69/680/MW
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S67_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S67/0/CalcPoint/OPRN2_MW
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S67_D1 | [17 empty] | none
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S67_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S67/0/CalcPoint/OPRN1; OPRD2: S67/0/CalcPoint/OPRN2; OPRD3: S67/0/CalcPoint/PRFL_UL
S67 | 歸仁SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S67_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S67/11/M1/MW; OPRD2: S67/11/M1/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S67_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S67/11/M2/MW; OPRD2: S67/11/M2/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S67_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S67/11/M3/MW; OPRD2: S67/11/M3/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S67_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S67/11/M4/MW; OPRD2: S67/11/M4/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS |  |  | 6MTR | 6MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S67_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S67/11/M6/MW; OPRD2: S67/11/M6/MVAR; OPRD3: NULL
S67 | 歸仁SS | 69 | 69kV | 630 | 歸仁～大亞線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S67_A1 | [12 empty] | 歸仁SS.630_AMP | 歸仁大亞線 AMP | LINE69 | AMP_CAL | C06R0500 | amp_cal | OPRD1: S67/69/630/MW; OPRD2: S67/69/630/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS | 69 | 69kV | 660 | 保安～歸仁線(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S67_A1 | [12 empty] | 歸仁SS.660_AMP | 歸仁保安線 AMP | LINE69 | AMP_CAL | C10R0800 | amp_cal | OPRD1: S67/69/660/MW; OPRD2: S67/69/660/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS | 69 | 69kV | 670 | 新市～歸仁線(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S67_A1 | [12 empty] | 歸仁SS.670_AMP | 新市歸仁線 AMP | LINE69 | AMP_CAL | C10R1000 | amp_cal | OPRD1: S67/69/670/MW; OPRD2: S67/69/670/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS | 69 | 69kV | 680 | 山上～歸仁線(680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S67_A1 | [12 empty] | 歸仁SS.680_AMP | 山上歸仁線 AMP | LINE69 | AMP_CAL | C10R0800 | amp_cal | OPRD1: S67/69/680/MW; OPRD2: S67/69/680/MVAR; OPRD3: S67/0/CalcPoint/Vbs1
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S67_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 歸仁SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S67/11/M1/MW; OPRD2: S67/11/M1/MVAR
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S67_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 歸仁SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S67/11/M2/MW; OPRD2: S67/11/M2/MVAR
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S67_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 歸仁SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S67/11/M3/MW; OPRD2: S67/11/M3/MVAR
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S67_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 歸仁SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S67/11/M4/MW; OPRD2: S67/11/M4/MVAR
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S67_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 歸仁SS.#6MTR_MVA | #6MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S67/11/M6/MW; OPRD2: S67/11/M6/MVAR
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S67_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S67//1MTR/MVA; OPRD2: 0
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S67_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S67//2MTR/MVA; OPRD2: 0
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S67_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S67//3MTR/MVA; OPRD2: 0
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/S67_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S67//4MTR/MVA; OPRD2: 0
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | LOAD | [9 empty] | B1/S67_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S67//6MTR/MVA; OPRD2: 0
S67 | 歸仁SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S67/11/M1/MW; OPRD2: S67/11/M1/MVAR
S67 | 歸仁SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S67/11/M2/MW; OPRD2: S67/11/M2/MVAR
S67 | 歸仁SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S67/11/M3/MW; OPRD2: S67/11/M3/MVAR
S67 | 歸仁SS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.#4MTR_PF | #4MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S67/11/M4/MW; OPRD2: S67/11/M4/MVAR
S67 | 歸仁SS |  |  | 6MTR | #6MTR |  | PF | [9 empty] | B1/S67_D1 | [12 empty] | 歸仁SS.#6MTR_PF | #6MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S67/11/M6/MW; OPRD2: S67/11/M6/MVAR
S67 | 歸仁SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S67_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S67//1MTR/SupLocal; OPRD2: S67//1MTR/Tap Chan; OPRD3: NULL
S67 | 歸仁SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S67_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S67//2MTR/SupLocal; OPRD2: S67//2MTR/Tap Chan; OPRD3: NULL
S67 | 歸仁SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S67_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S67//3MTR/SupLocal; OPRD2: S67//3MTR/Tap Chan; OPRD3: NULL
S67 | 歸仁SS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/S67_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S67//4MTR/SupLocal; OPRD2: S67//4MTR/Tap Chan; OPRD3: NULL
S67 | 歸仁SS |  |  | 6MTR | 6MTR |  | TR_PERM | [9 empty] | B1/S67_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S67//6MTR/SupLocal; OPRD2: S67//6MTR/Tap Chan; OPRD3: NULL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR21/I_R; OPRD3: S67/11/KR21/I_S; OPRD4: S67/11/KR21/I_T
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR22/I_R; OPRD3: S67/11/KR22/I_S; OPRD4: S67/11/KR22/I_T
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR23/I_R; OPRD3: S67/11/KR23/I_S; OPRD4: S67/11/KR23/I_T
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR24/I_R; OPRD3: S67/11/KR24/I_S; OPRD4: S67/11/KR24/I_T
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR25/I_R; OPRD3: S67/11/KR25/I_S; OPRD4: S67/11/KR25/I_T
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR26/I_R; OPRD3: S67/11/KR26/I_S; OPRD4: S67/11/KR26/I_T
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR27/I_R; OPRD3: S67/11/KR27/I_S; OPRD4: S67/11/KR27/I_T
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR28/I_R; OPRD3: S67/11/KR28/I_S; OPRD4: S67/11/KR28/I_T
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR29/I_R; OPRD3: S67/11/KR29/I_S; OPRD4: S67/11/KR29/I_T
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR30/I_R; OPRD3: S67/11/KR30/I_S; OPRD4: S67/11/KR30/I_T
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR31/I_R; OPRD3: S67/11/KR31/I_S; OPRD4: S67/11/KR31/I_T
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR32/I_R; OPRD3: S67/11/KR32/I_S; OPRD4: S67/11/KR32/I_T
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR33/I_R; OPRD3: S67/11/KR33/I_S; OPRD4: S67/11/KR33/I_T
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR34/I_R; OPRD3: S67/11/KR34/I_S; OPRD4: S67/11/KR34/I_T
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR35/I_R; OPRD3: S67/11/KR35/I_S; OPRD4: S67/11/KR35/I_T
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR36/I_R; OPRD3: S67/11/KR36/I_S; OPRD4: S67/11/KR36/I_T
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR37/I_R; OPRD3: S67/11/KR37/I_S; OPRD4: S67/11/KR37/I_T
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR38/I_R; OPRD3: S67/11/KR38/I_S; OPRD4: S67/11/KR38/I_T
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR39/I_R; OPRD3: S67/11/KR39/I_S; OPRD4: S67/11/KR39/I_T
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR40/I_R; OPRD3: S67/11/KR40/I_S; OPRD4: S67/11/KR40/I_T
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR41/I_R; OPRD3: S67/11/KR41/I_S; OPRD4: S67/11/KR41/I_T
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR42/I_R; OPRD3: S67/11/KR42/I_S; OPRD4: S67/11/KR42/I_T
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR43/I_R; OPRD3: S67/11/KR43/I_S; OPRD4: S67/11/KR43/I_T
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR44/I_R; OPRD3: S67/11/KR44/I_S; OPRD4: S67/11/KR44/I_T
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S67/11/KR45/I_R; OPRD3: S67/11/KR45/I_S; OPRD4: S67/11/KR45/I_T
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR21/kVA; OPRD2: S67/11/KR21/KVAR
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR22/kVA; OPRD2: S67/11/KR22/KVAR
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR23/kVA; OPRD2: S67/11/KR23/KVAR
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR24/kVA; OPRD2: S67/11/KR24/KVAR
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR25/kVA; OPRD2: S67/11/KR25/KVAR
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR26/kVA; OPRD2: S67/11/KR26/KVAR
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR27/kVA; OPRD2: S67/11/KR27/KVAR
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR28/kVA; OPRD2: S67/11/KR28/KVAR
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR29/kVA; OPRD2: S67/11/KR29/KVAR
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR30/kVA; OPRD2: S67/11/KR30/KVAR
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR31/kVA; OPRD2: S67/11/KR31/KVAR
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR32/kVA; OPRD2: S67/11/KR32/KVAR
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR33/kVA; OPRD2: S67/11/KR33/KVAR
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR34/kVA; OPRD2: S67/11/KR34/KVAR
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR35/kVA; OPRD2: S67/11/KR35/KVAR
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR36/kVA; OPRD2: S67/11/KR36/KVAR
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR37/kVA; OPRD2: S67/11/KR37/KVAR
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR38/kVA; OPRD2: S67/11/KR38/KVAR
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR39/kVA; OPRD2: S67/11/KR39/KVAR
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR40/kVA; OPRD2: S67/11/KR40/KVAR
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR41/kVA; OPRD2: S67/11/KR41/KVAR
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR42/kVA; OPRD2: S67/11/KR42/KVAR
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR43/kVA; OPRD2: S67/11/KR43/KVAR
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR44/kVA; OPRD2: S67/11/KR44/KVAR
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S67_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S67/11/KR45/kVA; OPRD2: S67/11/KR45/KVAR
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S67_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: S67/11/M1/MW; OPRD2: S67/11/M2/MW; OPRD3: S67/11/M3/MW; OPRD4: S67/11/M4/MW; OPRD5: S67/11/M6/MW
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S67_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: S67/11/M1/MVAR; OPRD2: S67/11/M2/MVAR; OPRD3: S67/11/M3/MVAR; OPRD4: S67/11/M4/MVAR; OPRD5: S67/11/M6/MVAR
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_D1 | [12 empty] | 歸仁SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S67/11/210/CB; OPRD2: 6.9; OPRD3: 0
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_D1 | [12 empty] | 歸仁SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S67/11/220/CB; OPRD2: 6.9; OPRD3: 0
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_D1 | [12 empty] | 歸仁SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S67/11/230/CB; OPRD2: 6.9; OPRD3: 0
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_D1 | [12 empty] | 歸仁SS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S67/11/240/CB; OPRD2: 6.9; OPRD3: 0
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_D1 | [12 empty] | 歸仁SS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S67/11/260/CB; OPRD2: 6.9; OPRD3: 0
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S67_A1 | [12 empty] | 歸仁SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S67/69/810/CB; OPRD2: 69; OPRD3: 0
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S67_D1 | [12 empty] | 歸仁SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_20 |  | com_alarm_40 | S67//1MTR/TRA | S67//1MTR/96B2 | S67//1MTR/96D | S67//1MTR/96PA | S67//1MTR/87A | S67//1MTR/51ZA | S67//1MTR/96B1 | S67//1MTR/63Q | S67//2MTR/96B1 | S67//2MTR/96PA | S67//2MTR/63Q | S67//2MTR/TRA | S67//2MTR/51ZA | S67//2MTR/87A | S67//2MTR/96B2 | S67//2MTR/96D | S67//3MTR/96D | S67//3MTR/63Q | S67//3MTR/96B1 | S67//3MTR/96B2 | S67//3MTR/TRA | S67//3MTR/87A | S67//3MTR/51ZA | S67//3MTR/96PA | S67//4MTR/51ZA | S67//4MTR/87A | S67//4MTR/96PA | S67//4MTR/96D | S67//4MTR/TRA | S67//4MTR/96B2 | S67//4MTR/63Q | S67//4MTR/96B1 | S67//6MTR/96B1 | S67//6MTR/63Q | S67//6MTR/96D | S67//6MTR/96B2 | S67//6MTR/87A | S67//6MTR/51ZA | S67//6MTR/96PA | S67//6MTR/TRA
S67 | 歸仁SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S67_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_5 | OPRD1: S67//1MTR/TRF; OPRD2: S67//2MTR/TRF; OPRD3: S67//3MTR/TRF; OPRD4: S67//4MTR/TRF; OPRD5: S67//6MTR/TRF
S67 | 歸仁SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/RTU/RTU_R_L
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/DCE
S67 | 歸仁SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S67_D1 | [17 empty] | lamp2CC | OPRD1: S67/69/ComPoint/CBA
S67 | 歸仁SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S67_D1 | [17 empty] | lamp2CC | OPRD1: S67/69/ComPoint/CBF
S67 | 歸仁SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S67_D1 | [17 empty] | lamp2CC | OPRD1: S67/69/ComPoint/ABS_89A
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/DCA
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/Fire
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | DTU通訊故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/PSA
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | DTU內部故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/PSF
S67 | 歸仁SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S67_A1 | [17 empty] | lamp2CC | OPRD1: S67/0/StaDev/PMA
S67 | 歸仁SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S67_D1 | [17 empty] | lamp2CC | OPRD1: S67/69/ComPoint/CFA
S67 | 歸仁SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S67_D1 | [17 empty] | lamp2CC | OPRD1: S67/69/ComPoint/IRFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S67 | 歸仁SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S67/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.630_AMP | 歸仁大亞線 AMP | LINE69 | S67/69/630/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C06R0500 | 450.000000 | 450.000000 | 500.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | I | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.660_AMP | 歸仁保安線 AMP | LINE69 | S67/69/660/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C10R0800 | 650.000000 | 720.000000 | 800.000000 | 1000.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | I | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.670_AMP | 新市歸仁線 AMP | LINE69 | S67/69/670/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C10R1000 | 900.000000 | 900.000000 | 1000.000000 | 1000.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | I | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.680_AMP | 山上歸仁線 AMP | LINE69 | S67/69/680/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C10R0800 | 650.000000 | 720.000000 | 800.000000 | 1000.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S67 | 歸仁SS | 0 |  |  |  |  | 八甲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.八甲線KVA | 11KV八甲線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 八甲線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.八甲線KW | 11KV八甲線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 仁傑線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線KVA | 11KV仁傑線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 仁傑線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線KW | 11KV仁傑線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 六合線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.六合線KVA | 11KV六合線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 六合線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.六合線KW | 11KV六合線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 古厝線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.古厝線KVA | 11KV古厝線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 古厝線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.古厝線KW | 11KV古厝線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 沙崙線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線KVA | 11KV沙崙線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 沙崙線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線KW | 11KV沙崙線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 貝汝線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線KVA | 11KV貝汝線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 貝汝線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線KW | 11KV貝汝線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 東盈線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.東盈線KVA | 11KV東盈線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 東盈線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.東盈線KW | 11KV東盈線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 松根線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.松根線KVA | 11KV松根線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 松根線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.松根線KW | 11KV松根線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 南保線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.南保線KVA | 11KV南保線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 南保線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.南保線KW | 11KV南保線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 南潭線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.南潭線KVA | 11KV南潭線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 南潭線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.南潭線KW | 11KV南潭線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 看西線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.看西線KVA | 11KV看西線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 看西線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.看西線KW | 11KV看西線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 崙頂線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線KVA | 11KV崙頂線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 崙頂線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線KW | 11KV崙頂線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 深坑線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.深坑線KVA | 11KV深坑線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 深坑線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.深坑線KW | 11KV深坑線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 媽廟線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線KVA | 11KV媽廟線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 媽廟線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線KW | 11KV媽廟線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 新田線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.新田線KVA | 11KV新田線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 新田線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.新田線KW | 11KV新田線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 萬芳線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線KVA | 11KV萬芳線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 萬芳線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線KW | 11KV萬芳線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 漢平線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.漢平線KVA | 11KV漢平線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 漢平線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.漢平線KW | 11KV漢平線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 龍崎線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線KVA | 11KV龍崎線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 龍崎線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線KW | 11KV龍崎線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸仁線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線KVA | 11KV歸仁線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸仁線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線KW | 11KV歸仁線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸南線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸南線KVA | 11KV歸南線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸南線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸南線KW | 11KV歸南線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 豐中線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.豐中線KVA | 11KV豐中線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 豐中線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.豐中線KW | 11KV豐中線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 關甲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.關甲線KVA | 11KV關甲線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 關甲線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.關甲線KW | 11KV關甲線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 關廟線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.關廟線KVA | 11KV關廟線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 關廟線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.關廟線KW | 11KV關廟線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S67//1MTR/MVA |  | MVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_PF | #1MTR 功率因素 | DTR | S67//1MTR/PF |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S67//2MTR/MVA |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_PF | #2MTR 功率因素 | DTR | S67//2MTR/PF |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S67//3MTR/MVA |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_PF | #3MTR 功率因素 | DTR | S67//3MTR/PF |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | S67//4MTR/MVA |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_PF | #4MTR 功率因素 | DTR | S67//4MTR/PF |  | RPDC_PF_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_MVA | #6MTR二次側 MVA | DTR | S67//6MTR/MVA |  | MVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_PF | #6MTR 功率因素 | DTR | S67//6MTR/PF |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S67 | 歸仁SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S67/11/210/MVAR |  | SC_CAL_11 |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S67/11/220/MVAR |  | SC_CAL_11 |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S67/11/230/MVAR |  | SC_CAL_11 |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_SC_MVAR | 11KV#4SC MVAR | SC | S67/11/240/MVAR |  | SC_CAL_11 |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_SC_MVAR | 11KV#6SC MVAR | SC | S67/11/260/MVAR |  | SC_CAL_11 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S67/69/810/MVAR |  | SC_CAL_69 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸33線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸33線KVA | 11KV歸33線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸33線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸33線KW | 11KV歸33線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸38線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸38線KVA | 11KV歸38線KVA | FEEDER |  |  | KVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 歸38線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.歸38線KW | 11KV歸38線KW | FEEDER |  |  | KW_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 大聚線KVA | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.大聚線KVA | 11KV大聚線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 0 |  |  |  |  | 大聚線KW | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.大聚線KW | 11KV大聚線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 69 | 69kV | 630_CB | 歸仁大亞線(630_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.630_CB_4 | 630(歸仁大亞線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660_CB | 歸仁保安線(660_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.660_CB_4 | 660(歸仁保安線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670_CB | 新市歸仁線(670_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.670_CB_4 | 670(新市歸仁線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680_CB | 山上歸仁線(680_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.680_CB_4 | 680(山上歸仁線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 80 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 81 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 82 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 83 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 歸仁SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S67/0/CalcPoint/SUBA |  | STATION_FAULT_20 |  |  | 84 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 85 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_5 |  |  | 86 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630_AMP | 歸仁大亞線 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.630_AMP_A | 歸仁大亞線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630_AMP | 歸仁大亞線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.630_AMP_4 | 歸仁大亞線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660_AMP | 歸仁保安線 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.660_AMP_A | 歸仁保安線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660_AMP | 歸仁保安線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.660_AMP_4 | 歸仁保安線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670_AMP | 新市歸仁線 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.670_AMP_A | 新市歸仁線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670_AMP | 新市歸仁線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.670_AMP_4 | 新市歸仁線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680_AMP | 山上歸仁線 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.680_AMP_A | 山上歸仁線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680_AMP | 山上歸仁線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.680_AMP_4 | 山上歸仁線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR_MVA | #3MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_MVA_4 | #3MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR_MVA | #4MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_MVA_4 | #4MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR_MVA | #6MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_MVA_4 | #6MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_PERM | #6MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 歸仁SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S67/0/RTU/ADCH1 |  |  |  | CDC | 106 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S67/0/RTU/ADCH2 |  |  |  | CDC | 107 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S67/0/RTU/ADCH3 |  |  |  | CDC | 108 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | S67/0/RTU/ADCH4 |  |  |  | CDC | 109 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S67/0/RTU/ADCL1 |  |  |  | CDC | 110 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S67/0/RTU/ADCL2 |  |  |  | CDC | 111 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S67/0/RTU/ADCL3 |  |  |  | CDC | 112 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | S67/0/RTU/ADCL4 |  |  |  | CDC | 113 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S67/69/1BUS/V |  |  |  | CDC | 114 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S67 | 歸仁SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S67/11/1BUS/V_R |  |  |  | CDC | 115 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S67/11/2BUS/V_R |  |  |  | CDC | 116 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S67/11/3BUS/V_R |  |  |  | CDC | 117 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 4BUS | #4BUS |  | V | [17 empty] | 2-89 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS | S67/11/4BUS/V_R |  |  |  | CDC | 118 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 6BUS | #6BUS |  | V | [17 empty] | 2-AD | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS | S67/11/6BUS/V_R |  |  |  | CDC | 119 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.630_MW | 歸仁大亞線 MW | LINE69 | S67/69/630/MW |  |  |  | CDC | 120 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.630_MVAR | 歸仁大亞線 MVAR | LINE69 | S67/69/630/MVAR |  |  |  | CDC | 121 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.660_MW | 歸仁保安線 MW | LINE69 | S67/69/660/MW |  |  |  | CDC | 122 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.660_MVAR | 歸仁保安線 MVAR | LINE69 | S67/69/660/MVAR |  |  |  | CDC | 123 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.670_MW | 新市歸仁線 MW | LINE69 | S67/69/670/MW |  |  |  | CDC | 124 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.670_MVAR | 新市歸仁線 MVAR | LINE69 | S67/69/670/MVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.680_MW | 山上歸仁線 MW | LINE69 | S67/69/680/MW |  |  |  | CDC | 126 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 歸仁SS.680_MVAR | 山上歸仁線 MVAR | LINE69 | S67/69/680/MVAR |  |  |  | CDC | 127 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.240000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 八甲線 | 八甲線 |  | 八甲線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.八甲線KVAR | 11KV八甲線 KVAR | FEEDER | S67/11/KR32/KVAR |  |  |  | CDC | 128 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 八甲線 | 八甲線 |  | 八甲線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.八甲線A1 | 11KV八甲線 R相AMP | FEEDER | S67/11/KR32/I_R |  |  |  | CDC | 129 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 八甲線 | 八甲線 |  | 八甲線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.八甲線A2 | 11KV八甲線 S相AMP | FEEDER | S67/11/KR32/I_S |  |  |  | CDC | 130 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 八甲線 | 八甲線 |  | 八甲線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.八甲線A3 | 11KV八甲線 T相AMP | FEEDER | S67/11/KR32/I_T |  |  |  | CDC | 131 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 八甲線 | 八甲線 |  | 八甲線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.八甲線A0 | 11KV八甲線 N相AMP | FEEDER | S67/11/KR32/I_N |  |  |  | CDC | 132 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 仁傑線 | 仁傑線 |  | 仁傑線KVAR | [17 empty] | 2-C8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線KVAR | 11KV仁傑線 KVAR | FEEDER | S67/11/KR45/KVAR |  |  |  | CDC | 133 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 仁傑線 | 仁傑線 |  | 仁傑線A1 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線A1 | 11KV仁傑線 R相AMP | FEEDER | S67/11/KR45/I_R |  |  |  | CDC | 134 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 仁傑線 | 仁傑線 |  | 仁傑線A2 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線A2 | 11KV仁傑線 S相AMP | FEEDER | S67/11/KR45/I_S |  |  |  | CDC | 135 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 仁傑線 | 仁傑線 |  | 仁傑線A3 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線A3 | 11KV仁傑線 T相AMP | FEEDER | S67/11/KR45/I_T |  |  |  | CDC | 136 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 仁傑線 | 仁傑線 |  | 仁傑線A0 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.仁傑線A0 | 11KV仁傑線 N相AMP | FEEDER | S67/11/KR45/I_N |  |  |  | CDC | 137 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 六合線 | 六合線 |  | 六合線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.六合線KVAR | 11KV六合線 KVAR | FEEDER | S67/11/KR36/KVAR |  |  |  | CDC | 138 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 六合線 | 六合線 |  | 六合線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.六合線A1 | 11KV六合線 R相AMP | FEEDER | S67/11/KR36/I_R |  |  |  | CDC | 139 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 六合線 | 六合線 |  | 六合線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.六合線A2 | 11KV六合線 S相AMP | FEEDER | S67/11/KR36/I_S |  |  |  | CDC | 140 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 六合線 | 六合線 |  | 六合線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.六合線A3 | 11KV六合線 T相AMP | FEEDER | S67/11/KR36/I_T |  |  |  | CDC | 141 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 六合線 | 六合線 |  | 六合線A0 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.六合線A0 | 11KV六合線 N相AMP | FEEDER | S67/11/KR36/I_N |  |  |  | CDC | 142 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 古厝線 | 古厝線 |  | 古厝線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.古厝線KVAR | 11KV古厝線 KVAR | FEEDER | S67/11/KR42/KVAR |  |  |  | CDC | 143 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 古厝線 | 古厝線 |  | 古厝線A1 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.古厝線A1 | 11KV古厝線 R相AMP | FEEDER | S67/11/KR42/I_R |  |  |  | CDC | 144 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 古厝線 | 古厝線 |  | 古厝線A2 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.古厝線A2 | 11KV古厝線 S相AMP | FEEDER | S67/11/KR42/I_S |  |  |  | CDC | 145 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 古厝線 | 古厝線 |  | 古厝線A3 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.古厝線A3 | 11KV古厝線 T相AMP | FEEDER | S67/11/KR42/I_T |  |  |  | CDC | 146 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 古厝線 | 古厝線 |  | 古厝線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.古厝線A0 | 11KV古厝線 N相AMP | FEEDER | S67/11/KR42/I_N |  |  |  | CDC | 147 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 沙崙線 | 沙崙線 |  | 沙崙線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線KVAR | 11KV沙崙線 KVAR | FEEDER | S67/11/KR39/KVAR |  |  |  | CDC | 148 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 沙崙線 | 沙崙線 |  | 沙崙線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線A1 | 11KV沙崙線 R相AMP | FEEDER | S67/11/KR39/I_R |  |  |  | CDC | 149 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 沙崙線 | 沙崙線 |  | 沙崙線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線A2 | 11KV沙崙線 S相AMP | FEEDER | S67/11/KR39/I_S |  |  |  | CDC | 150 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 沙崙線 | 沙崙線 |  | 沙崙線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線A3 | 11KV沙崙線 T相AMP | FEEDER | S67/11/KR39/I_T |  |  |  | CDC | 151 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 沙崙線 | 沙崙線 |  | 沙崙線A0 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.沙崙線A0 | 11KV沙崙線 N相AMP | FEEDER | S67/11/KR39/I_N |  |  |  | CDC | 152 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 貝汝線 | 貝汝線 |  | 貝汝線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線KVAR | 11KV貝汝線 KVAR | FEEDER | S67/11/KR25/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 貝汝線 | 貝汝線 |  | 貝汝線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線A1 | 11KV貝汝線 R相AMP | FEEDER | S67/11/KR25/I_R |  |  |  | CDC | 154 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 貝汝線 | 貝汝線 |  | 貝汝線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線A2 | 11KV貝汝線 S相AMP | FEEDER | S67/11/KR25/I_S |  |  |  | CDC | 155 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 貝汝線 | 貝汝線 |  | 貝汝線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線A3 | 11KV貝汝線 T相AMP | FEEDER | S67/11/KR25/I_T |  |  |  | CDC | 156 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 貝汝線 | 貝汝線 |  | 貝汝線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.貝汝線A0 | 11KV貝汝線 N相AMP | FEEDER | S67/11/KR25/I_N |  |  |  | CDC | 157 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 東盈線 | 東盈線 |  | 東盈線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.東盈線KVAR | 11KV東盈線 KVAR | FEEDER | S67/11/KR26/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 東盈線 | 東盈線 |  | 東盈線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.東盈線A1 | 11KV東盈線 R相AMP | FEEDER | S67/11/KR26/I_R |  |  |  | CDC | 159 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 東盈線 | 東盈線 |  | 東盈線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.東盈線A2 | 11KV東盈線 S相AMP | FEEDER | S67/11/KR26/I_S |  |  |  | CDC | 160 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 東盈線 | 東盈線 |  | 東盈線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.東盈線A3 | 11KV東盈線 T相AMP | FEEDER | S67/11/KR26/I_T |  |  |  | CDC | 161 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 東盈線 | 東盈線 |  | 東盈線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.東盈線A0 | 11KV東盈線 N相AMP | FEEDER | S67/11/KR26/I_N |  |  |  | CDC | 162 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 松根線 | 松根線 |  | 松根線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.松根線KVAR | 11KV松根線 KVAR | FEEDER | S67/11/KR37/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 松根線 | 松根線 |  | 松根線A1 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.松根線A1 | 11KV松根線 R相AMP | FEEDER | S67/11/KR37/I_R |  |  |  | CDC | 164 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 松根線 | 松根線 |  | 松根線A2 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.松根線A2 | 11KV松根線 S相AMP | FEEDER | S67/11/KR37/I_S |  |  |  | CDC | 165 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 松根線 | 松根線 |  | 松根線A3 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.松根線A3 | 11KV松根線 T相AMP | FEEDER | S67/11/KR37/I_T |  |  |  | CDC | 166 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 松根線 | 松根線 |  | 松根線A0 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.松根線A0 | 11KV松根線 N相AMP | FEEDER | S67/11/KR37/I_N |  |  |  | CDC | 167 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南保線 | 南保線 |  | 南保線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南保線KVAR | 11KV南保線 KVAR | FEEDER | S67/11/KR24/KVAR |  |  |  | CDC | 168 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南保線 | 南保線 |  | 南保線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南保線A1 | 11KV南保線 R相AMP | FEEDER | S67/11/KR24/I_R |  |  |  | CDC | 169 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南保線 | 南保線 |  | 南保線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南保線A2 | 11KV南保線 S相AMP | FEEDER | S67/11/KR24/I_S |  |  |  | CDC | 170 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南保線 | 南保線 |  | 南保線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南保線A3 | 11KV南保線 T相AMP | FEEDER | S67/11/KR24/I_T |  |  |  | CDC | 171 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南保線 | 南保線 |  | 南保線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南保線A0 | 11KV南保線 N相AMP | FEEDER | S67/11/KR24/I_N |  |  |  | CDC | 172 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南潭線 | 南潭線 |  | 南潭線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南潭線KVAR | 11KV南潭線 KVAR | FEEDER | S67/11/KR35/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南潭線 | 南潭線 |  | 南潭線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南潭線A1 | 11KV南潭線 R相AMP | FEEDER | S67/11/KR35/I_R |  |  |  | CDC | 174 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南潭線 | 南潭線 |  | 南潭線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南潭線A2 | 11KV南潭線 S相AMP | FEEDER | S67/11/KR35/I_S |  |  |  | CDC | 175 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南潭線 | 南潭線 |  | 南潭線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南潭線A3 | 11KV南潭線 T相AMP | FEEDER | S67/11/KR35/I_T |  |  |  | CDC | 176 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 南潭線 | 南潭線 |  | 南潭線A0 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.南潭線A0 | 11KV南潭線 N相AMP | FEEDER | S67/11/KR35/I_N |  |  |  | CDC | 177 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 看西線 | 看西線 |  | 看西線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.看西線KVAR | 11KV看西線 KVAR | FEEDER | S67/11/KR29/KVAR |  |  |  | CDC | 178 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 看西線 | 看西線 |  | 看西線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.看西線A1 | 11KV看西線 R相AMP | FEEDER | S67/11/KR29/I_R |  |  |  | CDC | 179 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 看西線 | 看西線 |  | 看西線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.看西線A2 | 11KV看西線 S相AMP | FEEDER | S67/11/KR29/I_S |  |  |  | CDC | 180 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 看西線 | 看西線 |  | 看西線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.看西線A3 | 11KV看西線 T相AMP | FEEDER | S67/11/KR29/I_T |  |  |  | CDC | 181 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 看西線 | 看西線 |  | 看西線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.看西線A0 | 11KV看西線 N相AMP | FEEDER | S67/11/KR29/I_N |  |  |  | CDC | 182 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 崙頂線 | 崙頂線 |  | 崙頂線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線KVAR | 11KV崙頂線 KVAR | FEEDER | S67/11/KR28/KVAR |  |  |  | CDC | 183 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 崙頂線 | 崙頂線 |  | 崙頂線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線A1 | 11KV崙頂線 R相AMP | FEEDER | S67/11/KR28/I_R |  |  |  | CDC | 184 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 崙頂線 | 崙頂線 |  | 崙頂線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線A2 | 11KV崙頂線 S相AMP | FEEDER | S67/11/KR28/I_S |  |  |  | CDC | 185 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 崙頂線 | 崙頂線 |  | 崙頂線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線A3 | 11KV崙頂線 T相AMP | FEEDER | S67/11/KR28/I_T |  |  |  | CDC | 186 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 崙頂線 | 崙頂線 |  | 崙頂線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.崙頂線A0 | 11KV崙頂線 N相AMP | FEEDER | S67/11/KR28/I_N |  |  |  | CDC | 187 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 深坑線 | 深坑線 |  | 深坑線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.深坑線KVAR | 11KV深坑線 KVAR | FEEDER | S67/11/KR34/KVAR |  |  |  | CDC | 188 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 深坑線 | 深坑線 |  | 深坑線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.深坑線A1 | 11KV深坑線 R相AMP | FEEDER | S67/11/KR34/I_R |  |  |  | CDC | 189 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 深坑線 | 深坑線 |  | 深坑線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.深坑線A2 | 11KV深坑線 S相AMP | FEEDER | S67/11/KR34/I_S |  |  |  | CDC | 190 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 深坑線 | 深坑線 |  | 深坑線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.深坑線A3 | 11KV深坑線 T相AMP | FEEDER | S67/11/KR34/I_T |  |  |  | CDC | 191 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 深坑線 | 深坑線 |  | 深坑線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.深坑線A0 | 11KV深坑線 N相AMP | FEEDER | S67/11/KR34/I_N |  |  |  | CDC | 192 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 媽廟線 | 媽廟線 |  | 媽廟線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線KVAR | 11KV媽廟線 KVAR | FEEDER | S67/11/KR23/KVAR |  |  |  | CDC | 193 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 媽廟線 | 媽廟線 |  | 媽廟線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線A1 | 11KV媽廟線 R相AMP | FEEDER | S67/11/KR23/I_R |  |  |  | CDC | 194 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 媽廟線 | 媽廟線 |  | 媽廟線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線A2 | 11KV媽廟線 S相AMP | FEEDER | S67/11/KR23/I_S |  |  |  | CDC | 195 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 媽廟線 | 媽廟線 |  | 媽廟線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線A3 | 11KV媽廟線 T相AMP | FEEDER | S67/11/KR23/I_T |  |  |  | CDC | 196 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 媽廟線 | 媽廟線 |  | 媽廟線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.媽廟線A0 | 11KV媽廟線 N相AMP | FEEDER | S67/11/KR23/I_N |  |  |  | CDC | 197 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 新田線 | 新田線 |  | 新田線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.新田線KVAR | 11KV新田線 KVAR | FEEDER | S67/11/KR22/KVAR |  |  |  | CDC | 198 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 新田線 | 新田線 |  | 新田線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.新田線A1 | 11KV新田線 R相AMP | FEEDER | S67/11/KR22/I_R |  |  |  | CDC | 199 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 新田線 | 新田線 |  | 新田線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.新田線A2 | 11KV新田線 S相AMP | FEEDER | S67/11/KR22/I_S |  |  |  | CDC | 200 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 新田線 | 新田線 |  | 新田線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.新田線A3 | 11KV新田線 T相AMP | FEEDER | S67/11/KR22/I_T |  |  |  | CDC | 201 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 新田線 | 新田線 |  | 新田線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.新田線A0 | 11KV新田線 N相AMP | FEEDER | S67/11/KR22/I_N |  |  |  | CDC | 202 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 萬芳線 | 萬芳線 |  | 萬芳線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線KVAR | 11KV萬芳線 KVAR | FEEDER | S67/11/KR31/KVAR |  |  |  | CDC | 203 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 萬芳線 | 萬芳線 |  | 萬芳線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線A1 | 11KV萬芳線 R相AMP | FEEDER | S67/11/KR31/I_R |  |  |  | CDC | 204 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 萬芳線 | 萬芳線 |  | 萬芳線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線A2 | 11KV萬芳線 S相AMP | FEEDER | S67/11/KR31/I_S |  |  |  | CDC | 205 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 萬芳線 | 萬芳線 |  | 萬芳線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線A3 | 11KV萬芳線 T相AMP | FEEDER | S67/11/KR31/I_T |  |  |  | CDC | 206 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 萬芳線 | 萬芳線 |  | 萬芳線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.萬芳線A0 | 11KV萬芳線 N相AMP | FEEDER | S67/11/KR31/I_N |  |  |  | CDC | 207 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 漢平線 | 漢平線 |  | 漢平線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.漢平線KVAR | 11KV漢平線 KVAR | FEEDER | S67/11/KR40/KVAR |  |  |  | CDC | 208 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 漢平線 | 漢平線 |  | 漢平線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.漢平線A1 | 11KV漢平線 R相AMP | FEEDER | S67/11/KR40/I_R |  |  |  | CDC | 209 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 漢平線 | 漢平線 |  | 漢平線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.漢平線A2 | 11KV漢平線 S相AMP | FEEDER | S67/11/KR40/I_S |  |  |  | CDC | 210 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 漢平線 | 漢平線 |  | 漢平線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.漢平線A3 | 11KV漢平線 T相AMP | FEEDER | S67/11/KR40/I_T |  |  |  | CDC | 211 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 漢平線 | 漢平線 |  | 漢平線A0 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.漢平線A0 | 11KV漢平線 N相AMP | FEEDER | S67/11/KR40/I_N |  |  |  | CDC | 212 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 龍崎線 | 龍崎線 |  | 龍崎線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線KVAR | 11KV龍崎線 KVAR | FEEDER | S67/11/KR43/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 龍崎線 | 龍崎線 |  | 龍崎線A1 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線A1 | 11KV龍崎線 R相AMP | FEEDER | S67/11/KR43/I_R |  |  |  | CDC | 214 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 龍崎線 | 龍崎線 |  | 龍崎線A2 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線A2 | 11KV龍崎線 S相AMP | FEEDER | S67/11/KR43/I_S |  |  |  | CDC | 215 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 龍崎線 | 龍崎線 |  | 龍崎線A3 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線A3 | 11KV龍崎線 T相AMP | FEEDER | S67/11/KR43/I_T |  |  |  | CDC | 216 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 龍崎線 | 龍崎線 |  | 龍崎線A0 | [17 empty] | 2-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.龍崎線A0 | 11KV龍崎線 N相AMP | FEEDER | S67/11/KR43/I_N |  |  |  | CDC | 217 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸仁線 | 歸仁線 |  | 歸仁線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線KVAR | 11KV歸仁線 KVAR | FEEDER | S67/11/KR21/KVAR |  |  |  | CDC | 218 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸仁線 | 歸仁線 |  | 歸仁線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線A1 | 11KV歸仁線 R相AMP | FEEDER | S67/11/KR21/I_R |  |  |  | CDC | 219 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸仁線 | 歸仁線 |  | 歸仁線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線A2 | 11KV歸仁線 S相AMP | FEEDER | S67/11/KR21/I_S |  |  |  | CDC | 220 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸仁線 | 歸仁線 |  | 歸仁線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線A3 | 11KV歸仁線 T相AMP | FEEDER | S67/11/KR21/I_T |  |  |  | CDC | 221 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸仁線 | 歸仁線 |  | 歸仁線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸仁線A0 | 11KV歸仁線 N相AMP | FEEDER | S67/11/KR21/I_N |  |  |  | CDC | 222 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸南線 | 歸南線 |  | 歸南線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸南線KVAR | 11KV歸南線 KVAR | FEEDER | S67/11/KR41/KVAR |  |  |  | CDC | 223 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸南線 | 歸南線 |  | 歸南線A1 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸南線A1 | 11KV歸南線 R相AMP | FEEDER | S67/11/KR41/I_R |  |  |  | CDC | 224 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸南線 | 歸南線 |  | 歸南線A2 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸南線A2 | 11KV歸南線 S相AMP | FEEDER | S67/11/KR41/I_S |  |  |  | CDC | 225 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸南線 | 歸南線 |  | 歸南線A3 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸南線A3 | 11KV歸南線 T相AMP | FEEDER | S67/11/KR41/I_T |  |  |  | CDC | 226 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸南線 | 歸南線 |  | 歸南線A0 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸南線A0 | 11KV歸南線 N相AMP | FEEDER | S67/11/KR41/I_N |  |  |  | CDC | 227 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 豐中線 | 豐中線 |  | 豐中線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.豐中線KVAR | 11KV豐中線 KVAR | FEEDER | S67/11/KR27/KVAR |  |  |  | CDC | 228 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 豐中線 | 豐中線 |  | 豐中線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.豐中線A1 | 11KV豐中線 R相AMP | FEEDER | S67/11/KR27/I_R |  |  |  | CDC | 229 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 豐中線 | 豐中線 |  | 豐中線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.豐中線A2 | 11KV豐中線 S相AMP | FEEDER | S67/11/KR27/I_S |  |  |  | CDC | 230 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 豐中線 | 豐中線 |  | 豐中線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.豐中線A3 | 11KV豐中線 T相AMP | FEEDER | S67/11/KR27/I_T |  |  |  | CDC | 231 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 豐中線 | 豐中線 |  | 豐中線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.豐中線A0 | 11KV豐中線 N相AMP | FEEDER | S67/11/KR27/I_N |  |  |  | CDC | 232 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關甲線 | 關甲線 |  | 關甲線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關甲線KVAR | 11KV關甲線 KVAR | FEEDER | S67/11/KR44/KVAR |  |  |  | CDC | 233 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關甲線 | 關甲線 |  | 關甲線A1 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關甲線A1 | 11KV關甲線 R相AMP | FEEDER | S67/11/KR44/I_R |  |  |  | CDC | 234 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關甲線 | 關甲線 |  | 關甲線A2 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關甲線A2 | 11KV關甲線 S相AMP | FEEDER | S67/11/KR44/I_S |  |  |  | CDC | 235 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關甲線 | 關甲線 |  | 關甲線A3 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關甲線A3 | 11KV關甲線 T相AMP | FEEDER | S67/11/KR44/I_T |  |  |  | CDC | 236 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關甲線 | 關甲線 |  | 關甲線A0 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關甲線A0 | 11KV關甲線 N相AMP | FEEDER | S67/11/KR44/I_N |  |  |  | CDC | 237 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關廟線 | 關廟線 |  | 關廟線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關廟線KVAR | 11KV關廟線 KVAR | FEEDER | S67/11/KR30/KVAR |  |  |  | CDC | 238 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關廟線 | 關廟線 |  | 關廟線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關廟線A1 | 11KV關廟線 R相AMP | FEEDER | S67/11/KR30/I_R |  |  |  | CDC | 239 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關廟線 | 關廟線 |  | 關廟線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關廟線A2 | 11KV關廟線 S相AMP | FEEDER | S67/11/KR30/I_S |  |  |  | CDC | 240 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關廟線 | 關廟線 |  | 關廟線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關廟線A3 | 11KV關廟線 T相AMP | FEEDER | S67/11/KR30/I_T |  |  |  | CDC | 241 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 關廟線 | 關廟線 |  | 關廟線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.關廟線A0 | 11KV關廟線 N相AMP | FEEDER | S67/11/KR30/I_N |  |  |  | CDC | 242 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE1 | #1-#2 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE1_A1 | 11KV #1-#2 TIE R相AMP | TIE | S67/11/TIE1/I_R |  |  |  | CDC | 243 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE1 | #1-#2 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE1_A2 | 11KV #1-#2 TIE S相AMP | TIE | S67/11/TIE1/I_S |  |  |  | CDC | 244 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE1 | #1-#2 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE1_A3 | 11KV #1-#2 TIE T相AMP | TIE | S67/11/TIE1/I_T |  |  |  | CDC | 245 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE2 | #3-#2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE2_A1 | 11KV #3-#2 TIE R相AMP | TIE | S67/11/TIE2/I_R |  |  |  | CDC | 246 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE2 | #3-#2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE2_A2 | 11KV #3-#2 TIE S相AMP | TIE | S67/11/TIE2/I_S |  |  |  | CDC | 247 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE2 | #3-#2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE2_A3 | 11KV #3-#2 TIE T相AMP | TIE | S67/11/TIE2/I_T |  |  |  | CDC | 248 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE3 | #6-#3 |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE3_A1 | 11KV #6-#3 TIE R相AMP | TIE | S67/11/TIE3/I_R |  |  |  | CDC | 249 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE3 | #6-#3 |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE3_A2 | 11KV #6-#3 TIE S相AMP | TIE | S67/11/TIE3/I_S |  |  |  | CDC | 250 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE3 | #6-#3 |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE3_A3 | 11KV #6-#3 TIE T相AMP | TIE | S67/11/TIE3/I_T |  |  |  | CDC | 251 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE4 | #4-#1 |  | I_R | [17 empty] | 2-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE4_A1 | 11KV #4-#1 TIE R相AMP | TIE | S67/11/TIE4/I_R |  |  |  | CDC | 252 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE4 | #4-#1 |  | I_S | [17 empty] | 2-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE4_A2 | 11KV #4-#1 TIE S相AMP | TIE | S67/11/TIE4/I_S |  |  |  | CDC | 253 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | _TIE4 | #4-#1 |  | I_T | [17 empty] | 2-A8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11KV_TIE4_A3 | 11KV #4-#1 TIE T相AMP | TIE | S67/11/TIE4/I_T |  |  |  | CDC | 254 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_MW | #1MTR二次側 MW | DTR | S67/11/M1/MW |  |  |  | CDC | 255 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S67/11/M1/MVAR |  |  |  | CDC | 256 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S67/11/M1/I_R |  |  |  | CDC | 257 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S67/11/M1/I_S |  |  |  | CDC | 258 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S67/11/M1/I_T |  |  |  | CDC | 259 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_OIL | #1MTR 油溫 | DTR | S67//1MTR/OilTemp |  |  |  | CDC | 260 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_COIL | #1MTR 線溫 | DTR | S67//1MTR/CoilTemp |  |  |  | CDC | 261 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S67//1MTR/TapPosMv |  |  |  | CDC | 262 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_MW | #2MTR二次側 MW | DTR | S67/11/M2/MW |  |  |  | CDC | 263 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S67/11/M2/MVAR |  |  |  | CDC | 264 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S67/11/M2/I_R |  |  |  | CDC | 265 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S67/11/M2/I_S |  |  |  | CDC | 266 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S67/11/M2/I_T |  |  |  | CDC | 267 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_OIL | #2MTR 油溫 | DTR | S67//2MTR/OilTemp |  |  |  | CDC | 268 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_COIL | #2MTR 線溫 | DTR | S67//2MTR/CoilTemp |  |  |  | CDC | 269 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S67//2MTR/TapPosMv |  |  |  | CDC | 270 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_MW | #3MTR二次側 MW | DTR | S67/11/M3/MW |  |  |  | CDC | 271 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S67/11/M3/MVAR |  |  |  | CDC | 272 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S67/11/M3/I_R |  |  |  | CDC | 273 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S67/11/M3/I_S |  |  |  | CDC | 274 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S67/11/M3/I_T |  |  |  | CDC | 275 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_OIL | #3MTR 油溫 | DTR | S67//3MTR/OilTemp |  |  |  | CDC | 276 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_COIL | #3MTR 線溫 | DTR | S67//3MTR/CoilTemp |  |  |  | CDC | 277 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-62 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S67//3MTR/TapPosMv |  |  |  | CDC | 278 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 2-8D | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_MW | #4MTR二次側 MW | DTR | S67/11/M4/MW |  |  |  | CDC | 279 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 2-8E | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR | S67/11/M4/MVAR |  |  |  | CDC | 280 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR | S67/11/M4/I_R |  |  |  | CDC | 281 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR | S67/11/M4/I_S |  |  |  | CDC | 282 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR二次側 |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR | S67/11/M4/I_T |  |  |  | CDC | 283 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 2-8B | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_OIL | #4MTR 油溫 | DTR | S67//4MTR/OilTemp |  |  |  | CDC | 284 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 2-8A | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_COIL | #4MTR 線溫 | DTR | S67//4MTR/CoilTemp |  |  |  | CDC | 285 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 2-8C |  | 1-76 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_TAP | #4MTR OLTC TAP | DTR | S67//4MTR/TapPosMv |  |  |  | CDC | 286 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | MW | [17 empty] | 2-B1 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_MW | #6MTR二次側 MW | DTR | S67/11/M6/MW |  |  |  | CDC | 287 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | MVAR | [17 empty] | 2-B2 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_MVAR | #6MTR二次側 MVAR | DTR | S67/11/M6/MVAR |  |  |  | CDC | 288 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | I_R | [17 empty] | 2-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_A1 | #6MTR二次側 R相AMP | DTR | S67/11/M6/I_R |  |  |  | CDC | 289 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | I_S | [17 empty] | 2-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_A2 | #6MTR二次側 S相AMP | DTR | S67/11/M6/I_S |  |  |  | CDC | 290 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR二次側 |  | I_T | [17 empty] | 2-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_A3 | #6MTR二次側 T相AMP | DTR | S67/11/M6/I_T |  |  |  | CDC | 291 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | OilTemp | [17 empty] | 2-AF | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_OIL | #6MTR 油溫 | DTR | S67//6MTR/OilTemp |  |  |  | CDC | 292 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | CoilTemp | [17 empty] | 2-AE | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_COIL | #6MTR 線溫 | DTR | S67//6MTR/CoilTemp |  |  |  | CDC | 293 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | TapPosMv | [17 empty] | 2-B0 |  | 2-09 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_TAP | #6MTR OLTC TAP | DTR | S67//6MTR/TapPosMv |  |  |  | CDC | 294 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S67 | 歸仁SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.直流電源電壓 | 直流電源電壓 | OTHER | S67/0/StaDev/DCV |  |  |  | CDC | 295 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸33線 | 歸33線 |  | 歸33線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸33線KVAR | 11KV歸33線 KVAR | FEEDER | S67/11/KR33/KVAR |  |  |  | CDC | 296 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸33線 | 歸33線 |  | 歸33線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸33線A1 | 11KV歸33線 R相AMP | FEEDER | S67/11/KR33/I_R |  |  |  | CDC | 297 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸33線 | 歸33線 |  | 歸33線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸33線A2 | 11KV歸33線 S相AMP | FEEDER | S67/11/KR33/I_S |  |  |  | CDC | 298 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸33線 | 歸33線 |  | 歸33線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸33線A3 | 11KV歸33線 T相AMP | FEEDER | S67/11/KR33/I_T |  |  |  | CDC | 299 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸33線 | 歸33線 |  | 歸33線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸33線A0 | 11KV歸33線 N相AMP | FEEDER | S67/11/KR33/I_N |  |  |  | CDC | 300 | GENERICAIPoint | SS409_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸38線 | 歸38線 |  | 歸38線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸38線KVAR | 11KV歸38線 KVAR | FEEDER | S67/11/KR38/KVAR |  |  |  | CDC | 301 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸38線 | 歸38線 |  | 歸38線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸38線A1 | 11KV歸38線 R相AMP | FEEDER | S67/11/KR38/I_R |  |  |  | CDC | 302 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸38線 | 歸38線 |  | 歸38線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸38線A2 | 11KV歸38線 S相AMP | FEEDER | S67/11/KR38/I_S |  |  |  | CDC | 303 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸38線 | 歸38線 |  | 歸38線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸38線A3 | 11KV歸38線 T相AMP | FEEDER | S67/11/KR38/I_T |  |  |  | CDC | 304 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 歸38線 | 歸38線 |  | 歸38線A0 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.歸38線A0 | 11KV歸38線 N相AMP | FEEDER | S67/11/KR38/I_N |  |  |  | CDC | 305 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 0 |  | 11S11BUS | 11S1 |  | V | [17 empty] | 2-CE | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | S67/11/1BUS/V_S |  |  |  | CDC | 306 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11S12BUS | 11S1 |  | V | [17 empty] | 2-D0 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS | S67/11/2BUS/V_S |  |  |  | CDC | 307 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11T11BUS | 11T1 |  | V | [17 empty] | 2-CF | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | S67/11/1BUS/V_T |  |  |  | CDC | 308 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11T12BUS | 11T1 |  | V | [17 empty] | 2-D1 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS | S67/11/2BUS/V_T |  |  |  | CDC | 309 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11S13BUS | 11S1 |  | V | [17 empty] | 2-D2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | S67/11/3BUS/V_S |  |  |  | CDC | 310 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11S16BUS | 11S1 |  | V | [17 empty] | 2-D6 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11S1#6BUS_KV | 11S1 #6BUS KV | BUS | S67/11/6BUS/V_S |  |  |  | CDC | 311 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11T13BUS | 11T1 |  | V | [17 empty] | 2-D3 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | S67/11/3BUS/V_T |  |  |  | CDC | 312 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11T16BUS | 11T1 |  | V | [17 empty] | 2-D7 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11T1#6BUS_KV | 11T1 #6BUS KV | BUS | S67/11/6BUS/V_T |  |  |  | CDC | 313 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11S14BUS | 11S1 |  | V | [17 empty] | 2-D4 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11S1#4BUS_KV | 11S1 #4BUS KV | BUS | S67/11/4BUS/V_S |  |  |  | CDC | 314 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | 11T14BUS | 11T1 |  | V | [17 empty] | 2-D5 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.11T1#4BUS_KV | 11T1 #4BUS KV | BUS | S67/11/4BUS/V_T |  |  |  | CDC | 315 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | TAR17BUS | TAR1 |  | V | [17 empty] | 2-E4 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.TAR1#7BUS_KV | TAR1 #7BUS KV | BUS | S67/11/7BUS/V_R |  |  |  | CDC | 316 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | TAS17BUS | TAS1 |  | V | [17 empty] | 2-E5 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.TAS1#7BUS_KV | TAS1 #7BUS KV | BUS | S67/11/7BUS/V_S |  |  |  | CDC | 317 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 0 |  | TAT17BUS | TAT1 |  | V | [17 empty] | 2-E6 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.TAT1#7BUS_KV | TAT1 #7BUS KV | BUS | S67/11/7BUS/V_T |  |  |  | CDC | 318 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S67 | 歸仁SS | 11 | 11kV | 大聚線 | 大聚線 |  | 大聚線KVAR | [17 empty] | 2-E8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.大聚線KVAR | 11KV大聚線 KVAR | FEEDER | S67/11/TA/KVAR |  |  |  | CDC | 319 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 大聚線 | 大聚線 |  | 大聚線A1 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.大聚線A1 | 11KV大聚線 R相AMP | FEEDER | S67/11/TA/I_R |  |  |  | CDC | 320 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 大聚線 | 大聚線 |  | 大聚線A2 | [17 empty] | 2-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.大聚線A2 | 11KV大聚線 S相AMP | FEEDER | S67/11/TA/I_S |  |  |  | CDC | 321 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 大聚線 | 大聚線 |  | 大聚線A3 | [17 empty] | 2-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.大聚線A3 | 11KV大聚線 T相AMP | FEEDER | S67/11/TA/I_T |  |  |  | CDC | 322 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 11 | 11kV | 大聚線 | 大聚線 |  | 大聚線A0 | [17 empty] | 2-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 歸仁SS.大聚線A0 | 11KV大聚線 N相AMP | FEEDER | S67/11/TA/I_N |  |  |  | CDC | 323 | GENERICAIPoint | SS409_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.630_PHA | 歸仁大亞線(630) 相間RY | LINE69 | S67/69/630/PHA |  |  |  | CDC | 324 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.630_GDA | 歸仁大亞線(630) 接地RY | LINE69 | S67/69/630/GDA |  |  |  | CDC | 325 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | 85A | [17 empty] | 1-11-01 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.630_85A | 歸仁大亞線(630) 85RY | LINE69 |  |  |  |  | CDC | 326 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | 74A | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.630_74A | 歸仁大亞線(630) 74RY | LINE69 |  |  |  |  | CDC | 327 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | 85UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.630_85UL | 歸仁大亞線(630) 85RY U/L | LINE69 | S67/69/630/79UL |  |  |  | CDC | 328 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | CB | [17 empty] | 1-11-00 |  | 1-03 | [5 empty] | 69KV_S | [8 empty] | 歸仁SS.630_CB | 630(歸仁大亞線) CB | LINE69 | S67/69/630/CB |  |  |  | CDC | 329 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | ABS1 | 631 | [16 empty] | 1-35-08 | 1-35-09 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.631_ABS | 631(歸仁大亞線) ABS | LINE69 | S67/69/630/ABS1 |  |  |  | CDC | 330 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | ABS2 | 632 | [16 empty] | 1-35-10 | 1-35-11 | 1-19 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.632_ABS | 632(歸仁大亞線) ABS | LINE69 | S67/69/630/ABS2 |  |  |  | CDC | 331 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | E2 | 632E | [16 empty] | 1-35-12 | 1-35-13 | 1-1A | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.632E_ES | 632E(歸仁大亞線) ES | LINE69 | S67/69/630/ES2 |  |  |  | CDC | 332 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PHA | [17 empty] | 1-11-06 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.660_PHA | 歸仁保安線(660) 相間RY | LINE69 | S67/69/660/PHA |  |  |  | CDC | 333 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | GDA | [17 empty] | 1-11-07 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.660_GDA | 歸仁保安線(660) 接地RY | LINE69 | S67/69/660/GDA |  |  |  | CDC | 334 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | CB | [17 empty] | 1-11-04 |  | 1-04 | [5 empty] | 69KV_S | [8 empty] | 歸仁SS.660_CB | 660(歸仁保安線) CB | LINE69 | S67/69/660/CB |  |  |  | CDC | 335 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | ABS1 | 661 | [16 empty] | 1-35-14 | 1-35-15 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.661_ABS | 661(歸仁保安線) ABS | LINE69 | S67/69/660/ABS1 |  |  |  | CDC | 336 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | ABS2 | 662 | [16 empty] | 2-36-00 | 2-36-01 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.662_ABS | 662(歸仁保安線) ABS | LINE69 | S67/69/660/ABS2 |  |  |  | CDC | 337 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | E2 | 662E | [16 empty] | 2-36-02 | 2-36-03 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.662E_ES | 662E(歸仁保安線) ES | LINE69 | S67/69/660/ES2 |  |  |  | CDC | 338 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.670_PHA | 新市歸仁線(670) 相間RY | LINE69 | S67/69/670/PHA |  |  |  | CDC | 339 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.670_GDA | 新市歸仁線(670) 接地RY | LINE69 | S67/69/670/GDA |  |  |  | CDC | 340 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 山上臨時線(670) |  | 74A | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.670_74A | 山上臨時線(670) 74RY | LINE69 |  |  |  |  | CDC | 341 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | CB | [17 empty] | 1-10-00 |  | 1-01 | [5 empty] | 69KV_S | [8 empty] | 歸仁SS.670_CB | 670(新市歸仁線) CB | LINE69 | S67/69/670/CB |  |  |  | CDC | 342 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | ABS1 | 671 | [16 empty] | 1-34-12 | 1-34-13 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.671_ABS | 671(新市歸仁線) ABS | LINE69 | S67/69/670/ABS1 |  |  |  | CDC | 343 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | ABS2 | 672 | [16 empty] | 1-34-14 | 1-34-15 | 1-13 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.672_ABS | 672(新市歸仁線) ABS | LINE69 | S67/69/670/ABS2 |  |  |  | CDC | 344 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | E2 | 672E | [16 empty] | 1-35-00 | 1-35-01 | 1-14 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.672E_ES | 672E(新市歸仁線) ES | LINE69 | S67/69/670/ES2 |  |  |  | CDC | 345 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | PHA | [17 empty] | 1-10-06 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.680_PHA | 山上歸仁線(680) 相間RY | LINE69 | S67/69/680/PHA |  |  |  | CDC | 346 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | GDA | [17 empty] | 1-10-07 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.680_GDA | 山上歸仁線(680) 接地RY | LINE69 | S67/69/680/GDA |  |  |  | CDC | 347 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | 74A | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.680_74A | 山上歸仁線(680) 74RY | LINE69 |  |  |  |  | CDC | 348 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | CB | [17 empty] | 1-10-04 |  | 1-02 | [5 empty] | 69KV_S | [8 empty] | 歸仁SS.680_CB | 680(山上歸仁線) CB | LINE69 | S67/69/680/CB |  |  |  | CDC | 349 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | ABS1 | 681 | [16 empty] | 1-35-02 | 1-35-03 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.681_ABS | 681(山上歸仁線) ABS | LINE69 | S67/69/680/ABS1 |  |  |  | CDC | 350 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | ABS2 | 682 | [16 empty] | 1-35-04 | 1-35-05 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.682_ABS | 682(山上歸仁線) ABS | LINE69 | S67/69/680/ABS2 |  |  |  | CDC | 351 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | E2 | 682E | [16 empty] | 1-35-06 | 1-35-07 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.682E_ES | 682E(山上歸仁線) ES | LINE69 | S67/69/680/ES2 |  |  |  | CDC | 352 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | PHA | [17 empty] | 1-15-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_PHA | 11KV歸仁線(KR21) 相間RY | FEEDER | S67/11/KR21/PHA |  |  |  | CDC | 353 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) |  | GDA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_GDA | 11KV歸仁線(KR21) 接地RY | FEEDER | S67/11/KR21/GDA |  |  |  | CDC | 354 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_79UL | 11KV歸仁線(KR21) 79RY U/L | FEEDER | S67/11/KR21/79UL |  |  |  | CDC | 355 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR21 | 歸仁線(KR21) LCO分流器 |  | ADJ | [17 empty] | 2-34-00 |  | 2-18 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_ADJ | 11KV歸仁線(KR21) LCO分流器 U/L | FEEDER | S67/11/KR21/ADJ |  |  |  | CDC | 356 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR21 | KR21(11KV歸仁線) |  | CB | [17 empty] | 1-14-00 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_CB | KR21(11KV歸仁線) CB | FEEDER | S67/11/KR21/CB |  |  |  | CDC | 357 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_PHA | 11KV新田線(KR22) 相間RY | FEEDER | S67/11/KR22/PHA |  |  |  | CDC | 358 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_GDA | 11KV新田線(KR22) 接地RY | FEEDER | S67/11/KR22/GDA |  |  |  | CDC | 359 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_79UL | 11KV新田線(KR22) 79RY U/L | FEEDER | S67/11/KR22/79UL |  |  |  | CDC | 360 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR22 | 新田線(KR22) LCO分流器 |  | ADJ | [17 empty] | 2-34-01 |  | 2-19 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_ADJ | 11KV新田線(KR22) LCO分流器 U/L | FEEDER | S67/11/KR22/ADJ |  |  |  | CDC | 361 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR22 | KR22(11KV新田線) |  | CB | [17 empty] | 1-14-01 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_CB | KR22(11KV新田線) CB | FEEDER | S67/11/KR22/CB |  |  |  | CDC | 362 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_PHA | 11KV媽廟線(KR23) 相間RY | FEEDER | S67/11/KR23/PHA |  |  |  | CDC | 363 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_GDA | 11KV媽廟線(KR23) 接地RY | FEEDER | S67/11/KR23/GDA |  |  |  | CDC | 364 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_79UL | 11KV媽廟線(KR23) 79RY U/L | FEEDER | S67/11/KR23/79UL |  |  |  | CDC | 365 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR23 | 媽廟線(KR23) LCO分流器 |  | ADJ | [17 empty] | 2-34-02 |  | 2-1A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_ADJ | 11KV媽廟線(KR23) LCO分流器 U/L | FEEDER | S67/11/KR23/ADJ |  |  |  | CDC | 366 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR23 | KR23(11KV媽廟線) |  | CB | [17 empty] | 1-14-02 |  | 1-36 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_CB | KR23(11KV媽廟線) CB | FEEDER | S67/11/KR23/CB |  |  |  | CDC | 367 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | PHA | [17 empty] | 1-15-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_PHA | 11KV南保線(KR24) 相間RY | FEEDER | S67/11/KR24/PHA |  |  |  | CDC | 368 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) |  | GDA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_GDA | 11KV南保線(KR24) 接地RY | FEEDER | S67/11/KR24/GDA |  |  |  | CDC | 369 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_79UL | 11KV南保線(KR24) 79RY U/L | FEEDER | S67/11/KR24/79UL |  |  |  | CDC | 370 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR24 | 南保線(KR24) LCO分流器 |  | ADJ | [17 empty] | 2-34-03 |  | 2-1B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_ADJ | 11KV南保線(KR24) LCO分流器 U/L | FEEDER | S67/11/KR24/ADJ |  |  |  | CDC | 371 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR24 | KR24(11KV南保線) |  | CB | [17 empty] | 1-14-03 |  | 1-37 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_CB | KR24(11KV南保線) CB | FEEDER | S67/11/KR24/CB |  |  |  | CDC | 372 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_PHA | 11KV貝汝線(KR25) 相間RY | FEEDER | S67/11/KR25/PHA |  |  |  | CDC | 373 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_GDA | 11KV貝汝線(KR25) 接地RY | FEEDER | S67/11/KR25/GDA |  |  |  | CDC | 374 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_79UL | 11KV貝汝線(KR25) 79RY U/L | FEEDER | S67/11/KR25/79UL |  |  |  | CDC | 375 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR25 | 貝汝線(KR25) LCO分流器 |  | ADJ | [17 empty] | 2-34-04 |  | 2-1C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_ADJ | 11KV貝汝線(KR25) LCO分流器 U/L | FEEDER | S67/11/KR25/ADJ |  |  |  | CDC | 376 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR25 | KR25(11KV貝汝線) |  | CB | [17 empty] | 1-14-04 |  | 1-38 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_CB | KR25(11KV貝汝線) CB | FEEDER | S67/11/KR25/CB |  |  |  | CDC | 377 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_PHA | 11KV東盈線(KR26) 相間RY | FEEDER | S67/11/KR26/PHA |  |  |  | CDC | 378 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_GDA | 11KV東盈線(KR26) 接地RY | FEEDER | S67/11/KR26/GDA |  |  |  | CDC | 379 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) 79RY |  | 79UL | [17 empty] | 2-30-07 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_79UL | 11KV東盈線(KR26) 79RY U/L | FEEDER | S67/11/KR26/79UL |  |  |  | CDC | 380 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR26 | 東盈線(KR26) LCO分流器 |  | ADJ | [17 empty] | 2-34-05 |  | 2-1D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_ADJ | 11KV東盈線(KR26) LCO分流器 U/L | FEEDER | S67/11/KR26/ADJ |  |  |  | CDC | 381 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR26 | KR26(11KV東盈線) |  | CB | [17 empty] | 1-16-06 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_CB | KR26(11KV東盈線) CB | FEEDER | S67/11/KR26/CB |  |  |  | CDC | 382 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | PHA | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_PHA | 11KV豐中線(KR27) 相間RY | FEEDER | S67/11/KR27/PHA |  |  |  | CDC | 383 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) |  | GDA | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_GDA | 11KV豐中線(KR27) 接地RY | FEEDER | S67/11/KR27/GDA |  |  |  | CDC | 384 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_79UL | 11KV豐中線(KR27) 79RY U/L | FEEDER | S67/11/KR27/79UL |  |  |  | CDC | 385 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR27 | 豐中線(KR27) LCO分流器 |  | ADJ | [17 empty] | 2-34-06 |  | 2-1E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_ADJ | 11KV豐中線(KR27) LCO分流器 U/L | FEEDER | S67/11/KR27/ADJ |  |  |  | CDC | 386 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR27 | KR27(11KV豐中線) |  | CB | [17 empty] | 1-16-07 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_CB | KR27(11KV豐中線) CB | FEEDER | S67/11/KR27/CB |  |  |  | CDC | 387 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | PHA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_PHA | 11KV崙頂線(KR28) 相間RY | FEEDER | S67/11/KR28/PHA |  |  |  | CDC | 388 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) |  | GDA | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_GDA | 11KV崙頂線(KR28) 接地RY | FEEDER | S67/11/KR28/GDA |  |  |  | CDC | 389 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) 79RY |  | 79UL | [17 empty] | 2-30-09 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_79UL | 11KV崙頂線(KR28) 79RY U/L | FEEDER | S67/11/KR28/79UL |  |  |  | CDC | 390 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR28 | 崙頂線(KR28) LCO分流器 |  | ADJ | [17 empty] | 2-34-07 |  | 2-1F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_ADJ | 11KV崙頂線(KR28) LCO分流器 U/L | FEEDER | S67/11/KR28/ADJ |  |  |  | CDC | 391 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR28 | KR28(11KV崙頂線) |  | CB | [17 empty] | 1-17-00 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_CB | KR28(11KV崙頂線) CB | FEEDER | S67/11/KR28/CB |  |  |  | CDC | 392 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_PHA | 11KV看西線(KR29) 相間RY | FEEDER | S67/11/KR29/PHA |  |  |  | CDC | 393 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_GDA | 11KV看西線(KR29) 接地RY | FEEDER | S67/11/KR29/GDA |  |  |  | CDC | 394 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_79UL | 11KV看西線(KR29) 79RY U/L | FEEDER | S67/11/KR29/79UL |  |  |  | CDC | 395 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR29 | 看西線(KR29) LCO分流器 |  | ADJ | [17 empty] | 2-34-08 |  | 2-20 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_ADJ | 11KV看西線(KR29) LCO分流器 U/L | FEEDER | S67/11/KR29/ADJ |  |  |  | CDC | 396 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR29 | KR29(11KV看西線) |  | CB | [17 empty] | 1-17-01 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_CB | KR29(11KV看西線) CB | FEEDER | S67/11/KR29/CB |  |  |  | CDC | 397 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | PHA | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_PHA | 11KV關廟線(KR30) 相間RY | FEEDER | S67/11/KR30/PHA |  |  |  | CDC | 398 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) |  | GDA | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_GDA | 11KV關廟線(KR30) 接地RY | FEEDER | S67/11/KR30/GDA |  |  |  | CDC | 399 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_79UL | 11KV關廟線(KR30) 79RY U/L | FEEDER | S67/11/KR30/79UL |  |  |  | CDC | 400 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR30 | 關廟線(KR30) LCO分流器 |  | ADJ | [17 empty] | 2-34-09 |  | 2-21 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_ADJ | 11KV關廟線(KR30) LCO分流器 U/L | FEEDER | S67/11/KR30/ADJ |  |  |  | CDC | 401 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR30 | KR30(11KV關廟線) |  | CB | [17 empty] | 1-17-02 |  | 1-4D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_CB | KR30(11KV關廟線) CB | FEEDER | S67/11/KR30/CB |  |  |  | CDC | 402 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | PHA | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_PHA | 11KV萬芳線(KR31) 相間RY | FEEDER | S67/11/KR31/PHA |  |  |  | CDC | 403 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) |  | GDA | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_GDA | 11KV萬芳線(KR31) 接地RY | FEEDER | S67/11/KR31/GDA |  |  |  | CDC | 404 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 1-65 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_79UL | 11KV萬芳線(KR31) 79RY U/L | FEEDER | S67/11/KR31/79UL |  |  |  | CDC | 405 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR31 | 萬芳線(KR31) LCO分流器 |  | ADJ | [17 empty] | 2-34-10 |  | 2-22 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_ADJ | 11KV萬芳線(KR31) LCO分流器 U/L | FEEDER | S67/11/KR31/ADJ |  |  |  | CDC | 406 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR31 | KR31(11KV萬芳線) |  | CB | [17 empty] | 1-19-04 |  | 1-5D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_CB | KR31(11KV萬芳線) CB | FEEDER | S67/11/KR31/CB |  |  |  | CDC | 407 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_PHA | 11KV八甲線(KR32) 相間RY | FEEDER | S67/11/KR32/PHA |  |  |  | CDC | 408 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_GDA | 11KV八甲線(KR32) 接地RY | FEEDER | S67/11/KR32/GDA |  |  |  | CDC | 409 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 1-66 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_79UL | 11KV八甲線(KR32) 79RY U/L | FEEDER | S67/11/KR32/79UL |  |  |  | CDC | 410 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR32 | 八甲線(KR32) LCO分流器 |  | ADJ | [17 empty] | 2-34-11 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_ADJ | 11KV八甲線(KR32) LCO分流器 U/L | FEEDER | S67/11/KR32/ADJ |  |  |  | CDC | 411 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR32 | KR32(11KV八甲線) |  | CB | [17 empty] | 1-19-05 |  | 1-5E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_CB | KR32(11KV八甲線) CB | FEEDER | S67/11/KR32/CB |  |  |  | CDC | 412 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | PHA | [17 empty] | 1-1B-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_PHA | 11KV歸33線(KR33) 相間RY | FEEDER | S67/11/KR33/PHA |  |  |  | CDC | 413 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) |  | GDA | [17 empty] | 1-1B-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_GDA | 11KV歸33線(KR33) 接地RY | FEEDER | S67/11/KR33/GDA |  |  |  | CDC | 414 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 1-67 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_79UL | 11KV歸33線(KR33) 79RY U/L | FEEDER | S67/11/KR33/79UL |  |  |  | CDC | 415 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR33 | 歸33線(KR33) LCO分流器 |  | ADJ | [17 empty] | 2-34-12 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_ADJ | 11KV歸33線(KR33) LCO分流器 U/L | FEEDER | S67/11/KR33/ADJ |  |  |  | CDC | 416 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR33 | KR33(11KV歸33線) |  | CB | [17 empty] | 1-19-06 |  | 1-5F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_CB | KR33(11KV歸33線) CB | FEEDER | S67/11/KR33/CB |  |  |  | CDC | 417 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | PHA | [17 empty] | 1-1B-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_PHA | 11KV深坑線(KR34) 相間RY | FEEDER | S67/11/KR34/PHA |  |  |  | CDC | 418 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) |  | GDA | [17 empty] | 1-1B-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_GDA | 11KV深坑線(KR34) 接地RY | FEEDER | S67/11/KR34/GDA |  |  |  | CDC | 419 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 1-68 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_79UL | 11KV深坑線(KR34) 79RY U/L | FEEDER | S67/11/KR34/79UL |  |  |  | CDC | 420 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR34 | 深坑線(KR34) LCO分流器 |  | ADJ | [17 empty] | 2-34-13 |  | 2-25 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_ADJ | 11KV深坑線(KR34) LCO分流器 U/L | FEEDER | S67/11/KR34/ADJ |  |  |  | CDC | 421 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR34 | KR34(11KV深坑線) |  | CB | [17 empty] | 1-19-07 |  | 1-60 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_CB | KR34(11KV深坑線) CB | FEEDER | S67/11/KR34/CB |  |  |  | CDC | 422 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | PHA | [17 empty] | 1-1B-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_PHA | 11KV南潭線(KR35) 相間RY | FEEDER | S67/11/KR35/PHA |  |  |  | CDC | 423 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) |  | GDA | [17 empty] | 1-1B-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_GDA | 11KV南潭線(KR35) 接地RY | FEEDER | S67/11/KR35/GDA |  |  |  | CDC | 424 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) 79RY |  | 79UL | [17 empty] | 2-31-11 |  | 1-69 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_79UL | 11KV南潭線(KR35) 79RY U/L | FEEDER | S67/11/KR35/79UL |  |  |  | CDC | 425 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR35 | 南潭線(KR35) LCO分流器 |  | ADJ | [17 empty] | 2-34-14 |  | 2-26 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_ADJ | 11KV南潭線(KR35) LCO分流器 U/L | FEEDER | S67/11/KR35/ADJ |  |  |  | CDC | 426 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR35 | KR35(11KV南潭線) |  | CB | [17 empty] | 1-1A-00 |  | 1-61 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_CB | KR35(11KV南潭線) CB | FEEDER | S67/11/KR35/CB |  |  |  | CDC | 427 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | PHA | [17 empty] | 1-1D-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_PHA | 11KV六合線(KR36) 相間RY | FEEDER | S67/11/KR36/PHA |  |  |  | CDC | 428 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) |  | GDA | [17 empty] | 1-1D-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_GDA | 11KV六合線(KR36) 接地RY | FEEDER | S67/11/KR36/GDA |  |  |  | CDC | 429 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) 79RY |  | 79UL | [17 empty] | 2-32-07 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_79UL | 11KV六合線(KR36) 79RY U/L | FEEDER | S67/11/KR36/79UL |  |  |  | CDC | 430 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR36 | 六合線(KR36) LCO分流器 |  | ADJ | [17 empty] | 2-34-15 |  | 2-27 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_ADJ | 11KV六合線(KR36) LCO分流器 U/L | FEEDER | S67/11/KR36/ADJ |  |  |  | CDC | 431 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR36 | KR36(11KV六合線) |  | CB | [17 empty] | 1-1C-03 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_CB | KR36(11KV六合線) CB | FEEDER | S67/11/KR36/CB |  |  |  | CDC | 432 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | PHA | [17 empty] | 1-1D-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_PHA | 11KV松根線(KR37) 相間RY | FEEDER | S67/11/KR37/PHA |  |  |  | CDC | 433 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) |  | GDA | [17 empty] | 1-1D-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_GDA | 11KV松根線(KR37) 接地RY | FEEDER | S67/11/KR37/GDA |  |  |  | CDC | 434 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) 79RY |  | 79UL | [17 empty] | 2-32-08 |  | 1-7A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_79UL | 11KV松根線(KR37) 79RY U/L | FEEDER | S67/11/KR37/79UL |  |  |  | CDC | 435 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR37 | 松根線(KR37) LCO分流器 |  | ADJ | [17 empty] | 2-35-00 |  | 2-28 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_ADJ | 11KV松根線(KR37) LCO分流器 U/L | FEEDER | S67/11/KR37/ADJ |  |  |  | CDC | 436 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR37 | KR37(11KV松根線) |  | CB | [17 empty] | 1-1C-04 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_CB | KR37(11KV松根線) CB | FEEDER | S67/11/KR37/CB |  |  |  | CDC | 437 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | PHA | [17 empty] | 1-1E-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_PHA | 11KV歸38線(KR38) 相間RY | FEEDER | S67/11/KR38/PHA |  |  |  | CDC | 438 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) |  | GDA | [17 empty] | 1-1E-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_GDA | 11KV歸38線(KR38) 接地RY | FEEDER | S67/11/KR38/GDA |  |  |  | CDC | 439 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) 79RY |  | 79UL | [17 empty] | 2-32-09 |  | 1-7B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_79UL | 11KV歸38線(KR38) 79RY U/L | FEEDER | S67/11/KR38/79UL |  |  |  | CDC | 440 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR38 | 歸38線(KR38) LCO分流器 |  | ADJ | [17 empty] | 2-35-01 |  | 2-29 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_ADJ | 11KV歸38線(KR38) LCO分流器 U/L | FEEDER | S67/11/KR38/ADJ |  |  |  | CDC | 441 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR38 | KR38(11KV歸38線) |  | CB | [17 empty] | 1-1C-05 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_CB | KR38(11KV歸38線) CB | FEEDER | S67/11/KR38/CB |  |  |  | CDC | 442 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | PHA | [17 empty] | 1-1E-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_PHA | 11KV沙崙線(KR39) 相間RY | FEEDER | S67/11/KR39/PHA |  |  |  | CDC | 443 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) |  | GDA | [17 empty] | 1-1E-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_GDA | 11KV沙崙線(KR39) 接地RY | FEEDER | S67/11/KR39/GDA |  |  |  | CDC | 444 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) 79RY |  | 79UL | [17 empty] | 2-32-10 |  | 1-7C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_79UL | 11KV沙崙線(KR39) 79RY U/L | FEEDER | S67/11/KR39/79UL |  |  |  | CDC | 445 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR39 | 沙崙線(KR39) LCO分流器 |  | ADJ | [17 empty] | 2-35-02 |  | 2-2A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_ADJ | 11KV沙崙線(KR39) LCO分流器 U/L | FEEDER | S67/11/KR39/ADJ |  |  |  | CDC | 446 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR39 | KR39(11KV沙崙線) |  | CB | [17 empty] | 1-1C-06 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_CB | KR39(11KV沙崙線) CB | FEEDER | S67/11/KR39/CB |  |  |  | CDC | 447 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | PHA | [17 empty] | 1-1E-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_PHA | 11KV漢平線(KR40) 相間RY | FEEDER | S67/11/KR40/PHA |  |  |  | CDC | 448 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) |  | GDA | [17 empty] | 1-1E-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_GDA | 11KV漢平線(KR40) 接地RY | FEEDER | S67/11/KR40/GDA |  |  |  | CDC | 449 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) 79RY |  | 79UL | [17 empty] | 2-32-11 |  | 1-7D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_79UL | 11KV漢平線(KR40) 79RY U/L | FEEDER | S67/11/KR40/79UL |  |  |  | CDC | 450 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR40 | 漢平線(KR40) LCO分流器 |  | ADJ | [17 empty] | 2-35-03 |  | 2-2B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_ADJ | 11KV漢平線(KR40) LCO分流器 U/L | FEEDER | S67/11/KR40/ADJ |  |  |  | CDC | 451 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR40 | KR40(11KV漢平線) |  | CB | [17 empty] | 1-1C-07 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_CB | KR40(11KV漢平線) CB | FEEDER | S67/11/KR40/CB |  |  |  | CDC | 452 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | TIE1 | #1-#2 |  | CB | [17 empty] | 1-14-05 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE1_CB | 11KV #1-#2 TIE CB | TIE | S67/11/TIE1/CB |  |  |  | CDC | 453 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE1 | #1-#2 |  | 51A | [17 empty] | 1-16-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE1_51A | 11KV #1-#2 TIE 51RY | TIE | S67/11/TIE1/51A |  |  |  | CDC | 454 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE1 | #1-#2 |  | 51NA | [17 empty] | 1-16-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE1_51NA | 11KV #1-#2 TIE 51N RY | TIE | S67/11/TIE1/51NA |  |  |  | CDC | 455 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE2 | #3-#2 |  | CB | [17 empty] | 1-17-03 |  | 1-47 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE2_CB | 11KV #3-#2 TIE CB | TIE | S67/11/TIE2/CB |  |  |  | CDC | 456 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE2 | #3-#2 |  | 51A | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE2_51A | 11KV #3-#2 TIE 51RY | TIE | S67/11/TIE2/51A |  |  |  | CDC | 457 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE2 | #3-#2 |  | 51NA | [17 empty] | 1-19-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE2_51NA | 11KV #3-#2 TIE 51N RY | TIE | S67/11/TIE2/51NA |  |  |  | CDC | 458 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE3 | #6-#3 |  | CB | [17 empty] | 1-1A-01 |  | 1-5B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE3_CB | 11KV #6-#3 TIE CB | TIE | S67/11/TIE3/CB |  |  |  | CDC | 459 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE3 | #6-#3 |  | 51A | [17 empty] | 1-1C-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE3_51A | 11KV #6-#3 TIE 51RY | TIE | S67/11/TIE3/51A |  |  |  | CDC | 460 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE3 | #6-#3 |  | 51NA | [17 empty] | 1-1C-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE3_51NA | 11KV #6-#3 TIE 51N RY | TIE | S67/11/TIE3/51NA |  |  |  | CDC | 461 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE4 | #4-#1 |  | CB | [17 empty] | 1-1D-00 |  | 1-6F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE4_CB | 11KV #4-#1 TIE CB | TIE | S67/11/TIE4/CB |  |  |  | CDC | 462 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 11 | 11kV | TIE4 | #4-#1 |  | 51A | [17 empty] | 1-1E-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE4_51A | 11KV #4-#1 TIE 51RY | TIE | S67/11/TIE4/51A |  |  |  | CDC | 463 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | TIE4 | #4-#1 |  | 51NA | [17 empty] | 1-1E-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE4_51NA | 11KV #4-#1 TIE 51N RY | TIE | S67/11/TIE4/51NA |  |  |  | CDC | 464 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.750_CB | 750(#1MTR) CB | DTR | S67/69/750/CB |  |  |  | CDC | 465 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.1M_CB | 1M(#1MTR) CB | DTR | S67/11/M1/CB |  |  |  | CDC | 466 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_51A | #1MTR 51RY | DTR | S67/69/750/51A |  |  |  | CDC | 467 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_51NA | #1MTR 51N RY | DTR | S67/69/750/51NA |  |  |  | CDC | 468 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S67//1MTR/51ZA |  |  |  | CDC | 469 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_87A | #1MTR 87RY | DTR | S67//1MTR/87A |  |  |  | CDC | 470 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #750 |  | 81AS | [17 empty] | 1-14-06 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_81A/S | #750 81RY A/S | DTR | S67/69/750/81AS |  |  |  | CDC | 471 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S67 | 歸仁SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S67/11/M1/51A |  |  |  | CDC | 472 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_TRA | #1MTR 重故障 | DTR | S67//1MTR/TRA |  |  |  | CDC | 473 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S67//1MTR/TRF |  |  |  | CDC | 474 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S67//1MTR/SupLocal |  |  |  | CDC | 475 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S67//1MTR/Tap Chan |  |  |  | CDC | 476 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-34-00 | 1-34-01 | 1-28 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.751_ABS | 751(#1MTR) ABS | DTR | S67/69/750/ABS1 |  |  |  | CDC | 477 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S67//1MTR/OLTC_DLY |  |  |  | CDC | 478 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S67//1MTR/AC_Fault |  |  |  | CDC | 479 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.760_CB | 760(#2MTR) CB | DTR | S67/69/760/CB |  |  |  | CDC | 480 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.2M_CB | 2M(#2MTR) CB | DTR | S67/11/M2/CB |  |  |  | CDC | 481 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_51A | #2MTR 51RY | DTR | S67/69/760/51A |  |  |  | CDC | 482 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_51NA | #2MTR 51N RY | DTR | S67/69/760/51NA |  |  |  | CDC | 483 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S67//2MTR/51ZA |  |  |  | CDC | 484 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_87A | #2MTR 87RY | DTR | S67//2MTR/87A |  |  |  | CDC | 485 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #760.#780 |  | 81AS | [17 empty] | 1-17-04 |  | 1-56 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_81A/S | #760.#780 81RY A/S | DTR | S67/69/760/81AS |  |  |  | CDC | 486 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S67 | 歸仁SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S67/11/M2/51A |  |  |  | CDC | 487 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 2-30-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_TRA | #2MTR 重故障 | DTR | S67//2MTR/TRA |  |  |  | CDC | 488 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 2-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S67//2MTR/TRF |  |  |  | CDC | 489 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 2-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S67//2MTR/SupLocal |  |  |  | CDC | 490 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 2-30-05 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S67//2MTR/Tap Chan |  |  |  | CDC | 491 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-34-02 | 1-34-03 | 1-29 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.761_ABS | 761(#2MTR) ABS | DTR | S67/69/760/ABS1 |  |  |  | CDC | 492 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 2-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S67//2MTR/OLTC_DLY |  |  |  | CDC | 493 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 2-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S67//2MTR/AC_Fault |  |  |  | CDC | 494 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.770_CB | 770(#3MTR) CB | DTR | S67/69/770/CB |  |  |  | CDC | 495 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.3M_CB | 3M(#3MTR) CB | DTR | S67/11/M3/CB |  |  |  | CDC | 496 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_51A | #3MTR 51RY | DTR | S67/69/770/51A |  |  |  | CDC | 497 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_51NA | #3MTR 51N RY | DTR | S67/69/770/51NA |  |  |  | CDC | 498 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S67//3MTR/51ZA |  |  |  | CDC | 499 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_87A | #3MTR 87RY | DTR | S67//3MTR/87A |  |  |  | CDC | 500 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #770 |  | 81AS | [17 empty] | 1-1A-02 |  | 1-6A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_81A/S | #770 81RY A/S | DTR | S67/69/770/81AS |  |  |  | CDC | 501 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S67 | 歸仁SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S67/11/M3/51A |  |  |  | CDC | 502 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 2-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_TRA | #3MTR 重故障 | DTR | S67//3MTR/TRA |  |  |  | CDC | 503 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 2-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S67//3MTR/TRF |  |  |  | CDC | 504 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 2-31-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S67//3MTR/SupLocal |  |  |  | CDC | 505 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 2-31-05 |  | 1-63 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S67//3MTR/Tap Chan |  |  |  | CDC | 506 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-34-04 | 1-34-05 | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.771_ABS | 771(#3MTR) ABS | DTR | S67/69/770/ABS1 |  |  |  | CDC | 507 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 2-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S67//3MTR/OLTC_DLY |  |  |  | CDC | 508 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 2-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S67//3MTR/AC_Fault |  |  |  | CDC | 509 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 1-04-02 |  | 1-6C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.780_CB | 780(#4MTR) CB | DTR | S67/69/780/CB |  |  |  | CDC | 510 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 4M | #4MTR |  | CB | [17 empty] | 1-04-03 |  | 1-6D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.4M_CB | 4M(#4MTR) CB | DTR | S67/11/M4/CB |  |  |  | CDC | 511 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 51A | [17 empty] | 1-04-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_51A | #4MTR 51RY | DTR | S67/69/780/51A |  |  |  | CDC | 512 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 51NA | [17 empty] | 1-04-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_51NA | #4MTR 51N RY | DTR | S67/69/780/51NA |  |  |  | CDC | 513 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 1-05-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_51ZA | #4MTR 51Z RY | DTR | S67//4MTR/51ZA |  |  |  | CDC | 514 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-05-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_87A | #4MTR 87RY | DTR | S67//4MTR/87A |  |  |  | CDC | 515 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4M | #4MTR二次側(4M) |  | 51A | [17 empty] | 1-05-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.4M_51A | #4MTR二次側(4M) 51RY | DTR | S67/11/M4/51A |  |  |  | CDC | 516 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 2-32-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_TRA | #4MTR 重故障 | DTR | S67//4MTR/TRA |  |  |  | CDC | 517 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 2-32-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_TRF | #4MTR 輕故障 | DTR | S67//4MTR/TRF |  |  |  | CDC | 518 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 2-32-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_S/L | #4MTR OLTC S/L | DTR | S67//4MTR/SupLocal |  |  |  | CDC | 519 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 2-32-05 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_A/M | #4MTR OLTC A/M | DTR | S67//4MTR/Tap Chan |  |  |  | CDC | 520 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | [16 empty] | 1-34-06 | 1-34-07 | 1-2B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.781_ABS | 781(#4MTR) ABS | DTR | S67/69/780/ABS1 |  |  |  | CDC | 521 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | OLTC_DLY | [17 empty] | 2-32-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR | S67//4MTR/OLTC_DLY |  |  |  | CDC | 522 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR_AC | #4MTR |  | FAULT | [17 empty] | 2-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR | S67//4MTR/AC_Fault |  |  |  | CDC | 523 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | CB | [17 empty] | 1-05-06 |  | 2-00 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.790_CB | 790(#6MTR) CB | DTR | S67/69/790/CB |  |  |  | CDC | 524 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 6M | #6MTR |  | CB | [17 empty] | 1-05-07 |  | 2-01 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.6M_CB | 6M(#6MTR) CB | DTR | S67/11/M6/CB |  |  |  | CDC | 525 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_51A | #6MTR 51RY | DTR | S67/69/790/51A |  |  |  | CDC | 526 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_51NA | #6MTR 51N RY | DTR | S67/69/790/51NA |  |  |  | CDC | 527 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 51ZA | [17 empty] | 1-07-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_51ZA | #6MTR 51Z RY | DTR | S67//6MTR/51ZA |  |  |  | CDC | 528 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 87A | [17 empty] | 1-06-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_87A | #6MTR 87RY | DTR | S67//6MTR/87A |  |  |  | CDC | 529 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #790 |  | 81AS | [17 empty] | 1-1F-06 |  | 2-11 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_81A/S | #790 81RY A/S | DTR | S67/69/790/81AS |  |  |  | CDC | 530 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S67 | 歸仁SS | 0 |  | 6M | #6MTR二次側(6M) |  | 51A | [17 empty] | 1-06-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.6M_51A | #6MTR二次側(6M) 51RY | DTR | S67/11/M6/51A |  |  |  | CDC | 531 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | TRA | [17 empty] | 2-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_TRA | #6MTR 重故障 | DTR | S67//6MTR/TRA |  |  |  | CDC | 532 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | TRF | [17 empty] | 2-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_TRF | #6MTR 輕故障 | DTR | S67//6MTR/TRF |  |  |  | CDC | 533 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | SupLocal | [17 empty] | 2-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_S/L | #6MTR OLTC S/L | DTR | S67//6MTR/SupLocal |  |  |  | CDC | 534 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | A_M | [17 empty] | 2-33-05 |  | 2-0A | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_A/M | #6MTR OLTC A/M | DTR | S67//6MTR/Tap Chan |  |  |  | CDC | 535 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | ABS1 | 791 | [16 empty] | 1-34-08 | 1-34-09 | 1-2C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.791_ABS | 791(#6MTR) ABS | DTR | S67/69/790/ABS1 |  |  |  | CDC | 536 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | OLTC_DLY | [17 empty] | 2-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_OLTC遲滯 | #6MTR OLTC遲滯 | DTR | S67//6MTR/OLTC_DLY |  |  |  | CDC | 537 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR_AC | #6MTR |  | FAULT | [17 empty] | 2-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_AC_FAULT | #6MTR AC電源失效 | DTR | S67//6MTR/AC_Fault |  |  |  | CDC | 538 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-13-07 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_CB | 210(11KV #1SC) CB | SC | S67/11/210/CB |  |  |  | CDC | 539 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S67/11/210/SC_A_M |  |  |  | CDC | 540 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_SCA | 11KV #1SC 51,51N RY | SC | S67/11/210/SCA |  |  |  | CDC | 541 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S67/11/210/UVA |  |  |  | CDC | 542 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-16-05 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_CB | 220(11KV #2SC) CB | SC | S67/11/220/CB |  |  |  | CDC | 543 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-06 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S67/11/220/SC_A_M |  |  |  | CDC | 544 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_SCA | 11KV #2SC 51,51N RY | SC | S67/11/220/SCA |  |  |  | CDC | 545 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S67/11/220/UVA |  |  |  | CDC | 546 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-03 |  | 1-5C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_CB | 230(11KV #3SC) CB | SC | S67/11/230/CB |  |  |  | CDC | 547 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-06 |  | 1-64 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S67/11/230/SC_A_M |  |  |  | CDC | 548 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-1A-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_SCA | 11KV #3SC 51,51N RY | SC | S67/11/230/SCA |  |  |  | CDC | 549 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S67/11/230/UVA |  |  |  | CDC | 550 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1C-02 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_CB | 240(11KV #4SC) CB | SC | S67/11/240/CB |  |  |  | CDC | 551 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-32-06 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_A/M | 11KV #4SC 乏控器 A/M | SC | S67/11/240/SC_A_M |  |  |  | CDC | 552 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1D-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_SCA | 11KV #4SC 51,51N RY | SC | S67/11/240/SCA |  |  |  | CDC | 553 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1D-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | S67/11/240/UVA |  |  |  | CDC | 554 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-1F-00 |  | 2-03 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_CB | 260(11KV #6SC) CB | SC | S67/11/260/CB |  |  |  | CDC | 555 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-33-06 |  | 2-0B | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_A/M | 11KV #6SC 乏控器 A/M | SC | S67/11/260/SC_A_M |  |  |  | CDC | 556 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-1F-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_SCA | 11KV #6SC 51,51N RY | SC | S67/11/260/SCA |  |  |  | CDC | 557 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | S67/11/260/UVA |  |  |  | CDC | 558 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-13-04 |  | 1-08 | [5 empty] | 69KV_S | [8 empty] | 歸仁SS.810_CB | 810(69KV #1SC) CB | SC | S67/69/810/CB |  |  |  | CDC | 559 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-34-10 | 1-34-11 | 1-27 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.811_ABS | 811(69KV #1SC) ABS | SC | S67/69/810/ABS1 |  |  |  | CDC | 560 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-13-05 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.810_SCA | 69KV #1SC 51,51N RY | SC | S67/69/810/SCA |  |  |  | CDC | 561 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-13-06 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.810_OUVA | 69KV #1SC 27,59RY | SC | S67/69/810/UVA |  |  |  | CDC | 562 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S67/69/1BUS/BUS_VUA |  |  |  | CDC | 563 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S67/11/ComPoint/CBA |  |  |  | CDC | 564 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S67/11/ComPoint/CBF |  |  |  | CDC | 565 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S67/69/ComPoint/ABS_89A |  |  |  | CDC | 566 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S67/69/ComPoint/CBA |  |  |  | CDC | 567 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S67/69/ComPoint/CBF |  |  |  | CDC | 568 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S67/0/RTU/RTU_R_L |  |  |  | CDC | 569 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S67 | 歸仁SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TEST_CB | TEST CB | OTHER | S67/0/RTU/Test_CB |  |  |  | CDC | 570 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.火災警報(1) | 火警 | OTHER | S67/0/StaDev/Fire |  |  |  | CDC | 571 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-33-13 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S67/0/StaDev/ACB1 |  |  |  | CDC | 572 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S67 | 歸仁SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-33-14 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S67/0/StaDev/ACB2 |  |  |  | CDC | 573 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S67 | 歸仁SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S67/0/StaDev/STUV |  |  |  | CDC | 574 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.直流充電機故障 | 直流充電機故障 | OTHER | S67/0/StaDev/CHG1 |  |  |  | CDC | 575 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S67/0/StaDev/DCA |  |  |  | CDC | 576 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S67/0/StaDev/DCE |  |  |  | CDC | 577 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S67/0/StaDev/OilLeak |  |  |  | CDC | 578 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | SUBA | [17 empty] | 2-35-13 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S67/0/StaDev/5A5Other |  |  |  | CDC | 579 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | SUBF | [17 empty] | 2-35-14 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S67/0/StaDev/6A5Other |  |  |  | CDC | 580 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 2-35-15 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S67/0/StaDev/7A5Other |  |  |  | CDC | 581 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | CommACF | [17 empty] | 2-35-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S67/0/StaDev/CommACF |  |  |  | CDC | 582 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S67/0/StaDev/Door1 |  |  |  | CDC | 583 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S67 | 歸仁SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S67/0/StaDev/Lights1 |  |  |  | CDC | 584 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S67 | 歸仁SS | 0 |  | 1_MAIN | #1 |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1_MAIN_51NA | #1 MAIN 51NA | OTHER | S67/11/M1/51NA |  |  |  | CDC | 585 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2_MAIN | #2 |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2_MAIN_51NA | #2 MAIN 51NA | OTHER | S67/11/M2/51NA |  |  |  | CDC | 586 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3_MAIN | #3 |  | 51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3_MAIN_51NA | #3 MAIN 51NA | OTHER | S67/11/M3/51NA |  |  |  | CDC | 587 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4_MAIN | #4 |  | 51NA | [17 empty] | 1-05-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4_MAIN_51NA | #4 MAIN 51NA | OTHER | S67/11/M4/51NA |  |  |  | CDC | 588 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6_MAIN | #6 |  | 51NA | [17 empty] | 1-06-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6_MAIN_51NA | #6 MAIN 51NA | OTHER | S67/11/M6/51NA |  |  |  | CDC | 589 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.69KVSC警報 | 69KVSC警報 | OTHER | S67/69/810/60A |  |  |  | CDC | 590 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.RTU_DC故障 | RTU DC故障 | OTHER | S67/0/RTU/DCA |  |  |  | CDC | 591 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.水氣霧故障 | 水氣霧故障 | OTHER | S67/0/StaDev/2A5Other |  |  |  | CDC | 592 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.水氣霧警報 | 水氣霧警報 | OTHER | S67/0/StaDev/3A5Other |  |  |  | CDC | 593 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.門禁小門 | 門禁小門 | OTHER | S67/0/StaDev/Door2 |  |  |  | CDC | 594 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S67/0/StaDev/Lights |  |  |  | CDC | 595 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | 50A | [17 empty] | 1-13-00 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.660_50RY | 保安線(660) 50+2 RY | LINE69 |  |  |  |  | CDC | 596 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | 50UL | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.670_50UL | 山上臨時線(670) 50+2 RY UL | LINE69 |  |  |  |  | CDC | 597 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | 50UL | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.680_50UL | 山上線(680) 50+2 RY UL | LINE69 |  |  |  |  | CDC | 598 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-1D-01 |  | 1-7E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S67/0/StaDev/4A5Other |  |  |  | CDC | 599 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | PHA | [17 empty] | 2-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_PHA | 11KV歸南線(KR41) 相間RY | FEEDER | S67/11/KR41/PHA |  |  |  | CDC | 600 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) |  | GDA | [17 empty] | 2-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_GDA | 11KV歸南線(KR41) 接地RY | FEEDER | S67/11/KR41/GDA |  |  |  | CDC | 601 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) 79RY |  | 79UL | [17 empty] | 2-33-07 |  | 2-0C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_79UL | 11KV歸南線(KR41) 79RY U/L | FEEDER | S67/11/KR41/79UL |  |  |  | CDC | 602 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR41 | 歸南線(KR41) LCO分流器 |  | ADJ | [17 empty] | 2-35-04 |  | 2-2C | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_ADJ | 11KV歸南線(KR41) LCO分流器 U/L | FEEDER | S67/11/KR41/ADJ |  |  |  | CDC | 603 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR41 | KR41(11KV歸南線) |  | CB | [17 empty] | 1-1F-01 |  | 2-04 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_CB | KR41(11KV歸南線) CB | FEEDER | S67/11/KR41/CB |  |  |  | CDC | 604 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | PHA | [17 empty] | 2-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_PHA | 11KV古厝線(KR42) 相間RY | FEEDER | S67/11/KR42/PHA |  |  |  | CDC | 605 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) |  | GDA | [17 empty] | 2-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_GDA | 11KV古厝線(KR42) 接地RY | FEEDER | S67/11/KR42/GDA |  |  |  | CDC | 606 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) 79RY |  | 79UL | [17 empty] | 2-33-08 |  | 2-0D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_79UL | 11KV古厝線(KR42) 79RY U/L | FEEDER | S67/11/KR42/79UL |  |  |  | CDC | 607 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR42 | 古厝線(KR42) LCO分流器 |  | ADJ | [17 empty] | 2-35-05 |  | 2-2D | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_ADJ | 11KV古厝線(KR42) LCO分流器 U/L | FEEDER | S67/11/KR42/ADJ |  |  |  | CDC | 608 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR42 | KR42(11KV古厝線) |  | CB | [17 empty] | 1-1F-02 |  | 2-05 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_CB | KR42(11KV古厝線) CB | FEEDER | S67/11/KR42/CB |  |  |  | CDC | 609 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | PHA | [17 empty] | 2-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_PHA | 11KV龍崎線(KR43) 相間RY | FEEDER | S67/11/KR43/PHA |  |  |  | CDC | 610 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) |  | GDA | [17 empty] | 2-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_GDA | 11KV龍崎線(KR43) 接地RY | FEEDER | S67/11/KR43/GDA |  |  |  | CDC | 611 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) 79RY |  | 79UL | [17 empty] | 2-33-09 |  | 2-0E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_79UL | 11KV龍崎線(KR43) 79RY U/L | FEEDER | S67/11/KR43/79UL |  |  |  | CDC | 612 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR43 | 龍崎線(KR43) LCO分流器 |  | ADJ | [17 empty] | 2-35-06 |  | 2-2E | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_ADJ | 11KV龍崎線(KR43) LCO分流器 U/L | FEEDER | S67/11/KR43/ADJ |  |  |  | CDC | 613 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR43 | KR43(11KV龍崎線) |  | CB | [17 empty] | 1-1F-03 |  | 2-06 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_CB | KR43(11KV龍崎線) CB | FEEDER | S67/11/KR43/CB |  |  |  | CDC | 614 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | PHA | [17 empty] | 2-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_PHA | 11KV關甲線(KR44) 相間RY | FEEDER | S67/11/KR44/PHA |  |  |  | CDC | 615 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) |  | GDA | [17 empty] | 2-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_GDA | 11KV關甲線(KR44) 接地RY | FEEDER | S67/11/KR44/GDA |  |  |  | CDC | 616 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) 79RY |  | 79UL | [17 empty] | 2-33-10 |  | 2-0F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_79UL | 11KV關甲線(KR44) 79RY U/L | FEEDER | S67/11/KR44/79UL |  |  |  | CDC | 617 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR44 | 關甲線(KR44) LCO分流器 |  | ADJ | [17 empty] | 2-35-07 |  | 2-2F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_ADJ | 11KV關甲線(KR44) LCO分流器 U/L | FEEDER | S67/11/KR44/ADJ |  |  |  | CDC | 618 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR44 | KR44(11KV關甲線) |  | CB | [17 empty] | 1-1F-04 |  | 2-07 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_CB | KR44(11KV關甲線) CB | FEEDER | S67/11/KR44/CB |  |  |  | CDC | 619 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | PHA | [17 empty] | 2-11-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_PHA | 11KV仁傑線(KR45) 相間RY | FEEDER | S67/11/KR45/PHA |  |  |  | CDC | 620 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) |  | GDA | [17 empty] | 2-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_GDA | 11KV仁傑線(KR45) 接地RY | FEEDER | S67/11/KR45/GDA |  |  |  | CDC | 621 | GENERICDIPoint | SS409_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) 79RY |  | 79UL | [17 empty] | 2-33-11 |  | 2-10 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_79UL | 11KV仁傑線(KR45) 79RY U/L | FEEDER | S67/11/KR45/79UL |  |  |  | CDC | 622 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 11 | 11kV | KR45 | 仁傑線(KR45) LCO分流器 |  | ADJ | [17 empty] | 2-35-08 |  | 2-30 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_ADJ | 11KV仁傑線(KR45) LCO分流器 U/L | FEEDER | S67/11/KR45/ADJ |  |  |  | CDC | 623 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 11 | 11kV | KR45 | KR45(11KV仁傑線) |  | CB | [17 empty] | 1-1F-05 |  | 2-08 | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_CB | KR45(11KV仁傑線) CB | FEEDER | S67/11/KR45/CB |  |  |  | CDC | 624 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  |  |  |  | 保全設定 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.保全設定 | 保全設定 | OTHER | S67/0/StaDev/1A5Other |  |  |  | CDC | 625 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | DTU內部故障 | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.DTU內部故障 | DTU內部故障 | OTHER | S67/0/StaDev/PSF |  |  |  | CDC | 626 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | DTU通訊故障 | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.DTU通訊故障 | DTU通訊故障 | OTHER | S67/0/StaDev/PSA |  |  |  | CDC | 627 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.11KV_IED_FA | 11KV IED故障 | OTHER | S67/11/ComPoint/IRFA |  |  |  | CDC | 628 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S67/69/ComPoint/CFA |  |  |  | CDC | 629 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.69KV_IED_FA | 69KV IED故障 | OTHER | S67/69/ComPoint/IRFA |  |  |  | CDC | 630 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.81RY_IED_FA | 低頻IED故障 | OTHER | S67/0/StaDev/81A_RYFA |  |  |  | CDC | 631 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.PM_CFA | PM通訊故障 | OTHER | S67/0/StaDev/PMA |  |  |  | CDC | 632 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 670 | 新市歸仁線(670) |  | 87A | [17 empty] | 1-10-01 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.670_87A | 670新市歸仁線87RY | OTHER | S67/69/670/87A |  |  |  | CDC | 633 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 670 | 新市歸仁線(670) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.670_87UL | 670新市歸仁線87RY UL | OTHER | S67/69/670/87UL |  |  |  | CDC | 634 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 680 | 山上歸仁線(680) |  | 87A | [17 empty] | 1-10-05 | [7 empty] | ADCS_S | [8 empty] | 歸仁SS.680_87A | 680山上歸仁線87RY | OTHER | S67/69/680/87A |  |  |  | CDC | 635 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 680 | 山上歸仁線(680) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.680_87UL | 680山上歸仁線87RY UL | OTHER | S67/69/680/87UL |  |  |  | CDC | 636 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-0C-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S67//1MTR/63Q |  |  |  | CDC | 637 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-0C-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S67//1MTR/96B1 |  |  |  | CDC | 638 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-0C-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S67//1MTR/96B2 |  |  |  | CDC | 639 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-0C-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S67//1MTR/96D |  |  |  | CDC | 640 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-0C-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S67//1MTR/96P |  |  |  | CDC | 641 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S67//2MTR/63Q |  |  |  | CDC | 642 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S67//2MTR/96B1 |  |  |  | CDC | 643 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S67//2MTR/96B2 |  |  |  | CDC | 644 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-0C-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S67//2MTR/96D |  |  |  | CDC | 645 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-0C-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S67//2MTR/96P |  |  |  | CDC | 646 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | S67//3MTR/63Q |  |  |  | CDC | 647 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | S67//3MTR/96B1 |  |  |  | CDC | 648 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | S67//3MTR/96B2 |  |  |  | CDC | 649 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | S67//3MTR/96D |  |  |  | CDC | 650 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | S67//3MTR/96P |  |  |  | CDC | 651 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 63Q | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | S67//4MTR/63Q |  |  |  | CDC | 652 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 96B1 | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | S67//4MTR/96B1 |  |  |  | CDC | 653 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 96B2 | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | S67//4MTR/96B2 |  |  |  | CDC | 654 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 96D | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | S67//4MTR/96D |  |  |  | CDC | 655 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 96P | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | S67//4MTR/96P |  |  |  | CDC | 656 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 63Q | [17 empty] | 1-0E-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_63Q | #6MTR ULTC電驛動作 | OTHER | S67//6MTR/63Q |  |  |  | CDC | 657 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 96B1 | [17 empty] | 1-0E-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_96B1 | #6MTR 撲氣電驛警報 | OTHER | S67//6MTR/96B1 |  |  |  | CDC | 658 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 96B2 | [17 empty] | 1-0F-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_96B2 | #6MTR 撲氣電驛動作 | OTHER | S67//6MTR/96B2 |  |  |  | CDC | 659 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 96D | [17 empty] | 1-0E-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_96D | #6MTR 放壓電驛動作 | OTHER | S67//6MTR/96D |  |  |  | CDC | 660 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 96P | [17 empty] | 1-0E-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_96P | #6MTR 突壓電驛動作 | OTHER | S67//6MTR/96P |  |  |  | CDC | 661 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR31 | 萬芳線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_LOA | 萬芳線 復閉失敗閉鎖 | OTHER | S67/11/KR31/LOA |  |  |  | CDC | 662 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR32 | 八甲線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_LOA | 八甲線 復閉失敗閉鎖 | OTHER | S67/11/KR32/LOA |  |  |  | CDC | 663 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR33 | 歸33線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_LOA | 歸33線 復閉失敗閉鎖 | OTHER | S67/11/KR33/LOA |  |  |  | CDC | 664 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR34 | 深坑線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_LOA | 深坑線 復閉失敗閉鎖 | OTHER | S67/11/KR34/LOA |  |  |  | CDC | 665 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR35 | 南潭線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_LOA | 南潭線 復閉失敗閉鎖 | OTHER | S67/11/KR35/LOA |  |  |  | CDC | 666 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR36 | 六合線 |  | LOA | [17 empty] | 1-3F-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_LOA | 六合線 復閉失敗閉鎖 | OTHER | S67/11/KR36/LOA |  |  |  | CDC | 667 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR37 | 松根線 |  | LOA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_LOA | 松根線 復閉失敗閉鎖 | OTHER | S67/11/KR37/LOA |  |  |  | CDC | 668 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR38 | 歸38線 |  | LOA | [17 empty] | 1-3F-08 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_LOA | 歸38線 復閉失敗閉鎖 | OTHER | S67/11/KR38/LOA |  |  |  | CDC | 669 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR39 | 沙崙線 |  | LOA | [17 empty] | 1-3F-09 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_LOA | 沙崙線 復閉失敗閉鎖 | OTHER | S67/11/KR39/LOA |  |  |  | CDC | 670 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR40 | 漢平線 |  | LOA | [17 empty] | 1-3F-10 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_LOA | 漢平線 復閉失敗閉鎖 | OTHER | S67/11/KR40/LOA |  |  |  | CDC | 671 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR41 | 歸南線 |  | LOA | [17 empty] | 1-3F-11 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_LOA | 歸南線 復閉失敗閉鎖 | OTHER | S67/11/KR41/LOA |  |  |  | CDC | 672 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR42 | 古厝線 |  | LOA | [17 empty] | 1-3F-12 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_LOA | 古厝線 復閉失敗閉鎖 | OTHER | S67/11/KR42/LOA |  |  |  | CDC | 673 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR43 | 龍崎線 |  | LOA | [17 empty] | 1-3F-13 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_LOA | 龍崎線 復閉失敗閉鎖 | OTHER | S67/11/KR43/LOA |  |  |  | CDC | 674 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR44 | 關甲線 |  | LOA | [17 empty] | 1-3F-14 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_LOA | 關甲線 復閉失敗閉鎖 | OTHER | S67/11/KR44/LOA |  |  |  | CDC | 675 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR45 | 仁傑線 |  | LOA | [17 empty] | 1-3F-15 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_LOA | 仁傑線 復閉失敗閉鎖 | OTHER | S67/11/KR45/LOA |  |  |  | CDC | 676 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.變電所低水位 | 變電所低水位 | OTHER | S67/0/StaDev/Water1 |  |  |  | CDC | 677 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.變電所高水位 | 變電所高水位 | OTHER | S67/0/StaDev/Water2 |  |  |  | CDC | 678 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 660 | 歸仁保安線(660) |  | 87A | [17 empty] | 1-11-05 | [7 empty] | 69KV_S | [8 empty] | 歸仁SS.660_87A | 660歸仁保安線87RY | OTHER | S67/69/660/87A |  |  |  | CDC | 679 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 660 | 歸仁保安線(660) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_S | [8 empty] | 歸仁SS.660_87UL | 660歸仁保安線87RY UL | OTHER | S67/69/660/87UL |  |  |  | CDC | 680 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S67//1MTR/96PA |  |  |  | CDC | 681 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S67//2MTR/96PA |  |  |  | CDC | 682 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR | S67//3MTR/96PA |  |  |  | CDC | 683 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 1-04-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR | S67//4MTR/96PA |  |  |  | CDC | 684 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 96PA | [17 empty] | 1-06-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_96PA | #6MTR 機械保護動作 | DTR | S67//6MTR/96PA |  |  |  | CDC | 685 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | S67//1MTR/51Z_UL |  |  |  | CDC | 686 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-0A-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | S67//1MTR/MTR_86A |  |  |  | CDC | 687 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER | S67//1MTR/87UL |  |  |  | CDC | 688 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | S67//1MTR/1_87UL2 |  |  |  | CDC | 689 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3E-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | S67//2MTR/51Z_UL |  |  |  | CDC | 690 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-0A-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | S67//2MTR/MTR_86A |  |  |  | CDC | 691 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 2-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER | S67//2MTR/87UL |  |  |  | CDC | 692 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-3E-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | S67//2MTR/1_87UL2 |  |  |  | CDC | 693 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-3E-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | S67//3MTR/51Z_UL |  |  |  | CDC | 694 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-0A-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | S67//3MTR/MTR_86A |  |  |  | CDC | 695 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 2-31-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_87UL1 | #3MTR 第一套87RY U/L | OTHER | S67//3MTR/87UL |  |  |  | CDC | 696 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 1-3E-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | S67//3MTR/1_87UL2 |  |  |  | CDC | 697 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 51Z_UL | [17 empty] | 1-3E-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_51ZUL | #4MTR 51Z U/L | OTHER | S67//4MTR/51Z_UL |  |  |  | CDC | 698 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | MTR_86A | [17 empty] | 1-0A-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_86A | #4MTR 86(51Z/87/96)RY | OTHER | S67//4MTR/MTR_86A |  |  |  | CDC | 699 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 1_87UL1 | [17 empty] | 2-32-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_87UL1 | #4MTR 第一套87RY U/L | OTHER | S67//4MTR/87UL |  |  |  | CDC | 700 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 4MTR | #4MTR |  | 1_87UL2 | [17 empty] | 1-3E-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4MTR_87UL2 | #4MTR 第二套87RY U/L | OTHER | S67//4MTR/1_87UL2 |  |  |  | CDC | 701 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 51Z_UL | [17 empty] | 1-3E-09 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_51ZUL | #6MTR 51Z U/L | OTHER | S67//6MTR/51Z_UL |  |  |  | CDC | 702 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | MTR_86A | [17 empty] | 1-0B-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_86A | #6MTR 86(51Z/87/96)RY | OTHER | S67//6MTR/MTR_86A |  |  |  | CDC | 703 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 1_87UL1 | [17 empty] | 2-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_87UL1 | #6MTR 第一套87RY U/L | OTHER | S67//6MTR/87UL |  |  |  | CDC | 704 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | 6MTR | #6MTR |  | 1_87UL2 | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#6MTR_87UL2 | #6MTR 第二套87RY U/L | OTHER | S67//6MTR/1_87UL2 |  |  |  | CDC | 705 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | MTR | MTR |  | IEDGA | [17 empty] | 1-3E-10 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.MTR_IED故障 | MTR IED故障 | OTHER | S67/0/MTR/IRFA |  |  |  | CDC | 706 | GENERICDIPoint | SS409_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4SSTR | #4SSTR |  | 51A | [17 empty] | 1-0B-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4SSTR_51A | #4SSTR 51RY | OTHER | S67/11/4SSTR/PHA |  |  |  | CDC | 707 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4SSTR | #4SSTR |  | 51NA | [17 empty] | 1-0B-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4SSTR_51NA | #4SSTR 51N RY | OTHER | S67/11/4SSTR/GDA |  |  |  | CDC | 708 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | 4SSTR | #4SSTR |  | CB | [17 empty] | 1-0B-02 |  | 1-7F | [5 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4SSTR_CB | #4SSTR CB | OTHER | S67/11/4SSTR/CB |  |  |  | CDC | 709 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 27A | [17 empty] | 1-09-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_27A | 大聚太陽光電 27A | OTHER | S67/11/TA/27A |  |  |  | CDC | 710 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 50A | [17 empty] | 1-09-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_50A | 大聚太陽光電 50A | OTHER | S67/11/TA/50A |  |  |  | CDC | 711 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 50NA | [17 empty] | 1-09-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_50NA | 大聚太陽光電 50NA | OTHER | S67/11/TA/1A3Other |  |  |  | CDC | 712 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 51A | [17 empty] | 1-09-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_51A | 大聚太陽光電 51A | OTHER | S67/11/TA/51A |  |  |  | CDC | 713 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 51NA | [17 empty] | 1-09-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_51NA | 大聚太陽光電 51NA | OTHER | S67/11/TA/51NA |  |  |  | CDC | 714 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 59A | [17 empty] | 1-09-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_59A | 大聚太陽光電 59A | OTHER | S67/11/TA/59A |  |  |  | CDC | 715 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | 59V0A | [17 empty] | 1-09-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_59V0A | 大聚太陽光電 59V0A | OTHER | S67/11/TA/59A_V0 |  |  |  | CDC | 716 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | CB | [17 empty] | 1-09-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_CB | 大聚太陽光電 CB | OTHER | S67/11/TA/CB |  |  |  | CDC | 717 | GENERICDIPoint | SS409_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | DS1 | TA | [16 empty] | 2-36-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_DS | 大聚太陽光電 DS | OTHER | S67/11/TA/D1 |  |  |  | CDC | 718 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | TA | 大聚太陽光電 |  | LE0 | TA | [16 empty] | 2-36-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TA_ES | 大聚太陽光電 ES | OTHER | S67/11/TA/ES |  |  |  | CDC | 719 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR21 | 歸仁線 |  | LOA | [17 empty] | 2-37-00 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_LOA | 歸仁線 復閉失敗閉鎖 | OTHER | S67/11/KR21/LOA |  |  |  | CDC | 720 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR22 | 新田線 |  | LOA | [17 empty] | 2-37-01 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_LOA | 新田線 復閉失敗閉鎖 | OTHER | S67/11/KR22/LOA |  |  |  | CDC | 721 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR23 | 媽廟線 |  | LOA | [17 empty] | 2-37-02 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_LOA | 媽廟線 復閉失敗閉鎖 | OTHER | S67/11/KR23/LOA |  |  |  | CDC | 722 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR24 | 南保線 |  | LOA | [17 empty] | 2-37-03 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_LOA | 南保線 復閉失敗閉鎖 | OTHER | S67/11/KR24/LOA |  |  |  | CDC | 723 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR25 | 貝汝線 |  | LOA | [17 empty] | 2-37-04 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_LOA | 貝汝線 復閉失敗閉鎖 | OTHER | S67/11/KR25/LOA |  |  |  | CDC | 724 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR26 | 東盈線 |  | LOA | [17 empty] | 2-37-05 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_LOA | 東盈線 復閉失敗閉鎖 | OTHER | S67/11/KR26/LOA |  |  |  | CDC | 725 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR27 | 豐中線 |  | LOA | [17 empty] | 2-37-06 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_LOA | 豐中線 復閉失敗閉鎖 | OTHER | S67/11/KR27/LOA |  |  |  | CDC | 726 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR28 | 崙頂線 |  | LOA | [17 empty] | 2-37-07 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_LOA | 崙頂線 復閉失敗閉鎖 | OTHER | S67/11/KR28/LOA |  |  |  | CDC | 727 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR29 | 看西線 |  | LOA | [17 empty] | 2-37-08 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_LOA | 看西線 復閉失敗閉鎖 | OTHER | S67/11/KR29/LOA |  |  |  | CDC | 728 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 0 |  | KR30 | 關廟線 |  | LOA | [17 empty] | 2-37-09 | [7 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_LOA | 關廟線 復閉失敗閉鎖 | OTHER | S67/11/KR30/LOA |  |  |  | CDC | 729 | GENERICDIPoint | SS409_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S67 | 歸仁SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_SC_CAP | 11KV#1SC 容量 | SC | S67/11/210/1AI_Oth |  |  |  |  | 730 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_SC_CAP | 11KV#2SC 容量 | SC | S67/11/220/2AI_Oth |  |  |  |  | 731 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_SC_CAP | 11KV#3SC 容量 | SC | S67/11/230/3AI_Oth |  |  |  |  | 732 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_SC_CAP | 11KV#4SC 容量 | SC | S67/11/240/4AI_Oth |  |  |  |  | 733 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_SC_CAP | 11KV#6SC 容量 | SC | S67/11/260/6AI_Oth |  |  |  |  | 734 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 歸仁SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 735 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S67 | 歸仁SS | 69 | 69kV | 630 | 外港線(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.630LE | 630LE (非取樣點) | LINE69 | S67/69/630/LE0 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | LE0 | 660LE | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.660LE | 660LE (非取樣點) | LINE69 | S67/69/660/LE0 |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 670 | 新市歸仁線(670) |  | LE0 | 670LE | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.670LE | 670LE (非取樣點) | LINE69 | S67/69/670/LE0 |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 680 | 山上歸仁線(680) |  | LE0 | 680LE | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.680LE | 680LE (非取樣點) | LINE69 | S67/69/680/LE0 |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR21_KR22 | KR21_KR22_DS |  | DS1 | KR21_KR22_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_KR22_DS | KR21_KR22_DS (非取樣點) | FEEDER | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR21 | KR21_ES |  | LE0 | KR21_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_ES | KR21_ES (非取樣點) | FEEDER | S67/11/KR21/ES |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR22_KR23 | KR22_KR23_DS |  | DS1 | KR22_KR23_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_KR23_DS | KR22_KR23_DS (非取樣點) | FEEDER | [5 empty] | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR22 | KR22_ES |  | LE0 | KR22_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_ES | KR22_ES (非取樣點) | FEEDER | S67/11/KR22/ES |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR23 | KR23_ES |  | LE0 | KR23_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_ES | KR23_ES (非取樣點) | FEEDER | S67/11/KR23/ES |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR24_KR38 | KR24_KR38_DS |  | DS1 | KR24_KR38_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_KR38_DS | KR24_KR38_DS (非取樣點) | FEEDER | [5 empty] | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR24 | KR24_ES |  | LE0 | KR24_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_ES | KR24_ES (非取樣點) | FEEDER | S67/11/KR24/ES |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR25 | KR25_ES |  | LE0 | KR25_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_ES | KR25_ES (非取樣點) | FEEDER | S67/11/KR25/ES |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR26_KR27 | KR26_KR27_DS |  | DS1 | KR26_KR27_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_KR27_DS | KR26_KR27_DS (非取樣點) | FEEDER | [5 empty] | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR26 | KR26_ES |  | LE0 | KR26_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_ES | KR26_ES (非取樣點) | FEEDER | S67/11/KR26/ES |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR27 | KR27_ES |  | LE0 | KR27_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_ES | KR27_ES (非取樣點) | FEEDER | S67/11/KR27/ES |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR28 | KR28_ES |  | LE0 | KR28_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_ES | KR28_ES (非取樣點) | FEEDER | S67/11/KR28/ES |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR29 | KR29_ES |  | LE0 | KR29_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_ES | KR29_ES (非取樣點) | FEEDER | S67/11/KR29/ES |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR30 | KR30_ES |  | LE0 | KR30_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_ES | KR30_ES (非取樣點) | FEEDER | S67/11/KR30/ES |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR31 | KR31_DS |  | DS1 | KR31_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_DS | KR31_DS (非取樣點) | FEEDER | S67/11/KR31/DS |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR31 | KR31_ES |  | LE0 | KR31_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR31_ES | KR31_ES (非取樣點) | FEEDER | S67/11/KR31/ES |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR32 | KR32_DS |  | DS1 | KR32_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_DS | KR32_DS (非取樣點) | FEEDER | S67/11/KR32/DS |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR32 | KR32_ES |  | LE0 | KR32_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR32_ES | KR32_ES (非取樣點) | FEEDER | S67/11/KR32/ES |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR33 | KR33_DS |  | DS1 | KR33_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_DS | KR33_DS (非取樣點) | FEEDER | S67/11/KR33/DS |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR33 | KR33_ES |  | LE0 | KR33_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR33_ES | KR33_ES (非取樣點) | FEEDER | S67/11/KR33/ES |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR34 | KR34_DS |  | DS1 | KR34_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_DS | KR34_DS (非取樣點) | FEEDER | S67/11/KR34/DS |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR34 | KR34_ES |  | LE0 | KR34_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR34_ES | KR34_ES (非取樣點) | FEEDER | S67/11/KR34/ES |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR35 | KR35_DS |  | DS1 | KR35_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_DS | KR35_DS (非取樣點) | FEEDER | S67/11/KR35/DS |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR35 | KR35_ES |  | LE0 | KR35_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR35_ES | KR35_ES (非取樣點) | FEEDER | S67/11/KR35/ES |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR36 | KR36_DS |  | DS1 | KR36_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_DS | KR36_DS (非取樣點) | FEEDER | S67/11/KR36/DS |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR36 | KR36_ES |  | LE0 | KR36_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR36_ES | KR36_ES (非取樣點) | FEEDER | S67/11/KR36/ES |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR37 | KR37_DS |  | DS1 | KR37_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_DS | KR37_DS (非取樣點) | FEEDER | S67/11/KR37/DS |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR37 | KR37_ES |  | LE0 | KR37_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR37_ES | KR37_ES (非取樣點) | FEEDER | S67/11/KR37/ES |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR38 | KR38_DS |  | DS1 | KR38_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_DS | KR38_DS (非取樣點) | FEEDER | S67/11/KR38/DS |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR38 | KR38_ES |  | LE0 | KR38_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR38_ES | KR38_ES (非取樣點) | FEEDER | S67/11/KR38/ES |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR39 | KR39_DS |  | DS1 | KR39_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_DS | KR39_DS (非取樣點) | FEEDER | S67/11/KR39/DS |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR39 | KR39_ES |  | LE0 | KR39_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR39_ES | KR39_ES (非取樣點) | FEEDER | S67/11/KR39/ES |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR40 | KR40_DS |  | DS1 | KR40_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_DS | KR40_DS (非取樣點) | FEEDER | S67/11/KR40/DS |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR40 | KR40_ES |  | LE0 | KR40_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR40_ES | KR40_ES (非取樣點) | FEEDER | S67/11/KR40/ES |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | TIE1 | #1-#2 |  | DS1 | TIE1_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE1_DS | #1-#2 TIE_DS (非取樣點) | TIE | S67/11/TIE1/D1 |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | TIE2 | #3-#2 |  | DS1 | TIE2_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE2_DS | #3-#2 TIE_DS (非取樣點) | TIE | S67/11/TIE2/D1 |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | TIE3 | #6-#3 |  | DS1 | TIE3_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE3_DS | #6-#3 TIE_DS (非取樣點) | TIE | S67/11/TIE3/D1 |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | TIE4 | #4-#1 |  | DS1 | TIE4_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE4_DS | #4-#1 TIE_DS (非取樣點) | TIE | S67/11/TIE4/D1 |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.1M_DS | 1M_DS (非取樣點) | DTR | S67/11/M1/DS |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.1M_ES | 1M_ES (非取樣點) | DTR | S67/11/M1/ES |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.2M_DS | 2M_DS (非取樣點) | DTR | S67/11/M2/DS |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.2M_ES | 2M_ES (非取樣點) | DTR | S67/11/M2/ES |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.3M_DS | 3M_DS (非取樣點) | DTR | S67/11/M3/DS |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.3M_ES | 3M_ES (非取樣點) | DTR | S67/11/M3/ES |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 4M | 4M_DS |  | DS1 | 4M_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.4M_DS | 4M_DS (非取樣點) | DTR | S67/11/M4/DS |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 4M | 4M_ES |  | M0 | 4M_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.4M_ES | 4M_ES (非取樣點) | DTR | S67/11/M4/ES |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 6M | 6M_DS |  | DS1 | 6M_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.6M_DS | 6M_DS (非取樣點) | DTR | S67/11/M6/DS |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 6M | 6M_ES |  | M0 | 6M_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.6M_ES | 6M_ES (非取樣點) | DTR | S67/11/M6/ES |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_ES | 210_ES (非取樣點) | SC | S67/11/210/ES |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS1 | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.210_DS1 | 210_DS1 (非取樣點) | SC | S67/11/210/DS |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_ES | 220_ES (非取樣點) | SC | S67/11/220/ES |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS1 | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.220_DS1 | 220_DS1 (非取樣點) | SC | S67/11/220/DS |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_ES | 230_ES (非取樣點) | SC | S67/11/230/ES |  |  |  |  | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.230_DS | 230_DS (非取樣點) | SC | S67/11/230/DS |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_ES | 240_ES (非取樣點) | SC | S67/11/240/ES |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.240_DS | 240_DS (非取樣點) | SC | S67/11/240/DS |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_ES | 260_ES (非取樣點) | SC | S67/11/260/ES |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.260_DS | 260_DS (非取樣點) | SC | S67/11/260/DS |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.69B1E | 69B1E (非取樣點) | BUS | S67/69/1BUS/BE1 |  |  |  |  | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 799 | NotelDIPoint | [38 empty] | START/STOP | STOP
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PW1UL | 660_PW1UL | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.660_PW1UL | 保安線(660)PW1_UL(非取樣點) | LINE69 | [5 empty] | 800 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | PW2UL | 660_PW2UL | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.660_PW2UL | 保安線(660)PW2_UL(非取樣點) | LINE69 | [5 empty] | 801 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
S67 | 歸仁SS | 69 | 69kV | 660 | 歸仁保安線(660) |  | HCBUL | 660_HCBUL | [24 empty] | ADCS_S | [8 empty] | 歸仁SS.660_HCBUL | 保安線(660)HCB_UL(非取樣點) | LINE69 | [5 empty] | 802 | NotelDIPoint | [38 empty] | USE/LOCK | USE
S67 | 歸仁SS | 0 |  | KR41 | KR41_DS |  | DS1 | KR41_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_DS | KR41_DS (非取樣點) | FEEDER | S67/11/KR41/DS |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR41 | KR41_ES |  | LE0 | KR41_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR41_ES | KR41_ES (非取樣點) | FEEDER | S67/11/KR41/ES |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR42 | KR42_DS |  | DS1 | KR42_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_DS | KR42_DS (非取樣點) | FEEDER | S67/11/KR42/DS |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR42 | KR42_ES |  | LE0 | KR42_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR42_ES | KR42_ES (非取樣點) | FEEDER | S67/11/KR42/ES |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR43 | KR43_DS |  | DS1 | KR43_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_DS | KR43_DS (非取樣點) | FEEDER | S67/11/KR43/DS |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR43 | KR43_ES |  | LE0 | KR43_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR43_ES | KR43_ES (非取樣點) | FEEDER | S67/11/KR43/ES |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR44 | KR44_DS |  | DS1 | KR44_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_DS | KR44_DS (非取樣點) | FEEDER | S67/11/KR44/DS |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR44 | KR44_ES |  | LE0 | KR44_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR44_ES | KR44_ES (非取樣點) | FEEDER | S67/11/KR44/ES |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR45 | KR45_DS |  | DS1 | KR45_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_DS | KR45_DS (非取樣點) | FEEDER | S67/11/KR45/DS |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR45 | KR45_ES |  | LE0 | KR45_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR45_ES | KR45_ES (非取樣點) | FEEDER | S67/11/KR45/ES |  |  |  |  | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | BR1 | BR1_DS |  | DS1 | BR1_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR1_DS | BR1_DS (非取樣點) | TIE | [5 empty] | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | BR2 | BR2_DS |  | DS1 | BR2_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR2_DS | BR2_DS (非取樣點) | TIE | [5 empty] | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | BR3 | BR3_DS |  | DS1 | BR3_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR3_DS | BR3_DS (非取樣點) | TIE | [5 empty] | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.750TE | 750TE (非取樣點) | DTR | S67/69/750/TE0 |  |  |  |  | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.750BE | 750BE (非取樣點) | DTR | S67/69/750/BE0 |  |  |  |  | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.760TE | 760TE (非取樣點) | DTR | S67/69/760/TE0 |  |  |  |  | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.760BE | 760BE (非取樣點) | DTR | S67/69/760/BE0 |  |  |  |  | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.770TE | 770TE (非取樣點) | DTR | S67/69/770/TE0 |  |  |  |  | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.770BE | 770BE (非取樣點) | DTR | S67/69/770/BE0 |  |  |  |  | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.780TE | 780TE (非取樣點) | DTR | S67/69/780/TE0 |  |  |  |  | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.780BE | 780BE (非取樣點) | DTR | S67/69/780/BE0 |  |  |  |  | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | TE0 | 790TE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.790TE | 790TE (非取樣點) | DTR | S67/69/790/TE0 |  |  |  |  | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 69 | 69kV | 790 | #6MTR(790) |  | BE0 | 790BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.790BE | 790BE (非取樣點) | DTR | S67/69/790/BE0 |  |  |  |  | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | BR1 | BR1 |  | LE0 | BR1_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR1_ES | BR1 ES(非取樣點) | OTHER | [5 empty] | 826 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | BR2 | BR2 |  | LE0 | BR2_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR2_ES | BR2 ES(非取樣點) | OTHER | [5 empty] | 827 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | TIE1 | #1-#2 |  | LE0 | TIE1_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE1_ES | #1-#2 TIE ES(非取樣點) | OTHER | S67/11/TIE1/E1 |  |  |  |  | 828 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | TIE2 | #3-#2 |  | LE0 | TIE2_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE2_ES | #3-#2 TIE ES(非取樣點) | OTHER | S67/11/TIE2/E1 |  |  |  |  | 829 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | KR21 | KR21_DS |  | DS1 | KR21_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR21_DS | KR21_DS (非取樣點) | FEEDER | S67/11/KR21/DS |  |  |  |  | 830 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR22 | KR22_DS |  | DS1 | KR22_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR22_DS | KR22_DS (非取樣點) | FEEDER | S67/11/KR22/DS |  |  |  |  | 831 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR23 | KR23_DS |  | DS1 | KR23_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR23_DS | KR23_DS (非取樣點) | FEEDER | S67/11/KR23/DS |  |  |  |  | 832 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR24 | KR24_DS |  | DS1 | KR24_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR24_DS | KR24_DS (非取樣點) | FEEDER | S67/11/KR24/DS |  |  |  |  | 833 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR25 | KR25_DS |  | DS1 | KR25_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR25_DS | KR25_DS (非取樣點) | FEEDER | S67/11/KR25/DS |  |  |  |  | 834 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR26 | KR26_DS |  | DS1 | KR26_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR26_DS | KR26_DS (非取樣點) | FEEDER | S67/11/KR26/DS |  |  |  |  | 835 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR27 | KR27_DS |  | DS1 | KR27_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR27_DS | KR27_DS (非取樣點) | FEEDER | S67/11/KR27/DS |  |  |  |  | 836 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR28 | KR28_DS |  | DS1 | KR28_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR28_DS | KR28_DS (非取樣點) | FEEDER | S67/11/KR28/DS |  |  |  |  | 837 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR29 | KR29_DS |  | DS1 | KR29_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR29_DS | KR29_DS (非取樣點) | FEEDER | S67/11/KR29/DS |  |  |  |  | 838 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | KR30 | KR30_DS |  | DS1 | KR30_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.KR30_DS | KR30_DS (非取樣點) | FEEDER | S67/11/KR30/DS |  |  |  |  | 839 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | BR | BR_DS |  | DS1 | BR_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR_DS | BR_DS (非取樣點) | TIE | [5 empty] | 840 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S67 | 歸仁SS | 0 |  | BR | BR |  | LE0 | BR_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.BR_ES | BR ES(非取樣點) | OTHER | [5 empty] | 841 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 4SSTR | #4SSTR |  | ISOBB | #4SSTR_DS | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4SSTR_DS | #4SSTR DS(非取樣點) | OTHER | S67/11/4SSTR/DS |  |  |  |  | 842 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 4SSTR | #4SSTR |  | E0 | #4SSTR_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4SSTR_ES | #4SSTR ES(非取樣點) | OTHER | S67/11/4SSTR/ES |  |  |  |  | 843 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | TIE4 | #4-#1 |  | LE0 | TIE4_ES | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.TIE4_ES | #4-#1 TIE ES(非取樣點) | OTHER | [5 empty] | 844 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 1 | #1 |  | BE | #1_BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#1_BE | #1 BE(非取樣點) | OTHER | S67/11/1BUS/BE0 |  |  |  |  | 845 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 2 | #2 |  | BE | #2_BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#2_BE | #2 BE(非取樣點) | OTHER | S67/11/2BUS/BE0 |  |  |  |  | 846 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S67 | 歸仁SS | 0 |  | 4 | #4 |  | BE | #4_BE | [24 empty] | DDCS4_2 | [8 empty] | 歸仁SS.#4_BE | #4 BE(非取樣點) | OTHER | S67/11/4BUS/BE0 |  |  |  |  | 847 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo