## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S70 | 山頂SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S70_A1 | [8 empty] | 山頂SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S70 | 山頂SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S70_D1 | [8 empty] | 山頂SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 11 | 11kV | 2BUS | #2BUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S70_D1 | [8 empty] | 山頂SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP |  | 1BUS | [14 empty] | not found | B2/S70_A1 | [8 empty] | 山頂SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 5 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 6 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 山上山頂二路 (620) 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.620_MW | 山上山頂二路 MW | LINE69 |  |  |  |  | CDC | 7 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 山上山頂二路 (620) 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.620_MVAR | 山上山頂二路 MVAR | LINE69 |  |  |  |  | CDC | 8 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0026 |  |  | 1-5A |  |  | 山上山頂二路 (620) MWH(+) |  |  |  |  | B2/S70_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 9 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 山頂宏遠線 (630) 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.630_MW | 宏遠線 MW | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 山頂宏遠線 (630) 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.630_MVAR | 宏遠線 MVAR | LINE69 |  |  |  |  | CDC | 11 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 山頂宏遠線 (630) MWH(+) |  |  |  |  | B2/S70_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 12 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 山上山頂一路 (610) 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.610_MW | 山上山頂一路 MW | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 山上山頂一路 (610) 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S70_A1 | [8 empty] | 山頂SS.610_MVAR | 山上山頂一路 MVAR | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 山上山頂一路 (610) MWH(+) |  |  |  |  | B2/S70_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 15 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 山上山頂二路 (620) 67 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.620_PHA | 山上山頂二路(620) 相間RY | LINE69 |  |  |  |  | CDC | 16 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 山上山頂二路 (620) 67N RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.620_GDA | 山上山頂二路(620) 接地RY | LINE69 |  |  |  |  | CDC | 17 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 山上山頂二路 (620) 85 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.620_87A | 620山上山頂二路87RY | OTHER |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 山頂宏遠線 (630) 67 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_PHA | 宏遠線(630) 相間RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 山頂宏遠線 (630) 67N RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_GDA | 宏遠線(630) 接地RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 山頂宏遠線 (630) 85 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_85A | 宏遠線(630) 85RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | 山頂宏遠線 (630) 74RY U/L |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_74A | 宏遠線(630) 74RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 山上山頂一路 (610) 67 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.610_PHA | 山上山頂一路(610) 相間RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 山上山頂一路 (610) 67N RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.610_GDA | 山上山頂一路(610) 接地RY | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 山上山頂一路 (610) 85 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.610_87A | 610山上山頂一路87RY | OTHER |  |  |  |  | CDC | 25 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | 山上山頂二路 (620) 87RY U/L |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.620_87UL | 620山上山頂二路87RY UL | OTHER |  |  |  |  | CDC | 26 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0011 | 1-32-04 |  | 1-0B | 山頂宏遠線 (630) 85RY U/L |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_85UL | 宏遠線(630) 85RY U/L | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0012 | 1-32-06 |  | 1-0C | 山上山頂一路 (610) 87RY U/L |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.610_87UL | 610山上山頂一路87RY UL | OTHER |  |  |  |  | CDC | 28 | DI_LINE69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0068 |  | 0002 | 1-08-04 |  | 1-02 | 山上山頂二路 (620) CB |  |  |  | aaaa | B2/S70_A1 | [8 empty] | 山頂SS.620_CB | 620(山上山頂二路) CB | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0072 |  | 0003 | 1-09-00 |  | 1-03 | 山頂宏遠線 (630) CB |  |  |  | aada | B2/S70_A1 | [8 empty] | 山頂SS.630_CB | 630(宏遠線) CB | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0000 |  | 0017 | 1-00-00 |  | 1-11 | 69KV 81 RY 山頂宏遠線 (630) |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.630_81A/S | (630) 81RY A/S | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbI | B/1BUS | L |  |  | 0076 |  | 0004 | 1-09-04 |  | 1-04 | 山上山頂一路 (610) CB |  |  |  | aafa | B2/S70_A1 | [8 empty] | 山頂SS.610_CB | 610(山上山頂一路) CB | LINE69 |  |  |  |  | CDC | 32 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ABS1 | 621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0021 | 1-38-14 | 1-38-15 | 1-15 | 山上山頂二路 (621) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.621_ABS | 621(山上山頂二路) ABS | LINE69 |  |  |  |  | CDC | 33 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ABS2 | 622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0022 | 1-39-00 | 1-39-01 | 1-16 | 山上山頂二路 (622) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.622_ABS | 622(山上山頂二路) ABS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | ABS1 | 631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0404 | 405 | 0024 | 1-39-04 | 1-39-05 | 1-18 | 山頂宏遠線 (631) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.631_ABS | 631(宏遠線) ABS | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | ABS2 | 632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0025 | 1-39-06 | 1-39-07 | 1-19 | 山頂宏遠線 (632) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.632_ABS | 632(宏遠線) ABS | LINE69 |  |  |  |  | CDC | 36 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | DS1 | 611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0410 | 411 | 0027 | 1-39-10 | 1-39-11 | 1-1B | 山上山頂一路 (611) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.611_DS | 611(山上山頂一路) DS | LINE69 |  |  |  |  | CDC | 37 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | DS2 | 612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 | 0028 | 1-39-12 | 1-39-13 | 1-1C | 山上山頂一路 (612) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.612_DS | 612(山上山頂一路) DS | LINE69 |  |  |  |  | CDC | 38 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | ES2 | 622E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0402 | 403 | 0023 | 1-39-02 | 1-39-03 | 1-17 | 山上山頂二路 (622E) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.622E_ES | 622E(山上山頂二路) ES | LINE69 |  |  |  |  | CDC | 39 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | LE0 | 620LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_A1 | [8 empty] | 山頂SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 40 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | ES2 | 632E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0408 | 409 | 0026 | 1-39-08 | 1-39-09 | 1-1A | 山頂宏遠線 (632E) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.632E_ES | 632E(宏遠線) ES | LINE69 |  |  |  |  | CDC | 41 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | LE0 | 630LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_A1 | [8 empty] | 山頂SS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 42 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | ES2 | 612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0414 | 415 | 0029 | 1-39-14 | 1-39-15 | 1-1D | 山上山頂一路 (612E) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.612E_ES | 612E(山上山頂一路) ES | LINE69 |  |  |  |  | CDC | 43 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | LE0 | 610LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_A1 | [8 empty] | 山頂SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 44 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | BE0 | 610BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_A1 | [8 empty] | 山頂SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 45 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 山30線 (KK30) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山30線KVAR | 11KV山30線 KVAR | FEEDER |  |  |  |  | CDC | 46 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 山30線 (KK30) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山30線A1 | 11KV山30線 R相AMP | FEEDER |  |  |  |  | CDC | 47 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 山30線 (KK30) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山30線A2 | 11KV山30線 S相AMP | FEEDER |  |  |  |  | CDC | 48 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 山30線 (KK30) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山30線A3 | 11KV山30線 T相AMP | FEEDER |  |  |  |  | CDC | 49 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 山30線 (KK30) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山30線A0 | 11KV山30線 N相AMP | FEEDER |  |  |  |  | CDC | 50 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 山30線 (KK30) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 51 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 大庄線 (KK21) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK21_PHA | 11KV大庄線(KK21) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 大庄線 (KK21) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK21_GDA | 11KV大庄線(KK21) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | 大庄線（KK21) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK21_79UL | 11KV大庄線(KK21) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | 大庄線 (KK21) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK21_ADJ | 11KV大庄線(KK21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | 南化線 (KK22) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK22_PHA | 11KV南化線(KK22) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 南化線 (KK22) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK22_GDA | 11KV南化線(KK22) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | 南化線（KK22) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK22_79UL | 11KV南化線(KK22) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | 南化線 (KK22) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK22_ADJ | 11KV南化線(KK22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 牧場線 (KK23) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK23_PHA | 11KV牧場線(KK23) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 牧場線 (KK23) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK23_GDA | 11KV牧場線(KK23) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | 牧場線（KK23) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK23_79UL | 11KV牧場線(KK23) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | 牧場線 (KK23) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK23_ADJ | 11KV牧場線(KK23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 永安線 (KK24) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK24_PHA | 11KV永安線(KK24) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 永安線 (KK24) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK24_GDA | 11KV永安線(KK24) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | 永安線（KK24) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK24_79UL | 11KV永安線(KK24) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | 永安線 (KK24) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK24_ADJ | 11KV永安線(KK24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 南醫線 (KK25) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK25_PHA | 11KV南醫線(KK25) 相間RY | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 南醫線 (KK25) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK25_GDA | 11KV南醫線(KK25) 接地RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | 南醫線 (KK25) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK25_79UL | 11KV南醫線(KK25) 79RY U/L | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | 南醫線 (KK25) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK25_ADJ | 11KV南醫線(KK25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 那拔線 (KK26) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK26_PHA | 11KV那拔線(KK26) 相間RY | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 那拔線 (KK26) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK26_GDA | 11KV那拔線(KK26) 接地RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | 那拔線 (KK26) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK26_79UL | 11KV那拔線(KK26) 79RY U/L | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | 那拔線 (KK26) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK26_ADJ | 11KV那拔線(KK26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 山上線 (KK27) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK27_PHA | 11KV山上線(KK27) 相間RY | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 山上線 (KK27) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK27_GDA | 11KV山上線(KK27) 接地RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | 山上線 (KK27) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK27_79UL | 11KV山上線(KK27) 79RY U/L | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | 山上線 (KK27) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK27_ADJ | 11KV山上線(KK27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 玉井線 (KK28) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK28_PHA | 11KV玉井線(KK28) 相間RY | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 玉井線 (KK28) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK28_GDA | 11KV玉井線(KK28) 接地RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | 玉井線 (KK28) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK28_79UL | 11KV玉井線(KK28) 79RY U/L | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | 玉井線 (KK28) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK28_ADJ | 11KV玉井線(KK28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 山工線 (KK29) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK29_PHA | 11KV山工線(KK29) 相間RY | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 山工線 (KK29) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK29_GDA | 11KV山工線(KK29) 接地RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | 山工線 (KK29) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK29_79UL | 11KV山工線(KK29) 79RY U/L | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | 山工線 (KK29) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK29_ADJ | 11KV山工線(KK29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 山30線 (KK30) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK30_PHA | 11KV山30線(KK30) 相間RY | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 山30線 (KK30) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK30_GDA | 11KV山30線(KK30) 接地RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | 山30線 (KK30) 79RY U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK30_79UL | 11KV山30線(KK30) 79RY U/L | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | 山30線 (KK30) LCO ADJ U/L |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK30_ADJ | 11KV山30線(KK30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/1BUS | KK21/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | 大庄線 (KK21) CB |  |  |  | aabb | B2/S70_D1 | [8 empty] | 山頂SS.KK21_CB | KK21(11KV大庄線) CB | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK21DS1 | KK21DS1 (非取樣點) | FEEDER | [5 empty] | 93 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK21DS2 | KK21DS2 (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | ES | KK21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK21_ES | KK21_ES (非取樣點) | FEEDER | [5 empty] | 95 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/1BUS | KK22/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | 南化線 (KK22) CB |  |  |  | aadb | B2/S70_D1 | [8 empty] | 山頂SS.KK22_CB | KK22(11KV南化線) CB | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK22DS1 | KK22DS1 (非取樣點) | FEEDER | [5 empty] | 97 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK22DS2 | KK22DS2 (非取樣點) | FEEDER | [5 empty] | 98 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | ES | KK22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK22_ES | KK22_ES (非取樣點) | FEEDER | [5 empty] | 99 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/1BUS | KK23/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | 牧場線 (KK23) CB |  |  |  | aaeb | B2/S70_D1 | [8 empty] | 山頂SS.KK23_CB | KK23(11KV牧場線) CB | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK23DS1 | KK23DS1 (非取樣點) | FEEDER | [5 empty] | 101 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK23DS2 | KK23DS2 (非取樣點) | FEEDER | [5 empty] | 102 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | ES | KK23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK23_ES | KK23_ES (非取樣點) | FEEDER | [5 empty] | 103 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/1BUS | KK24/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | 永安線 (KK24) CB |  |  |  | aafb | B2/S70_D1 | [8 empty] | 山頂SS.KK24_CB | KK24(11KV永安線) CB | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK24DS1 | KK24DS1 (非取樣點) | FEEDER | [5 empty] | 105 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK24DS2 | KK24DS2 (非取樣點) | FEEDER | [5 empty] | 106 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | ES | KK24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK24_ES | KK24_ES (非取樣點) | FEEDER | [5 empty] | 107 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/1BUS | KK25/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | 南醫線 (KK25) CB |  |  |  | aagb | B2/S70_D1 | [8 empty] | 山頂SS.KK25_CB | KK25(11KV南醫線) CB | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK25DS1 | KK25DS1 (非取樣點) | FEEDER | [5 empty] | 109 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK25DS2 | KK25DS2 (非取樣點) | FEEDER | [5 empty] | 110 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | ES | KK25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK25_ES | KK25_ES (非取樣點) | FEEDER | [5 empty] | 111 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/2BUS | KK26/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | 那拔線 (KK26) CB |  |  |  | abab | B2/S70_D1 | [8 empty] | 山頂SS.KK26_CB | KK26(11KV那拔線) CB | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK26DS1 | KK26DS1 (非取樣點) | FEEDER | [5 empty] | 113 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK26DS2 | KK26DS2 (非取樣點) | FEEDER | [5 empty] | 114 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | ES | KK26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK26_ES | KK26_ES (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/2BUS | KK27/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | 山上線 (KK27) CB |  |  |  | abbb | B2/S70_D1 | [8 empty] | 山頂SS.KK27_CB | KK27(11KV山上線) CB | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK27DS1 | KK27DS1 (非取樣點) | FEEDER | [5 empty] | 117 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK27DS2 | KK27DS2 (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | ES | KK27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK27_ES | KK27_ES (非取樣點) | FEEDER | [5 empty] | 119 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/2BUS | KK28/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | 玉井線 (KK28) CB |  |  |  | abdb | B2/S70_D1 | [8 empty] | 山頂SS.KK28_CB | KK28(11KV玉井線) CB | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK28DS1 | KK28DS1 (非取樣點) | FEEDER | [5 empty] | 121 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK28DS2 | KK28DS2 (非取樣點) | FEEDER | [5 empty] | 122 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | ES | KK28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK28_ES | KK28_ES (非取樣點) | FEEDER | [5 empty] | 123 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/2BUS | KK29/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | 山工線 (KK29) CB |  |  |  | abeb | B2/S70_D1 | [8 empty] | 山頂SS.KK29_CB | KK29(11KV山工線) CB | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK29DS1 | KK29DS1 (非取樣點) | FEEDER | [5 empty] | 125 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK29DS2 | KK29DS2 (非取樣點) | FEEDER | [5 empty] | 126 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | ES | KK29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK29_ES | KK29_ES (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbN | B/2BUS | KK30/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | 山30線 (KK30) CB |  |  |  | abfb | B2/S70_D1 | [8 empty] | 山頂SS.KK30_CB | KK30(11KV山30線) CB | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | D1 | (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK30DS1 | KK30DS1 (非取樣點) | FEEDER | [5 empty] | 129 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | D2 | (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK30DS2 | KK30DS2 (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | ES | KK30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.KK30_ES | KK30_ES (非取樣點) | FEEDER | [5 empty] | 131 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R | #1-#2 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #2- #1 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE |  |  |  |  | CDC | 132 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S | #1-#2 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #2- # TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE |  |  |  |  | CDC | 133 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T | #1-#2 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #2- # TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE |  |  |  |  | CDC | 134 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB | #1-#2 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BUS | B/2BUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #1-#2 TIE CB |  |  |  | zzzz | B2/S70_D1 | [8 empty] | 山頂SS.TIE1_CB | 11KV TIE1 CB | TIE |  |  |  |  | CDC | 135 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A | #1-#2 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1-#2 TIE 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.TIE1_51A | 11KV TIE1 51RY | TIE |  |  |  |  | CDC | 136 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA | #1-#2 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1-#2 TIE 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.TIE1_51NA | 11KV TIE1 51N RY | TIE |  |  |  |  | CDC | 137 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | #1-#2(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | [5 empty] | 138 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 139 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 140 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 141 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 142 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 143 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 144 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 145 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 146 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 147 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 148 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 149 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 150 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 151 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.5 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.500000
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #1 TR MWH(+) |  |  |  |  | B1/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 152 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 153 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 154 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 155 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 156 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2 TR MWH(+) |  |  |  |  | B1/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 157 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 158 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | #1TR 一次 (750) CB |  |  |  | aabb | B3/S70_D1 | [8 empty] | 山頂SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 159 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/2MTR |  |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | #2TR 一次 (760) CB |  |  |  | aaeb | B3/S70_D1 | [8 empty] | 山頂SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 160 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1TR 二次 (#1MT) CB |  |  |  | aaca | B2/S70_D1 | [8 empty] | 山頂SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 161 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2TR 二次 (#2MT) CB |  |  |  | abca | B2/S70_D1 | [8 empty] | 山頂SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 162 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次 (750) 51 RY(PHA) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 163 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 一次 (750) 51N RY(GDA) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 164 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 51Z RY(51ZA) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 165 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 87 RY(87A) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 166 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S(87T1S) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 167 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0065 | 1-0C-06 |  | 1-41 | #760 牧場線 81 RY(81A) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.#2MTR_81A/S | #760.牧場 81RY A/S | DTR |  |  |  |  | CDC | 168 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 一次 (760) 51 RY(PHA) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 169 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 一次 (760) 51N RY(GDA) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 170 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2TR 51Z RY(51ZA) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 171 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2TR 87 RY(87A) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 172 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2TR 87 LS1S(87T1S) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER |  |  |  |  | CDC | 173 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1TR 二次 (#1MT) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 174 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 175 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 176 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 177 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1TR OLTC A/M |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 178 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2TR 二次 (#2MT) 51 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 179 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 1-34-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 180 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 181 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 182 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2TR OLTC A/M |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 183 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0384 | 385 | 0042 | 1-38-00 | 1-38-01 | 1-2A | #1TR (751) ABS |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 184 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | B2 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0386 | 387 | 0043 | 1-38-02 | 1-38-03 | 1-2B | #2TR (761) ABS |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.761_ABS | 761(#2MTR) ABS | DTR |  |  |  |  | CDC | 185 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 186 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 187 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 機械保護動作(96PA) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 188 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 189 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1TR AC電源失效 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 190 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 191 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 192 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 193 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 194 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2TR AC電源失效 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 195 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0092 |  | 0008 | 1-0B-04 |  | 1-08 | 69KV (810) SC CB |  |  |  | aacb | B2/S70_A1 | [8 empty] | 山頂SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 196 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #1 11KV SC CB |  |  |  | aaab | B2/S70_D1 | [8 empty] | 山頂SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 197 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1SC Q-CTL A/M |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 198 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 199 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC CB |  |  |  | abgb | B2/S70_D1 | [8 empty] | 山頂SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 200 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2SC Q-CTL A/M |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 201 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 202 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0390 | 391 | 0039 | 1-38-06 | 1-38-07 | 1-27 | 69KV SC (811) ABS |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.811_ABS | 811(69KV #1SC) ABS | SC |  |  |  |  | CDC | 203 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 69KV (810) SC 51,51N RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 204 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 69KV (810) SC 27,59 RY |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 205 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 206 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 207 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 208 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 209 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.210_DS1 | 210_DS1 (非取樣點) | SC | [5 empty] | 210 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.220_DS1 | 220_DS1 (非取樣點) | SC | [5 empty] | 211 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S70_D1 | [8 empty] | 山頂SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 212 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S70_D1 | [8 empty] | 山頂SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 213 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S70_D1 | [8 empty] | 山頂SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 214 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S70_D1 | [8 empty] | 山頂SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 215 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 山頂SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 216 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 217 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 |  | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 218 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 219 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 220 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 221 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 開關場照明 C/T |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 222 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 223 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 224 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 225 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 226 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 227 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 228 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 229 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 230 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 231 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 232 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 233 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-37-00 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 234 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 1-37-01 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 235 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-37-02 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 236 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0371 |  |  | 1-37-03 |  |  | 博碼調變器故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 237 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 238 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 239 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 開關場照明 A/M |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 240 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 241 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV (810) SC 警報 |  |  |  |  | B2/S70_A1 | [8 empty] | 山頂SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 242 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 243 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 244 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次 (#1MT) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.#1_MAIN_51NA | #1MCB GDA | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 二次 (#2MT) 51N RY |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.#2_MAIN_51NA | #2MCB GDA | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S70_D1 | [8 empty] | 山頂SS.火災警報 | 火警 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0165 |  | 0087 | 1-14-05 |  | 1-57 | 全所故障指示器復歸點 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S70 | 山頂SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | [13 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S70_D1 | [8 empty] | 山頂SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 大庄線 (KK21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.大庄線KVAR | 11KV大庄線 KVAR | FEEDER |  |  |  |  | CDC | 256 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 大庄線 (KK21) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.大庄線A1 | 11KV大庄線 R相AMP | FEEDER |  |  |  |  | CDC | 257 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 大庄線 (KK21) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.大庄線A2 | 11KV大庄線 S相AMP | FEEDER |  |  |  |  | CDC | 258 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 大庄線 (KK21) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.大庄線A3 | 11KV大庄線 T相AMP | FEEDER |  |  |  |  | CDC | 259 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 大庄線 (KK21) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.大庄線A0 | 11KV大庄線 N相AMP | FEEDER |  |  |  |  | CDC | 260 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 山上線 (KK27) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山上線KVAR | 11KV山上線 KVAR | FEEDER |  |  |  |  | CDC | 261 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 山上線 (KK27) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山上線A1 | 11KV山上線 R相AMP | FEEDER |  |  |  |  | CDC | 262 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 山上線 (KK27) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山上線A2 | 11KV山上線 S相AMP | FEEDER |  |  |  |  | CDC | 263 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 山上線 (KK27) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山上線A3 | 11KV山上線 T相AMP | FEEDER |  |  |  |  | CDC | 264 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 山上線 (KK27) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山上線A0 | 11KV山上線 N相AMP | FEEDER |  |  |  |  | CDC | 265 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 山工線 (KK29) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山工線KVAR | 11KV山工線 KVAR | FEEDER |  |  |  |  | CDC | 266 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 山工線 (KK29) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山工線A1 | 11KV山工線 R相AMP | FEEDER |  |  |  |  | CDC | 267 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 山工線 (KK29) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山工線A2 | 11KV山工線 S相AMP | FEEDER |  |  |  |  | CDC | 268 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 山工線 (KK29) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山工線A3 | 11KV山工線 T相AMP | FEEDER |  |  |  |  | CDC | 269 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 山工線 (KK29) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.山工線A0 | 11KV山工線 N相AMP | FEEDER |  |  |  |  | CDC | 270 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 永安線 (KK24) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.永安線KVAR | 11KV永安線 KVAR | FEEDER |  |  |  |  | CDC | 271 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 永安線 (KK24) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.永安線A1 | 11KV永安線 R相AMP | FEEDER |  |  |  |  | CDC | 272 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 永安線 (KK24) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.永安線A2 | 11KV永安線 S相AMP | FEEDER |  |  |  |  | CDC | 273 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 永安線 (KK24) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.永安線A3 | 11KV永安線 T相AMP | FEEDER |  |  |  |  | CDC | 274 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 永安線 (KK24) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.永安線A0 | 11KV永安線 N相AMP | FEEDER |  |  |  |  | CDC | 275 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 玉井線 (KK28) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.玉井線KVAR | 11KV玉井線 KVAR | FEEDER |  |  |  |  | CDC | 276 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 玉井線 (KK28) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.玉井線A1 | 11KV玉井線 R相AMP | FEEDER |  |  |  |  | CDC | 277 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 玉井線 (KK28) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.玉井線A2 | 11KV玉井線 S相AMP | FEEDER |  |  |  |  | CDC | 278 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 玉井線 (KK28) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.玉井線A3 | 11KV玉井線 T相AMP | FEEDER |  |  |  |  | CDC | 279 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 玉井線 (KK28) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.玉井線A0 | 11KV玉井線 N相AMP | FEEDER |  |  |  |  | CDC | 280 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 那拔線 (KK26) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.那拔線KVAR | 11KV那拔線 KVAR | FEEDER |  |  |  |  | CDC | 281 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 那拔線 (KK26) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.那拔線A1 | 11KV那拔線 R相AMP | FEEDER |  |  |  |  | CDC | 282 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 那拔線 (KK26) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.那拔線A2 | 11KV那拔線 S相AMP | FEEDER |  |  |  |  | CDC | 283 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 那拔線 (KK26) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.那拔線A3 | 11KV那拔線 T相AMP | FEEDER |  |  |  |  | CDC | 284 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 那拔線 (KK26) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.那拔線A0 | 11KV那拔線 N相AMP | FEEDER |  |  |  |  | CDC | 285 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 牧場線 (KK23) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.牧場線KVAR | 11KV牧場線 KVAR | FEEDER |  |  |  |  | CDC | 286 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 牧場線 (KK23) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.牧場線A1 | 11KV牧場線 R相AMP | FEEDER |  |  |  |  | CDC | 287 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 牧場線 (KK23) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.牧場線A2 | 11KV牧場線 S相AMP | FEEDER |  |  |  |  | CDC | 288 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 牧場線 (KK23) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.牧場線A3 | 11KV牧場線 T相AMP | FEEDER |  |  |  |  | CDC | 289 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 牧場線 (KK23) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.牧場線A0 | 11KV牧場線 N相AMP | FEEDER |  |  |  |  | CDC | 290 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 南化線 (KK22) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南化線KVAR | 11KV南化線 KVAR | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 南化線 (KK22) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南化線A1 | 11KV南化線 R相AMP | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 南化線 (KK22) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南化線A2 | 11KV南化線 S相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 南化線 (KK22) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南化線A3 | 11KV南化線 T相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 南化線 (KK22) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南化線A0 | 11KV南化線 N相AMP | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 南醫線 (KK25) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南醫線KVAR | 11KV南醫線 KVAR | FEEDER |  |  |  |  | CDC | 296 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 南醫線 (KK25) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南醫線A1 | 11KV南醫線 R相AMP | FEEDER |  |  |  |  | CDC | 297 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 南醫線 (KK25) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南醫線A2 | 11KV南醫線 S相AMP | FEEDER |  |  |  |  | CDC | 298 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 南醫線 (KK25) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南醫線A3 | 11KV南醫線 T相AMP | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 南醫線 (KK25) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S70_D1 | [8 empty] | 山頂SS.南醫線A0 | 11KV南醫線 N相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S70_D1 | [8 empty] | 山頂SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 301 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 1BUS | #1BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0168 |  |  | 2-A8 |  |  | #1 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S70_D1 | [8 empty] | 山頂SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | [5 empty] | 302 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 11 | 11kV | 2BUS | #2BUS |  | V_S |  | INSERT | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0170 |  |  | 2-AA |  |  | #2 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S70_D1 | [8 empty] | 山頂SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS | [5 empty] | 303 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 11 | 11kV | 1BUS | #1BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | #1 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S70_D1 | [8 empty] | 山頂SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | [5 empty] | 304 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 11 | 11kV | 2BUS | #2BUS |  | V_T |  | INSERT | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0171 |  |  | 2-AB |  |  | #2 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S70_D1 | [8 empty] | 山頂SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS | [5 empty] | 305 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #1DTR 63Q |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 306 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #1DTR 96B1 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 307 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #1DTR 96B2 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 308 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #1DTR 96D |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 309 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #1DTR 96P |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 310 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2DTR 63Q |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | [5 empty] | 311 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2DTR 96B1 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | [5 empty] | 312 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2DTR 96B2 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | [5 empty] | 313 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2DTR 96D |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | [5 empty] | 314 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2DTR 96P |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | [5 empty] | 315 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | 大庄線 (KK21) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK21_LOA | 大庄線 復閉失敗閉鎖 | OTHER | [5 empty] | 316 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | 南化線 (KK22) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK22_LOA | 南化線 復閉失敗閉鎖 | OTHER | [5 empty] | 317 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | 牧場線 (KK23) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK23_LOA | 牧場線 復閉失敗閉鎖 | OTHER | [5 empty] | 318 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | 永安線 (KK24) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK24_LOA | 永安線 復閉失敗閉鎖 | OTHER | [5 empty] | 319 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | 南醫線 (KK25) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK25_LOA | 南醫線 復閉失敗閉鎖 | OTHER | [5 empty] | 320 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 那拔線 (KK26) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK26_LOA | 那拔線 復閉失敗閉鎖 | OTHER | [5 empty] | 321 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 山上線 (KK27) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK27_LOA | 山上線 復閉失敗閉鎖 | OTHER | [5 empty] | 322 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 玉井線 (KK28) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK28_LOA | 玉井線 復閉失敗閉鎖 | OTHER | [5 empty] | 323 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 山工線 (KK29) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK29_LOA | 山工線 復閉失敗閉鎖 | OTHER | [5 empty] | 324 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 山30線 (KK30) LOA |  |  |  |  | B2/S70_D1 | [8 empty] | 山頂SS.KK30_LOA | 山30線 復閉失敗閉鎖 | OTHER | [5 empty] | 325 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 326 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #1DTR 86A |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 327 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 328 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #2DTR 51ZLS |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | [5 empty] | 329 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | #2DTR 86A |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 330 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 331 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S70 | 山頂SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S70_D1 | [8 empty] | 山頂SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 332 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 大庄線 (KK21) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 333 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 南化線 (KK22) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 334 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 牧場線 (KK23) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 335 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 永安線 (KK24) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 336 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 南醫線 (KK25) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 337 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 那拔線 (KK26) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 338 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 山上線 (KK27) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 339 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 玉井線 (KK28) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 340 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 山工線 (KK29) KWH(+) |  |  |  |  | B2/S70_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 341 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S70 | 山頂SS | 11 | 11kV | KK21_KK22 | KK21_KK22 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK21/T1 | KK22/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK21_KK22_DS | KK21_KK22_DS (非取樣點) | FEEDER | [5 empty] | 342 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK22_KK23 | KK22_KK23 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK22/T1 | KK23/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK22_KK23_DS | KK22_KK23_DS (非取樣點) | FEEDER | [5 empty] | 343 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK24_KK25 | KK24_KK25 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK24/T1 | KK25/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK24_KK25_DS | KK24_KK25_DS (非取樣點) | FEEDER | [5 empty] | 344 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK26_KK27 | KK26_KK27 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK26/T1 | KK27/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK26_KK27_DS | KK26_KK27_DS (非取樣點) | FEEDER | [5 empty] | 345 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK27_KK28 | KK27_KK28 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK27/T1 | KK28/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK27_KK28_DS | KK27_KK28_DS (非取樣點) | FEEDER | [5 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | KK29_KK30 | KK29_KK30 |  | D1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | Bay1BbC | KK29/T1 | KK30/T1 | [12 empty] | no rule | B2/S70_D1 | [8 empty] | 山頂SS.KK29_KK30_DS | KK29_KK30_DS (非取樣點) | FEEDER | [5 empty] | 347 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 348 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S70_D1 | [8 empty] | 山頂SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 349 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S70 | 山頂SS | 0 |  | CalcPoint |  |  | Vbs1 | [9 empty] | B1/S70_D1 | [12 empty] | 山頂SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_1 | LG_69 | v_best_69_1 | OPRD1: S70/69/1BUS/V
S70 | 山頂SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S70_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: S70/0/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S70 | 山頂SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S70_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_5 | OPRD1: S70/11/M1/MW; OPRD2: S70/11/M2/MW; OPRD3: S70/69/610/MW; OPRD4: S70/69/620/MW; OPRD5: S70/69/630/MW
S70 | 山頂SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S70_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S70/0/CalcPoint/OPRN2_MW
S70 | 山頂SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S70_D1 | [17 empty] | none
S70 | 山頂SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S70_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S70/0/CalcPoint/OPRN1; OPRD2: S70/0/CalcPoint/OPRN2; OPRD3: S70/0/CalcPoint/PRFL_UL
S70 | 山頂SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S70_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S70/11/M1/MW; OPRD2: S70/11/M1/MVAR; OPRD3: S70/0/CalcPoint/Vbs1
S70 | 山頂SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S70_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S70/11/M2/MW; OPRD2: S70/11/M2/MVAR; OPRD3: S70/0/CalcPoint/Vbs1
S70 | 山頂SS | 69 | 69kV | 610 | 山上～山頂一路(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S70_A1 | [12 empty] | 山頂SS.610_AMP | 山上山頂一路 AMP | LINE69 | AMP_CAL | C12R0800 | amp_cal | OPRD1: S70/69/610/MW; OPRD2: S70/69/610/MVAR; OPRD3: S70/0/CalcPoint/Vbs1
S70 | 山頂SS | 69 | 69kV | 620 | 山上～山頂二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S70_A1 | [12 empty] | 山頂SS.620_AMP | 山上山頂二路 AMP | LINE69 | AMP_CAL | C12R0800 | amp_cal | OPRD1: S70/69/620/MW; OPRD2: S70/69/620/MVAR; OPRD3: S70/0/CalcPoint/Vbs1
S70 | 山頂SS | 69 | 69kV | 630 | 山頂～宏遠、東展線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S70_A1 | [12 empty] | 山頂SS.630_AMP | 宏遠線 AMP | LINE69 | AMP_CAL | C12R0800 | amp_cal | OPRD1: S70/69/630/MW; OPRD2: S70/69/630/MVAR; OPRD3: S70/0/CalcPoint/Vbs1
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S70_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 山頂SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S70/11/M1/MW; OPRD2: S70/11/M1/MVAR
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S70_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 山頂SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S70/11/M2/MW; OPRD2: S70/11/M2/MVAR
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S70_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S70//1MTR/MVA; OPRD2: 0
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S70_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S70//2MTR/MVA; OPRD2: 0
S70 | 山頂SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S70_D1 | [12 empty] | 山頂SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S70/11/M1/MW; OPRD2: S70/11/M1/MVAR
S70 | 山頂SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S70_D1 | [12 empty] | 山頂SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S70/11/M2/MW; OPRD2: S70/11/M2/MVAR
S70 | 山頂SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S70_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S70//1MTR/SupLocal; OPRD2: S70//1MTR/Tap Chan; OPRD3: NULL
S70 | 山頂SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S70_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S70//2MTR/SupLocal; OPRD2: S70//2MTR/Tap Chan; OPRD3: NULL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK21/I_R; OPRD3: S70/11/KK21/I_S; OPRD4: S70/11/KK21/I_T
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK22/I_R; OPRD3: S70/11/KK22/I_S; OPRD4: S70/11/KK22/I_T
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK23/I_R; OPRD3: S70/11/KK23/I_S; OPRD4: S70/11/KK23/I_T
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK24/I_R; OPRD3: S70/11/KK24/I_S; OPRD4: S70/11/KK24/I_T
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK25/I_R; OPRD3: S70/11/KK25/I_S; OPRD4: S70/11/KK25/I_T
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK26/I_R; OPRD3: S70/11/KK26/I_S; OPRD4: S70/11/KK26/I_T
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK27/I_R; OPRD3: S70/11/KK27/I_S; OPRD4: S70/11/KK27/I_T
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK28/I_R; OPRD3: S70/11/KK28/I_S; OPRD4: S70/11/KK28/I_T
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK29/I_R; OPRD3: S70/11/KK29/I_S; OPRD4: S70/11/KK29/I_T
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S70/11/KK30/I_R; OPRD3: S70/11/KK30/I_S; OPRD4: S70/11/KK30/I_T
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK21/kVA; OPRD2: S70/11/KK21/KVAR
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK22/kVA; OPRD2: S70/11/KK22/KVAR
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK23/kVA; OPRD2: S70/11/KK23/KVAR
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK24/kVA; OPRD2: S70/11/KK24/KVAR
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK25/kVA; OPRD2: S70/11/KK25/KVAR
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK26/kVA; OPRD2: S70/11/KK26/KVAR
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK27/kVA; OPRD2: S70/11/KK27/KVAR
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK28/kVA; OPRD2: S70/11/KK28/KVAR
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK29/kVA; OPRD2: S70/11/KK29/KVAR
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S70_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S70/11/KK30/kVA; OPRD2: S70/11/KK30/KVAR
S70 | 山頂SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S70_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S70/11/M1/MW; OPRD2: S70/11/M2/MW
S70 | 山頂SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S70_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S70/11/M1/MVAR; OPRD2: S70/11/M2/MVAR
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S70_D1 | [12 empty] | 山頂SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S70/11/210/CB; OPRD2: 6.9; OPRD3: 0
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S70_D1 | [12 empty] | 山頂SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S70/11/220/CB; OPRD2: 6.9; OPRD3: 0
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S70_A1 | [12 empty] | 山頂SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S70/69/810/CB; OPRD2: 69; OPRD3: 0
S70 | 山頂SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S70_D1 | [12 empty] | 山頂SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_8 |  | com_alarm_16 | OPRD1: S70//1MTR/96B1; OPRD2: S70//1MTR/TRA; OPRD3: S70//1MTR/63Q; OPRD4: S70//1MTR/96PA; OPRD5: S70//1MTR/87A; OPRD6: S70//1MTR/51ZA; OPRD7: S70//1MTR/96B2; OPRD8: S70//1MTR/96D; OPRD9: S70//2MTR/96B2; OPRD10: S70//2MTR/96D; OPRD11: S70//2MTR/63Q; OPRD12: S70//2MTR/96B1; OPRD13: S70//2MTR/87A; OPRD14: S70//2MTR/51ZA; OPRD15: S70//2MTR/96PA; OPRD16: S70//2MTR/TRA
S70 | 山頂SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S70_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S70//1MTR/TRF; OPRD2: S70//2MTR/TRF
S70 | 山頂SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/RTU/RTU_R_L
S70 | 山頂SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/StaDev/PSF
S70 | 山頂SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/StaDev/PMA
S70 | 山頂SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/StaDev/DCE
S70 | 山頂SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S70_D1 | [17 empty] | lamp2CC | OPRD1: S70/69/ComPoint/CBA
S70 | 山頂SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S70_D1 | [17 empty] | lamp2CC | OPRD1: S70/69/ComPoint/CBF
S70 | 山頂SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S70_D1 | [17 empty] | lamp2CC | OPRD1: S70/69/ComPoint/ABS_89A
S70 | 山頂SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/StaDev/DCA
S70 | 山頂SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S70_A1 | [17 empty] | lamp2CC | OPRD1: S70/0/StaDev/Fire
S70 | 山頂SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S70_D1 | [17 empty] | lamp2CC | OPRD1: S70/69/ComPoint/CFA
S70 | 山頂SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S70_D1 | [17 empty] | lamp2CC | OPRD1: S70/69/ComPoint/IRFA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S70 | 山頂SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S70/0/CalcPoint/Vbs1 |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | I | [25 empty] | ADCS_S | [8 empty] | 山頂SS.610_AMP | 山上山頂一路 AMP | LINE69 | S70/69/610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0800 | 720.000000 | 720.000000 | 800.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 山頂SS.620_AMP | 山上山頂二路 AMP | LINE69 | S70/69/620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0800 | 720.000000 | 720.000000 | 800.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 山頂SS.630_AMP | 宏遠線 AMP | LINE69 | S70/69/630/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0800 | 720.000000 | 720.000000 | 800.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S70 | 山頂SS | 0 |  |  |  |  | 大庄線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.大庄線KVA | 11KV大庄線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 大庄線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.大庄線KW | 11KV大庄線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山上線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山上線KVA | 11KV山上線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山上線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山上線KW | 11KV山上線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山工線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山工線KVA | 11KV山工線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山工線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山工線KW | 11KV山工線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 永安線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.永安線KVA | 11KV永安線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 永安線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.永安線KW | 11KV永安線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 玉井線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.玉井線KVA | 11KV玉井線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 玉井線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.玉井線KW | 11KV玉井線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 那拔線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.那拔線KVA | 11KV那拔線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 那拔線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.那拔線KW | 11KV那拔線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 牧場線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.牧場線KVA | 11KV牧場線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 牧場線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.牧場線KW | 11KV牧場線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 南化線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.南化線KVA | 11KV南化線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 南化線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.南化線KW | 11KV南化線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 南醫線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.南醫線KVA | 11KV南醫線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 南醫線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.南醫線KW | 11KV南醫線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S70//1MTR/MVA |  | MVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_PF | #1MTR 功率因素 | DTR | S70//1MTR/PF |  | RPDC_PF_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S70//2MTR/MVA |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_PF | #2MTR 功率因素 | DTR | S70//2MTR/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S70 | 山頂SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S70/11/210/MVAR |  | SC_CAL_11 |  |  | 28 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S70/11/220/MVAR |  | SC_CAL_11 |  |  | 29 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S70/69/810/MVAR |  | SC_CAL_69 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山30線KVA | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山30線KVA | 11KV山30線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 0 |  |  |  |  | 山30線KW | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.山30線KW | 11KV山30線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 69 | 69kV | 610_CB | 山上山頂一路(610_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.610_CB_4 | 610(山上山頂一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 33 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 620_CB | 山上山頂二路(620_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.620_CB_4 | 620(山上山頂二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 34 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 630_CB | 宏遠線(630_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.630_CB_4 | 630(宏遠線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 37 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 38 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_S | [8 empty] | 山頂SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 40 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 山頂SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S70/0/CalcPoint/SUBA |  | STATION_FAULT_8 |  |  | 41 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_2 |  |  | 43 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610_AMP | 山上山頂一路 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.610_AMP_A | 山上山頂一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 44 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | 610_AMP | 山上山頂一路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.610_AMP_4 | 山上山頂一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 45 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | 620_AMP | 山上山頂二路 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.620_AMP_A | 山上山頂二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | 620_AMP | 山上山頂二路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.620_AMP_4 | 山上山頂二路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | 630_AMP | 宏遠線 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.630_AMP_A | 宏遠線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | 630_AMP | 宏遠線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.630_AMP_4 | 宏遠線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 49 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 50 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 51 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 53 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 69 | 69kV | _IED_CFA | IED通訊故障 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_IED_CFA_A | 69KV IED通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | _IED_FA | IED故障 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_IED_FA_A | 69KV IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 山頂SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S70/0/RTU/ADCH1 |  |  |  | CDC | 57 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S70/0/RTU/ADCH2 |  |  |  | CDC | 58 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S70/0/RTU/ADCL1 |  |  |  | CDC | 59 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S70/0/RTU/ADCL2 |  |  |  | CDC | 60 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S70/69/1BUS/V |  |  |  | CDC | 61 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S70 | 山頂SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S70/11/1BUS/V_R |  |  |  | CDC | 62 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S70/11/2BUS/V_R |  |  |  | CDC | 63 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.610_MW | 山上山頂一路 MW | LINE69 | S70/69/610/MW |  |  |  | CDC | 64 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.610_MVAR | 山上山頂一路 MVAR | LINE69 | S70/69/610/MVAR |  |  |  | CDC | 65 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.620_MW | 山上山頂二路 MW | LINE69 | S70/69/620/MW |  |  |  | CDC | 66 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.620_MVAR | 山上山頂二路 MVAR | LINE69 | S70/69/620/MVAR |  |  |  | CDC | 67 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.630_MW | 宏遠線 MW | LINE69 | S70/69/630/MW |  |  |  | CDC | 68 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 山頂SS.630_MVAR | 宏遠線 MVAR | LINE69 | S70/69/630/MVAR |  |  |  | CDC | 69 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 大庄線 | 大庄線 |  | 大庄線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.大庄線KVAR | 11KV大庄線 KVAR | FEEDER | S70/11/KK21/KVAR |  |  |  | CDC | 70 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 大庄線 | 大庄線 |  | 大庄線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.大庄線A1 | 11KV大庄線 R相AMP | FEEDER | S70/11/KK21/I_R |  |  |  | CDC | 71 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 大庄線 | 大庄線 |  | 大庄線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.大庄線A2 | 11KV大庄線 S相AMP | FEEDER | S70/11/KK21/I_S |  |  |  | CDC | 72 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 大庄線 | 大庄線 |  | 大庄線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.大庄線A3 | 11KV大庄線 T相AMP | FEEDER | S70/11/KK21/I_T |  |  |  | CDC | 73 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 大庄線 | 大庄線 |  | 大庄線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.大庄線A0 | 11KV大庄線 N相AMP | FEEDER | S70/11/KK21/I_N |  |  |  | CDC | 74 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山上線 | 山上線 |  | 山上線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山上線KVAR | 11KV山上線 KVAR | FEEDER | S70/11/KK27/KVAR |  |  |  | CDC | 75 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山上線 | 山上線 |  | 山上線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山上線A1 | 11KV山上線 R相AMP | FEEDER | S70/11/KK27/I_R |  |  |  | CDC | 76 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山上線 | 山上線 |  | 山上線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山上線A2 | 11KV山上線 S相AMP | FEEDER | S70/11/KK27/I_S |  |  |  | CDC | 77 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山上線 | 山上線 |  | 山上線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山上線A3 | 11KV山上線 T相AMP | FEEDER | S70/11/KK27/I_T |  |  |  | CDC | 78 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山上線 | 山上線 |  | 山上線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山上線A0 | 11KV山上線 N相AMP | FEEDER | S70/11/KK27/I_N |  |  |  | CDC | 79 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山工線 | 山工線 |  | 山工線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山工線KVAR | 11KV山工線 KVAR | FEEDER | S70/11/KK29/KVAR |  |  |  | CDC | 80 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山工線 | 山工線 |  | 山工線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山工線A1 | 11KV山工線 R相AMP | FEEDER | S70/11/KK29/I_R |  |  |  | CDC | 81 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山工線 | 山工線 |  | 山工線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山工線A2 | 11KV山工線 S相AMP | FEEDER | S70/11/KK29/I_S |  |  |  | CDC | 82 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山工線 | 山工線 |  | 山工線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山工線A3 | 11KV山工線 T相AMP | FEEDER | S70/11/KK29/I_T |  |  |  | CDC | 83 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山工線 | 山工線 |  | 山工線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山工線A0 | 11KV山工線 N相AMP | FEEDER | S70/11/KK29/I_N |  |  |  | CDC | 84 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 永安線 | 永安線 |  | 永安線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.永安線KVAR | 11KV永安線 KVAR | FEEDER | S70/11/KK24/KVAR |  |  |  | CDC | 85 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 永安線 | 永安線 |  | 永安線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.永安線A1 | 11KV永安線 R相AMP | FEEDER | S70/11/KK24/I_R |  |  |  | CDC | 86 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 永安線 | 永安線 |  | 永安線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.永安線A2 | 11KV永安線 S相AMP | FEEDER | S70/11/KK24/I_S |  |  |  | CDC | 87 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 永安線 | 永安線 |  | 永安線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.永安線A3 | 11KV永安線 T相AMP | FEEDER | S70/11/KK24/I_T |  |  |  | CDC | 88 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 永安線 | 永安線 |  | 永安線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.永安線A0 | 11KV永安線 N相AMP | FEEDER | S70/11/KK24/I_N |  |  |  | CDC | 89 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 玉井線 | 玉井線 |  | 玉井線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.玉井線KVAR | 11KV玉井線 KVAR | FEEDER | S70/11/KK28/KVAR |  |  |  | CDC | 90 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 玉井線 | 玉井線 |  | 玉井線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.玉井線A1 | 11KV玉井線 R相AMP | FEEDER | S70/11/KK28/I_R |  |  |  | CDC | 91 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 玉井線 | 玉井線 |  | 玉井線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.玉井線A2 | 11KV玉井線 S相AMP | FEEDER | S70/11/KK28/I_S |  |  |  | CDC | 92 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 玉井線 | 玉井線 |  | 玉井線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.玉井線A3 | 11KV玉井線 T相AMP | FEEDER | S70/11/KK28/I_T |  |  |  | CDC | 93 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 玉井線 | 玉井線 |  | 玉井線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.玉井線A0 | 11KV玉井線 N相AMP | FEEDER | S70/11/KK28/I_N |  |  |  | CDC | 94 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 那拔線 | 那拔線 |  | 那拔線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.那拔線KVAR | 11KV那拔線 KVAR | FEEDER | S70/11/KK26/KVAR |  |  |  | CDC | 95 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 那拔線 | 那拔線 |  | 那拔線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.那拔線A1 | 11KV那拔線 R相AMP | FEEDER | S70/11/KK26/I_R |  |  |  | CDC | 96 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 那拔線 | 那拔線 |  | 那拔線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.那拔線A2 | 11KV那拔線 S相AMP | FEEDER | S70/11/KK26/I_S |  |  |  | CDC | 97 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 那拔線 | 那拔線 |  | 那拔線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.那拔線A3 | 11KV那拔線 T相AMP | FEEDER | S70/11/KK26/I_T |  |  |  | CDC | 98 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 那拔線 | 那拔線 |  | 那拔線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.那拔線A0 | 11KV那拔線 N相AMP | FEEDER | S70/11/KK26/I_N |  |  |  | CDC | 99 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 牧場線 | 牧場線 |  | 牧場線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.牧場線KVAR | 11KV牧場線 KVAR | FEEDER | S70/11/KK23/KVAR |  |  |  | CDC | 100 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 牧場線 | 牧場線 |  | 牧場線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.牧場線A1 | 11KV牧場線 R相AMP | FEEDER | S70/11/KK23/I_R |  |  |  | CDC | 101 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 牧場線 | 牧場線 |  | 牧場線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.牧場線A2 | 11KV牧場線 S相AMP | FEEDER | S70/11/KK23/I_S |  |  |  | CDC | 102 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 牧場線 | 牧場線 |  | 牧場線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.牧場線A3 | 11KV牧場線 T相AMP | FEEDER | S70/11/KK23/I_T |  |  |  | CDC | 103 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 牧場線 | 牧場線 |  | 牧場線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.牧場線A0 | 11KV牧場線 N相AMP | FEEDER | S70/11/KK23/I_N |  |  |  | CDC | 104 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南化線 | 南化線 |  | 南化線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南化線KVAR | 11KV南化線 KVAR | FEEDER | S70/11/KK22/KVAR |  |  |  | CDC | 105 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南化線 | 南化線 |  | 南化線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南化線A1 | 11KV南化線 R相AMP | FEEDER | S70/11/KK22/I_R |  |  |  | CDC | 106 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南化線 | 南化線 |  | 南化線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南化線A2 | 11KV南化線 S相AMP | FEEDER | S70/11/KK22/I_S |  |  |  | CDC | 107 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南化線 | 南化線 |  | 南化線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南化線A3 | 11KV南化線 T相AMP | FEEDER | S70/11/KK22/I_T |  |  |  | CDC | 108 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南化線 | 南化線 |  | 南化線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南化線A0 | 11KV南化線 N相AMP | FEEDER | S70/11/KK22/I_N |  |  |  | CDC | 109 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南醫線 | 南醫線 |  | 南醫線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南醫線KVAR | 11KV南醫線 KVAR | FEEDER | S70/11/KK25/KVAR |  |  |  | CDC | 110 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南醫線 | 南醫線 |  | 南醫線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南醫線A1 | 11KV南醫線 R相AMP | FEEDER | S70/11/KK25/I_R |  |  |  | CDC | 111 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南醫線 | 南醫線 |  | 南醫線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南醫線A2 | 11KV南醫線 S相AMP | FEEDER | S70/11/KK25/I_S |  |  |  | CDC | 112 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南醫線 | 南醫線 |  | 南醫線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南醫線A3 | 11KV南醫線 T相AMP | FEEDER | S70/11/KK25/I_T |  |  |  | CDC | 113 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 南醫線 | 南醫線 |  | 南醫線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.南醫線A0 | 11KV南醫線 N相AMP | FEEDER | S70/11/KK25/I_N |  |  |  | CDC | 114 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | _TIE1 | TIE1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11KV_TIE1_A1 | 11KV TIE1 R相AMP | TIE | S70/11/TIE1/I_R |  |  |  | CDC | 115 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | _TIE1 | TIE1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11KV_TIE1_A2 | 11KV TIE1 S相AMP | TIE | S70/11/TIE1/I_S |  |  |  | CDC | 116 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | _TIE1 | TIE1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11KV_TIE1_A3 | 11KV TIE1 T相AMP | TIE | S70/11/TIE1/I_T |  |  |  | CDC | 117 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_MW | #1MTR二次側 MW | DTR | S70/11/M1/MW |  |  |  | CDC | 118 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S70/11/M1/MVAR |  |  |  | CDC | 119 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S70/11/M1/I_R |  |  |  | CDC | 120 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S70/11/M1/I_S |  |  |  | CDC | 121 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S70/11/M1/I_T |  |  |  | CDC | 122 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_OIL | #1MTR 油溫 | DTR | S70//1MTR/OilTemp |  |  |  | CDC | 123 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_COIL | #1MTR 線溫 | DTR | S70//1MTR/CoilTemp |  |  |  | CDC | 124 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S70//1MTR/TapPosMv |  |  |  | CDC | 125 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.500000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_MW | #2MTR二次側 MW | DTR | S70/11/M2/MW |  |  |  | CDC | 126 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S70/11/M2/MVAR |  |  |  | CDC | 127 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S70/11/M2/I_R |  |  |  | CDC | 128 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S70/11/M2/I_S |  |  |  | CDC | 129 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S70/11/M2/I_T |  |  |  | CDC | 130 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_OIL | #2MTR 油溫 | DTR | S70//2MTR/OilTemp |  |  |  | CDC | 131 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_COIL | #2MTR 線溫 | DTR | S70//2MTR/CoilTemp |  |  |  | CDC | 132 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S70//2MTR/TapPosMv |  |  |  | CDC | 133 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S70 | 山頂SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.直流電源電壓 | 直流電源電壓 | OTHER | S70/0/StaDev/DCV |  |  |  | CDC | 134 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山30線 | 山30線 |  | 山30線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山30線KVAR | 11KV山30線 KVAR | FEEDER | S70/11/KK30/KVAR |  |  |  | CDC | 135 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山30線 | 山30線 |  | 山30線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山30線A1 | 11KV山30線 R相AMP | FEEDER | S70/11/KK30/I_R |  |  |  | CDC | 136 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山30線 | 山30線 |  | 山30線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山30線A2 | 11KV山30線 S相AMP | FEEDER | S70/11/KK30/I_S |  |  |  | CDC | 137 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山30線 | 山30線 |  | 山30線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山30線A3 | 11KV山30線 T相AMP | FEEDER | S70/11/KK30/I_T |  |  |  | CDC | 138 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 11 | 11kV | 山30線 | 山30線 |  | 山30線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.山30線A0 | 11KV山30線 N相AMP | FEEDER | S70/11/KK30/I_N |  |  |  | CDC | 139 | GENERICAIPoint | SS412_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S70 | 山頂SS | 0 |  | 11S11BUS | 11S1 |  | V | [17 empty] | 2-A8 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11S1#1BUS_KV | 11S1 #1BUS KV | BUS | S70/11/1BUS/V_S |  |  |  | CDC | 140 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 0 |  | 11S12BUS | 11S1 |  | V | [17 empty] | 2-AA | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS | S70/11/2BUS/V_S |  |  |  | CDC | 141 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 0 |  | 11T11BUS | 11T1 |  | V | [17 empty] | 2-A9 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11T1#1BUS_KV | 11T1 #1BUS KV | BUS | S70/11/1BUS/V_T |  |  |  | CDC | 142 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 0 |  | 11T12BUS | 11T1 |  | V | [17 empty] | 2-AB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 山頂SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS | S70/11/2BUS/V_T |  |  |  | CDC | 143 | GENERICAIPoint | SS412_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.610_PHA | 山上山頂一路(610) 相間RY | LINE69 | S70/69/610/PHA |  |  |  | CDC | 144 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.610_GDA | 山上山頂一路(610) 接地RY | LINE69 | S70/69/610/GDA |  |  |  | CDC | 145 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | CB | [17 empty] | 1-09-04 |  | 1-04 | [5 empty] | 69KV_S | [8 empty] | 山頂SS.610_CB | 610(山上山頂一路) CB | LINE69 | S70/69/610/CB |  |  |  | CDC | 146 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | DS1 | 611 | [16 empty] | 1-39-10 | 1-39-11 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 山頂SS.611_DS | 611(山上山頂一路) DS | LINE69 | S70/69/610/DS1 |  |  |  | CDC | 147 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | DS2 | 612 | [16 empty] | 1-39-12 | 1-39-13 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 山頂SS.612_DS | 612(山上山頂一路) DS | LINE69 | S70/69/610/DS2 |  |  |  | CDC | 148 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | E2 | 612E | [16 empty] | 1-39-14 | 1-39-15 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 山頂SS.612E_ES | 612E(山上山頂一路) ES | LINE69 | S70/69/610/ES2 |  |  |  | CDC | 149 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.620_PHA | 山上山頂二路(620) 相間RY | LINE69 | S70/69/620/PHA |  |  |  | CDC | 150 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.620_GDA | 山上山頂二路(620) 接地RY | LINE69 | S70/69/620/GDA |  |  |  | CDC | 151 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | CB | [17 empty] | 1-08-04 |  | 1-02 | [5 empty] | 69KV_S | [8 empty] | 山頂SS.620_CB | 620(山上山頂二路) CB | LINE69 | S70/69/620/CB |  |  |  | CDC | 152 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | ABS1 | 621 | [16 empty] | 1-38-14 | 1-38-15 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.621_ABS | 621(山上山頂二路) ABS | LINE69 | S70/69/620/ABS1 |  |  |  | CDC | 153 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | ABS2 | 622 | [16 empty] | 1-39-00 | 1-39-01 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.622_ABS | 622(山上山頂二路) ABS | LINE69 | S70/69/620/ABS2 |  |  |  | CDC | 154 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | E2 | 622E | [16 empty] | 1-39-02 | 1-39-03 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.622E_ES | 622E(山上山頂二路) ES | LINE69 | S70/69/620/ES2 |  |  |  | CDC | 155 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | PHA | [17 empty] | 1-09-02 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.630_PHA | 宏遠線(630) 相間RY | LINE69 | S70/69/630/PHA |  |  |  | CDC | 156 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.630_GDA | 宏遠線(630) 接地RY | LINE69 | S70/69/630/GDA |  |  |  | CDC | 157 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | 85A | [17 empty] | 1-09-01 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.630_85A | 宏遠線(630) 85RY | LINE69 | S70/69/630/85A |  |  |  | CDC | 158 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | 74A | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 山頂SS.630_74A | 宏遠線(630) 74RY | LINE69 | S70/69/630/74A |  |  |  | CDC | 159 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | 85UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | ADCS_S | [8 empty] | 山頂SS.630_85UL | 宏遠線(630) 85RY U/L | LINE69 | S70/69/630/85UL |  |  |  | CDC | 160 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | CB | [17 empty] | 1-09-00 |  | 1-03 | [5 empty] | 69KV_S | [8 empty] | 山頂SS.630_CB | 630(宏遠線) CB | LINE69 | S70/69/630/CB |  |  |  | CDC | 161 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | 81AS | [17 empty] | 1-00-00 |  | 1-11 | [5 empty] | 69KV_S | [8 empty] | 山頂SS.630_81A/S | (630) 81RY A/S | LINE69 | S70/69/630/81AS |  |  |  | CDC | 162 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | ABS1 | 631 | [16 empty] | 1-39-04 | 1-39-05 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.631_ABS | 631(宏遠線) ABS | LINE69 | S70/69/630/ABS1 |  |  |  | CDC | 163 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | ABS2 | 632 | [16 empty] | 1-39-06 | 1-39-07 | 1-19 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.632_ABS | 632(宏遠線) ABS | LINE69 | S70/69/630/ABS2 |  |  |  | CDC | 164 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | E2 | 632E | [16 empty] | 1-39-08 | 1-39-09 | 1-1A | [5 empty] | ADCS_S | [8 empty] | 山頂SS.632E_ES | 632E(宏遠線) ES | LINE69 | S70/69/630/ES2 |  |  |  | CDC | 165 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_PHA | 11KV大庄線(KK21) 相間RY | FEEDER | S70/11/KK21/PHA |  |  |  | CDC | 166 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_GDA | 11KV大庄線(KK21) 接地RY | FEEDER | S70/11/KK21/GDA |  |  |  | CDC | 167 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_79UL | 11KV大庄線(KK21) 79RY U/L | FEEDER | S70/11/KK21/79UL |  |  |  | CDC | 168 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK21 | 大庄線(KK21) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_ADJ | 11KV大庄線(KK21) LCO分流器 U/L | FEEDER | S70/11/KK21/ADJ |  |  |  | CDC | 169 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK21 | KK21(11KV大庄線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_CB | KK21(11KV大庄線) CB | FEEDER | S70/11/KK21/CB |  |  |  | CDC | 170 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_PHA | 11KV南化線(KK22) 相間RY | FEEDER | S70/11/KK22/PHA |  |  |  | CDC | 171 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_GDA | 11KV南化線(KK22) 接地RY | FEEDER | S70/11/KK22/GDA |  |  |  | CDC | 172 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_79UL | 11KV南化線(KK22) 79RY U/L | FEEDER | S70/11/KK22/79UL |  |  |  | CDC | 173 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK22 | 南化線(KK22) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_ADJ | 11KV南化線(KK22) LCO分流器 U/L | FEEDER | S70/11/KK22/ADJ |  |  |  | CDC | 174 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK22 | KK22(11KV南化線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_CB | KK22(11KV南化線) CB | FEEDER | S70/11/KK22/CB |  |  |  | CDC | 175 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_PHA | 11KV牧場線(KK23) 相間RY | FEEDER | S70/11/KK23/PHA |  |  |  | CDC | 176 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_GDA | 11KV牧場線(KK23) 接地RY | FEEDER | S70/11/KK23/GDA |  |  |  | CDC | 177 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_79UL | 11KV牧場線(KK23) 79RY U/L | FEEDER | S70/11/KK23/79UL |  |  |  | CDC | 178 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK23 | 牧場線(KK23) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_ADJ | 11KV牧場線(KK23) LCO分流器 U/L | FEEDER | S70/11/KK23/ADJ |  |  |  | CDC | 179 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK23 | KK23(11KV牧場線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_CB | KK23(11KV牧場線) CB | FEEDER | S70/11/KK23/CB |  |  |  | CDC | 180 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_PHA | 11KV永安線(KK24) 相間RY | FEEDER | S70/11/KK24/PHA |  |  |  | CDC | 181 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_GDA | 11KV永安線(KK24) 接地RY | FEEDER | S70/11/KK24/GDA |  |  |  | CDC | 182 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_79UL | 11KV永安線(KK24) 79RY U/L | FEEDER | S70/11/KK24/79UL |  |  |  | CDC | 183 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK24 | 永安線(KK24) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_ADJ | 11KV永安線(KK24) LCO分流器 U/L | FEEDER | S70/11/KK24/ADJ |  |  |  | CDC | 184 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK24 | KK24(11KV永安線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_CB | KK24(11KV永安線) CB | FEEDER | S70/11/KK24/CB |  |  |  | CDC | 185 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_PHA | 11KV南醫線(KK25) 相間RY | FEEDER | S70/11/KK25/PHA |  |  |  | CDC | 186 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_GDA | 11KV南醫線(KK25) 接地RY | FEEDER | S70/11/KK25/GDA |  |  |  | CDC | 187 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_79UL | 11KV南醫線(KK25) 79RY U/L | FEEDER | S70/11/KK25/79UL |  |  |  | CDC | 188 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK25 | 南醫線(KK25) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_ADJ | 11KV南醫線(KK25) LCO分流器 U/L | FEEDER | S70/11/KK25/ADJ |  |  |  | CDC | 189 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK25 | KK25(11KV南醫線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_CB | KK25(11KV南醫線) CB | FEEDER | S70/11/KK25/CB |  |  |  | CDC | 190 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_PHA | 11KV那拔線(KK26) 相間RY | FEEDER | S70/11/KK26/PHA |  |  |  | CDC | 191 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_GDA | 11KV那拔線(KK26) 接地RY | FEEDER | S70/11/KK26/GDA |  |  |  | CDC | 192 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_79UL | 11KV那拔線(KK26) 79RY U/L | FEEDER | S70/11/KK26/79UL |  |  |  | CDC | 193 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK26 | 那拔線(KK26) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_ADJ | 11KV那拔線(KK26) LCO分流器 U/L | FEEDER | S70/11/KK26/ADJ |  |  |  | CDC | 194 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK26 | KK26(11KV那拔線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_CB | KK26(11KV那拔線) CB | FEEDER | S70/11/KK26/CB |  |  |  | CDC | 195 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_PHA | 11KV山上線(KK27) 相間RY | FEEDER | S70/11/KK27/PHA |  |  |  | CDC | 196 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_GDA | 11KV山上線(KK27) 接地RY | FEEDER | S70/11/KK27/GDA |  |  |  | CDC | 197 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_79UL | 11KV山上線(KK27) 79RY U/L | FEEDER | S70/11/KK27/79UL |  |  |  | CDC | 198 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK27 | 山上線(KK27) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_ADJ | 11KV山上線(KK27) LCO分流器 U/L | FEEDER | S70/11/KK27/ADJ |  |  |  | CDC | 199 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK27 | KK27(11KV山上線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_CB | KK27(11KV山上線) CB | FEEDER | S70/11/KK27/CB |  |  |  | CDC | 200 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_PHA | 11KV玉井線(KK28) 相間RY | FEEDER | S70/11/KK28/PHA |  |  |  | CDC | 201 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_GDA | 11KV玉井線(KK28) 接地RY | FEEDER | S70/11/KK28/GDA |  |  |  | CDC | 202 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_79UL | 11KV玉井線(KK28) 79RY U/L | FEEDER | S70/11/KK28/79UL |  |  |  | CDC | 203 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK28 | 玉井線(KK28) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_ADJ | 11KV玉井線(KK28) LCO分流器 U/L | FEEDER | S70/11/KK28/ADJ |  |  |  | CDC | 204 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK28 | KK28(11KV玉井線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_CB | KK28(11KV玉井線) CB | FEEDER | S70/11/KK28/CB |  |  |  | CDC | 205 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_PHA | 11KV山工線(KK29) 相間RY | FEEDER | S70/11/KK29/PHA |  |  |  | CDC | 206 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_GDA | 11KV山工線(KK29) 接地RY | FEEDER | S70/11/KK29/GDA |  |  |  | CDC | 207 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_79UL | 11KV山工線(KK29) 79RY U/L | FEEDER | S70/11/KK29/79UL |  |  |  | CDC | 208 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK29 | 山工線(KK29) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_ADJ | 11KV山工線(KK29) LCO分流器 U/L | FEEDER | S70/11/KK29/ADJ |  |  |  | CDC | 209 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK29 | KK29(11KV山工線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_CB | KK29(11KV山工線) CB | FEEDER | S70/11/KK29/CB |  |  |  | CDC | 210 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_PHA | 11KV山30線(KK30) 相間RY | FEEDER | S70/11/KK30/PHA |  |  |  | CDC | 211 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_GDA | 11KV山30線(KK30) 接地RY | FEEDER | S70/11/KK30/GDA |  |  |  | CDC | 212 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_79UL | 11KV山30線(KK30) 79RY U/L | FEEDER | S70/11/KK30/79UL |  |  |  | CDC | 213 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 11 | 11kV | KK30 | 山30線(KK30) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_ADJ | 11KV山30線(KK30) LCO分流器 U/L | FEEDER | S70/11/KK30/ADJ |  |  |  | CDC | 214 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S70 | 山頂SS | 11 | 11kV | KK30 | KK30(11KV山30線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_CB | KK30(11KV山30線) CB | FEEDER | S70/11/KK30/CB |  |  |  | CDC | 215 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE1 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.TIE1_CB | 11KV TIE1 CB | TIE | S70/11/TIE1/CB |  |  |  | CDC | 216 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE1 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.TIE1_51A | 11KV TIE1 51RY | TIE | S70/11/TIE1/51A |  |  |  | CDC | 217 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | TIE1 | TIE1 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.TIE1_51NA | 11KV TIE1 51N RY | TIE | S70/11/TIE1/51NA |  |  |  | CDC | 218 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.750_CB | 750(#1MTR) CB | DTR | S70/69/750/CB |  |  |  | CDC | 219 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.1M_CB | 1M(#1MTR) CB | DTR | S70/11/M1/CB |  |  |  | CDC | 220 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_51A | #1MTR 51RY | DTR | S70/69/750/51A |  |  |  | CDC | 221 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_51NA | #1MTR 51N RY | DTR | S70/69/750/51NA |  |  |  | CDC | 222 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S70//1MTR/51ZA |  |  |  | CDC | 223 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_87A | #1MTR 87RY | DTR | S70//1MTR/87A |  |  |  | CDC | 224 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S70/11/M1/51A |  |  |  | CDC | 225 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_TRA | #1MTR 重故障 | DTR | S70//1MTR/TRA |  |  |  | CDC | 226 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S70//1MTR/TRF |  |  |  | CDC | 227 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S70//1MTR/SupLocal |  |  |  | CDC | 228 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S70//1MTR/Tap Chan |  |  |  | CDC | 229 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S70 | 山頂SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.751_ABS | 751(#1MTR) ABS | DTR | S70/69/750/ABS1 |  |  |  | CDC | 230 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S70//1MTR/OLTC_DLY |  |  |  | CDC | 231 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S70//1MTR/AC_Fault |  |  |  | CDC | 232 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.760_CB | 760(#2MTR) CB | DTR | S70/69/760/CB |  |  |  | CDC | 233 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.2M_CB | 2M(#2MTR) CB | DTR | S70/11/M2/CB |  |  |  | CDC | 234 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_51A | #2MTR 51RY | DTR | S70/69/760/51A |  |  |  | CDC | 235 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_51NA | #2MTR 51N RY | DTR | S70/69/760/51NA |  |  |  | CDC | 236 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S70//2MTR/51ZA |  |  |  | CDC | 237 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_87A | #2MTR 87RY | DTR | S70//2MTR/87A |  |  |  | CDC | 238 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #760.牧場 |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_81A/S | #760.牧場 81RY A/S | DTR | S70/69/750/81AS |  |  |  | CDC | 239 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S70 | 山頂SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S70/11/M2/51A |  |  |  | CDC | 240 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_TRA | #2MTR 重故障 | DTR | S70//2MTR/TRA |  |  |  | CDC | 241 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S70//2MTR/TRF |  |  |  | CDC | 242 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S70//2MTR/SupLocal |  |  |  | CDC | 243 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S70//2MTR/Tap Chan |  |  |  | CDC | 244 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S70 | 山頂SS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-38-02 | 1-38-03 | 1-2B | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.761_ABS | 761(#2MTR) ABS | DTR | S70/69/760/ABS1 |  |  |  | CDC | 245 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S70//2MTR/OLTC_DLY |  |  |  | CDC | 246 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S70//2MTR/AC_Fault |  |  |  | CDC | 247 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_CB | 210(11KV #1SC) CB | SC | S70/11/210/CB |  |  |  | CDC | 248 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S70/11/210/SC_A_M |  |  |  | CDC | 249 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_SCA | 11KV #1SC 51,51N RY | SC | S70/11/210/SCA |  |  |  | CDC | 250 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S70/11/210/UVA |  |  |  | CDC | 251 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_CB | 220(11KV #2SC) CB | SC | S70/11/220/CB |  |  |  | CDC | 252 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S70/11/220/SC_A_M |  |  |  | CDC | 253 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_SCA | 11KV #2SC 51,51N RY | SC | S70/11/220/SCA |  |  |  | CDC | 254 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S70/11/220/UVA |  |  |  | CDC | 255 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-04 |  | 1-08 | [5 empty] | 69KV_S | [8 empty] | 山頂SS.810_CB | 810(69KV #1SC) CB | SC | S70/69/810/CB |  |  |  | CDC | 256 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | ABS1 | 811 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | ADCS_S | [8 empty] | 山頂SS.811_ABS | 811(69KV #1SC) ABS | SC | S70/69/810/ABS1 |  |  |  | CDC | 257 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.810_SCA | 69KV #1SC 51,51N RY | SC | S70/69/810/SCA |  |  |  | CDC | 258 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-06 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.810_OUVA | 69KV #1SC 27,59RY | SC | S70/69/810/UVA |  |  |  | CDC | 259 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 山頂SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S70/69/1BUS/BUS_VUA |  |  |  | CDC | 260 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S70/11/ComPoint/CBA |  |  |  | CDC | 261 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S70/11/ComPoint/CBF |  |  |  | CDC | 262 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S70/69/ComPoint/ABS_89A |  |  |  | CDC | 263 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S70/69/ComPoint/CBA |  |  |  | CDC | 264 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S70/69/ComPoint/CBF |  |  |  | CDC | 265 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S70/0/RTU/RTU_R_L |  |  |  | CDC | 266 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S70 | 山頂SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.TEST_CB | TEST CB | OTHER | S70/0/RTU/Test_CB |  |  |  | CDC | 267 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S70/0/StaDev/PSF |  |  |  | CDC | 268 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S70/0/StaDev/ACB1 |  |  |  | CDC | 269 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S70 | 山頂SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S70/0/StaDev/ACB2 |  |  |  | CDC | 270 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S70 | 山頂SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S70/0/StaDev/STUV |  |  |  | CDC | 271 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.直流充電機故障 | 直流充電機故障 | OTHER | S70/0/StaDev/CHG1 |  |  |  | CDC | 272 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S70/0/StaDev/DCA |  |  |  | CDC | 273 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S70/0/StaDev/DCE |  |  |  | CDC | 274 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S70/0/StaDev/OilLeak |  |  |  | CDC | 275 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S70/0/StaDev/5A5Other |  |  |  | CDC | 276 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S70/0/StaDev/6A5Other |  |  |  | CDC | 277 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S70/0/StaDev/7A5Other |  |  |  | CDC | 278 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S70/0/StaDev/CHG2 |  |  |  | CDC | 279 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S70/0/StaDev/CommACF |  |  |  | CDC | 280 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S70/0/StaDev/Door1 |  |  |  | CDC | 281 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S70 | 山頂SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S70/0/StaDev/Lights1 |  |  |  | CDC | 282 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S70 | 山頂SS | 0 |  | 1_MAIN | #1MCB |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1_MAIN_51NA | #1MCB GDA | OTHER | S70/11/M1/51NA |  |  |  | CDC | 283 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2_MAIN | #2MCB |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2_MAIN_51NA | #2MCB GDA | OTHER | S70/11/M2/51NA |  |  |  | CDC | 284 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.69KVSC警報 | 69KVSC警報 | OTHER | S70/69/810/60A |  |  |  | CDC | 285 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.RTU_DC故障 | RTU DC故障 | OTHER | S70/0/RTU/DCA |  |  |  | CDC | 286 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.水氣霧故障 | 水氣霧故障 | OTHER | S70/0/StaDev/2A5Other |  |  |  | CDC | 287 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.水氣霧警報 | 水氣霧警報 | OTHER | S70/0/StaDev/3A5Other |  |  |  | CDC | 288 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.火災警報 | 火警 | OTHER | S70/0/StaDev/Fire |  |  |  | CDC | 289 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.安全監控 | 保全設定 | OTHER | S70/0/StaDev/1A5Other |  |  |  | CDC | 290 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.門禁小門 | 門禁小門 | OTHER | S70/0/StaDev/Door2 |  |  |  | CDC | 291 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S70/0/StaDev/Lights |  |  |  | CDC | 292 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-05 |  | 1-57 | [5 empty] | DDCS4_2 | [8 empty] | 山頂SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S70/0/StaDev/4A5Other |  |  |  | CDC | 293 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S70 | 山頂SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.11KV_IED_FA | 11KV IED故障 | OTHER | S70/11/ComPoint/IRFA |  |  |  | CDC | 294 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S70/69/ComPoint/CFA |  |  |  | CDC | 295 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 山頂SS.69KV_IED_FA | 69KV IED故障 | OTHER | S70/69/ComPoint/IRFA |  |  |  | CDC | 296 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.81RY_IED_FA | 低頻IED故障 | OTHER | S70/0/StaDev/81A_RYFA |  |  |  | CDC | 297 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.PM_CFA | PM通訊故障 | OTHER | S70/0/StaDev/PMA |  |  |  | CDC | 298 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S70//1MTR/63Q |  |  |  | CDC | 299 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S70//1MTR/96B1 |  |  |  | CDC | 300 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S70//1MTR/96B2 |  |  |  | CDC | 301 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S70//1MTR/96D |  |  |  | CDC | 302 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S70//1MTR/96P |  |  |  | CDC | 303 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S70//2MTR/63Q |  |  |  | CDC | 304 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S70//2MTR/96B1 |  |  |  | CDC | 305 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S70//2MTR/96B2 |  |  |  | CDC | 306 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S70//2MTR/96D |  |  |  | CDC | 307 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S70//2MTR/96P |  |  |  | CDC | 308 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.變電所低水位 | 變電所低水位 | OTHER | S70/0/StaDev/Water1 |  |  |  | CDC | 309 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.變電所高水位 | 變電所高水位 | OTHER | S70/0/StaDev/Water2 |  |  |  | CDC | 310 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 620 | 山上山頂二路(620) |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.620_87A | 620山上山頂二路87RY | OTHER | S70/69/620/87A |  |  |  | CDC | 311 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 620 | 山上山頂二路(620) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_S | [8 empty] | 山頂SS.620_87UL | 620山上山頂二路87RY UL | OTHER | S70/69/620/87UL |  |  |  | CDC | 312 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 610 | 山上山頂一路(610) |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 69KV_S | [8 empty] | 山頂SS.610_87A | 610山上山頂一路87RY | OTHER | S70/69/610/87A |  |  |  | CDC | 313 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 610 | 山上山頂一路(610) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0C | [5 empty] | ADCS_S | [8 empty] | 山頂SS.610_87UL | 610山上山頂一路87RY UL | OTHER | S70/69/610/87UL |  |  |  | CDC | 314 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S70//1MTR/96PA |  |  |  | CDC | 315 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S70//2MTR/96PA |  |  |  | CDC | 316 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK21 | 大庄線 |  | LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_LOA | 大庄線 復閉失敗閉鎖 | OTHER | S70/11/KK21/LOA |  |  |  | CDC | 317 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK22 | 南化線 |  | LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_LOA | 南化線 復閉失敗閉鎖 | OTHER | S70/11/KK22/LOA |  |  |  | CDC | 318 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK23 | 牧場線 |  | LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_LOA | 牧場線 復閉失敗閉鎖 | OTHER | S70/11/KK23/LOA |  |  |  | CDC | 319 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK24 | 永安線 |  | LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_LOA | 永安線 復閉失敗閉鎖 | OTHER | S70/11/KK24/LOA |  |  |  | CDC | 320 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK25 | 南醫線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_LOA | 南醫線 復閉失敗閉鎖 | OTHER | S70/11/KK25/LOA |  |  |  | CDC | 321 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK26 | 那拔線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_LOA | 那拔線 復閉失敗閉鎖 | OTHER | S70/11/KK26/LOA |  |  |  | CDC | 322 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK27 | 山上線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_LOA | 山上線 復閉失敗閉鎖 | OTHER | S70/11/KK27/LOA |  |  |  | CDC | 323 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK28 | 玉井線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_LOA | 玉井線 復閉失敗閉鎖 | OTHER | S70/11/KK28/LOA |  |  |  | CDC | 324 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK29 | 山工線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_LOA | 山工線 復閉失敗閉鎖 | OTHER | S70/11/KK29/LOA |  |  |  | CDC | 325 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | KK30 | 山30線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_LOA | 山30線 復閉失敗閉鎖 | OTHER | S70/11/KK30/LOA |  |  |  | CDC | 326 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | S70//1MTR/51Z_UL |  |  |  | CDC | 327 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | S70//1MTR/MTR_86A |  |  |  | CDC | 328 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_87UL1 | #1MTR 第一套87RY U/L | OTHER | S70//1MTR/87UL |  |  |  | CDC | 329 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | S70//1MTR/1_87UL2 |  |  |  | CDC | 330 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-3E-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | S70//2MTR/51Z_UL |  |  |  | CDC | 331 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | S70//2MTR/MTR_86A |  |  |  | CDC | 332 | GENERICDIPoint | SS412_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-34-03 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_87UL1 | #2MTR 第一套87RY U/L | OTHER | S70//2MTR/87UL |  |  |  | CDC | 333 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-3E-02 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | S70//2MTR/1_87UL2 |  |  |  | CDC | 334 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S70 | 山頂SS | 0 |  | MTR | MTR |  | IEDGA | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_2 | [8 empty] | 山頂SS.MTR_IED故障 | MTR IED故障 | OTHER | S70/0/MTR/IRFA |  |  |  | CDC | 335 | GENERICDIPoint | SS412_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S70 | 山頂SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_SC_CAP | 11KV#1SC 容量 | SC | S70/11/210/1AI_Oth |  |  |  |  | 336 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_SC_CAP | 11KV#2SC 容量 | SC | S70/11/220/2AI_Oth |  |  |  |  | 337 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 山頂SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 338 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | LE0 | 610LE | [24 empty] | ADCS_S | [8 empty] | 山頂SS.610LE | 610LE (非取樣點) | LINE69 | S70/69/610/LE0 |  |  |  |  | 339 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 620 | 山上山頂二路(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 山頂SS.620LE | 620LE (非取樣點) | LINE69 | S70/69/620/LE0 |  |  |  |  | 340 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 69 | 69kV | 630 | 宏遠線(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 山頂SS.630LE | 630LE (非取樣點) | LINE69 | S70/69/630/LE0 |  |  |  |  | 341 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK21DS1 | KK21DS1 |  | KK21DS1 | KK21DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21DS1 | KK21DS1 (非取樣點) | FEEDER | S70/11/KK21/D1 |  |  |  |  | 342 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK21DS2 | KK21DS2 |  | KK21DS2 | KK21DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21DS2 | KK21DS2 (非取樣點) | FEEDER | S70/11/KK21/D2 |  |  |  |  | 343 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK21_KK22 | KK21_KK22_DS |  | DS1 | KK21_KK22_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_KK22_DS | KK21_KK22_DS (非取樣點) | FEEDER | S70/11/KK21_KK22/DS |  |  |  |  | 344 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK21 | KK21_ES |  | LE0 | KK21_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK21_ES | KK21_ES (非取樣點) | FEEDER | S70/11/KK21/ES |  |  |  |  | 345 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK22DS1 | KK22DS1 |  | KK22DS1 | KK22DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22DS1 | KK22DS1 (非取樣點) | FEEDER | S70/11/KK22/D1 |  |  |  |  | 346 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK22DS2 | KK22DS2 |  | KK22DS2 | KK22DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22DS2 | KK22DS2 (非取樣點) | FEEDER | S70/11/KK22/D2 |  |  |  |  | 347 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK22_KK23 | KK22_KK23_DS |  | DS1 | KK22_KK23_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_KK23_DS | KK22_KK23_DS (非取樣點) | FEEDER | S70/11/KK22_KK23/DS |  |  |  |  | 348 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK22 | KK22_ES |  | LE0 | KK22_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK22_ES | KK22_ES (非取樣點) | FEEDER | S70/11/KK22/ES |  |  |  |  | 349 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK23DS1 | KK23DS1 |  | KK23DS1 | KK23DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23DS1 | KK23DS1 (非取樣點) | FEEDER | S70/11/KK23/D1 |  |  |  |  | 350 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK23DS2 | KK23DS2 |  | KK23DS2 | KK23DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23DS2 | KK23DS2 (非取樣點) | FEEDER | S70/11/KK23/D2 |  |  |  |  | 351 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK23 | KK23_ES |  | LE0 | KK23_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK23_ES | KK23_ES (非取樣點) | FEEDER | S70/11/KK23/ES |  |  |  |  | 352 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK24DS1 | KK24DS1 |  | KK24DS1 | KK24DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24DS1 | KK24DS1 (非取樣點) | FEEDER | S70/11/KK24/D1 |  |  |  |  | 353 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK24DS2 | KK24DS2 |  | KK24DS2 | KK24DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24DS2 | KK24DS2 (非取樣點) | FEEDER | S70/11/KK24/D2 |  |  |  |  | 354 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK24_KK25 | KK24_KK25_DS |  | DS1 | KK24_KK25_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_KK25_DS | KK24_KK25_DS (非取樣點) | FEEDER | S70/11/KK24_KK25/DS |  |  |  |  | 355 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK24 | KK24_ES |  | LE0 | KK24_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK24_ES | KK24_ES (非取樣點) | FEEDER | S70/11/KK24/ES |  |  |  |  | 356 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK25DS1 | KK25DS1 |  | KK25DS1 | KK25DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25DS1 | KK25DS1 (非取樣點) | FEEDER | S70/11/KK25/D1 |  |  |  |  | 357 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK25DS2 | KK25DS2 |  | KK25DS2 | KK25DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25DS2 | KK25DS2 (非取樣點) | FEEDER | S70/11/KK25/D2 |  |  |  |  | 358 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK25 | KK25_ES |  | LE0 | KK25_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK25_ES | KK25_ES (非取樣點) | FEEDER | S70/11/KK25/ES |  |  |  |  | 359 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK26DS1 | KK26DS1 |  | KK26DS1 | KK26DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26DS1 | KK26DS1 (非取樣點) | FEEDER | S70/11/KK26/D1 |  |  |  |  | 360 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK26DS2 | KK26DS2 |  | KK26DS2 | KK26DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26DS2 | KK26DS2 (非取樣點) | FEEDER | S70/11/KK26/D2 |  |  |  |  | 361 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK26_KK27 | KK26_KK27_DS |  | DS1 | KK26_KK27_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_KK27_DS | KK26_KK27_DS (非取樣點) | FEEDER | S70/11/KK26_KK27/DS |  |  |  |  | 362 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK26 | KK26_ES |  | LE0 | KK26_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK26_ES | KK26_ES (非取樣點) | FEEDER | S70/11/KK26/ES |  |  |  |  | 363 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK27DS1 | KK27DS1 |  | KK27DS1 | KK27DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27DS1 | KK27DS1 (非取樣點) | FEEDER | S70/11/KK27/D1 |  |  |  |  | 364 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK27DS2 | KK27DS2 |  | KK27DS2 | KK27DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27DS2 | KK27DS2 (非取樣點) | FEEDER | S70/11/KK27/D2 |  |  |  |  | 365 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK27_KK28 | KK27_KK28_DS |  | DS1 | KK27_KK28_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_KK28_DS | KK27_KK28_DS (非取樣點) | FEEDER | S70/11/KK27_KK28/DS |  |  |  |  | 366 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK27 | KK27_ES |  | LE0 | KK27_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK27_ES | KK27_ES (非取樣點) | FEEDER | S70/11/KK27/ES |  |  |  |  | 367 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK28DS1 | KK28DS1 |  | KK28DS1 | KK28DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28DS1 | KK28DS1 (非取樣點) | FEEDER | S70/11/KK28/D1 |  |  |  |  | 368 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK28DS2 | KK28DS2 |  | KK28DS2 | KK28DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28DS2 | KK28DS2 (非取樣點) | FEEDER | S70/11/KK28/D2 |  |  |  |  | 369 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK28 | KK28_ES |  | LE0 | KK28_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK28_ES | KK28_ES (非取樣點) | FEEDER | S70/11/KK28/ES |  |  |  |  | 370 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK29DS1 | KK29DS1 |  | KK29DS1 | KK29DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29DS1 | KK29DS1 (非取樣點) | FEEDER | S70/11/KK29/D1 |  |  |  |  | 371 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK29DS2 | KK29DS2 |  | KK29DS2 | KK29DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29DS2 | KK29DS2 (非取樣點) | FEEDER | S70/11/KK29/D2 |  |  |  |  | 372 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK29_KK30 | KK29_KK30_DS |  | DS1 | KK29_KK30_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_KK30_DS | KK29_KK30_DS (非取樣點) | FEEDER | S70/11/KK29_KK30/DS |  |  |  |  | 373 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK29 | KK29_ES |  | LE0 | KK29_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK29_ES | KK29_ES (非取樣點) | FEEDER | S70/11/KK29/ES |  |  |  |  | 374 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | KK30DS1 | KK30DS1 |  | KK30DS1 | KK30DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30DS1 | KK30DS1 (非取樣點) | FEEDER | S70/11/KK30/D1 |  |  |  |  | 375 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK30DS2 | KK30DS2 |  | KK30DS2 | KK30DS2 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30DS2 | KK30DS2 (非取樣點) | FEEDER | S70/11/KK30/D2 |  |  |  |  | 376 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | KK30 | KK30_ES |  | LE0 | KK30_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.KK30_ES | KK30_ES (非取樣點) | FEEDER | S70/11/KK30/ES |  |  |  |  | 377 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | TIE1 | TIE1_DS |  | DS1 | TIE1_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.TIE1_DS | TIE1_DS (非取樣點) | TIE | S70/11/TIE1/D1 |  |  |  |  | 378 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.1M_DS | 1M_DS (非取樣點) | DTR | S70/11/M1/DS |  |  |  |  | 379 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.1M_ES | 1M_ES (非取樣點) | DTR | S70/11/M1/ES |  |  |  |  | 380 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.2M_DS | 2M_DS (非取樣點) | DTR | S70/11/M2/DS |  |  |  |  | 381 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.2M_ES | 2M_ES (非取樣點) | DTR | S70/11/M2/ES |  |  |  |  | 382 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_ES | 210_ES (非取樣點) | SC | S70/11/210/ES |  |  |  |  | 383 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.210_DS1 | 210_DS1 (非取樣點) | SC | S70/11/210/DS |  |  |  |  | 384 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_ES | 220_ES (非取樣點) | SC | S70/11/220/ES |  |  |  |  | 385 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS1 | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.220_DS1 | 220_DS1 (非取樣點) | SC | S70/11/220/DS |  |  |  |  | 386 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S70 | 山頂SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 山頂SS.69B1E | 69B1E (非取樣點) | BUS | S70/69/1BUS/BE1 |  |  |  |  | 387 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S70 | 山頂SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 山頂SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 388 | NotelDIPoint | [38 empty] | START/STOP | STOP
S70 | 山頂SS | 69 | 69kV | 610 | 山上山頂一路(610) |  | BE0 | 610BE | [24 empty] | ADCS_S | [8 empty] | 山頂SS.610BE | 610BE (非取樣點) | LINE69 | S70/69/610/BE0 |  |  |  |  | 389 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo