## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS1 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S75_A1 | [8 empty] | 南化SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 69KV BUS2 電壓 |  |  | kV_-90_90(-2000_2000) | aab | B2/S75_A1 | [8 empty] | 南化SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S75 | 南化SS | 11 | 11kV | 2BUS | #2BUS |  | V_R | V | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S75_D1 | [8 empty] | 南化SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 2BUS | #2BUS |  | V_S | V | B2,Element | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0170 |  |  | 2-AA |  |  | #2 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S75_D1 | [8 empty] | 南化SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 2BUS | #2BUS |  | V_T | V | B2,Element | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0171 |  |  | 2-AB |  |  | #2 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S75_D1 | [8 empty] | 南化SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 3BUS | #3BUS |  | V_R | V | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | #3 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S75_D1 | [8 empty] | 南化SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 3BUS | #3BUS |  | V_S | V | B2,Element | MvMoment | S相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0172 |  |  | 2-AC |  |  | #3 TR S相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S75_D1 | [8 empty] | 南化SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS |  |  |  |  | CDC | 8 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 3BUS | #3BUS |  | V_T | V | B2,Element | MvMoment | T相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0173 |  |  | 2-AD |  |  | #3 TR T相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S75_D1 | [8 empty] | 南化SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS |  |  |  |  | CDC | 9 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV GIS BUS #1 衡相監視 |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | BE2 | 69B2E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 12 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV GIS BUS #2 衡相監視 |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 13 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 南化隆田線 (610) 瓦 |  |  | MW_-96_96(-2000_2000) |  | B2/S75_A1 | [8 empty] | 南化SS.610_MW | 南化隆田線 MW | LINE69 |  |  |  |  | CDC | 14 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 南化隆田線 (610) 乏 |  |  | MVAR_-96_96(-2000_2000) |  | B2/S75_A1 | [8 empty] | 南化SS.610_MVAR | 南化隆田線 MVAR | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | 南化隆田線（610) MWH(+) |  |  |  |  | B2/S75_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 16 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 曾文南化線 (640) 瓦 |  |  | MW_-96_96(-2000_2000) |  | B2/S75_A1 | [8 empty] | 南化SS.640_MW | 曾文南化西口線 MW | LINE69 |  |  |  |  | CDC | 17 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 曾文南化線 (640) 乏 |  |  | MVAR_-96_96(-2000_2000) |  | B2/S75_A1 | [8 empty] | 南化SS.640_MVAR | 曾文南化西口線 MVAR | LINE69 |  |  |  |  | CDC | 18 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.192 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0030 |  |  | 1-5E |  |  | 曾文南化線（640) MWH(+) |  |  |  |  | B2/S75_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 19 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 南化隆田線（610) 67 RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_PHA | 南化隆田線(610) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | 南化隆田線（610) 67N RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_GDA | 南化隆田線(610) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 曾文南化線（640) 67 RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_PHA | 曾文南化西口線(640) 相間RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 曾文南化線（640) 67N RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_GDA | 曾文南化西口線(640) 接地RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S41TN08/T2 |  | 0060 |  | 0003 | 1-07-04 |  | 1-03 | 南化隆田線（610) CB |  |  |  | aaba | B2/S75_A1 | [8 empty] | 南化SS.610_CB | 610(南化隆田線) CB | LINE69 |  |  |  |  | CDC | 24 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/H03TN06/T2 |  | 0064 |  | 0004 | 1-08-00 |  | 1-04 | 曾文南化線（640) CB |  |  |  | aada | B2/S75_A1 | [8 empty] | 南化SS.640_CB | 640(曾文南化西口線) CB | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | DS1 | 611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0416 | 417 | 0024 | 1-3A-00 | 1-3A-01 | 1-18 | 南化隆田線（611) 1AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.611_DS | 611(南化隆田線) DS | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | DS2 | 612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0418 | 419 | 0025 | 1-3A-02 | 1-3A-03 | 1-19 | 南化隆田線（612) 2AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.612_DS | 612(南化隆田線) DS | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | DS1 | 641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0424 | 425 | 0028 | 1-3A-08 | 1-3A-09 | 1-1C | 曾文南化線（641) 1AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.641_DS | 641(曾文南化西口線) DS | LINE69 |  |  |  |  | CDC | 28 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | DS2 | 642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0426 | 427 | 0029 | 1-3A-10 | 1-3A-11 | 1-1D | 曾文南化線（642) 2AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.642_DS | 642(曾文南化西口線) DS | LINE69 |  |  |  |  | CDC | 29 | DI_LINE69(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | DS3 | 613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0420 | 421 | 0026 | 1-3A-04 | 1-3A-05 | 1-1A | 南化隆田線（613) 3AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.613_DS | 613(南化隆田線) DS | LINE69 |  |  |  |  | CDC | 30 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | ES3 | 613E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0422 | 423 | 0027 | 1-3A-06 | 1-3A-07 | 1-1B | 南化隆田線（613E) 3EAS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.613E_ES | 613E(南化隆田線) ES | LINE69 |  |  |  |  | CDC | 31 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | LE0 | 610LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 32 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | BE0 | 610BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 33 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | DS3 | 643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0428 | 429 | 0030 | 1-3A-12 | 1-3A-13 | 1-1E | 曾文南化線（643) 3AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.643_DS | 643(曾文南化西口線) DS | LINE69 |  |  |  |  | CDC | 34 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | ES3 | 643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0430 | 431 | 0031 | 1-3A-14 | 1-3A-15 | 1-1F | 曾文南化線（643E) 3EAS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.643E_ES | 643E(曾文南化西口線) ES | LINE69 |  |  |  |  | CDC | 35 | DI_LINE69(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | LE0 | 640LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 36 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | BE0 | 640BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 37 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 化21線（KX21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化21線KVAR | 11KV化21線 KVAR | FEEDER |  |  |  |  | CDC | 38 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 化21線（KX21) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化21線A1 | 11KV化21線 R相AMP | FEEDER |  |  |  |  | CDC | 39 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 化21線（KX21) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化21線A2 | 11KV化21線 S相AMP | FEEDER |  |  |  |  | CDC | 40 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 化21線（KX21) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化21線A3 | 11KV化21線 T相AMP | FEEDER |  |  |  |  | CDC | 41 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 化21線（KX21) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化21線A0 | 11KV化21線 N相AMP | FEEDER |  |  |  |  | CDC | 42 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 化21線（KX21) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 43 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 化22線（KX22) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化22線KVAR | 11KV化22線 KVAR | FEEDER |  |  |  |  | CDC | 44 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 化22線（KX22) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化22線A1 | 11KV化22線 R相AMP | FEEDER |  |  |  |  | CDC | 45 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 化22線（KX22) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化22線A2 | 11KV化22線 S相AMP | FEEDER |  |  |  |  | CDC | 46 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 化22線（KX22) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化22線A3 | 11KV化22線 T相AMP | FEEDER |  |  |  |  | CDC | 47 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 化22線（KX22) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.化22線A0 | 11KV化22線 N相AMP | FEEDER |  |  |  |  | CDC | 48 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 化22線（KX22) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 49 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 預備線（F9) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備24線KVAR | 11KV備24線 KVAR | FEEDER |  |  |  |  | CDC | 50 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 預備線（F9) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備24線A1 | 11KV備24線 R相AMP | FEEDER |  |  |  |  | CDC | 51 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 預備線（F9) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備24線A2 | 11KV備24線 S相AMP | FEEDER |  |  |  |  | CDC | 52 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 預備線（F9) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備24線A3 | 11KV備24線 T相AMP | FEEDER |  |  |  |  | CDC | 53 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 預備線（F9) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備24線A0 | 11KV備24線 N相AMP | FEEDER |  |  |  |  | CDC | 54 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 預備線（F9) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 55 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 預備線（F10) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備25線KVAR | 11KV備25線 KVAR | FEEDER |  |  |  |  | CDC | 56 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 預備線（F10) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備25線A1 | 11KV備25線 R相AMP | FEEDER |  |  |  |  | CDC | 57 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 預備線（F10) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備25線A2 | 11KV備25線 S相AMP | FEEDER |  |  |  |  | CDC | 58 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 預備線（F10) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備25線A3 | 11KV備25線 T相AMP | FEEDER |  |  |  |  | CDC | 59 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 預備線（F10) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備25線A0 | 11KV備25線 N相AMP | FEEDER |  |  |  |  | CDC | 60 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 預備線（F10) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 61 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 預備線（F14) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備34線KVAR | 11KV備34線 KVAR | FEEDER |  |  |  |  | CDC | 62 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 預備線（F14) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備34線A1 | 11KV備34線 R相AMP | FEEDER |  |  |  |  | CDC | 63 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 預備線（F14) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備34線A2 | 11KV備34線 S相AMP | FEEDER |  |  |  |  | CDC | 64 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 預備線（F14) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備34線A3 | 11KV備34線 T相AMP | FEEDER |  |  |  |  | CDC | 65 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 預備線（F14) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備34線A0 | 11KV備34線 N相AMP | FEEDER |  |  |  |  | CDC | 66 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | 預備線（F14) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 67 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 預備線（F15) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備35線KVAR | 11KV備35線 KVAR | FEEDER |  |  |  |  | CDC | 68 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 預備線（F15) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備35線A1 | 11KV備35線 R相AMP | FEEDER |  |  |  |  | CDC | 69 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 預備線（F15) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備35線A2 | 11KV備35線 S相AMP | FEEDER |  |  |  |  | CDC | 70 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 預備線（F15) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備35線A3 | 11KV備35線 T相AMP | FEEDER |  |  |  |  | CDC | 71 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 預備線（F15) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.備35線A0 | 11KV備35線 N相AMP | FEEDER |  |  |  |  | CDC | 72 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | 預備線（F15) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 73 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 化21線（KX21) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX21_PHA | 11KV化21線(KX21) 相間RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 化21線（KX21) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX21_GDA | 11KV化21線(KX21) 接地RY | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | 化21線（KX21) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX21_79UL | 11KV化21線(KX21) 79RY U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | 化21線（KX21) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX21_ADJ | 11KV化21線(KX21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 化22線（KX22) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX22_PHA | 11KV化22線(KX22) 相間RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 化22線（KX22) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX22_GDA | 11KV化22線(KX22) 接地RY | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | 化22線（KX22) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX22_79UL | 11KV化22線(KX22) 79RY U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | 化22線（KX22) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX22_ADJ | 11KV化22線(KX22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 玉楠線（KX23) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX23_PHA | 11KV玉楠線(KX23) 相間RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 玉楠線（KX23) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX23_GDA | 11KV玉楠線(KX23) 接地RY | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | 玉楠線（KX23) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX23_79UL | 11KV玉楠線(KX23) 79RY U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | 玉楠線（KX23) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX23_ADJ | 11KV玉楠線(KX23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 預備線（F9) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX24_PHA | 11KV備24線(KX24) 相間RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 預備線（F9) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX24_GDA | 11KV備24線(KX24) 接地RY | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | 預備線（F9) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX24_79UL | 11KV備24線(KX24) 79RY U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | 預備線（F9) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX24_ADJ | 11KV備24線(KX24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 預備線（F10) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX25_PHA | 11KV備25線(KX25) 相間RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 預備線（F10) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX25_GDA | 11KV備25線(KX25) 接地RY | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | 預備線（F10) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX25_79UL | 11KV備25線(KX25) 79RY U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | 預備線（F10) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX25_ADJ | 11KV備25線(KX25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | 玉山線（KX31) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX31_PHA | 11KV玉山線(KX31) 相間RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | 玉山線（KX31) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX31_GDA | 11KV玉山線(KX31) 接地RY | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0343 |  | 0100 | 1-35-07 |  | 1-64 | 玉山線（KX31) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX31_79UL | 11KV玉山線(KX31) 79RY U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0362 |  | 0122 | 1-36-10 |  | 1-7A | 玉山線（KX31) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX31_ADJ | 11KV玉山線(KX31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 水庫線（KX32) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX32_PHA | 11KV水庫線(KX32) 相間RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | 水庫線（KX32) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX32_GDA | 11KV水庫線(KX32) 接地RY | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0344 |  | 0101 | 1-35-08 |  | 1-65 | 水庫線（KX32) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX32_79UL | 11KV水庫線(KX32) 79RY U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0363 |  | 0123 | 1-36-11 |  | 1-7B | 水庫線（KX32) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX32_ADJ | 11KV水庫線(KX32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | 玉寮線 (KX33) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX33_PHA | 11KV玉寮線(KX33) 相間RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | 玉寮線 (KX33) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX33_GDA | 11KV玉寮線(KX33) 接地RY | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0345 |  | 0102 | 1-35-09 |  | 1-66 | 玉寮線 (KX33) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX33_79UL | 11KV玉寮線(KX33) 79RY U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0364 |  | 0124 | 1-36-12 |  | 1-7C | 玉寮線 (KX33) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX33_ADJ | 11KV玉寮線(KX33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | 預備線（F14) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX34_PHA | 11KV備34線(KX34) 相間RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | 預備線（F14) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX34_GDA | 11KV備34線(KX34) 接地RY | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0346 |  | 0103 | 1-35-10 |  | 1-67 | 預備線（F14) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX34_79UL | 11KV備34線(KX34) 79RY U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0365 |  | 0125 | 1-36-13 |  | 1-7D | 預備線（F14) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX34_ADJ | 11KV備34線(KX34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | 預備線（F15) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX35_PHA | 11KV備35線(KX35) 相間RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 預備線（F15) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX35_GDA | 11KV備35線(KX35) 接地RY | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0347 |  | 0104 | 1-35-11 |  | 1-68 | 預備線（F15) 79RY U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX35_79UL | 11KV備35線(KX35) 79RY U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0366 |  | 0126 | 1-36-14 |  | 1-7E | 預備線（F15) LCO ADJ U/L |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX35_ADJ | 11KV備35線(KX35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/KX21/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | 化21線（KX21) CB |  |  |  | aabb | B2/S75_D1 | [8 empty] | 南化SS.KX21_CB | KX21(11KV化21線) CB | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX21_DS | KX21_DS (非取樣點) | FEEDER | [5 empty] | 115 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | ES | KX21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX21_ES | KX21_ES (非取樣點) | FEEDER | [5 empty] | 116 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/KX22/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | 化22線（KX22) CB |  |  |  | aacb | B2/S75_D1 | [8 empty] | 南化SS.KX22_CB | KX22(11KV化22線) CB | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX22_DS | KX22_DS (非取樣點) | FEEDER | [5 empty] | 118 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | ES | KX22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX22_ES | KX22_ES (非取樣點) | FEEDER | [5 empty] | 119 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/KX23/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | 玉楠線（KX23) CB |  |  |  | aaeb | B2/S75_D1 | [8 empty] | 南化SS.KX23_CB | KX23(11KV玉楠線) CB | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX23_DS | KX23_DS (非取樣點) | FEEDER | [5 empty] | 121 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | ES | KX23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX23_ES | KX23_ES (非取樣點) | FEEDER | [5 empty] | 122 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/KX24/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | 預備線（F9) CB |  |  |  | aafb | B2/S75_D1 | [8 empty] | 南化SS.KX24_CB | KX24(11KV備24線) CB | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX24_DS | KX24_DS (非取樣點) | FEEDER | [5 empty] | 124 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | ES | KX24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX24_ES | KX24_ES (非取樣點) | FEEDER | [5 empty] | 125 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | L/KX25/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | 預備線（F10) CB |  |  |  | aagb | B2/S75_D1 | [8 empty] | 南化SS.KX25_CB | KX25(11KV備25線) CB | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX25_DS | KX25_DS (非取樣點) | FEEDER | [5 empty] | 127 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | ES | KX25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX25_ES | KX25_ES (非取樣點) | FEEDER | [5 empty] | 128 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KX31/T1 |  |  | 0140 |  | 0092 | 1-11-04 |  | 1-5C | 玉山線（KX31) CB |  |  |  | abab | B2/S75_D1 | [8 empty] | 南化SS.KX31_CB | KX31(11KV玉山線) CB | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX31_DS | KX31_DS (非取樣點) | FEEDER | [5 empty] | 130 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | ES | KX31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX31_ES | KX31_ES (非取樣點) | FEEDER | [5 empty] | 131 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KX32/T1 |  |  | 0141 |  | 0093 | 1-11-05 |  | 1-5D | 水庫線（KX32） CB |  |  |  | abbb | B2/S75_D1 | [8 empty] | 南化SS.KX32_CB | KX32(11KV水庫線) CB | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX32_DS | KX32_DS (非取樣點) | FEEDER | [5 empty] | 133 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | ES | KX32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX32_ES | KX32_ES (非取樣點) | FEEDER | [5 empty] | 134 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KX33/T1 |  |  | 0142 |  | 0094 | 1-11-06 |  | 1-5E | 玉寮線 (KX33) CB |  |  |  | abdb | B2/S75_D1 | [8 empty] | 南化SS.KX33_CB | KX33(11KV玉寮線) CB | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX33_DS | KX33_DS (非取樣點) | FEEDER | [5 empty] | 136 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | ES | KX33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX33_ES | KX33_ES (非取樣點) | FEEDER | [5 empty] | 137 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KX34/T1 |  |  | 0143 |  | 0095 | 1-11-07 |  | 1-5F | 預備線（F14) CB |  |  |  | abeb | B2/S75_D1 | [8 empty] | 南化SS.KX34_CB | KX34(11KV備34線) CB | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX34_DS | KX34_DS (非取樣點) | FEEDER | [5 empty] | 139 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | ES | KX34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX34_ES | KX34_ES (非取樣點) | FEEDER | [5 empty] | 140 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KX35/T1 |  |  | 0144 |  | 0096 | 1-12-00 |  | 1-60 | 預備線（F15) CB |  |  |  | abfb | B2/S75_D1 | [8 empty] | 南化SS.KX35_CB | KX35(11KV備35線) CB | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX35_DS | KX35_DS (非取樣點) | FEEDER | [5 empty] | 142 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | ES | KX35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.KX35_ES | KX35_ES (非取樣點) | FEEDER | [5 empty] | 143 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | I |  | B3 | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | TIE （600） 電流 |  |  | A_-800_800(-2000_2000) |  | B2/S75_A1 | [8 empty] | 南化SS.600TIE_AMP | 600TIE AMP | TIE |  |  |  |  | CDC | 144 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C08R0600 | 570 | 600 | 660 | 738 | 1 | -570 | -600 | -660 | -738 | 1 | 0.01 | C08R0600 | 540.000000 | 540.000000 | 600.000000 | 800.000000 | 1.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R | #2-#3 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #2-#3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE |  |  |  |  | CDC | 145 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S | #2-#3 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #2-#3 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE |  |  |  |  | CDC | 146 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T | #2-#3 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #2-#3 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE |  |  |  |  | CDC | 147 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | CouplerA | B/1BUS | B/2BUS |  |  | 0040 |  | 0007 | 1-05-00 |  | 1-07 | 69KV TIE CB |  |  |  | aafz | B2/S75_A1 | [8 empty] | 南化SS.600_CB | 600(TIE) CB | TIE |  |  |  |  | CDC | 148 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB | #2-#3 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BUS | B/3BUS |  |  | 0123 |  | 0071 | 1-0F-03 |  | 1-47 | #2- #3 TIE CB |  |  |  | zzzz | B2/S75_D1 | [8 empty] | 南化SS.TIE2_CB | 11KV TIE2 CB | TIE |  |  |  |  | CDC | 149 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A | #2-#3 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #2- #3 TIE 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.TIE2_51A | 11KV TIE2 51RY | TIE |  |  |  |  | CDC | 150 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA | #2-#3 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #2- #3 TIE 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.TIE2_51NA | 11KV TIE2 51N RY | TIE |  |  |  |  | CDC | 151 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | 433 | 0034 | 1-3B-00 | 1-3B-01 | 1-22 | 69KV SECTION 601AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.601_DS | 601(TIE) DS | TIE |  |  |  |  | CDC | 152 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0434 | 435 | 0035 | 1-3B-02 | 1-3B-03 | 1-23 | 69KV SECTION 602AS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.602_DS | 602(TIE) DS | TIE |  |  |  |  | CDC | 153 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.601E | 601E (非取樣點) | TIE | [5 empty] | 154 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.602E | 602E (非取樣點) | TIE | [5 empty] | 155 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | #2-#3(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | [5 empty] | 156 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 157 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 158 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 159 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 160 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 161 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 162 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 163 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 164 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 165 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 166 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 167 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 168 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 169 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S75 | 南化SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #2 TR MWH(+) |  |  |  |  | B1/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 170 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 171 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 172 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 173 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0097 | 1-E5 |  | 1-61 | #3 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 174 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S75 | 南化SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | #3 TR MWH(+) |  |  |  |  | B1/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 175 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0022 |  |  | 1-56 |  |  | #3 TR MVARH(+) |  |  |  |  | B1/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 176 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/2MTR |  | 0009 |  | 0068 | 1-01-01 |  | 1-44 | #2TR 一次 (760) CB |  |  |  | aaab | B3/S75_D1 | [8 empty] | 南化SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 177 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S75_D1 | [8 empty] | 南化SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 178 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S75_D1 | [8 empty] | 南化SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 179 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/3MTR |  | 0019 |  | 0088 | 1-02-03 |  | 1-58 | #3TR 一次 (770) CB |  |  |  | aaeb | B3/S75_D1 | [8 empty] | 南化SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 180 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S75_D1 | [8 empty] | 南化SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 181 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S75_D1 | [8 empty] | 南化SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 182 | DI_DTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | T/2MTR |  |  | 0010 |  | 0069 | 1-01-02 |  | 1-45 | #2TR 二次 (#2MT) CB |  |  |  | aada | B2/S75_D1 | [8 empty] | 南化SS.2M_CB | 2M(#2MTR) CB | DTR |  |  |  |  | CDC | 183 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0020 |  | 0089 | 1-02-04 |  | 1-59 | #3TR 二次 (#3MT) CB |  |  |  | abca | B2/S75_D1 | [8 empty] | 南化SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 184 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | #2TR 一次 (760) 51 RY |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 185 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 一次 (760) 51N RY |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 186 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 51Z RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 187 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 87 RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 188 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #2TR 87 LS1S |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 189 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | 81A |  | B2,B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  | 0086 | 1-0F-04 |  | 1-56 | #2 BUS 81 RY |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR |  |  |  |  | CDC | 190 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | #3TR 一次 (770) 51 RY |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 191 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | #3TR 一次 (770) 51N RY |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 192 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3TR 51Z RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 193 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3TR 87 RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 194 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 1-35-03 |  |  | #3TR 87 LS1S |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 195 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  | 0105 | 1-12-01 |  | 1-69 | #3 BUS 81 RY |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR |  |  |  |  | CDC | 196 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2TR 二次 (#2MT) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.2M_51A | #2MTR二次側(2M) 51RY | DTR |  |  |  |  | CDC | 197 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 198 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 199 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 200 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S75 | 南化SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #2TR OLTC A/M |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 201 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3TR 二次 (#3MAT) 51 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 202 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0336 |  |  | 1-35-00 |  |  | #3TR 重故障 |  |  |  | a | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 203 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0337 |  |  | 1-35-01 |  |  | #3TR 輕故障 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 204 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | #3TR OLTC R/L |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 205 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S75 | 南化SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0341 |  | 0098 | 1-35-05 |  | 1-62 | #3TR OLTC A/M |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 206 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0388 | 389 | 0038 | 1-38-04 | 1-38-05 | 1-26 | #2TR (761) ABS |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.761_DS | 761(#2MTR) DS | DTR |  |  |  |  | CDC | 207 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0390 | 391 | 0039 | 1-38-06 | 1-38-07 | 1-27 | #2TR (762) ABS |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.762_DS | 762(#2MTR) DS | DTR |  |  |  |  | CDC | 208 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | B2 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0040 | 1-38-08 | 1-38-09 | 1-28 | #3TR (771) ABS |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.771_DS | 771(#3MTR) DS | DTR |  |  |  |  | CDC | 209 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | B2 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0041 | 1-38-10 | 1-38-11 | 1-29 | #3TR (772) ABS |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.772_DS | 772(#3MTR) DS | DTR |  |  |  |  | CDC | 210 | DI_DTR(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.2M_DS | 2M_DS (非取樣點) | DTR | [5 empty] | 211 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.2M_ES | 2M_ES (非取樣點) | DTR | [5 empty] | 212 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 213 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #2TR 冷卻電源故障 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 214 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 215 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 216 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 1-35-02 |  |  | #3TR OLTC 遲滯 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 217 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0333 |  |  | 1-34-13 |  |  | #3TR 冷卻電源故障 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 218 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 219 | DI_DTR(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | #3TR 機械保護動作(96PA) |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR |  |  |  |  | CDC | 220 | DI_DTR(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | C/1SC |  | 0045 |  | 0008 | 1-05-05 |  | 1-08 | 69KV SC（810）CB |  |  |  | aacb | B2/S75_A1 | [8 empty] | 南化SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 221 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | ES | 810E(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.810CE | 810CE (非取樣點) | SC | [5 empty] | 222 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2BUS | C/2SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #2 11KV SC CB |  |  |  | aaab | B2/S75_D1 | [8 empty] | 南化SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 223 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #2SC Q-CTL A/M |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 224 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.220ES | 220ES (非取樣點) | SC | [5 empty] | 225 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | C/3SC |  |  | 0139 |  | 0091 | 1-11-03 |  | 1-5B | #3 11KV SC CB |  |  |  | abgb | B2/S75_D1 | [8 empty] | 南化SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 226 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0342 |  | 0099 | 1-35-06 |  | 1-63 | #3SC Q-CTL A/M |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 227 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.230ES | 230ES (非取樣點) | SC | [5 empty] | 228 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0396 | 397 | 0032 | 1-38-12 | 1-38-13 | 1-20 | 69KV SC (811) ABS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.811_DS | 811(69KV #1SC) DS | SC |  |  |  |  | CDC | 229 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | B3 | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0033 | 1-38-14 | 1-38-15 | 1-21 | 69KV SC (812) ABS |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.812_DS | 812(69KV #1SC) DS | SC |  |  |  |  | CDC | 230 | DI_SC(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 69KV SC SCA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 231 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | 69KV SC OUVA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 232 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 233 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 234 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | #3SC 51,51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 235 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #3SC 27,59 RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 236 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 237 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 238 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 239 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 240 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 241 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 242 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 243 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 244 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 南化SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 245 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 246 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 247 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 248 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 249 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 250 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 開關場照明 C/T |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 251 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 252 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 253 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 254 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 255 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 256 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 257 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 258 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 259 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 260 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 261 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 262 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-37-00 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 263 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 1-37-01 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 264 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-37-02 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 265 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0371 |  |  | 1-37-03 |  |  | 博碼調變器故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 266 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 267 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 開關場照明 A/M |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 268 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所水位低 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 269 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所水位高 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 270 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 271 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69SC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV SC 警報 |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69SC警報 | 69SC警報 | OTHER |  |  |  |  | CDC | 272 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 273 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.火災警報 | 火災警報 | OTHER |  |  |  |  | CDC | 274 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 275 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧/CO2故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧/CO2 故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.水氣霧/CO2故障 | 水氣霧/CO2故障 | OTHER |  |  |  |  | CDC | 276 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧/CO2警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧/CO2 警報 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.水氣霧/CO2警報 | 水氣霧/CO2警報 | OTHER |  |  |  |  | CDC | 277 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0165 |  | 0087 | 1-14-05 |  | 1-57 | 全所故障指示器復歸點 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 278 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 | Element | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S75_D1 | [8 empty] | 南化SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 279 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | Element | [12 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 280 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 281 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 282 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 曾文南化線（640) 87 RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_87A | 曾文南化西口線(640) 87RY | OTHER |  |  |  |  | CDC | 283 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0297 |  | 0012 | 1-32-09 |  | 1-0C | 曾文南化線（640) 87RY U/L |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_87UL | 曾文南化西口線(640) 87RY UL | OTHER |  |  |  |  | CDC | 284 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-32-10 |  |  | 曾文南化線（640) 87RY CFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_87RY_CFA | 640 87RY IED通訊故障 | OTHER |  |  |  |  | CDC | 285 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 曾文南化線（640) RYFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.640_RYFA | 640 IED故障 | OTHER |  |  |  |  | CDC | 286 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 南化隆田線（610) 87 RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_87A | 610南化隆田線87RY | OTHER |  |  |  |  | CDC | 287 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0294 |  | 0011 | 1-32-06 |  | 1-0B | 南化隆田線（610) 87RY U/L |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_87UL | 610南化隆田線87RY UL | OTHER |  |  |  |  | CDC | 288 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 南化隆田線（610) 87RY CFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_87RY_CFA | 610 87RY IED通訊故障 | OTHER |  |  |  |  | CDC | 289 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 1-32-08 |  |  | 南化隆田線（610) RYFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.610_RYFA | 610 IED故障 | OTHER |  |  |  |  | CDC | 290 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint | #1BUS |  | BUS_RYFA | 69KV BUS IED故障 | B3 | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 1-35-14 |  |  | 69KV BUS RYFA |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER |  |  |  |  | CDC | 291 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | 12B_CTFA | 69KV BUS CT迴路故障 | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 1-35-15 |  |  | 69KV BUS CTFA |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER |  |  |  |  | CDC | 292 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | 69KV #1BUS 87RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER |  |  |  |  | CDC | 293 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0348 |  | 0014 | 1-35-12 |  | 1-0E | 69KV GIS #1BUS 87S |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER |  |  |  |  | CDC | 294 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 69KV #2BUS 87RY |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER |  |  |  |  | CDC | 295 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0015 | 1-35-13 |  | 1-0F | 69KV GIS #2BUS 87S |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER |  |  |  |  | CDC | 296 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 69KV TIE 1PHA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.600PHA(1) | 69KV #1BUS TIE(600) 67 | OTHER |  |  |  |  | CDC | 297 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 69KV TIE 1GDA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.600GDA(1) | 69KV #1BUS TIE(600) 67N | OTHER |  |  |  |  | CDC | 298 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 69KV TIE 2PHA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.600PHA(2) | 69KV #2BUS TIE(600) 67 | OTHER |  |  |  |  | CDC | 299 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 69KV TIE 2GDA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.600GDA(2) | 69KV #2BUS TIE(600) 67N | OTHER |  |  |  |  | CDC | 300 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | RYFA | 69KV TIE IED故障 | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | 69KV TIE RYFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER |  |  |  |  | CDC | 301 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | COMT |  | B2,Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | 69KV COMT 空壓機運轉超時警報 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV空壓機COMT | 空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 302 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-33-15 |  |  | 69KV SC RYFA |  |  |  |  | B2/S75_A1 | [8 empty] | 南化SS.69KV_SC_RYFA | 69KV SC IED故障 | OTHER |  |  |  |  | CDC | 303 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | B3,Element | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #2TR 86 RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_86A | #2MTR 86RY | OTHER |  |  |  |  | CDC | 304 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | B3,Element | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | #3TR 86 RY |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_86A | #3MTR 86RY | OTHER |  |  |  |  | CDC | 305 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | M2 | #2MTR(M2) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #2TR 二次 (#2MAT) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.#2M_51NA | #2M 51N RY | OTHER |  |  |  |  | CDC | 306 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | #3TR 二次 (#3MAT) 51N RY |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.#3M_51NA | #3M 51N RY | OTHER |  |  |  |  | CDC | 307 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0376 |  |  | 1-37-08 |  |  | #2TR RYFA |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_RYFA | #2MTR 數位電驛故障 | OTHER |  |  |  |  | CDC | 308 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 51_UL |  | B3,Element | Status | 51RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0377 |  |  | 1-37-09 |  |  | #2TR 51LS |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_51UL | #2MTR 51 RY U/L | OTHER |  |  |  |  | CDC | 309 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0378 |  |  | 1-37-10 |  |  | #2TR 51ZLS |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_51ZUL | #2MTR 51Z RY U/L | OTHER |  |  |  |  | CDC | 310 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS |  |  | 3MTR | #3MTR |  | RYFA |  | B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0379 |  |  | 1-37-11 |  |  | #3TR RYFA |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_RYFA | #3MTR 數位電驛故障 | OTHER |  |  |  |  | CDC | 311 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 51_UL |  | B3,Element | Status | 51RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0380 |  |  | 1-37-12 |  |  | #3TR 51LS |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_51UL | #3MTR 51 RY U/L | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | B3,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0381 |  |  | 1-37-13 |  |  | #3TR 51ZLS |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_51ZUL | #3MTR 51Z RY U/L | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #2DTR 96D |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #2DTR 96P |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #2DTR 63Q |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #2DTR 96B1 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #2DTR 96B2 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 96D |  | B3,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | #3DTR 96D |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 96P |  | B3,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | #3DTR 96P |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 63Q |  | B3,Element | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | #3DTR 63Q |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 96B1 |  | B3,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | #3DTR 96B1 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 96B2 |  | B3,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | #3DTR 96B2 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 水庫線（KX32) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.水庫線KVAR | 11KV水庫線 KVAR | FEEDER |  |  |  |  | CDC | 324 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 水庫線（KX32) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.水庫線A1 | 11KV水庫線 R相AMP | FEEDER |  |  |  |  | CDC | 325 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 水庫線（KX32) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.水庫線A2 | 11KV水庫線 S相AMP | FEEDER |  |  |  |  | CDC | 326 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 水庫線（KX32) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.水庫線A3 | 11KV水庫線 T相AMP | FEEDER |  |  |  |  | CDC | 327 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 水庫線（KX32) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.水庫線A0 | 11KV水庫線 N相AMP | FEEDER |  |  |  |  | CDC | 328 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 玉山線（KX31) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉山線KVAR | 11KV玉山線 KVAR | FEEDER |  |  |  |  | CDC | 329 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 玉山線（KX31) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉山線A1 | 11KV玉山線 R相AMP | FEEDER |  |  |  |  | CDC | 330 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 玉山線（KX31) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉山線A2 | 11KV玉山線 S相AMP | FEEDER |  |  |  |  | CDC | 331 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 玉山線（KX31) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉山線A3 | 11KV玉山線 T相AMP | FEEDER |  |  |  |  | CDC | 332 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 玉山線（KX31) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉山線A0 | 11KV玉山線 N相AMP | FEEDER |  |  |  |  | CDC | 333 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 玉寮線 (KX33) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉寮線KVAR | 11KV玉寮線 KVAR | FEEDER |  |  |  |  | CDC | 334 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 玉寮線 (KX33) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉寮線A1 | 11KV玉寮線 R相AMP | FEEDER |  |  |  |  | CDC | 335 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 玉寮線 (KX33) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉寮線A2 | 11KV玉寮線 S相AMP | FEEDER |  |  |  |  | CDC | 336 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 玉寮線 (KX33) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉寮線A3 | 11KV玉寮線 T相AMP | FEEDER |  |  |  |  | CDC | 337 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 玉寮線 (KX33) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉寮線A0 | 11KV玉寮線 N相AMP | FEEDER |  |  |  |  | CDC | 338 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 玉楠線（KX23) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉楠線KVAR | 11KV玉楠線 KVAR | FEEDER |  |  |  |  | CDC | 339 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 玉楠線（KX23) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉楠線A1 | 11KV玉楠線 R相AMP | FEEDER |  |  |  |  | CDC | 340 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 玉楠線（KX23) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉楠線A2 | 11KV玉楠線 S相AMP | FEEDER |  |  |  |  | CDC | 341 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 玉楠線（KX23) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉楠線A3 | 11KV玉楠線 T相AMP | FEEDER |  |  |  |  | CDC | 342 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 玉楠線（KX23) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S75_D1 | [8 empty] | 南化SS.玉楠線A0 | 11KV玉楠線 N相AMP | FEEDER |  |  |  |  | CDC | 343 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | DCV_N |  | INSERT | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | DC N電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.直流N電源電壓 | 直流N電源電壓 | OTHER |  |  |  |  | CDC | 344 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | DCV_P |  | INSERT | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | DC P電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/S75_D1 | [8 empty] | 南化SS.直流P電源電壓 | 直流P電源電壓 | OTHER |  |  |  |  | CDC | 345 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 化21線（KX21) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX21_LOA | 化21線 復閉失敗閉鎖 | OTHER | [5 empty] | 346 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 化22線（KX22) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX22_LOA | 化22線 復閉失敗閉鎖 | OTHER | [5 empty] | 347 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 玉楠線（KX23) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX23_LOA | 玉楠線 復閉失敗閉鎖 | OTHER | [5 empty] | 348 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 預備線（F9) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX24_LOA | 備24線 復閉失敗閉鎖 | OTHER | [5 empty] | 349 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 預備線（F10) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX25_LOA | 備25線 復閉失敗閉鎖 | OTHER | [5 empty] | 350 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | 玉山線（KX31) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX31_LOA | 玉山線 復閉失敗閉鎖 | OTHER | [5 empty] | 351 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0503 |  |  | 1-3F-07 |  |  | 水庫線（KX32) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX32_LOA | 水庫線 復閉失敗閉鎖 | OTHER | [5 empty] | 352 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0504 |  |  | 1-3F-08 |  |  | 玉寮線 (KX33) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX33_LOA | 玉寮線 復閉失敗閉鎖 | OTHER | [5 empty] | 353 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-3F-09 |  |  | 預備線（F14) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX34_LOA | 備34線 復閉失敗閉鎖 | OTHER | [5 empty] | 354 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0506 |  |  | 1-3F-10 |  |  | 預備線（F15) LOA |  |  |  |  | B2/S75_D1 | [8 empty] | 南化SS.KX35_LOA | 備35線 復閉失敗閉鎖 | OTHER | [5 empty] | 355 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | StaDev | 所內設施 |  | 1A3U_L | CO2 使用/閉鎖 | INSERT | Status | USE_LOCK動作1 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0511 |  |  | 1-3F-15 |  |  | CO2 使用/閉鎖 |  |  |  |  | B3/S75_D1 | [8 empty] | 南化SS.CO2_UL | CO2 UL | OTHER | [5 empty] | 356 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 玉楠線（KX23) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 357 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | 玉山線（KX31) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 358 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | 水庫線（KX32) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 359 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | 玉寮線 (KX33) KWH(+) |  |  |  |  | B2/S75_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 360 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 361 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | ComPoint |  |  | 1A3U_L | 69KV電驛標置G1/G2變更 |  | Status | USE_LOCK動作1 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0510 |  | 0106 | 1-3F-14 |  | 1-6A | 69KV電驛標置G1/G2 |  | 107.4.27增加 |  |  | B3/S75_D1 | [8 empty] | 南化SS.69KV標置變更 | 69KV電驛標置G1/G2變更 | OTHER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 363 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | 3AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值3 |  | Y |  | AI | [17 empty] | B2/S75_D1 | [8 empty] | 南化SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 364 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 365 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | #3DTR 87LS2S |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | [5 empty] | 366 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | LE0 | 810LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S75_A1 | [8 empty] | 南化SS.810LE | 810LE(非取樣點) | OTHER | [5 empty] | 367 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S75 | 南化SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S75_D1 | [8 empty] | 南化SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 368 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S75 | 南化SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S75_D1 | [12 empty] | 南化SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S75/69/1BUS/V; OPRD2: S75/69/2BUS/V
S75 | 南化SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S75_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S75/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S75 | 南化SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S75_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: S75/11/M2/MW; OPRD2: S75/11/M3/MW; OPRD3: S75/69/610/MW; OPRD4: S75/69/640/MW
S75 | 南化SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S75_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S75/0/CalcPoint/OPRN2_MW
S75 | 南化SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S75_D1 | [17 empty] | none
S75 | 南化SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S75_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S75/0/CalcPoint/OPRN1; OPRD2: S75/0/CalcPoint/OPRN2; OPRD3: S75/0/CalcPoint/PRFL_UL
S75 | 南化SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S75_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S75/11/M2/MW; OPRD2: S75/11/M2/MVAR; OPRD3: S75/0/CalcPoint/Vbs2
S75 | 南化SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S75_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S75/11/M3/MW; OPRD2: S75/11/M3/MVAR; OPRD3: S75/0/CalcPoint/Vbs2
S75 | 南化SS | 69 | 69kV | 610 | 隆田～南化、烏山頭線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S75_A1 | [12 empty] | 南化SS.610_AMP | 南化隆田線 AMP | LINE69 | AMP_CAL | C08R0664 | amp_cal | OPRD1: S75/69/610/MW; OPRD2: S75/69/610/MVAR; OPRD3: S75/0/CalcPoint/Vbs2
S75 | 南化SS | 69 | 69kV | 640 | 曾文～南化、西口線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S75_A1 | [12 empty] | 南化SS.640_AMP | 曾文南化西口線 AMP | LINE69 | AMP_CAL | C08R0600 | amp_cal | OPRD1: S75/69/640/MW; OPRD2: S75/69/640/MVAR; OPRD3: S75/0/CalcPoint/Vbs2
S75 | 南化SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S75_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 南化SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S75/11/M2/MW; OPRD2: S75/11/M2/MVAR
S75 | 南化SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S75_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 南化SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S75/11/M3/MW; OPRD2: S75/11/M3/MVAR
S75 | 南化SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S75_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S75//2MTR/MVA; OPRD2: 0
S75 | 南化SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S75_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S75//3MTR/MVA; OPRD2: 0
S75 | 南化SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S75_D1 | [12 empty] | 南化SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S75/11/M2/MW; OPRD2: S75/11/M2/MVAR
S75 | 南化SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S75_D1 | [12 empty] | 南化SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S75/11/M3/MW; OPRD2: S75/11/M3/MVAR
S75 | 南化SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S75_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S75//2MTR/SupLocal; OPRD2: S75//2MTR/Tap Chan; OPRD3: NULL
S75 | 南化SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S75_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S75//3MTR/SupLocal; OPRD2: S75//3MTR/Tap Chan; OPRD3: NULL
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX21/I_R; OPRD3: S75/11/KX21/I_S; OPRD4: S75/11/KX21/I_T
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX22/I_R; OPRD3: S75/11/KX22/I_S; OPRD4: S75/11/KX22/I_T
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX23/I_R; OPRD3: S75/11/KX23/I_S; OPRD4: S75/11/KX23/I_T
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX24/I_R; OPRD3: S75/11/KX24/I_S; OPRD4: S75/11/KX24/I_T
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX25/I_R; OPRD3: S75/11/KX25/I_S; OPRD4: S75/11/KX25/I_T
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX31/I_R; OPRD3: S75/11/KX31/I_S; OPRD4: S75/11/KX31/I_T
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX32/I_R; OPRD3: S75/11/KX32/I_S; OPRD4: S75/11/KX32/I_T
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX33/I_R; OPRD3: S75/11/KX33/I_S; OPRD4: S75/11/KX33/I_T
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX34/I_R; OPRD3: S75/11/KX34/I_S; OPRD4: S75/11/KX34/I_T
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S75/11/KX35/I_R; OPRD3: S75/11/KX35/I_S; OPRD4: S75/11/KX35/I_T
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX21/kVA; OPRD2: S75/11/KX21/KVAR
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX22/kVA; OPRD2: S75/11/KX22/KVAR
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX23/kVA; OPRD2: S75/11/KX23/KVAR
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX24/kVA; OPRD2: S75/11/KX24/KVAR
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX25/kVA; OPRD2: S75/11/KX25/KVAR
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX31/kVA; OPRD2: S75/11/KX31/KVAR
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX32/kVA; OPRD2: S75/11/KX32/KVAR
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX33/kVA; OPRD2: S75/11/KX33/KVAR
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX34/kVA; OPRD2: S75/11/KX34/KVAR
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S75_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S75/11/KX35/kVA; OPRD2: S75/11/KX35/KVAR
S75 | 南化SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S75_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S75/11/M2/MW; OPRD2: S75/11/M3/MW
S75 | 南化SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S75_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S75/11/M2/MVAR; OPRD2: S75/11/M3/MVAR
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S75_D1 | [12 empty] | 南化SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S75/11/220/CB; OPRD2: 6.9; OPRD3: 0
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S75_D1 | [12 empty] | 南化SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S75/11/230/CB; OPRD2: 6.9; OPRD3: 0
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S75_A1 | [12 empty] | 南化SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S75/69/810/CB; OPRD2: 69; OPRD3: 0
S75 | 南化SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S75_D1 | [12 empty] | 南化SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_8 |  | com_alarm_18 | OPRD1: S75//2MTR/96PA; OPRD2: S75//2MTR/96B2; OPRD3: S75//2MTR/96B1; OPRD4: S75//2MTR/96D; OPRD5: S75//2MTR/63Q; OPRD6: S75//2MTR/87A; OPRD7: S75//2MTR/51ZA; OPRD8: S75//2MTR/TRA; OPRD9: S75//3MTR/96D; OPRD10: S75//3MTR/63Q; OPRD11: S75//3MTR/TRA; OPRD12: S75//3MTR/87A; OPRD13: S75//3MTR/51ZA; OPRD14: S75//3MTR/96B1; OPRD15: S75//3MTR/96B2; OPRD16: S75//3MTR/96PA; OPRD17: S75/69/1BUS/87A; OPRD18: S75/69/2BUS/87A
S75 | 南化SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S75_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S75//2MTR/TRF; OPRD2: S75//3MTR/TRF
S75 | 南化SS | 69 | 69kV | 760_A1 | #2MTR(760) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/69/760/81A
S75 | 南化SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/RTU/RTU_R_L
S75 | 南化SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/StaDev/PSF
S75 | 南化SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/StaDev/DCE
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/CBA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/CBF
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/ABS_89A
S75 | 南化SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/StaDev/DCA
S75 | 南化SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/StaDev/Fire
S75 | 南化SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S75_A1 | [17 empty] | lamp2CC | OPRD1: S75/0/StaDev/PMA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/CFA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/IRFA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 | #1BUS |  | BUS_RYFA | 69KV BUS IED故障 |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/BUS_RYFA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | 12B_CTFA | 69KV BUS CT迴路故障 |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/12B_CTFA
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | COMT | 69KV空壓機COMT |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/COMT
S75 | 南化SS | 69 | 69kV | ComPoint_D1 |  |  | 1A3U_L | 69KV電驛標置G1/G2變更 |  | Status | USE_LOCK動作1 | Use/Lock | Y | 3 | DI-SP |  | B3/S75_D1 | [17 empty] | lamp2CC | OPRD1: S75/69/ComPoint/1A3U_L

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S75 | 南化SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 南化SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S75/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 南化SS.640_AMP | 曾文南化西口線 AMP | LINE69 | S75/69/640/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0600 | 540.000000 | 540.000000 | 600.000000 | 800.000000 | 1.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S75 | 南化SS | 0 |  |  |  |  | 水庫線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.水庫線KVA | 11KV水庫線KVA | FEEDER |  |  | KVA_CAL |  |  | 4 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 水庫線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.水庫線KW | 11KV水庫線KW | FEEDER |  |  | KW_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉山線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉山線KVA | 11KV玉山線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉山線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉山線KW | 11KV玉山線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉寮線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉寮線KVA | 11KV玉寮線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉寮線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉寮線KW | 11KV玉寮線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_MVA | #1MTR二次側 MVA | DTR |  |  | MVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_PF | #1MTR 功率因素 | DTR |  |  | RPDC_PF_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S75//3MTR/MVA |  | MVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_PF | #3MTR 功率因素 | DTR | S75//3MTR/PF |  | RPDC_PF_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S75 | 南化SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.210_SC_MVAR | 11KV#1SC MVAR | SC |  |  | SC_CAL_11 |  |  | 14 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S75/11/230/MVAR |  | SC_CAL_11 |  |  | 15 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉楠線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉楠線KVA | 11KV玉楠線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 玉楠線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.玉楠線KW | 11KV玉楠線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備24線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備24線KVA | 11KV備24線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備24線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備24線KW | 11KV備24線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備25線KVA | 11KV備25線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備25線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備25線KW | 11KV備25線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備34線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備34線KVA | 11KV備34線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備34線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備34線KW | 11KV備34線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備35線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備35線KVA | 11KV備35線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 備35線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.備35線KW | 11KV備35線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 化22線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.化22線KVA | 11KV化22線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 化22線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.化22線KW | 11KV化22線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S75//2MTR/MVA |  | MVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_PF | #2MTR 功率因素 | DTR | S75//2MTR/PF |  | RPDC_PF_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S75 | 南化SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S75/11/220/MVAR |  | SC_CAL_11 |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | ADCS_N | [8 empty] | 南化SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S75/69/810/MVAR |  | SC_CAL_69 |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 南化SS.610_AMP | 南化隆田線 AMP | LINE69 | S75/69/610/I |  | AMP_CAL |  |  | 32 | CalcAIPoint | [21 empty] | C08R0664 | 597.599976 | 597.599976 | 664.000000 | 800.000000 | 1.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S75 | 南化SS | 0 |  |  |  |  | 化21線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.化21線KVA | 11KV化21線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  |  |  |  | 化21線KW | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.化21線KW | 11KV化21線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 69 | 69kV | 640_CB | 曾文南化西口線(640_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.640_CB_4 | 640(曾文南化西口線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 35 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 600_CB | 600(600_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.600_CB_4 | 600 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 36 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 南化SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 37 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 南化SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 38 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 69SC警報 | 69SC警報 | [27 empty] | ADCS_N | [8 empty] | 南化SS.69SC警報_A | 69SC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 39 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_N | [8 empty] | 南化SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 40 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 南化SS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | S75/0/CalcPoint/SUBA |  | STATION_FAULT_8 |  |  | 41 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 42 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_2 |  |  | 43 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640_AMP | 曾文南化西口線 | [27 empty] | ADCS_N | [8 empty] | 南化SS.640_AMP_A | 曾文南化西口線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 44 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 69 | 69kV | 640_AMP | 曾文南化西口線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.640_AMP_4 | 曾文南化西口線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 45 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 46 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 47 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 3MTR_MVA | #3MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_MVA_4 | #3MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 48 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 49 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 南化SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 50 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 51 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 52 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | 69KV_N | [8 empty] | 南化SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 53 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | _SC_RYFA | SC | [27 empty] | ADCS_N | [8 empty] | 南化SS.69KV_SC_RYFA_A | 69KV SC IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 54 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _COMT | _COMT | [27 empty] | ADCS_N | [8 empty] | 南化SS.69KV_COMT_A | 空壓機運轉超時警報(AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 55 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600GDA(1) | #1BUS | [27 empty] | ADCS_N | [8 empty] | 南化SS.600GDA(1)_A | 69KV #1BUS TIE(600) 67N (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 56 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600GDA(2) | #2BUS | [27 empty] | ADCS_N | [8 empty] | 南化SS.600GDA(2)_A | 69KV #2BUS TIE(600) 67N (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 57 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600PHA(1) | #1BUS | [27 empty] | ADCS_N | [8 empty] | 南化SS.600PHA(1)_A | 69KV #1BUS TIE(600) 67 (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 58 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 600PHA(2) | #2BUS | [27 empty] | ADCS_N | [8 empty] | 南化SS.600PHA(2)_A | 69KV #2BUS TIE(600) 67 (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 59 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610_CB | 南化隆田線(610_CB) |  | 4 | [25 empty] | 69KV_N | [8 empty] | 南化SS.610_CB_4 | 610(南化隆田線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 60 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 610_AMP | 南化隆田線 | [27 empty] | ADCS_N | [8 empty] | 南化SS.610_AMP_A | 南化隆田線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 61 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 69 | 69kV | 610_AMP | 南化隆田線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.610_AMP_4 | 南化隆田線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 62 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S75/0/RTU/ADCH1 |  |  |  | CDC | 63 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S75/0/RTU/ADCH2 |  |  |  | CDC | 64 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S75/0/RTU/ADCH3 |  |  |  | CDC | 65 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S75/0/RTU/ADCL1 |  |  |  | CDC | 66 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S75/0/RTU/ADCL2 |  |  |  | CDC | 67 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S75/0/RTU/ADCL3 |  |  |  | CDC | 68 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S75/69/1BUS/V |  |  |  | CDC | 69 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S75/69/2BUS/V |  |  |  | CDC | 70 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S75 | 南化SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 71 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S75/11/3BUS/V_R |  |  |  | CDC | 72 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 69 | 69kV | 620 | 南化隆田線(620) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.620_MW | 南化隆田線 MW | LINE69 |  |  |  |  | CDC | 73 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S75 | 南化SS | 69 | 69kV | 620 | 南化隆田線(620) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.620_MVAR | 南化隆田線 MVAR | LINE69 |  |  |  |  | CDC | 74 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.640_MW | 曾文南化西口線 MW | LINE69 | S75/69/640/MW |  |  |  | CDC | 75 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.640_MVAR | 曾文南化西口線 MVAR | LINE69 | S75/69/640/MVAR |  |  |  | CDC | 76 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 11 | 11kV | 水庫線 | 水庫線 |  | 水庫線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.水庫線KVAR | 11KV水庫線 KVAR | FEEDER | S75/11/KX32/KVAR |  |  |  | CDC | 77 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 水庫線 | 水庫線 |  | 水庫線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.水庫線A1 | 11KV水庫線 R相AMP | FEEDER | S75/11/KX32/I_R |  |  |  | CDC | 78 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 水庫線 | 水庫線 |  | 水庫線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.水庫線A2 | 11KV水庫線 S相AMP | FEEDER | S75/11/KX32/I_S |  |  |  | CDC | 79 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 水庫線 | 水庫線 |  | 水庫線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.水庫線A3 | 11KV水庫線 T相AMP | FEEDER | S75/11/KX32/I_T |  |  |  | CDC | 80 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 水庫線 | 水庫線 |  | 水庫線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.水庫線A0 | 11KV水庫線 N相AMP | FEEDER | S75/11/KX32/I_N |  |  |  | CDC | 81 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉山線 | 玉山線 |  | 玉山線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉山線KVAR | 11KV玉山線 KVAR | FEEDER | S75/11/KX31/KVAR |  |  |  | CDC | 82 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉山線 | 玉山線 |  | 玉山線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉山線A1 | 11KV玉山線 R相AMP | FEEDER | S75/11/KX31/I_R |  |  |  | CDC | 83 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉山線 | 玉山線 |  | 玉山線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉山線A2 | 11KV玉山線 S相AMP | FEEDER | S75/11/KX31/I_S |  |  |  | CDC | 84 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉山線 | 玉山線 |  | 玉山線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉山線A3 | 11KV玉山線 T相AMP | FEEDER | S75/11/KX31/I_T |  |  |  | CDC | 85 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉山線 | 玉山線 |  | 玉山線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉山線A0 | 11KV玉山線 N相AMP | FEEDER | S75/11/KX31/I_N |  |  |  | CDC | 86 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉寮線 | 玉寮線 |  | 玉寮線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉寮線KVAR | 11KV玉寮線 KVAR | FEEDER | S75/11/KX33/KVAR |  |  |  | CDC | 87 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉寮線 | 玉寮線 |  | 玉寮線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉寮線A1 | 11KV玉寮線 R相AMP | FEEDER | S75/11/KX33/I_R |  |  |  | CDC | 88 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉寮線 | 玉寮線 |  | 玉寮線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉寮線A2 | 11KV玉寮線 S相AMP | FEEDER | S75/11/KX33/I_S |  |  |  | CDC | 89 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉寮線 | 玉寮線 |  | 玉寮線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉寮線A3 | 11KV玉寮線 T相AMP | FEEDER | S75/11/KX33/I_T |  |  |  | CDC | 90 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉寮線 | 玉寮線 |  | 玉寮線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉寮線A0 | 11KV玉寮線 N相AMP | FEEDER | S75/11/KX33/I_N |  |  |  | CDC | 91 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-8F | [5 empty] | A_-800_800(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.600TIE_AMP | 600TIE AMP | TIE | S75/69/600/I |  |  |  | CDC | 92 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C08R0600 | 540.000000 | 540.000000 | 600.000000 | 800.000000 | 1.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 93 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 94 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 95 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 96 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 97 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 98 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 99 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 100 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_MW | #3MTR二次側 MW | DTR | S75/11/M3/MW |  |  |  | CDC | 101 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S75/11/M3/MVAR |  |  |  | CDC | 102 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S75/11/M3/I_R |  |  |  | CDC | 103 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S75/11/M3/I_S |  |  |  | CDC | 104 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S75/11/M3/I_T |  |  |  | CDC | 105 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_OIL | #3MTR 油溫 | DTR | S75//3MTR/OilTemp |  |  |  | CDC | 106 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_COIL | #3MTR 線溫 | DTR | S75//3MTR/CoilTemp |  |  |  | CDC | 107 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-61 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S75//3MTR/TapPosMv |  |  |  | CDC | 108 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S75 | 南化SS | 11 | 11kV | 玉楠線 | 玉楠線 |  | 玉楠線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉楠線KVAR | 11KV玉楠線 KVAR | FEEDER | S75/11/KX23/KVAR |  |  |  | CDC | 109 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉楠線 | 玉楠線 |  | 玉楠線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉楠線A1 | 11KV玉楠線 R相AMP | FEEDER | S75/11/KX23/I_R |  |  |  | CDC | 110 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉楠線 | 玉楠線 |  | 玉楠線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉楠線A2 | 11KV玉楠線 S相AMP | FEEDER | S75/11/KX23/I_S |  |  |  | CDC | 111 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉楠線 | 玉楠線 |  | 玉楠線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉楠線A3 | 11KV玉楠線 T相AMP | FEEDER | S75/11/KX23/I_T |  |  |  | CDC | 112 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 玉楠線 | 玉楠線 |  | 玉楠線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.玉楠線A0 | 11KV玉楠線 N相AMP | FEEDER | S75/11/KX23/I_N |  |  |  | CDC | 113 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備24線 | 備24線 |  | 備24線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備24線KVAR | 11KV備24線 KVAR | FEEDER | S75/11/KX24/KVAR |  |  |  | CDC | 114 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備24線 | 備24線 |  | 備24線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備24線A1 | 11KV備24線 R相AMP | FEEDER | S75/11/KX24/I_R |  |  |  | CDC | 115 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備24線 | 備24線 |  | 備24線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備24線A2 | 11KV備24線 S相AMP | FEEDER | S75/11/KX24/I_S |  |  |  | CDC | 116 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備24線 | 備24線 |  | 備24線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備24線A3 | 11KV備24線 T相AMP | FEEDER | S75/11/KX24/I_T |  |  |  | CDC | 117 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備24線 | 備24線 |  | 備24線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備24線A0 | 11KV備24線 N相AMP | FEEDER | S75/11/KX24/I_N |  |  |  | CDC | 118 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備25線 | 備25線 |  | 備25線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備25線KVAR | 11KV備25線 KVAR | FEEDER | S75/11/KX25/KVAR |  |  |  | CDC | 119 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備25線 | 備25線 |  | 備25線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備25線A1 | 11KV備25線 R相AMP | FEEDER | S75/11/KX25/I_R |  |  |  | CDC | 120 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備25線 | 備25線 |  | 備25線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備25線A2 | 11KV備25線 S相AMP | FEEDER | S75/11/KX25/I_S |  |  |  | CDC | 121 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備25線 | 備25線 |  | 備25線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備25線A3 | 11KV備25線 T相AMP | FEEDER | S75/11/KX25/I_T |  |  |  | CDC | 122 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備25線 | 備25線 |  | 備25線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備25線A0 | 11KV備25線 N相AMP | FEEDER | S75/11/KX25/I_N |  |  |  | CDC | 123 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備34線 | 備34線 |  | 備34線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備34線KVAR | 11KV備34線 KVAR | FEEDER | S75/11/KX34/KVAR |  |  |  | CDC | 124 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備34線 | 備34線 |  | 備34線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備34線A1 | 11KV備34線 R相AMP | FEEDER | S75/11/KX34/I_R |  |  |  | CDC | 125 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備34線 | 備34線 |  | 備34線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備34線A2 | 11KV備34線 S相AMP | FEEDER | S75/11/KX34/I_S |  |  |  | CDC | 126 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備34線 | 備34線 |  | 備34線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備34線A3 | 11KV備34線 T相AMP | FEEDER | S75/11/KX34/I_T |  |  |  | CDC | 127 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備34線 | 備34線 |  | 備34線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備34線A0 | 11KV備34線 N相AMP | FEEDER | S75/11/KX34/I_N |  |  |  | CDC | 128 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備35線 | 備35線 |  | 備35線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備35線KVAR | 11KV備35線 KVAR | FEEDER | S75/11/KX35/KVAR |  |  |  | CDC | 129 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備35線 | 備35線 |  | 備35線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備35線A1 | 11KV備35線 R相AMP | FEEDER | S75/11/KX35/I_R |  |  |  | CDC | 130 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備35線 | 備35線 |  | 備35線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備35線A2 | 11KV備35線 S相AMP | FEEDER | S75/11/KX35/I_S |  |  |  | CDC | 131 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備35線 | 備35線 |  | 備35線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備35線A3 | 11KV備35線 T相AMP | FEEDER | S75/11/KX35/I_T |  |  |  | CDC | 132 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 備35線 | 備35線 |  | 備35線A0 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.備35線A0 | 11KV備35線 N相AMP | FEEDER | S75/11/KX35/I_N |  |  |  | CDC | 133 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化22線 | 化22線 |  | 化22線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化22線KVAR | 11KV化22線 KVAR | FEEDER | S75/11/KX22/KVAR |  |  |  | CDC | 134 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化22線 | 化22線 |  | 化22線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化22線A1 | 11KV化22線 R相AMP | FEEDER | S75/11/KX22/I_R |  |  |  | CDC | 135 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化22線 | 化22線 |  | 化22線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化22線A2 | 11KV化22線 S相AMP | FEEDER | S75/11/KX22/I_S |  |  |  | CDC | 136 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化22線 | 化22線 |  | 化22線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化22線A3 | 11KV化22線 T相AMP | FEEDER | S75/11/KX22/I_T |  |  |  | CDC | 137 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化22線 | 化22線 |  | 化22線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化22線A0 | 11KV化22線 N相AMP | FEEDER | S75/11/KX22/I_N |  |  |  | CDC | 138 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 2BUS | #2BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV#2BUS_KV | 11KV #2BUS KV | BUS | S75/11/2BUS/V_R |  |  |  | CDC | 139 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | _TIE2 | TIE2 |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV_TIE2_A1 | 11KV TIE2 R相AMP | TIE | S75/11/TIE2/I_R |  |  |  | CDC | 140 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | _TIE2 | TIE2 |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV_TIE2_A2 | 11KV TIE2 S相AMP | TIE | S75/11/TIE2/I_S |  |  |  | CDC | 141 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | _TIE2 | TIE2 |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11KV_TIE2_A3 | 11KV TIE2 T相AMP | TIE | S75/11/TIE2/I_T |  |  |  | CDC | 142 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_MW | #2MTR二次側 MW | DTR | S75/11/M2/MW |  |  |  | CDC | 143 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S75/11/M2/MVAR |  |  |  | CDC | 144 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S75/11/M2/I_R |  |  |  | CDC | 145 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S75/11/M2/I_S |  |  |  | CDC | 146 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S75/11/M2/I_T |  |  |  | CDC | 147 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_OIL | #2MTR 油溫 | DTR | S75//2MTR/OilTemp |  |  |  | CDC | 148 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_COIL | #2MTR 線溫 | DTR | S75//2MTR/CoilTemp |  |  |  | CDC | 149 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 南化SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S75//2MTR/TapPosMv |  |  |  | CDC | 150 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S75 | 南化SS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-91 | [5 empty] | kV_-150_150(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.直流N電源電壓 | 直流N電源電壓 | OTHER | S75/0/StaDev/DCV_N |  |  |  | CDC | 151 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
S75 | 南化SS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-90 | [5 empty] | kV_-150_150(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.直流P電源電壓 | 直流P電源電壓 | OTHER | S75/0/StaDev/DCV_P |  |  |  | CDC | 152 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.610_MW | 南化隆田線 MW | LINE69 | S75/69/610/MW |  |  |  | CDC | 153 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-96_96(-2000_2000) |  | ADCS_N | [8 empty] | 南化SS.610_MVAR | 南化隆田線 MVAR | LINE69 | S75/69/610/MVAR |  |  |  | CDC | 154 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.192000 | 0.010000
S75 | 南化SS | 0 |  | 11S12BUS | 11S1 |  | V | [17 empty] | 2-AA | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11S1#2BUS_KV | 11S1 #2BUS KV | BUS | S75/11/2BUS/V_S |  |  |  | CDC | 155 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 0 |  | 11S13BUS | 11S1 |  | V | [17 empty] | 2-AC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11S1#3BUS_KV | 11S1 #3BUS KV | BUS | S75/11/3BUS/V_S |  |  |  | CDC | 156 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 0 |  | 11T12BUS | 11T1 |  | V | [17 empty] | 2-AB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11T1#2BUS_KV | 11T1 #2BUS KV | BUS | S75/11/2BUS/V_T |  |  |  | CDC | 157 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 0 |  | 11T13BUS | 11T1 |  | V | [17 empty] | 2-AD | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.11T1#3BUS_KV | 11T1 #3BUS KV | BUS | S75/11/3BUS/V_T |  |  |  | CDC | 158 | GENERICAIPoint | SS418_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S75 | 南化SS | 11 | 11kV | 化21線 | 化21線 |  | 化21線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化21線KVAR | 11KV化21線 KVAR | FEEDER | S75/11/KX21/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化21線 | 化21線 |  | 化21線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化21線A1 | 11KV化21線 R相AMP | FEEDER | S75/11/KX21/I_R |  |  |  | CDC | 160 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化21線 | 化21線 |  | 化21線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化21線A2 | 11KV化21線 S相AMP | FEEDER | S75/11/KX21/I_S |  |  |  | CDC | 161 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化21線 | 化21線 |  | 化21線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化21線A3 | 11KV化21線 T相AMP | FEEDER | S75/11/KX21/I_T |  |  |  | CDC | 162 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 11 | 11kV | 化21線 | 化21線 |  | 化21線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南化SS.化21線A0 | 11KV化21線 N相AMP | FEEDER | S75/11/KX21/I_N |  |  |  | CDC | 163 | GENERICAIPoint | SS418_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | PHA | [17 empty] | 1-08-02 | [7 empty] | 69KV_N | [8 empty] | 南化SS.640_PHA | 曾文南化西口線(640) 相間RY | LINE69 | S75/69/640/PHA |  |  |  | CDC | 164 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | 69KV_N | [8 empty] | 南化SS.640_GDA | 曾文南化西口線(640) 接地RY | LINE69 | S75/69/640/GDA |  |  |  | CDC | 165 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | CB | [17 empty] | 1-08-00 |  | 1-04 | [5 empty] | 69KV_N | [8 empty] | 南化SS.640_CB | 640(曾文南化西口線) CB | LINE69 | S75/69/640/CB |  |  |  | CDC | 166 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_PHA | 11KV化21線(KX21) 相間RY | FEEDER | S75/11/KX21/PHA |  |  |  | CDC | 167 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_GDA | 11KV化21線(KX21) 接地RY | FEEDER | S75/11/KX21/GDA |  |  |  | CDC | 168 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_79UL | 11KV化21線(KX21) 79RY U/L | FEEDER | S75/11/KX21/79UL |  |  |  | CDC | 169 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX21 | 化21線(KX21) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_ADJ | 11KV化21線(KX21) LCO分流器 U/L | FEEDER | S75/11/KX21/ADJ |  |  |  | CDC | 170 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX21 | KX21(11KV化21線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_CB | KX21(11KV化21線) CB | FEEDER | S75/11/KX21/CB |  |  |  | CDC | 171 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_PHA | 11KV化22線(KX22) 相間RY | FEEDER | S75/11/KX22/PHA |  |  |  | CDC | 172 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_GDA | 11KV化22線(KX22) 接地RY | FEEDER | S75/11/KX22/GDA |  |  |  | CDC | 173 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_79UL | 11KV化22線(KX22) 79RY U/L | FEEDER | S75/11/KX22/79UL |  |  |  | CDC | 174 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX22 | 化22線(KX22) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_ADJ | 11KV化22線(KX22) LCO分流器 U/L | FEEDER | S75/11/KX22/ADJ |  |  |  | CDC | 175 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX22 | KX22(11KV化22線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_CB | KX22(11KV化22線) CB | FEEDER | S75/11/KX22/CB |  |  |  | CDC | 176 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | PHA | [17 empty] | 1-12-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_PHA | 11KV玉山線(KX31) 相間RY | FEEDER | S75/11/KX31/PHA |  |  |  | CDC | 177 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) |  | GDA | [17 empty] | 1-12-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_GDA | 11KV玉山線(KX31) 接地RY | FEEDER | S75/11/KX31/GDA |  |  |  | CDC | 178 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-64 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_79UL | 11KV玉山線(KX31) 79RY U/L | FEEDER | S75/11/KX31/79UL |  |  |  | CDC | 179 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX31 | 玉山線(KX31) LCO分流器 |  | ADJ | [17 empty] | 1-36-10 |  | 1-7A | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_ADJ | 11KV玉山線(KX31) LCO分流器 U/L | FEEDER | S75/11/KX31/ADJ |  |  |  | CDC | 180 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX31 | KX31(11KV玉山線) |  | CB | [17 empty] | 1-11-04 |  | 1-5C | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_CB | KX31(11KV玉山線) CB | FEEDER | S75/11/KX31/CB |  |  |  | CDC | 181 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_PHA | 11KV水庫線(KX32) 相間RY | FEEDER | S75/11/KX32/PHA |  |  |  | CDC | 182 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_GDA | 11KV水庫線(KX32) 接地RY | FEEDER | S75/11/KX32/GDA |  |  |  | CDC | 183 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) 79RY |  | 79UL | [17 empty] | 1-35-08 |  | 1-65 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_79UL | 11KV水庫線(KX32) 79RY U/L | FEEDER | S75/11/KX32/79UL |  |  |  | CDC | 184 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX32 | 水庫線(KX32) LCO分流器 |  | ADJ | [17 empty] | 1-36-11 |  | 1-7B | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_ADJ | 11KV水庫線(KX32) LCO分流器 U/L | FEEDER | S75/11/KX32/ADJ |  |  |  | CDC | 185 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX32 | KX32(11KV水庫線) |  | CB | [17 empty] | 1-11-05 |  | 1-5D | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_CB | KX32(11KV水庫線) CB | FEEDER | S75/11/KX32/CB |  |  |  | CDC | 186 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-05-00 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 南化SS.600_CB | 600(TIE) CB | TIE | S75/69/600/CB |  |  |  | CDC | 187 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 188 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 189 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 190 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 191 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 192 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 193 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 194 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_81A/S | #1MTR 81RY A/S | DTR |  |  |  |  | CDC | 195 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S75 | 南化SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 196 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 197 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 198 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 199 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 200 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S75 | 南化SS | 69 | 69kV | 750 | #1MTR(750) |  | ABS1 | 751 | [16 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.751_ABS | 751(#1MTR) ABS | DTR |  |  |  |  | CDC | 201 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_96A | #1MTR 96P RY | DTR |  |  |  |  | CDC | 202 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 203 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 204 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-03 |  | 1-58 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.770_CB | 770(#3MTR) CB | DTR | S75/69/770/CB |  |  |  | CDC | 205 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-04 |  | 1-59 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.3M_CB | 3M(#3MTR) CB | DTR | S75/11/M3/CB |  |  |  | CDC | 206 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-02-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_51A | #3MTR 51RY | DTR | S75/69/770/51A |  |  |  | CDC | 207 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-02-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_51NA | #3MTR 51N RY | DTR | S75/69/770/51NA |  |  |  | CDC | 208 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-03-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S75//3MTR/51ZA |  |  |  | CDC | 209 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_87A | #3MTR 87RY | DTR | S75//3MTR/87A |  |  |  | CDC | 210 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 1-35-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S75//3MTR/87UL |  |  |  | CDC | 211 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 81AS | [17 empty] | 1-12-01 |  | 1-69 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_81A/S | #3MTR 81RY A/S | DTR | S75/69/770/81AS |  |  |  | CDC | 212 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S75 | 南化SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S75/11/M3/51A |  |  |  | CDC | 213 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_TRA | #3MTR 重故障 | DTR | S75//3MTR/TRA |  |  |  | CDC | 214 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-35-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S75//3MTR/TRF |  |  |  | CDC | 215 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-35-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S75//3MTR/SupLocal |  |  |  | CDC | 216 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-35-05 |  | 1-62 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S75//3MTR/Tap Chan |  |  |  | CDC | 217 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 1-35-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S75//3MTR/OLTC_DLY |  |  |  | CDC | 218 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 1-34-13 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S75//3MTR/AC_Fault |  |  |  | CDC | 219 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 220 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 221 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S75 | 南化SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 222 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 223 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-11-03 |  | 1-5B | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.230_CB | 230(11KV #3SC) CB | SC | S75/11/230/CB |  |  |  | CDC | 224 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-35-06 |  | 1-63 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S75/11/230/SC_A_M |  |  |  | CDC | 225 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-12-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.230_SCA | 11KV #3SC 51,51N RY | SC | S75/11/230/SCA |  |  |  | CDC | 226 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-12-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S75/11/230/UVA |  |  |  | CDC | 227 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S75/69/1BUS/BUS_VUA |  |  |  | CDC | 228 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S75/69/2BUS/BUS_VUA |  |  |  | CDC | 229 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S75/11/ComPoint/CBA |  |  |  | CDC | 230 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S75/11/ComPoint/CBF |  |  |  | CDC | 231 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S75/69/ComPoint/ABS_89A |  |  |  | CDC | 232 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S75/69/ComPoint/CBA |  |  |  | CDC | 233 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S75/69/ComPoint/CBF |  |  |  | CDC | 234 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S75/0/RTU/RTU_R_L |  |  |  | CDC | 235 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S75 | 南化SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.TEST_CB | TEST CB | OTHER | S75/0/RTU/Test_CB |  |  |  | CDC | 236 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S75/0/StaDev/PSF |  |  |  | CDC | 237 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S75/0/StaDev/ACB1 |  |  |  | CDC | 238 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S75 | 南化SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S75/0/StaDev/ACB2 |  |  |  | CDC | 239 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S75 | 南化SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S75/0/StaDev/STUV |  |  |  | CDC | 240 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.直流充電機故障 | 直流充電機故障 | OTHER | S75/0/StaDev/CHG1 |  |  |  | CDC | 241 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S75/0/StaDev/DCA |  |  |  | CDC | 242 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S75/0/StaDev/DCE |  |  |  | CDC | 243 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S75/0/StaDev/OilLeak |  |  |  | CDC | 244 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S75/0/StaDev/5A5Other |  |  |  | CDC | 245 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S75/0/StaDev/6A5Other |  |  |  | CDC | 246 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S75/0/StaDev/7A5Other |  |  |  | CDC | 247 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S75/0/StaDev/CHG2 |  |  |  | CDC | 248 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S75/0/StaDev/CommACF |  |  |  | CDC | 249 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S75/0/StaDev/Door1 |  |  |  | CDC | 250 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S75 | 南化SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S75/0/StaDev/Lights1 |  |  |  | CDC | 251 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S75 | 南化SS | 0 |  |  |  |  | 69SC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69SC警報 | 69SC警報 | OTHER | S75/69/810/60A |  |  |  | CDC | 252 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.RTU_DC故障 | RTU DC故障 | OTHER | S75/0/RTU/DCA |  |  |  | CDC | 253 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 水氣霧/CO2故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.水氣霧/CO2故障 | 水氣霧/CO2故障 | OTHER | S75/0/StaDev/2A5Other |  |  |  | CDC | 254 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 水氣霧/CO2警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.水氣霧/CO2警報 | 水氣霧/CO2警報 | OTHER | S75/0/StaDev/3A5Other |  |  |  | CDC | 255 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.火災警報 | 火災警報 | OTHER | S75/0/StaDev/Fire |  |  |  | CDC | 256 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.安全監控 | 保全設定 | OTHER | S75/0/StaDev/1A5Other |  |  |  | CDC | 257 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.門禁小門 | 門禁小門 | OTHER | S75/0/StaDev/Door2 |  |  |  | CDC | 258 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S75/0/StaDev/Lights |  |  |  | CDC | 259 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_PHA | 11KV玉楠線(KX23) 相間RY | FEEDER | S75/11/KX23/PHA |  |  |  | CDC | 260 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_GDA | 11KV玉楠線(KX23) 接地RY | FEEDER | S75/11/KX23/GDA |  |  |  | CDC | 261 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_79UL | 11KV玉楠線(KX23) 79RY U/L | FEEDER | S75/11/KX23/79UL |  |  |  | CDC | 262 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX23 | 玉楠線(KX23) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_ADJ | 11KV玉楠線(KX23) LCO分流器 U/L | FEEDER | S75/11/KX23/ADJ |  |  |  | CDC | 263 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX23 | KX23(11KV玉楠線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_CB | KX23(11KV玉楠線) CB | FEEDER | S75/11/KX23/CB |  |  |  | CDC | 264 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-05 |  | 1-57 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S75/0/StaDev/4A5Other |  |  |  | CDC | 265 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_PHA | 11KV備24線(KX24) 相間RY | FEEDER | S75/11/KX24/PHA |  |  |  | CDC | 266 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_GDA | 11KV備24線(KX24) 接地RY | FEEDER | S75/11/KX24/GDA |  |  |  | CDC | 267 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_79UL | 11KV備24線(KX24) 79RY U/L | FEEDER | S75/11/KX24/79UL |  |  |  | CDC | 268 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX24 | 備24線(KX24) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_ADJ | 11KV備24線(KX24) LCO分流器 U/L | FEEDER | S75/11/KX24/ADJ |  |  |  | CDC | 269 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX24 | KX24(11KV備24線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_CB | KX24(11KV備24線) CB | FEEDER | S75/11/KX24/CB |  |  |  | CDC | 270 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_PHA | 11KV備25線(KX25) 相間RY | FEEDER | S75/11/KX25/PHA |  |  |  | CDC | 271 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_GDA | 11KV備25線(KX25) 接地RY | FEEDER | S75/11/KX25/GDA |  |  |  | CDC | 272 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_79UL | 11KV備25線(KX25) 79RY U/L | FEEDER | S75/11/KX25/79UL |  |  |  | CDC | 273 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX25 | 備25線(KX25) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_ADJ | 11KV備25線(KX25) LCO分流器 U/L | FEEDER | S75/11/KX25/ADJ |  |  |  | CDC | 274 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX25 | KX25(11KV備25線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_CB | KX25(11KV備25線) CB | FEEDER | S75/11/KX25/CB |  |  |  | CDC | 275 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | PHA | [17 empty] | 1-13-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_PHA | 11KV玉寮線(KX33) 相間RY | FEEDER | S75/11/KX33/PHA |  |  |  | CDC | 276 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) |  | GDA | [17 empty] | 1-13-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_GDA | 11KV玉寮線(KX33) 接地RY | FEEDER | S75/11/KX33/GDA |  |  |  | CDC | 277 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-66 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_79UL | 11KV玉寮線(KX33) 79RY U/L | FEEDER | S75/11/KX33/79UL |  |  |  | CDC | 278 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX33 | 玉寮線(KX33) LCO分流器 |  | ADJ | [17 empty] | 1-36-12 |  | 1-7C | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_ADJ | 11KV玉寮線(KX33) LCO分流器 U/L | FEEDER | S75/11/KX33/ADJ |  |  |  | CDC | 279 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX33 | KX33(11KV玉寮線) |  | CB | [17 empty] | 1-11-06 |  | 1-5E | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_CB | KX33(11KV玉寮線) CB | FEEDER | S75/11/KX33/CB |  |  |  | CDC | 280 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | PHA | [17 empty] | 1-13-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_PHA | 11KV備34線(KX34) 相間RY | FEEDER | S75/11/KX34/PHA |  |  |  | CDC | 281 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) |  | GDA | [17 empty] | 1-13-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_GDA | 11KV備34線(KX34) 接地RY | FEEDER | S75/11/KX34/GDA |  |  |  | CDC | 282 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) 79RY |  | 79UL | [17 empty] | 1-35-10 |  | 1-67 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_79UL | 11KV備34線(KX34) 79RY U/L | FEEDER | S75/11/KX34/79UL |  |  |  | CDC | 283 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX34 | 備34線(KX34) LCO分流器 |  | ADJ | [17 empty] | 1-36-13 |  | 1-7D | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_ADJ | 11KV備34線(KX34) LCO分流器 U/L | FEEDER | S75/11/KX34/ADJ |  |  |  | CDC | 284 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX34 | KX34(11KV備34線) |  | CB | [17 empty] | 1-11-07 |  | 1-5F | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_CB | KX34(11KV備34線) CB | FEEDER | S75/11/KX34/CB |  |  |  | CDC | 285 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_PHA | 11KV備35線(KX35) 相間RY | FEEDER | S75/11/KX35/PHA |  |  |  | CDC | 286 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_GDA | 11KV備35線(KX35) 接地RY | FEEDER | S75/11/KX35/GDA |  |  |  | CDC | 287 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-68 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_79UL | 11KV備35線(KX35) 79RY U/L | FEEDER | S75/11/KX35/79UL |  |  |  | CDC | 288 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 11 | 11kV | KX35 | 備35線(KX35) LCO分流器 |  | ADJ | [17 empty] | 1-36-14 |  | 1-7E | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_ADJ | 11KV備35線(KX35) LCO分流器 U/L | FEEDER | S75/11/KX35/ADJ |  |  |  | CDC | 289 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | KX35 | KX35(11KV備35線) |  | CB | [17 empty] | 1-12-00 |  | 1-60 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_CB | KX35(11KV備35線) CB | FEEDER | S75/11/KX35/CB |  |  |  | CDC | 290 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.11KV_IED_FA | 11KV IED故障 | OTHER | S75/11/ComPoint/IRFA |  |  |  | CDC | 291 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 640 | 曾文南化西口線(640) |  | 87A | [17 empty] | 1-08-01 | [7 empty] | ADCS_N | [8 empty] | 南化SS.640_87A | 曾文南化西口線(640) 87RY | OTHER | S75/69/640/87A |  |  |  | CDC | 292 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 640 | 曾文南化西口線(640) |  | 87UL | [17 empty] | 1-32-09 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 南化SS.640_87UL | 曾文南化西口線(640) 87RY UL | OTHER | S75/69/640/87UL |  |  |  | CDC | 293 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | 69KV_N | [8 empty] | 南化SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S75/69/ComPoint/CFA |  |  |  | CDC | 294 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | 69KV_N | [8 empty] | 南化SS.69KV_IED_FA | 69KV IED故障 | OTHER | S75/69/ComPoint/IRFA |  |  |  | CDC | 295 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.81RY_IED_FA | 低頻IED故障 | OTHER | S75/0/StaDev/81A_RYFA |  |  |  | CDC | 296 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.PM_CFA | PM通訊故障 | OTHER | S75/0/StaDev/PMA |  |  |  | CDC | 297 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | TIE2 | TIE2 |  | CB | [17 empty] | 1-0F-03 |  | 1-47 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.TIE2_CB | 11KV TIE2 CB | TIE | S75/11/TIE2/CB |  |  |  | CDC | 298 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 11 | 11kV | TIE2 | TIE2 |  | 51A | [17 empty] | 1-11-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.TIE2_51A | 11KV TIE2 51RY | TIE | S75/11/TIE2/51A |  |  |  | CDC | 299 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | TIE2 | TIE2 |  | 51NA | [17 empty] | 1-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.TIE2_51NA | 11KV TIE2 51N RY | TIE | S75/11/TIE2/51NA |  |  |  | CDC | 300 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-01 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.760_CB | 760(#2MTR) CB | DTR | S75/69/760/CB |  |  |  | CDC | 301 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 2M | #2MTR |  | CB | [17 empty] | 1-01-02 |  | 1-45 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.2M_CB | 2M(#2MTR) CB | DTR | S75/11/M2/CB |  |  |  | CDC | 302 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_51A | #2MTR 51RY | DTR | S75/69/760/51A |  |  |  | CDC | 303 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_51NA | #2MTR 51N RY | DTR | S75/69/760/51NA |  |  |  | CDC | 304 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S75//2MTR/51ZA |  |  |  | CDC | 305 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_87A | #2MTR 87RY | DTR | S75//2MTR/87A |  |  |  | CDC | 306 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S75//2MTR/87UL |  |  |  | CDC | 307 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 2M | #2MTR二次側(2M) |  | 51A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.2M_51A | #2MTR二次側(2M) 51RY | DTR | S75/11/M2/51A |  |  |  | CDC | 308 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_TRA | #2MTR 重故障 | DTR | S75//2MTR/TRA |  |  |  | CDC | 309 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S75//2MTR/TRF |  |  |  | CDC | 310 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S75//2MTR/SupLocal |  |  |  | CDC | 311 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S75//2MTR/Tap Chan |  |  |  | CDC | 312 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S75//2MTR/OLTC_DLY |  |  |  | CDC | 313 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S75//2MTR/AC_Fault |  |  |  | CDC | 314 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.220_CB | 220(11KV #2SC) CB | SC | S75/11/220/CB |  |  |  | CDC | 315 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S75/11/220/SC_A_M |  |  |  | CDC | 316 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.220_SCA | 11KV #2SC 51,51N RY | SC | S75/11/220/SCA |  |  |  | CDC | 317 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S75/11/220/UVA |  |  |  | CDC | 318 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 51UL | [17 empty] | 1-37-09 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_51UL | #2MTR 51 RY U/L | OTHER | S75//2MTR/51_UL |  |  |  | CDC | 319 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-37-10 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_51ZUL | #2MTR 51Z RY U/L | OTHER | S75//2MTR/51Z_UL |  |  |  | CDC | 320 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-03-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_86A | #2MTR 86RY | OTHER | S75//2MTR/MTR_86A |  |  |  | CDC | 321 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-37-08 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_RYFA | #2MTR 數位電驛故障 | OTHER | S75//2MTR/RYFA |  |  |  | CDC | 322 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2M | #2M |  | 51NA | [17 empty] | 1-04-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2M_51NA | #2M 51N RY | OTHER | S75/11/M2/51NA |  |  |  | CDC | 323 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 51UL | [17 empty] | 1-37-12 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_51UL | #3MTR 51 RY U/L | OTHER | S75//3MTR/51_UL |  |  |  | CDC | 324 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 1-37-13 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_51ZUL | #3MTR 51Z RY U/L | OTHER | S75//3MTR/51Z_UL |  |  |  | CDC | 325 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-03-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_86A | #3MTR 86RY | OTHER | S75//3MTR/MTR_86A |  |  |  | CDC | 326 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_RYFA | #3MTR 數位電驛故障 | OTHER | S75//3MTR/RYFA |  |  |  | CDC | 327 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3M | #3M |  | 51NA | [17 empty] | 1-04-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3M_51NA | #3M 51N RY | OTHER | S75/11/M3/51NA |  |  |  | CDC | 328 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S75//2MTR/63Q |  |  |  | CDC | 329 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S75//2MTR/96B1 |  |  |  | CDC | 330 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S75//2MTR/96B2 |  |  |  | CDC | 331 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S75//2MTR/96D |  |  |  | CDC | 332 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S75//2MTR/96P |  |  |  | CDC | 333 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-19-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | S75//3MTR/63Q |  |  |  | CDC | 334 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-19-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | S75//3MTR/96B1 |  |  |  | CDC | 335 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-19-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | S75//3MTR/96B2 |  |  |  | CDC | 336 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-19-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | S75//3MTR/96D |  |  |  | CDC | 337 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-19-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | S75//3MTR/96P |  |  |  | CDC | 338 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-38-08 | 1-38-09 | 1-28 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.771_DS | 771(#3MTR) DS | DTR | S75/69/770/DS1 |  |  |  | CDC | 339 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-38-10 | 1-38-11 | 1-29 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.772_DS | 772(#3MTR) DS | DTR | S75/69/770/DS2 |  |  |  | CDC | 340 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-05-05 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 南化SS.810_CB | 810(69KV #1SC) CB | SC | S75/69/810/CB |  |  |  | CDC | 341 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 1-38-12 | 1-38-13 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 南化SS.811_DS | 811(69KV #1SC) DS | SC | S75/69/810/DS1 |  |  |  | CDC | 342 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 1-38-14 | 1-38-15 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 南化SS.812_DS | 812(69KV #1SC) DS | SC | S75/69/810/DS2 |  |  |  | CDC | 343 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-05-07 | [7 empty] | 69KV_N | [8 empty] | 南化SS.810_SCA | 69KV #1SC 51,51N RY | SC | S75/69/810/SCA |  |  |  | CDC | 344 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-05-06 | [7 empty] | 69KV_N | [8 empty] | 南化SS.810_OUVA | 69KV #1SC 27,59RY | SC | S75/69/810/UVA |  |  |  | CDC | 345 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _SC | SC |  | RYFA | [17 empty] | 1-33-15 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69KV_SC_RYFA | 69KV SC IED故障 | OTHER | S75/69/810/RYFA |  |  |  | CDC | 346 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 69KV空壓機COMT | [17 empty] | 1-33-14 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.69KV空壓機COMT | 空壓機運轉超時警報 | OTHER | S75/69/ComPoint/COMT |  |  |  | CDC | 347 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | E3 | 643E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 南化SS.643E_ES | 643E(曾文南化西口線) ES | LINE69 | S75/69/640/ES3 |  |  |  | CDC | 348 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 600GDA(1) | [17 empty] | 1-05-02 | [7 empty] | ADCS_N | [8 empty] | 南化SS.600GDA(1) | 69KV #1BUS TIE(600) 67N | OTHER | S75/69/600/GDA1 |  |  |  | CDC | 349 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 600GDA(2) | [17 empty] | 1-05-04 | [7 empty] | ADCS_N | [8 empty] | 南化SS.600GDA(2) | 69KV #2BUS TIE(600) 67N | OTHER | S75/69/600/GDA2 |  |  |  | CDC | 350 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 600PHA(1) | [17 empty] | 1-05-01 | [7 empty] | ADCS_N | [8 empty] | 南化SS.600PHA(1) | 69KV #1BUS TIE(600) 67 | OTHER | S75/69/600/PHA1 |  |  |  | CDC | 351 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 600PHA(2) | [17 empty] | 1-05-03 | [7 empty] | ADCS_N | [8 empty] | 南化SS.600PHA(2) | 69KV #2BUS TIE(600) 67 | OTHER | S75/69/600/PHA2 |  |  |  | CDC | 352 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 640_87RY | 640 |  | CFA | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 南化SS.640_87RY_CFA | 640 87RY IED通訊故障 | OTHER | S75/69/640/87CFA |  |  |  | CDC | 353 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 640 | 曾文南化西口線(640) |  | RYFA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 南化SS.640_RYFA | 640 IED故障 | OTHER | S75/69/640/RYFA |  |  |  | CDC | 354 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 87A | [17 empty] | 1-06-00 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER | S75/69/1BUS/87A |  |  |  | CDC | 355 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL | [17 empty] | 1-35-12 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 南化SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER | S75/69/1BUS/87UL |  |  |  | CDC | 356 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 87A | [17 empty] | 1-06-01 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER | S75/69/2BUS/87A |  |  |  | CDC | 357 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL | [17 empty] | 1-35-13 |  | 1-0F | [5 empty] | ADCS_N | [8 empty] | 南化SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER | S75/69/2BUS/87UL |  |  |  | CDC | 358 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | S75/69/ComPoint/12B_CTFA |  |  |  | CDC | 359 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER | S75/69/ComPoint/BUS_RYFA |  |  |  | CDC | 360 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | _TIE | TIE |  | RYFA | [17 empty] | 1-33-13 | [7 empty] | ADCS_N | [8 empty] | 南化SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER | S75/69/600/RYFA |  |  |  | CDC | 361 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | PHA | [17 empty] | 1-07-06 | [7 empty] | 69KV_N | [8 empty] | 南化SS.610_PHA | 南化隆田線(610) 相間RY | LINE69 | S75/69/610/PHA |  |  |  | CDC | 362 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | GDA | [17 empty] | 1-07-07 | [7 empty] | 69KV_N | [8 empty] | 南化SS.610_GDA | 南化隆田線(610) 接地RY | LINE69 | S75/69/610/GDA |  |  |  | CDC | 363 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | CB | [17 empty] | 1-07-04 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 南化SS.610_CB | 610(南化隆田線) CB | LINE69 | S75/69/610/CB |  |  |  | CDC | 364 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | DS1 | 611 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-18 | [5 empty] | ADCS_N | [8 empty] | 南化SS.611_DS | 611(南化隆田線) DS | LINE69 | S75/69/610/DS1 |  |  |  | CDC | 365 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | DS2 | 612 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 南化SS.612_DS | 612(南化隆田線) DS | LINE69 | S75/69/610/DS2 |  |  |  | CDC | 366 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | DS3 | 613 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 南化SS.613_DS | 613(南化隆田線) DS | LINE69 | S75/69/610/DS3 |  |  |  | CDC | 367 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | E3 | 613E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 南化SS.613E_ES | 613E(南化隆田線) ES | LINE69 | S75/69/610/ES3 |  |  |  | CDC | 368 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | DS1 | 641 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 南化SS.641_DS | 641(曾文南化西口線) DS | LINE69 | S75/69/640/DS1 |  |  |  | CDC | 369 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | DS2 | 642 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 南化SS.642_DS | 642(曾文南化西口線) DS | LINE69 | S75/69/640/DS2 |  |  |  | CDC | 370 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | DS3 | 643 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 南化SS.643_DS | 643(曾文南化西口線) DS | LINE69 | S75/69/640/DS3 |  |  |  | CDC | 371 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-22 | [5 empty] | ADCS_N | [8 empty] | 南化SS.601_DS | 601(TIE) DS | TIE | S75/69/600/DS1 |  |  |  | CDC | 372 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-23 | [5 empty] | ADCS_N | [8 empty] | 南化SS.602_DS | 602(TIE) DS | TIE | S75/69/600/DS2 |  |  |  | CDC | 373 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 81AS | [17 empty] | 1-0F-04 |  | 1-56 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_81A/S | #2MTR 81RY A/S | DTR | S75/69/760/81A |  |  |  | CDC | 374 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-38-04 | 1-38-05 | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.761_DS | 761(#2MTR) DS | DTR | S75/69/760/DS1 |  |  |  | CDC | 375 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-38-06 | 1-38-07 | 1-27 | [5 empty] | DDCS4_2 | [8 empty] | 南化SS.762_DS | 762(#2MTR) DS | DTR | S75/69/760/DS2 |  |  |  | CDC | 376 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S75 | 南化SS | 0 |  | 610 | 南化隆田線(610) |  | 87A | [17 empty] | 1-07-05 | [7 empty] | ADCS_N | [8 empty] | 南化SS.610_87A | 610南化隆田線87RY | OTHER | S75/69/610/87A |  |  |  | CDC | 377 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 610_87RY | 610 |  | CFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 南化SS.610_87RY_CFA | 610 87RY IED通訊故障 | OTHER | S75/69/610/87CFA |  |  |  | CDC | 378 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 610 | 南化隆田線(610) |  | 87UL | [17 empty] | 1-32-06 |  | 1-0B | [5 empty] | ADCS_N | [8 empty] | 南化SS.610_87UL | 610南化隆田線87RY UL | OTHER | S75/69/610/87UL |  |  |  | CDC | 379 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  | 610 | 南化隆田線(610) |  | RYFA | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 南化SS.610_RYFA | 610 IED故障 | OTHER | S75/69/610/RYFA |  |  |  | CDC | 380 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.變電所低水位 | 變電所低水位 | OTHER | S75/0/StaDev/Water1 |  |  |  | CDC | 381 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.變電所高水位 | 變電所高水位 | OTHER | S75/0/StaDev/Water2 |  |  |  | CDC | 382 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S75//2MTR/96PA |  |  |  | CDC | 383 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-00 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR | S75//3MTR/96PA |  |  |  | CDC | 384 | GENERICDIPoint | SS418_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX21 | 化21線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_LOA | 化21線 復閉失敗閉鎖 | OTHER | S75/11/KX21/LOA |  |  |  | CDC | 385 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX22 | 化22線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_LOA | 化22線 復閉失敗閉鎖 | OTHER | S75/11/KX22/LOA |  |  |  | CDC | 386 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX23 | 玉楠線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_LOA | 玉楠線 復閉失敗閉鎖 | OTHER | S75/11/KX23/LOA |  |  |  | CDC | 387 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX24 | 備24線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_LOA | 備24線 復閉失敗閉鎖 | OTHER | S75/11/KX24/LOA |  |  |  | CDC | 388 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX25 | 備25線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_LOA | 備25線 復閉失敗閉鎖 | OTHER | S75/11/KX25/LOA |  |  |  | CDC | 389 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX31 | 玉山線 |  | LOA | [17 empty] | 1-3F-06 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_LOA | 玉山線 復閉失敗閉鎖 | OTHER | S75/11/KX31/LOA |  |  |  | CDC | 390 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX32 | 水庫線 |  | LOA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_LOA | 水庫線 復閉失敗閉鎖 | OTHER | S75/11/KX32/LOA |  |  |  | CDC | 391 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX33 | 玉寮線 |  | LOA | [17 empty] | 1-3F-08 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_LOA | 玉寮線 復閉失敗閉鎖 | OTHER | S75/11/KX33/LOA |  |  |  | CDC | 392 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX34 | 備34線 |  | LOA | [17 empty] | 1-3F-09 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_LOA | 備34線 復閉失敗閉鎖 | OTHER | S75/11/KX34/LOA |  |  |  | CDC | 393 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | KX35 | 備35線 |  | LOA | [17 empty] | 1-3F-10 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_LOA | 備35線 復閉失敗閉鎖 | OTHER | S75/11/KX35/LOA |  |  |  | CDC | 394 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S75 | 南化SS | 0 |  | CO2 | CO2 |  | UL | [17 empty] | 1-3F-15 | [7 empty] | DDCS4_2 | [8 empty] | 南化SS.CO2_UL | CO2 UL | OTHER | S75/0/StaDev/1A3U_L |  |  |  | CDC | 395 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S75 | 南化SS | 0 |  |  |  |  | 69KV標置變更 | [17 empty] | 1-3F-14 |  | 1-6A | [5 empty] | ADCS_N | [8 empty] | 南化SS.69KV標置變更 | 69KV電驛標置G1/G2變更 | OTHER | S75/69/ComPoint/1A3U_L |  |  |  | CDC | 396 | GENERICDIPoint | SS418_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S75 | 南化SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 397 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.230_SC_CAP | 11KV#3SC 容量 | SC | S75/11/230/3AI_Oth |  |  |  |  | 398 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 南化SS.220_SC_CAP | 11KV#2SC 容量 | SC | S75/11/220/2AI_Oth |  |  |  |  | 399 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | ADCS_N | [8 empty] | 南化SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 400 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S75 | 南化SS | 0 |  | KX21 | KX21_DS |  | DS1 | KX21_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_DS | KX21_DS (非取樣點) | FEEDER | S75/11/KX21/DS |  |  |  |  | 401 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX21 | KX21_ES |  | LE0 | KX21_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX21_ES | KX21_ES (非取樣點) | FEEDER | S75/11/KX21/ES |  |  |  |  | 402 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX22 | KX22_DS |  | DS1 | KX22_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_DS | KX22_DS (非取樣點) | FEEDER | S75/11/KX22/DS |  |  |  |  | 403 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX22 | KX22_ES |  | LE0 | KX22_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX22_ES | KX22_ES (非取樣點) | FEEDER | S75/11/KX22/ES |  |  |  |  | 404 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX31 | KX31_DS |  | DS1 | KX31_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_DS | KX31_DS (非取樣點) | FEEDER | S75/11/KX31/DS |  |  |  |  | 405 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX31 | KX31_ES |  | LE0 | KX31_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX31_ES | KX31_ES (非取樣點) | FEEDER | S75/11/KX31/ES |  |  |  |  | 406 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX32 | KX32_DS |  | DS1 | KX32_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_DS | KX32_DS (非取樣點) | FEEDER | S75/11/KX32/DS |  |  |  |  | 407 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX32 | KX32_ES |  | LE0 | KX32_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX32_ES | KX32_ES (非取樣點) | FEEDER | S75/11/KX32/ES |  |  |  |  | 408 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 409 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 410 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.3M_DS | 3M_DS (非取樣點) | DTR | S75/11/M3/DS |  |  |  |  | 411 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.3M_ES | 3M_ES (非取樣點) | DTR | S75/11/M3/ES |  |  |  |  | 412 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 210ES | 210ES |  | 210ES | 210ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.210ES | 210ES (非取樣點) | SC | [5 empty] | 413 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 414 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 230ES | 230ES |  | 230ES | 230ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.230ES | 230ES (非取樣點) | SC | S75/11/230/ES |  |  |  |  | 415 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.230_DS | 230_DS (非取樣點) | SC | S75/11/230/DS |  |  |  |  | 416 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 南化SS.69B1E | 69B1E (非取樣點) | BUS | S75/69/1BUS/BE1 |  |  |  |  | 417 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 南化SS.69B2E | 69B2E (非取樣點) | BUS | S75/69/2BUS/BE2 |  |  |  |  | 418 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 419 | NotelDIPoint | [38 empty] | START/STOP | STOP
S75 | 南化SS | 0 |  | KX23 | KX23_DS |  | DS1 | KX23_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_DS | KX23_DS (非取樣點) | FEEDER | S75/11/KX23/DS |  |  |  |  | 420 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX23 | KX23_ES |  | LE0 | KX23_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX23_ES | KX23_ES (非取樣點) | FEEDER | S75/11/KX23/ES |  |  |  |  | 421 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX24 | KX24_DS |  | DS1 | KX24_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_DS | KX24_DS (非取樣點) | FEEDER | S75/11/KX24/DS |  |  |  |  | 422 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX24 | KX24_ES |  | LE0 | KX24_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX24_ES | KX24_ES (非取樣點) | FEEDER | S75/11/KX24/ES |  |  |  |  | 423 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX25 | KX25_DS |  | DS1 | KX25_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_DS | KX25_DS (非取樣點) | FEEDER | S75/11/KX25/DS |  |  |  |  | 424 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX25 | KX25_ES |  | LE0 | KX25_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX25_ES | KX25_ES (非取樣點) | FEEDER | S75/11/KX25/ES |  |  |  |  | 425 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX33 | KX33_DS |  | DS1 | KX33_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_DS | KX33_DS (非取樣點) | FEEDER | S75/11/KX33/DS |  |  |  |  | 426 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX33 | KX33_ES |  | LE0 | KX33_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX33_ES | KX33_ES (非取樣點) | FEEDER | S75/11/KX33/ES |  |  |  |  | 427 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX34 | KX34_DS |  | DS1 | KX34_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_DS | KX34_DS (非取樣點) | FEEDER | S75/11/KX34/DS |  |  |  |  | 428 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX34 | KX34_ES |  | LE0 | KX34_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX34_ES | KX34_ES (非取樣點) | FEEDER | S75/11/KX34/ES |  |  |  |  | 429 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | KX35 | KX35_DS |  | DS1 | KX35_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_DS | KX35_DS (非取樣點) | FEEDER | S75/11/KX35/DS |  |  |  |  | 430 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | KX35 | KX35_ES |  | LE0 | KX35_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.KX35_ES | KX35_ES (非取樣點) | FEEDER | S75/11/KX35/ES |  |  |  |  | 431 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | TIE2 | TIE2_DS |  | DS1 | TIE2_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.TIE2_DS | TIE2_DS (非取樣點) | TIE | S75/11/TIE2/D1 |  |  |  |  | 432 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 2M | 2M_DS |  | DS1 | 2M_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.2M_DS | 2M_DS (非取樣點) | DTR | S75/11/M2/DS |  |  |  |  | 433 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 0 |  | 2M | 2M_ES |  | M0 | 2M_ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.2M_ES | 2M_ES (非取樣點) | DTR | S75/11/M2/ES |  |  |  |  | 434 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 220ES | 220ES |  | 220ES | 220ES | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.220ES | 220ES (非取樣點) | SC | S75/11/220/ES |  |  |  |  | 435 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.220_DS | 220_DS (非取樣點) | SC | S75/11/220/DS |  |  |  |  | 436 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.770TE | 770TE (非取樣點) | DTR | S75/69/770/TE0 |  |  |  |  | 437 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.770BE | 770BE (非取樣點) | DTR | S75/69/770/BE0 |  |  |  |  | 438 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 南化SS.810BE | 810BE (非取樣點) | SC | S75/69/810/BE0 |  |  |  |  | 439 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 0 |  | 810CE | 810CE |  | 810CE | 810CE | [24 empty] | ADCS_N | [8 empty] | 南化SS.810CE | 810CE (非取樣點) | SC | S75/69/810/ES |  |  |  |  | 440 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 南化SS.640LE | 640LE (非取樣點) | LINE69 | S75/69/640/LE0 |  |  |  |  | 441 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 640 | 曾文南化西口線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 南化SS.640BE | 640BE (非取樣點) | LINE69 | S75/69/640/BE0 |  |  |  |  | 442 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 南化SS.601E | 601E (非取樣點) | TIE | S75/69/600/E1 |  |  |  |  | 443 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 南化SS.602E | 602E (非取樣點) | TIE | S75/69/600/E2 |  |  |  |  | 444 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 南化SS.610LE | 610LE (非取樣點) | LINE69 | S75/69/610/LE0 |  |  |  |  | 445 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 610 | 南化隆田線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 南化SS.610BE | 610BE (非取樣點) | LINE69 | S75/69/610/BE0 |  |  |  |  | 446 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.760TE | 760TE (非取樣點) | DTR | S75/69/760/TE0 |  |  |  |  | 447 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S75 | 南化SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS4_2 | [8 empty] | 南化SS.760BE | 760BE (非取樣點) | DTR | S75/69/760/BE0 |  |  |  |  | 448 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo